## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 04-06-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 03-06-2025 | during | 04-06-2025 | during | 04-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 390 | 365 | 400.75 | 400.75 | 390 | 390 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 450 | 450 | 450 | 420 | 420 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 295 | 290 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 306 | 293 | 335 | 335 | 313 | 313 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 64 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 35 | 35 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 24 | 25 | 33 | 33 | 28 | 28 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 24 | 52.19 | 52.19 | 24 | 24 | Fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 30 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 50 | 50 | 149 | 149 | 149 | 149 | Machine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 72 | 90 | 105 | 105 | 72 | 90 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 32 | 104 | 104 | 85 | 85 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 54 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 34 | 0 | 25 | 0 | 25 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 350 | 350 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 108 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6123 | 5939.724 | 1996 | 2334 | 5027.1 | 5096.1 | 3459.38 | 3546.38
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 17 | 17 | 17 | 17 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 13 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 6 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 155 | 167 | 155 | 155 | 155 | 155 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 223 | 220 | 221 | 221 | 221 | 221 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 32 | 72 | 72 | 72 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 33 | 68 | 68 | 51 | 51 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 36 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 7 | 24 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 919 | 1104 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 2 | 34 | 28 | 19 | 28 | 19 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 470 | 491 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1789 | 2147 | 3587.22 | 3566.22 | 3570.22 | 3549.22
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 216 | 201 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 349 | 353 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 335 | 340 | 345 | 345 | 345 | 345 | machine problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 33 | 32 | 46.7 | 46.7 | 33 | 33 | machine problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 48 | 51 | 55 | 55 | 51 | 51 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 110 | 195 | 195 | 63 | 63 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 12 | 150 | 150 | 135 | 135 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 48 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 80 | 163 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 111 | 80 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 44 | 54 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 14 | 17.75 | 17.75 | 15 | 15 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 77 | 96 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 12 | 33 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 53 | 93 | 115 | 115 | 53 | 97 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 68 | 0 | 35 | 0 | 35 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2891.241 | 1417 | 1648 | 2434 | 2399 | 2025.55 | 2034.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 03-06-2025 | during | 04-06-2025 | during | 04-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 45 | 44 | 157.5 | 157.5 | 50 | 50 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 45 | 140 | 200 | 200 | 170 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 24 | 92 | 115 | 115 | 95 | 95 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 33.39 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 149.39 | 288 | 596.1 | 549 | 428.6 | 381.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 34 | 31 | 36 | 36 | 36 | 36 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 159 | 156 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 84 | 86 | 86 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 164 | 165 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 25 | 25 | 7 | 7 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 255 | 255 | 341 | 341 | 341 | 341 | Gas shortage
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 366 | 372 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2400 | 2325 | 1456 | 1461 | 1594 | 1594 | 1530 | 1530
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 891 | 854 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 77 | 410 | 410 | 310 | 310 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 90 | 90 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 98.12 | 0 | 65 | 0 | 65 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 787 | 1088 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3699.2 | 1776.12 | 2036 | 3577.2 | 3512.2 | 3462.2 | 3397.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 4 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 110 | 120 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 650 | 1112 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 186 | 200 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.7 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1166.7 | 1656 | 2172 | 2171 | 2122 | 2121
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 14 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 182 | 171 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 179 | 190 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 405 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 6 | 25 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.18 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 850 | 1415 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 58.21 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 114 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3460 | 3452.96 | 1799.39 | 2259 | 3192.47 | 3025.87 | 3129.09 | 2962.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 49 | 50 | 50 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 160 | 160 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.6 | 0 | 5.6 | 0 | 5.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 203 | 0 | 198.56 | 0 | 198.56 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 493.6 | 477 | 706.16 | 472 | 746.16 | 512
System Total |  |  |  |  | 28798.2 | 27044.055 | 12043.2 | 14306 | 22886.25 | 22385.39 | 20473.2 | 20034.34
Forecast Scenario (04-06-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13820 |  | 0 |  | 13820
|  |  |  | 1:00 | 13270 |  | 0 |  | 13270
|  |  |  | 2:00 | 12860 |  | 0 |  | 12860
|  |  |  | 3:00 | 12480 |  | 0 |  | 12480
|  |  |  | 4:00 | 12060 |  | 0 |  | 12060
|  |  |  | 5:00 | 11300 |  | 0 |  | 11300
|  |  |  | 6:00 | 10800 |  | 0 |  | 10800
|  |  |  | 7:00 | 10690 |  | 0 |  | 10690
|  |  |  | 8:00 | 10480 |  | 0 |  | 10480
|  |  |  | 9:00 | 11080 |  | 0 |  | 11080
|  |  |  | 10:00 | 11610 |  | 0 |  | 11610
|  |  |  | 11:00 | 12220 |  | 0 |  | 12220
|  |  |  | 12:00 | 12900 |  | 0 |  | 12900
|  |  |  | 13:00 | 13350 |  | 0 |  | 13350
|  |  |  | 14:00 | 13430 |  | 0 |  | 13430
|  |  |  | 15:00 | 13610 |  | 0 |  | 13610
|  |  |  | 16:00 | 13490 |  | 0 |  | 13490
|  |  |  | 17:00 | 13180 |  | 0 |  | 13180
|  |  |  | 18:00 | 12810 |  | 0 |  | 12810
|  |  |  | 18:30 | 13350 |  | 0 |  | 13350
|  |  |  | 19:00 | 14050 |  | 0 |  | 14050
|  |  |  | 19:30 | 15000 |  | 0 |  | 15000
|  |  |  | 20:00 | 14900 |  | 0 |  | 14900
|  |  |  | 21:00 | 14850 |  | 0 |  | 14850
|  |  |  | 22:00 | 14400 |  | 0 |  | 14400
|  |  |  | 23:00 | 13300 |  | 0 |  | 13300
Probable Maximum Temperature: |  |  | 32.00°C
Probable Maximum Demand at Day Peak: |  |  | 12900.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15000.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15000.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 306.94 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:30 hrs on 04-06-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 03-06-2025 | [28 empty] | Date: | 03-06-2025 | [28 empty] | Date: | 03-06-2025 | [28 empty] | Date: | 03-06-2025 | [28 empty] | Date: | 03-06-2025 | [12 empty] | Date: | 03-06-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [12 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 17 | 35 | 50 | 110 | 0 | 0 | 0 | 0 | 0 | 400 | 288 | 400 | 0 | 0 | 313 | 0 | 0 | 0 | 90 | 24.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 48 | 0 | 0 | 155 | 0 | 25 | 520 | 0 | 0 | 0 | 8 | 0 | 221 | 0 | 0 | 0 | 1016 | 0 | 43 | 0 | 8 | 0 | 334 | 335 | 49 | 215 | 33 | 34 | 0 | 200 | 15 | 15 | 114 | 32 | 43 | 0 | 40 | 260 | 320 | 354 | 35 | 30 | 151 | 7 | 0 | 84 | 28 | 0 | 18 | 164 | 0 | 81 | 146 | 45 | 0 | 0 | 7 | 7415.5 | 880 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 868 | 0 | 810.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 130 | 0 | 0 | 0 | 230 | 0 | 0 | 200 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 11 | 120 | 220 | 0 | 0 | 1015 | 0 | 5024.75 | 12440.25 | 88.29
01:00 | 0 | 54 | 8 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 17 | 35 | 50 | 62 | 0 | 0 | 0 | 0 | 0 | 320 | 283 | 470 | 0 | 0 | 266 | 0 | 0 | 0 | 90 | 26 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 12 | 0 | 0 | 155 | 0 | 29 | 477 | 0 | 0 | 0 | 8 | 0 | 223 | 0 | 0 | 0 | 1025 | 0 | 43 | 0 | 8 | 0 | 354 | 340 | 49 | 184 | 33 | 28 | 0 | 200 | 10 | 15 | 114 | 32 | 43 | 0 | 40 | 265 | 320 | 300 | 35 | 30 | 151 | 0 | 0 | 84 | 30 | 0 | 18 | 164 | 0 | 8 | 0 | 46 | 0 | 0 | 12 | 6959 | 891 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 762 | 0 | 812.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 130 | 0 | 0 | 0 | 230 | 0 | 0 | 200 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 11 | 120 | 220 | 0 | 0 | 850 | 0 | 4816.26 | 11775.26 | 88.41
02:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 17 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 286 | 420 | 0 | 0 | 273 | 0 | 0 | 0 | 0 | 26 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 34 | 406 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 885 | 0 | 5 | 0 | 8 | 0 | 334 | 300 | 48 | 188 | 33 | 17 | 0 | 200 | 9 | 15 | 114 | 32 | 43 | 0 | 40 | 265 | 320 | 300 | 35 | 30 | 138 | 0 | 0 | 61 | 30 | 0 | 18 | 164 | 0 | 0 | 0 | 49 | 0 | 0 | 12 | 6326 | 891 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 762 | 0 | 819.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 130 | 0 | 0 | 0 | 230 | 0 | 0 | 200 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 11 | 100 | 180 | 0 | 0 | 753 | 0 | 4665.87 | 10991.87 | 88.53
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 276 | 300 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 34 | 367 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 720 | 0 | 5 | 0 | 8 | 0 | 300 | 300 | 21 | 182 | 5 | 17 | 0 | 180 | 9 | 12 | 99 | 30 | 24 | 0 | 0 | 270 | 320 | 300 | 35 | 30 | 128 | 0 | 0 | 21 | 30 | 0 | 18 | 164 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 5567 | 890 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 819.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 130 | 0 | 0 | 0 | 230 | 0 | 0 | 200 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 11 | 90 | 180 | 0 | 0 | 520 | 0 | 4406.03 | 9973.03 | 88.65
04:00 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 290 | 291 | 200 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 35 | 366 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 650 | 0 | 0 | 0 | 0 | 0 | 280 | 280 | 0 | 182 | 0 | 17 | 0 | 68 | 9 | 0 | 52 | 20 | 0 | 0 | 0 | 200 | 320 | 291 | 34 | 18 | 129 | 0 | 0 | 0 | 10 | 0 | 18 | 163 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 4794 | 754 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 819.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 130 | 0 | 0 | 0 | 200 | 0 | 0 | 160 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 90 | 180 | 0 | 0 | 500 | 0 | 4114.76 | 8908.76 | 88.77
05:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 286 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 290 | 286 | 250 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 35 | 365 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 280 | 280 | 0 | 190 | 0 | 16 | 0 | 17 | 9 | 6 | 17 | 18 | 0 | 0 | 0 | 180 | 320 | 294 | 35 | 18 | 130 | 0 | 0 | 0 | 10 | 0 | 18 | 163 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 4695 | 754 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 746 | 0 | 828.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 130 | 0 | 0 | 0 | 200 | 0 | 0 | 161 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 96 | 180 | 0 | 0 | 500 | 0 | 4132.15 | 8827.15 | 88.89
06:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 290 | 280 | 250 | 0 | 0 | 260 | 0 | 0 | 1 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 35 | 361 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 610 | 1 | 5 | 0 | 8 | 0 | 280 | 280 | 3 | 182 | 27 | 17 | 0 | 17 | 10 | 6 | 17 | 18 | 0 | 1 | 0 | 180 | 320 | 295 | 35 | 18 | 147 | 0 | 0 | 40 | 30 | 0 | 18 | 164 | 0 | 3 | 3 | 50 | 0 | 0.57 | 0 | 4963.57 | 512 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.82 | 748 | 0 | 825.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1.53 | 140 | 0 | 130 | 0 | 0 | 0 | 200 | 0 | 0.14 | 162 | 47 | 0 | 2 | 0 | 0 | 0 | 0.3 | 10 | 0 | 0 | 150 | 0 | 90 | 220 | 0 | 0 | 500 | 0 | 3947.71 | 8911.28 | 89.01
07:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 290 | 297 | 200 | 0 | 0 | 298 | 0 | 0 | 5 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 18 | 366 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 600 | 5 | 34 | 0 | 8 | 0 | 280 | 280 | 25 | 209 | 28 | 17 | 0 | 17 | 9 | 6 | 17 | 22 | 0 | 1 | 0 | 180 | 320 | 295 | 34 | 20 | 130 | 0 | 0 | 11 | 30 | 0 | 18 | 164 | 0 | 16 | 16 | 49 | 0 | 2.52 | 0 | 4992.52 | 513 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.3 | 748 | 0 | 824.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 3.61 | 140 | 0 | 130 | 0 | 0 | 0 | 200 | 0 | 0.37 | 163 | 47 | 0 | 6 | 0 | 0 | 0 | 1.3 | 38 | 0.06 | 0 | 150 | 0 | 104 | 180 | 0 | 0 | 502 | 0 | 3992.07 | 8984.59 | 89.13
08:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 291 | 250 | 0 | 0 | 300 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 10 | 366 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 610 | 9 | 51 | 0 | 8 | 0 | 320 | 280 | 47 | 209 | 31 | 17 | 0 | 17 | 9 | 14 | 17 | 20 | 0 | 1 | 0 | 180 | 320 | 294 | 32 | 20 | 140 | 0 | 0 | 11 | 30 | 0 | 18 | 164 | 0 | 16 | 16 | 47 | 1 | 14.18 | 0 | 5257.18 | 465 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.54 | 747 | 0 | 823.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 25.93 | 140 | 0 | 130 | 0 | 0 | 0 | 300 | 0 | 2.25 | 163 | 51 | 0 | 14 | 0 | 0 | 0 | 2.9 | 87 | 0.16 | 0 | 150 | 0 | 100 | 180 | 0 | 0 | 500 | 0 | 4156.67 | 9413.85 | 89.25
09:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 291 | 250 | 0 | 0 | 295 | 0 | 0 | 11 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 4 | 366 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 615 | 0 | 51 | 0 | 8 | 0 | 320 | 280 | 50 | 198 | 26 | 17 | 0 | 17 | 9 | 14 | 17 | 20 | 0 | 7 | 0 | 180 | 320 | 295 | 34 | 20 | 156 | 0 | 0 | 11 | 30 | 0 | 18 | 165 | 0 | 24 | 45 | 48 | 2 | 12.16 | 0 | 5409.16 | 779 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.27 | 744 | 0 | 821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 25.59 | 140 | 0 | 130 | 0 | 0 | 0 | 350 | 0 | 2.86 | 160 | 52 | 0 | 22 | 0 | 0 | 0 | 4.6 | 144 | 0.29 | 0 | 150 | 0 | 100 | 220 | 0 | 0 | 500 | 0 | 4677.61 | 10086.77 | 89.35
10:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 0 | 40 | 16 | 0 | 0 | 16 | 0 | 0 | 400 | 293 | 250 | 0 | 0 | 300 | 0 | 0 | 18 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 4 | 431 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 630 | 0 | 51 | 0 | 8 | 0 | 320 | 280 | 51 | 211 | 27 | 24 | 0 | 17 | 10 | 12 | 17 | 22 | 0 | 12 | 0 | 235 | 320 | 329 | 34 | 30 | 158 | 0 | 0 | 11 | 30 | 0 | 18 | 165 | 0 | 24 | 45 | 48 | 2 | 25.86 | 0 | 5817.86 | 890 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.26 | 743 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 45.11 | 140 | 0 | 130 | 0 | 0 | 0 | 401 | 0 | 4.68 | 160 | 52 | 0 | 28 | 0 | 0 | 0 | 6.7 | 172 | 0.46 | 0 | 155 | 0 | 102 | 220 | 0 | 0 | 560 | 0 | 5005.21 | 10823.07 | 89.45
11:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 25 | 50 | 16 | 0 | 0 | 35 | 0 | 0 | 400 | 300 | 300 | 0 | 0 | 297 | 0 | 0 | 29 | 0 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 4 | 466 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 830 | 9 | 51 | 0 | 8 | 0 | 320 | 280 | 49 | 209 | 33 | 52 | 0 | 42 | 9 | 12 | 70 | 42 | 0 | 51 | 0 | 255 | 320 | 365 | 34 | 30 | 160 | 0 | 0 | 11 | 30 | 0 | 18 | 165 | 0 | 24 | 45 | 48 | 2 | 29.99 | 0 | 6437.99 | 890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.61 | 744 | 0 | 823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 49.93 | 147 | 0 | 168 | 0 | 0 | 0 | 414 | 0 | 4.73 | 160 | 50 | 0 | 31 | 0 | 0 | 0 | 7.3 | 192 | 0.67 | 0 | 174 | 0 | 100 | 220 | 0 | 0 | 625 | 0 | 4977.24 | 11415.23 | 89.55
12:00 | 0 | 72 | 24 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 0 | 50 | 16 | 0 | 0 | 35 | 0 | 0 | 400 | 295 | 350 | 0 | 0 | 306 | 0 | 0 | 34 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 7 | 470 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 919 | 13 | 51 | 0 | 8 | 0 | 349 | 335 | 48 | 216 | 33 | 53 | 0 | 111 | 12 | 12 | 77 | 44 | 0 | 68 | 0 | 255 | 320 | 366 | 34 | 30 | 159 | 0 | 0 | 80 | 30 | 0 | 18 | 164 | 0 | 24 | 45 | 45 | 2 | 33.39 | 0 | 6807.39 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.12 | 787 | 0 | 850 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 114 | 0 | 58.21 | 182 | 0 | 179 | 0 | 0 | 0 | 405 | 0 | 5.18 | 200 | 50 | 0 | 33 | 0 | 0 | 0 | 7.6 | 203 | 0.7 | 0 | 186 | 0 | 110 | 220 | 0 | 0 | 650 | 0 | 5235.81 | 12043.2 | 89.65
13:00 | 0 | 72 | 24 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 15 | 50 | 16 | 0 | 0 | 35 | 25 | 20 | 420 | 290 | 350 | 0 | 0 | 293 | 0 | 0 | 30 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 1 | 167 | 0 | 14 | 455 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1020 | 7 | 51 | 0 | 8 | 0 | 351 | 340 | 51 | 203 | 32 | 53 | 0 | 153 | 13 | 12 | 88 | 48 | 12 | 54 | 0 | 255 | 320 | 330 | 32 | 30 | 159 | 0 | 0 | 82 | 30 | 0 | 18 | 164 | 0 | 45 | 56 | 31 | 2 | 38 | 0 | 7042 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.4 | 857 | 0 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 55.31 | 178 | 0 | 176 | 0 | 0 | 0 | 405 | 0 | 4.84 | 200 | 50 | 0 | 30 | 0 | 0 | 0 | 4.1 | 197 | 0.77 | 0 | 170 | 0 | 100 | 220 | 0 | 0 | 870 | 0 | 5518.42 | 12560.42 | 89.75
14:00 | 0 | 72 | 24 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 17 | 50 | 32 | 0 | 0 | 35 | 35 | 0 | 420 | 296 | 350 | 0 | 0 | 299 | 0 | 0 | 25 | 35 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 1 | 167 | 0 | 6 | 466 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1124 | 0 | 51 | 0 | 8 | 0 | 347 | 345 | 51 | 206 | 32 | 53 | 50 | 68 | 9 | 12 | 88 | 50 | 0 | 64 | 0 | 255 | 320 | 362 | 32 | 30 | 156 | 0 | 0 | 83 | 30 | 0 | 18 | 164 | 0 | 45 | 82 | 32 | 1 | 42.22 | 0 | 7183.22 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.51 | 828 | 0 | 917.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 36.78 | 171 | 0 | 167 | 0 | 0 | 0 | 402 | 0 | 0 | 200 | 50 | 0 | 26 | 0 | 0 | 0 | 3.5 | 176 | 0 | 0 | 173 | 0 | 100 | 220 | 0 | 0 | 1070 | 0 | 5616.33 | 12799.55 | 89.85
15:00 | 0 | 72 | 24 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 0 | 50 | 32 | 0 | 0 | 35 | 35 | 0 | 450 | 293 | 350 | 0 | 0 | 305 | 0 | 0 | 20 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 20 | 0 | 2 | 167 | 0 | 10 | 480 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1113 | 7 | 51 | 0 | 8 | 0 | 345 | 340 | 49 | 212 | 32 | 52 | 50 | 68 | 9 | 8 | 88 | 48 | 0 | 54 | 0 | 250 | 320 | 337 | 33 | 30 | 157 | 0 | 0 | 81 | 30 | 0 | 18 | 164 | 0 | 55 | 95 | 31 | 1 | 25.43 | 6 | 7199.43 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.75 | 952 | 0 | 1076.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 37.78 | 180 | 0 | 175 | 0 | 0 | 0 | 405 | 0 | 3.28 | 155 | 50 | 35 | 21 | 0 | 0 | 0 | 5.8 | 112 | 0.14 | 0 | 175 | 0 | 100 | 220 | 0 | 0 | 1100 | 0 | 5821.22 | 13020.65 | 89.95
16:00 | 0 | 72 | 24 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 50 | 32 | 0 | 0 | 35 | 35 | 0 | 450 | 290 | 350 | 0 | 0 | 293 | 0 | 0 | 5 | 52 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 36 | 0 | 1 | 167 | 0 | 10 | 450 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1100 | 5 | 51 | 0 | 45 | 0 | 348 | 340 | 49 | 201 | 32 | 53 | 50 | 94 | 10 | 14 | 88 | 48 | 0 | 10 | 0 | 255 | 320 | 315 | 31 | 30 | 157 | 0 | 0 | 81 | 30 | 0 | 18 | 164 | 0 | 55 | 95 | 31 | 1 | 24.15 | 7 | 7154.15 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.67 | 965 | 0 | 1056.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 22.35 | 177 | 0 | 192 | 0 | 0 | 0 | 405 | 0 | 2.04 | 182 | 50 | 35 | 12 | 0 | 0 | 0 | 3.7 | 59 | 0.06 | 0 | 172 | 1 | 100 | 220 | 0 | 0 | 1091 | 0 | 5706.71 | 12860.86 | 90.05
17:00 | 0 | 72 | 24 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 50 | 32 | 0 | 0 | 35 | 35 | 0 | 450 | 292 | 350 | 0 | 0 | 273 | 0 | 0 | 0 | 52 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 36 | 0 | 1 | 167 | 0 | 16 | 450 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1030 | 3 | 51 | 0 | 45 | 0 | 354 | 340 | 50 | 186 | 32 | 52 | 50 | 90 | 9 | 14 | 88 | 46 | 0 | 3 | 0 | 250 | 320 | 304 | 31 | 30 | 149 | 0 | 0 | 83 | 30 | 0 | 18 | 164 | 0 | 55 | 95 | 46 | 1 | 10.44 | 1 | 6996.44 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.55 | 960 | 0 | 1015.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 11.04 | 161 | 0 | 186 | 0 | 0 | 0 | 325 | 0 | 1.07 | 200 | 50 | 35 | 7 | 22 | 0 | 0 | 1.9 | 28 | 0.05 | 0 | 162 | 2 | 90 | 180 | 0 | 0 | 1052 | 0 | 5402.8 | 12399.24 | 90.15
18:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 8 | 0 | 50 | 32 | 15 | 0 | 35 | 35 | 14 | 340 | 295 | 300 | 0 | 0 | 290 | 0 | 0 | 2 | 52 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 36 | 0 | 0 | 167 | 0 | 2 | 400 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1020 | 0 | 51 | 6 | 73 | 0 | 300 | 300 | 49 | 203 | 33 | 52 | 97 | 89 | 19 | 14 | 67 | 44 | 0 | 1 | 0 | 250 | 320 | 335 | 31 | 30 | 150 | 0 | 0 | 84 | 30 | 0 | 18 | 164 | 0 | 55 | 95 | 47 | 0 | 1.6 | 7 | 6857.6 | 793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 960 | 6 | 961.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 4.76 | 157 | 0 | 182 | 0 | 0 | 0 | 362 | 0 | 0.47 | 200 | 50 | 35 | 2 | 34 | 0 | 0 | 0.7 | 8 | 0.02 | 0 | 174 | 4 | 100 | 180 | 0 | 0 | 1000 | 0 | 5226.04 | 12083.64 | 90.23
19:00 | 0 | 90 | 24 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 35 | 0 | 50 | 64 | 30 | 0 | 35 | 45 | 28 | 400 | 299 | 350 | 0 | 17 | 303 | 0 | 0 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 33 | 32 | 0 | 36 | 24 | 0 | 167 | 5 | 15 | 432 | 0 | 0 | 7 | 0 | 10 | 220 | 0 | 0 | 0 | 1100 | 0 | 51 | 25 | 73 | 0 | 346 | 325 | 51 | 209 | 32 | 57 | 80 | 99 | 28 | 14 | 67 | 52 | 5 | 0 | 44 | 250 | 320 | 392 | 31 | 30 | 157 | 0 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 65 | 122 | 48 | 0 | 0 | 12 | 7637 | 746 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1015 | 17 | 1154.69 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 9 | 0 | 0 | 30 | 0 | 174 | 0 | 199 | 0 | 0 | 0 | 406 | 0 | 0 | 200 | 50 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 4 | 120 | 220 | 0 | 0 | 1010 | 0 | 5811.69 | 13448.69 | 90.31
19:30 | 0 | 90 | 24 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 35 | 0 | 50 | 64 | 30 | 0 | 35 | 72 | 32 | 400 | 295 | 350 | 0 | 17 | 306 | 0 | 0 | 0 | 95 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 33 | 32 | 0 | 36 | 24 | 0 | 167 | 17 | 12 | 431 | 0 | 0 | 18 | 0 | 17 | 220 | 0 | 0 | 0 | 1100 | 0 | 51 | 40 | 73 | 0 | 344 | 340 | 51 | 212 | 32 | 97 | 80 | 109 | 29 | 14 | 68 | 52 | 8 | 0 | 48 | 250 | 320 | 394 | 31 | 30 | 157 | 0 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 85 | 145 | 48 | 0 | 0 | 12 | 7888 | 746 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 17 | 1297.49 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 12 | 0 | 0 | 30 | 0 | 184 | 0 | 202 | 0 | 0 | 0 | 414 | 0 | 0 | 200 | 49 | 96 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 4 | 120 | 220 | 0 | 0 | 1120 | 0 | 6216.49 | 14104.49
20:00 | 0 | 90 | 24 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 35 | 0 | 50 | 64 | 30 | 0 | 35 | 72 | 32 | 400 | 296 | 350 | 0 | 17 | 292 | 0 | 0 | 0 | 108 | 3 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 33 | 32 | 0 | 36 | 12 | 0 | 167 | 0 | 16 | 403 | 0 | 0 | 19 | 0 | 0 | 220 | 0 | 0 | 0 | 1100 | 0 | 51 | 40 | 110 | 0 | 350 | 340 | 51 | 201 | 32 | 90 | 80 | 85 | 33 | 14 | 66 | 52 | 0 | 0 | 48 | 250 | 320 | 388 | 31 | 30 | 157 | 0 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 85 | 145 | 48 | 0 | 0 | 12 | 7781 | 807 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 17 | 1416.73 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 14 | 0 | 0 | 30 | 0 | 179 | 0 | 198 | 0 | 0 | 0 | 414 | 0 | 0 | 200 | 49 | 115 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 4 | 120 | 220 | 0 | 0 | 1112 | 0 | 6412.73 | 14193.73 | 90.35
21:00 | 0 | 90 | 24 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 35 | 0 | 50 | 64 | 30 | 0 | 35 | 54 | 32 | 450 | 290 | 350 | 0 | 17 | 293 | 0 | 0 | 0 | 108 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 33 | 32 | 0 | 36 | 0 | 0 | 167 | 0 | 24 | 491 | 0 | 0 | 6 | 0 | 0 | 220 | 0 | 0 | 0 | 1104 | 0 | 51 | 12 | 110 | 0 | 353 | 340 | 51 | 201 | 32 | 93 | 80 | 80 | 33 | 14 | 96 | 54 | 0 | 0 | 48 | 255 | 320 | 372 | 31 | 30 | 156 | 0 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 92 | 140 | 44 | 0 | 0 | 12 | 7878 | 854 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1088 | 17 | 1415 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 14 | 0 | 0 | 30 | 0 | 171 | 0 | 190 | 0 | 0 | 0 | 414 | 0 | 0 | 200 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 4 | 120 | 220 | 0 | 0 | 1112 | 0 | 6428 | 14306 | 90.39
22:00 | 0 | 90 | 24 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 35 | 0 | 50 | 82 | 30 | 0 | 17 | 54 | 32 | 450 | 292 | 350 | 0 | 17 | 288 | 0 | 0 | 0 | 108 | 25.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 33 | 32 | 0 | 36 | 0 | 0 | 167 | 0 | 30 | 486 | 0 | 0 | 6 | 0 | 0 | 222 | 0 | 0 | 0 | 1104 | 0 | 51 | 12 | 55 | 0 | 356 | 340 | 52 | 195 | 32 | 94 | 80 | 79 | 29 | 14 | 105 | 54 | 0 | 0 | 48 | 250 | 320 | 372 | 31 | 30 | 154 | 0 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 96 | 131 | 45 | 0 | 0 | 12 | 7804.5 | 854 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1054 | 17 | 1420 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 13 | 0 | 0 | 30 | 0 | 167 | 0 | 187 | 0 | 0 | 0 | 414 | 0 | 0 | 200 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 7 | 120 | 220 | 0 | 0 | 1100 | 0 | 6384 | 14188.5 | 90.43
23:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 35 | 0 | 50 | 82 | 30 | 0 | 17 | 54 | 32 | 450 | 289 | 350 | 0 | 17 | 290 | 0 | 0 | 0 | 108 | 26 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 33 | 23 | 0 | 36 | 0 | 0 | 167 | 0 | 32 | 484 | 0 | 0 | 6 | 0 | 0 | 223 | 0 | 0 | 0 | 1104 | 0 | 51 | 12 | 55 | 0 | 355 | 340 | 52 | 170 | 32 | 94 | 80 | 78 | 29 | 14 | 102 | 54 | 0 | 0 | 48 | 240 | 320 | 363 | 32 | 30 | 155 | 0 | 0 | 84 | 30 | 0 | 18 | 164 | 0 | 95 | 130 | 45 | 0 | 0 | 12 | 7738 | 855 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1065 | 35 | 1409 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 13 | 0 | 0 | 30 | 0 | 168 | 0 | 189 | 0 | 0 | 0 | 414 | 0 | 0 | 200 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 9 | 120 | 220 | 0 | 0 | 1110 | 0 | 6416 | 14154 | 90.47
Total KWH | 0 | 1349760 | 375840 | 0 | 0 | 0 | 0 | 0 | 8582400 | 0 | 0 | 245160 | 191160 | 898848 | 843360 | 190942 | 0 | 489923 | 518400 | 190080 | 9017500 | 6979287 | 7426377 | 0 | 95337 | 6917358 | 0 | 0 | 191356 | 964800 | 552600 | 299520 | 0 | 0 | 0 | 0 | 0 | 0 | 421440 | 175201 | 148653 | 0 | 393600 | 31680 | 5762 | 3442300 | 22600 | 460800 | 10385454.55 | 0 | 0 | 56640 | 8154 | 25090 | 5134313 | 0 | 0 | 0 | 21583634 | 64395 | 925608 | 158909 | 669091 | 0 | 8251500 | 7626000 | 1005120 | 4823000 | 671472 | 1125120 | 685020 | 2146560 | 354480 | 263250 | 1705440 | 907200 | 154277 | 322627 | 323840 | 5651000 | 7669700 | 8332000 | 774000 | 631200 | 3596155 | 0 | 0 | 1306560 | 672192 | 0 | 432000 | 4471000 | 0 | 996000 | 1552800 | 1005120 | 14950 | 265130 | 128400 | 158296445.55 | 19487272 | 2820384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 704160 | 20974540 | 138720 | 23908576 | 0 | 0 | 0 | 0 | 0 | 133760 | 0 | 55944 | 0 | 724870 | 146237 | 390000 | 3857727 | 0 | 4079300 | 0 | 0 | 0 | 8167927 | 0 | 32958 | 4500000 | 1154181 | 721857 | 228487 | 626102 | 0 | 0 | 50362.68 | 1461600 | 3163 | 0 | 4080000 | 84211 | 2503000 | 5202590 | 0 | 0 | 20472727.27 | 0 | 126710655.95 | 285007101.5

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 03-06-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12043.2 | MW | 12:00 Hr. | Energy Generated |  |  | 285.0071 |  | MKWHr.
| Day Peak Demand |  |  | 12043.2 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.112 |  | MKWHr.
| Evening Peak Generation |  |  | 14306 | MW | 21:00 Hr. | Energy Demand |  |  | 285.1191 |  | MKWHr.
| Evening Peak Demand |  |  | 14306 | MW | 21:00 Hr. | Maximum Temperature |  |  | 32.9 |  | °C
| Minimum Generation of the Day |  |  | 8827.15 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 967.23 |  | MMCFD
| Maximum Generation of the Day |  |  | 14306 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 5.9013 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.775 | 0 | 6.3536 | 0 | 0 | 0.19136 | 0 | 0 | 46.32 | Gas | 131.5463 | Gas | 469168335.87
| Chattogram Zone |  |  | 5.5951 | 31.9691 | 0.86162 | 0 | 3.4423 | 0.070157 | 0 | 0.42144 | 42.3597 | Coal | 83.1505 | Coal | 577306400.7109
| Cumilla Zone |  |  | 24.9201 | 0 | 5.9686 | 0 | 0 | 0.32263 | 0.9072 | 0 | 32.1185 | HFO | 17.6837 | HFO | 329543317.02
| Mymensingh Zone |  |  | 1.0051 | 0 | 2.6772 | 0 | 0 | 0.28008 | 0 | 0 | 3.9624 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 33.5358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.5358 | Hydro | 3.4423 | Hydro | 344230
| Khulna Zone |  |  | 2.8204 | 20.9745 | 0.13872 | 0 | 0 | 0.70416 | 19.4873 | 0 | 44.1251 | Solar | 4.4598 | Solar | 73534244.4548
| Barishal Zone |  |  | 7.7898 | 24.5527 | 0 | 0 | 0 | 0.003163 | 0 | 0 | 32.3457 | Import | 44.303 | Import | 225859070.24
| Rajshahi Zone |  |  | 16.105 | 0 | 0.33594 | 0 | 0 | 1.1478 | 23.9086 | 0 | 41.4973 | Wind | 0.42144 | Wind | 6169881.6
| Rangpur Zone |  |  | 0 | 5.6542 | 1.348 | 0 | 0 | 1.7404 | 0 | 0 | 8.7426
| Total |  |  | 131.5463 | 83.1505 | 17.6837 | 0 | 3.4423 | 4.4598 | 44.303 | 0.42144 | 285.0071
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 469168335.87 |  | Hydro | 344230
|  |  |  | Coal | 577306400.7109 |  | Solar | 73534244.4548
|  |  |  | HFO | 329543317.02 |  | Import | 225859070.24
|  |  |  | HSD | 0 |  | Wind | 6169881.6
[5 empty] | Total: | 168,19,25,479 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.4873 | Peak Hr Flow | 854.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 10320654.61 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 23.9086 | Peak Hr Flow | 1415.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 540 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.9072 | Peak Hr Flow | 54.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 938 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 44.303 | Peak Hr Flow | 2323.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4949
|  |  |  | Chattogram |  | 0 |  | 1240
|  |  |  | Cumilla |  | 0 |  | 1309
|  |  |  | Mymensingh |  | 0 |  | 1174
|  |  |  | Sylhet |  | 0 |  | 520
|  |  |  | Khulna |  | 0 |  | 1695
|  |  |  | Barishal |  | 0 |  | 338
|  |  |  | Rajshahi |  | 0 |  | 1539
|  |  |  | Rangpur |  | 0 |  | 933
|  |  |  | Total |  | 0 |  | 13697
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[5 empty] | Total | 300 |  |  |  | Total | 400
|  |  |  | Total Unavailable Capacity |  |  |  | 700
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:48 | 16:25 | Jamalpur-Mymensingh 132kV Ckt-1 Scheduled S/D from Jamalpur 132/33kV end Due to Disk
insulator replace work of Tower no.403
| 09:11 | 10:37 | Jamalpur United(20MW)-Sherpur 132kV Ckt-1 Forced S/D from Sherpur 132/33kV end Due to GCB
nut bolt hot point maintenance.
|  | 09:17 | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT is restored.
|  | 09:19 | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT is restored.
| 09:59 | 10:03 | Noapara 132/33kV S/S T-1 LT Tripped showing SIEMENS 7SJ81 relays Due to REB-1 33kV FEEDER | [7 empty] | 25.0MW load
|  |  | FAULT | [7 empty] | interrup.
| 09:59 | 10:03 | Noapara 132/33kV S/S T-2 LT Tripped showing SIEMENS 7SJ81 relays Due to REB-1 33kV FEEDER | [7 empty] | 12.5MW load
|  |  | FAULT | [7 empty] | interrup.
|  | 10:02 | Bogura 132/33kV S/S Transformer-3 HT is restored.
|  | 10:02 | Bogura 132/33kV S/S Transformer-3 LT is restored.
| 10:40 |  | Bheramara 410 MW CCPP was shutdown.
| 10:40 |  | Bheramara 410 MW CCPP was shutdown.
| 10:46 | 11:23 | Sherpur 132/33kV S/S Transformer- 01 LT Scheduled S/D
| 10:47 |  | Kurigram-Lalmonirhat 132 ckt syn.
|  | 10:47 | Madunaghat 132/33kV S/S TR-1(507T) HT is restored.
| 10:47 | 11:22 | Sherpur 132/33kV S/S Transformer- 01 HT Scheduled S/D
| 10:49 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is ON with remarks:- FGMO Minimum @ 10:48 hr by Mr.
Mosharraf, SDE, NLDC.
|  | 10:54 | Feni 132/33kV S/S T-1(405T) HT is restored.
|  | 10:55 | Feni 132/33kV S/S T-1(405T) LT is restored.
|  | 10:59 | Chandpur 132/33kV S/S 422T LT is restored.
|  | 10:59 | Chandpur 132/33kV S/S 422T HT is restored.
| 11:09 | 14:03 | Barapukuria-Bogura 230 kV Ckt-1 Project Work S/D from Barapukuria 230/132/33kV end.
| 11:19 | 13:57 | Barapukuria-Bogura 230 kV Ckt-1 Project Work S/D from Bogura 400/230kV end Due to VT
secondary link box replacement.
| 12:02 | 14:40 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) LT Scheduled S/D Due to Red
hot maintanence
| 12:02 | 14:38 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT Scheduled S/D Due to Red
hot maintanence
| 12:22 | 13:01 | Sherpur 132/33kV S/S Transformer- 03 LT Forced S/D Due to Hot Spot Maintenance Work.
| 12:22 | 12:56 | Sherpur 132/33kV S/S Transformer- 03 HT Forced S/D Due to Hot Spot Maintenance Work.
| 12:25 | 14:03 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 LT Scheduled S/D Due to
Maintenance.
| 12:26 | 14:03 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 HT Scheduled S/D Due to
Maintenance.
| 12:30 | 13:45 | Chhatak 132/33kV S/S T-2 HT Scheduled S/D Due to T-2 D/S status check from control panel
|  | 13:07 | Madunaghat 132/33kV S/S TR-2(517T) LT is restored.
|  | 13:35 | Gopalganj 400/132kV S/S 400kV Rampal Ckt-1 is restored.
|  | 13:36 | Gopalganj(N)-Rampal Ckt-1 is restored.
|  | 13:41 | Chhatak 132/33kV S/S T-2 LT is restored.
| 14:16 | 18:13 | Madunaghat 132/33kV S/S TR-2(517T) HT Tripped showing RET-670,REF-615,RET-670 relays Due
to OLTC PRD Trip
| 14:16 |  | Madunaghat 132/33kV S/S TR-2(517T) LT Tripped showing RET-650,REF-615,RET-670 relays Due
to OLTC PRD TRIP
| 14:28 | 15:30 | Patuakhali-Payra 132kV Ckt-1 Scheduled S/D from Patuakhali 132/33kV end Due to Payra end
red hot maintenance and from Payra 400/132/33kV end Due to CT R,Y,B phase point
maintenance.
|  | 14:31 | Kabirpur - Manikganj 132kV Ckt-1 is restored.
| 14:35 | 15:30 | Kalurghat 132/33kV S/S TRFO-01(506T) LT Forced S/D Due to 33kv Bus section ds | [7 empty] | 13.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 14:37 | 15:35 | Kalurghat 132/33kV S/S TRFO-02(516T) LT Forced S/D Due to 33kv bus section ds | [7 empty] | 13.0MW load
|  |  | maintenance | [7 empty] | interrup.
|  | 15:09 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-2 is restored.
|  | 15:21 | Naogaon 132/33kV S/S T-1 HT is restored.
|  | 15:22 | Naogaon 132/33kV S/S T-1 LT is restored.
| 15:38 | 16:15 | Gopalganj(N)-Madaripur 132kV Ckt-3 Tripped from Madaripur 132/33kV end showing Distance
Relay relays.
| 15:43 | 17:15 | Sirajganj 132/33kV S/S T4-(445) HT Forced S/D Due to Emergency Red hot of Riser Conductor | [7 empty] | 5.0MW load
|  |  | of 33 kv Economic Zoon. | [7 empty] | interrup.
| 15:43 | 17:15 | Sirajganj 132/33kV S/S T4-(445) LT Forced S/D Due to Emergency Red hot of Riser Conductor | [7 empty] | 5.0MW load
|  |  | of 33 kv Economic Zoon. | [7 empty] | interrup.
| 15:50 | 17:05 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT Scheduled S/D Due to Red
hot Mainteance
| 15:50 | 17:02 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) HT Scheduled S/D Due to Red
hot Mainteance
| 16:19 | 17:52 | Kishoreganj 132/33kV S/S Tr-3 (424T) LT Scheduled S/D Due to 33 kv T-3 bus hotspot | [7 empty] | 30.0MW load
|  |  | maintenance work | [7 empty] | interrup.
| 16:25 |  | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to Hizla 33 kV feeder Bus DS loop | [7 empty] | 20.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 16:25 | 17:51 | Kishoreganj 132/33kV S/S Tr-3 (424T) HT Scheduled S/D Due to 33 kv bus hotspot | [7 empty] | 30.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 16:26 |  | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to Hizla 33 kV feeder Bus DS loop | [7 empty] | 20.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 16:42 | 19:35 | Khagrachori 132/33kV S/S TR-1 LT Forced S/D Due to Maintenance of T-01 33kV underground
Cable.
| 16:43 | 19:30 | Khagrachori 132/33kV S/S TR-1 HT Forced S/D Due to Maintenance of T-01 33kV underground
Cable.
|  | 17:32 | Mongla 132/33kV S/S T-2 HT is restored.
|  | 17:41 | Haripur 230/132kV S/S 132KV Bhulta-2 is restored.
|  | 17:43 | Mongla 132/33kV S/S T-2 LT is restored.
| 17:50 | 18:43 | Barishal 230/132kV S/S T-4 LT Forced S/D Due to T-5 breaker fault | [7 empty] | 30.0MW load
interrup.
| 17:50 | 18:43 | Barishal 230/132kV S/S T-4 LT Forced S/D Due to T-5 breaker fault | [7 empty] | 30.0MW load
interrup.
| 18:02 | 20:08 | Chowmuhani 132/33kV S/S TR1-415T LT Scheduled S/D Due to TR-01, 33KV Incoming DS B-Phase | [7 empty] | 30.0MW load
|  |  | Loop Maintenance. | [7 empty] | interrup.
| 18:03 | 20:08 | Chowmuhani 132/33kV S/S TR1-415T HT Scheduled S/D Due to TR-01, 33KV Incoming DS B-Phase | [7 empty] | 30.0MW load
|  |  | Loop Maintenance. | [7 empty] | interrup.
| 18:13 | 20:11 | Mongla 132/33kV S/S T-1 LT Project Work S/D Due to Energy meter change.
|  | 18:14 | Dohazari-Sikalbaha 132 kV Ckt-2 is restored.
| 18:15 | 19:07 | Madunaghat 132/33kV S/S TR-2(517T) HT Tripped showing RET_650 relays Due to OLTC PRD TRIP
| 18:15 | 20:10 | Mongla 132/33kV S/S T-1 HT Project Work S/D Due to Energy meter change.
|  | 21:21 | Hasnabad 230/132kV S/S AUTO TR-1 HT is restored.
|  | 21:23 | Hasnabad 230/132kV S/S AUTO TR-1 LT is restored.
|  | 21:50 | Shahjibazar 132/33kV S/S TR-02 HT is restored.
|  | 22:01 | Shahjibazar 132/33kV S/S TR-02 LT is restored.
| 22:53 | 00:53 | Dohazari 132/33kV S/S Power Transformer -T-2 HT Forced S/D Due to Keranihat & Bandarban | [7 empty] | 51.0MW load
|  |  | feeder Redhot maintenance | [7 empty] | interrup.
| 22:53 | 00:54 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Forced S/D Due to Keranihat & Bandarban | [7 empty] | 51.0MW load
|  |  | feeder Redhot maintenance | [7 empty] | interrup.
| 23:05 |  | Ghorashal 230kV S/S TARFO-2 HT Tripped showing Siemens relays Due to Flashing jumper | [7 empty] | 82.0MW load
|  |  | cable of Incommer:-2 Between CT & CB Y phase | [7 empty] | interrup.
| 23:05 |  | Ghorashal 230kV S/S TARFO-2 LT Tripped showing Siemens relays Due to Flashing jumper | [7 empty] | 82.0MW load
|  |  | cable of Incommer:-2 Between CT & CB Y phase. | [7 empty] | interrup.
| 23:22 | 00:16 | Mirzapur 132/33kV S/S Transformer-01(E05) HT Forced S/D Due to Red Hot Maintenance | [7 empty] | 42.0MW load
interrup.
| 23:32 |  | Matarbari 2*600 MW (CPGCBL), FGMO is ON with remarks:-
| 02:39 | 02:39 | Bagerhat-Labanchura 132 kV Ckt-2 Tripped from Bagerhat 132/33kV end showing Distance
relay,tripA,TripB,TripC,zone1 relays.
| 03:34 |  | Aminbazar 400/230/132kV S/S Gopalganj-1 Tripped showing SEL 421 relays.
| 03:34 |  | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-1 Tripped showing Distance Relay. Distance
46.17 Km from Gopalganj 400 KV SS relays Due to Earth fault Phase(A) Fault Current 6640
Amp.
| 05:12 |  | Cumilla(S) 132/33kV S/S TR-1 HT Scheduled S/D Due to TR-01 33kv Incomer Bus loop change | [7 empty] | 30.0MW load
interrup.
| 05:12 |  | Cumilla(S) 132/33kV S/S TR-1 LT Scheduled S/D | [7 empty] | 30.0MW load
interrup.
| 06:00 |  | minimum generation 10098MW
| 06:00 |  | Minimum Generation is 10098 MW
| 06:05 | 06:20 | Shahjibazar 132/33kV S/S TR-02 HT Tripped showing WTI Trip(Micom), Lockout Relay relays
Due to Rain
| 06:05 | 06:30 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing Lockout Relay relays Due to Rain
| 07:03 |  | Goalpara 132/33kV S/S T-5 LT Scheduled S/D Due to 3rd transformer installation. | [7 empty] | 3.0MW load
interrup.
| 07:03 |  | Goalpara 132/33kV S/S T-6 LT Scheduled S/D Due to 3rd transformer installation | [7 empty] | 3.0MW load
interrup.
| 07:05 |  | Goalpara 132/33kV S/S T-5 HT Scheduled S/D Due to 3rd transformer installation | [7 empty] | 3.0MW load
interrup.
| 07:07 |  | Goalpara 132/33kV S/S T-6 HT Scheduled S/D Due to 3rd transformer installation | [7 empty] | 3.0MW load
interrup.
| 07:11 |  | Daudkandi-Sonargaon 132 kV Ckt-2 Forced S/D from Sonargaon 132/33kV end Due to
Instruction by NLDC
| 07:23 |  | Bagerhat 132/33kV S/S Transformer-1 (403T) LT Scheduled S/D Due to 33 kv CT R phase
overheat maintenance work
| 07:24 |  | Bagerhat 132/33kV S/S Transformer-1 (403T) HT Scheduled S/D
| 07:26 |  | Gopalganj(N)-Madaripur 132kV Ckt-1 Scheduled S/D from Madaripur 132/33kV end Due to Hot
spot maintenance and from Gopalganj 400/132kVend.
| 07:34 |  | Daudkandi-Sonargaon 132 kV Ckt-2 Scheduled S/D from Daudkandi 132/33kV end Due to
shutdown for Redhot maintenance work
| 07:45 |  | Gopalganj 132/33kV S/S T2 LT Forced S/D Due to Hot spot maintenance
| 07:46 |  | Gopalganj 132/33kV S/S T2 HT Forced S/D Due to Hot spot maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 03-06-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 365 | 8582400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9017500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 290 | 6979287 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 293 | 6917358 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 245160 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 64 | 843360 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 489923 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 95337 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 25 | 552600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 299520 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 24 | 375840 | Fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 30 | 190942 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 50 | 898848 | Machine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 90 | 1349760 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 32 | 190080 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 518400 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 191356 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 191160 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 350 | 7426377 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 964800 | -
Dhaka Area Total |  |  |  |  | 5939.724 | 2334 | 46320008
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 8154 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 64395 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 56640 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 167 | 3442300 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 5134313 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 25090 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 32 | 148653 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 33 | 175201 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 36 | 393600 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 24 | 460800 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 5762 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 22600 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 31680 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1104 | 21583634 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 34 | 421440 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 491 | 10385454.55 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4895.72 | 2147 | 42359716.55
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 201 | 4823000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 353 | 8251500 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 7626000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 32 | 671472 | machine problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 51 | 1005120 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 110 | 669091 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 925608 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 12 | 158909 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 48 | 323840 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 685020 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 80 | 2146560 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 54 | 907200 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 154277 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 263250 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 96 | 1705440 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 33 | 354480 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 93 | 1125120 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 322627 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1648 | 32118514
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 44 | 1005120 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14950 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 140 | 1552800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 92 | 996000 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 265130 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 128400 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 288 | 3962400
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 31 | 774000 | FGMO
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 631200 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 156 | 3596155 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 672192 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1306560 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 165 | 4471000 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 432000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 255 | 5651000 | Gas shortage
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 372 | 8332000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7669700 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1461 | 33535807
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 854 | 19487272 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 77 | 2820384 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 138720 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 704160 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1088 | 20974540 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3699.2 | 2036 | 44125076
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 4 | 84211 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2503000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1112 | 20472727.27 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5202590 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 200 | 4080000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3163 | -
Barishal Area Total |  |  |  |  | 2236 | 1656 | 32345691.27
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 14 | 55944 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 171 | 3857727 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 190 | 4079300 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8167927 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 146237 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 25 | 133760 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 32958 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1415 | 23908576 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 390000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 724870 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2259 | 41497299
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 49 | 1154181 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4500000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 626102 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 50362.68 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 721857 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 228487 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1461600 | -
Rangpur Area Total |  |  |  |  | 950 | 477 | 8742589.68
Eastern Grid Total |  |  |  |  | 16705.895 | 7878 | 158296445.55
Western Grid Total |  |  |  |  | 10338.16 | 6428 | 126710655.95
National Grid Total |  |  |  |  | 27044.055 | 14306 | 285007101.5
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 03-06-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9192.92 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4505.3 | MW
i) Dhaka area |  |  | 4949.3 |  | MW | i) Khulna area |  |  |  | 1695.1 | MW
ii) Chattogram area |  |  | 1240.5 |  | MW | ii) Barishal area |  |  |  | 338 | MW
iii) Cumilla area |  |  | 1309.12 |  | MW | iii) Rajshahi area |  |  |  | 1539.2 | MW
iv) Mymensingh area |  |  | 1174 |  | MW | iv) Rangpur area |  |  |  | 933 | MW
v) Sylhet area |  |  | 520 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13698.22 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 24 | 18:00 | 67 | Ishurdi | 84 | 19:30 | 133 | Patuakhali | 83 | 00:00
2 | AKSML | 106 | 02:00 | 68 | Jaldhaka | 84 | 19:30 | 134 | Payra | 34 | 01:00
3 | Aftabnagar | 34 | 13:00 | 69 | Jamalpur | 130 | 00:00 | 135 | Postogola | 54 | 15:00
4 | Agargaon | 122 | 13:00 | 70 | Jashore | 144 | 16:00 | 136 | Purbachal | 17 | 00:00
5 | Agrabad | 80 | 18:30 | 71 | Jhenaidah | 130 | 22:00 | 137 | Purbasadipur | 118 | 23:00
6 | Amnura | 38 | 22:00 | 72 | Joydebpur | 143 | 15:00 | 138 | Rahanpur | 34 | 20:00
7 | Ashuganj | 90 | 02:00 | 73 | Joypurhat | 77 | 19:30 | 139 | Rahim | 21 | 11:00
8 | BSRM | 202 | 18:30 | 74 | Juldah | 13 | 00:00 | 140 | Rajbari | 82 | 00:00
9 | Bagerhat | 83 | 22:00 | 75 | KSRM | 22 | 06:00 | 141 | Rajendrapur | 117 | 00:00
10 | Bajitpur | 56 | 21:00 | 76 | Kabirpur | 250 | 18:30 | 142 | Rajshahi | 113 | 20:00
11 | Bakulia | 85 | 15:00 | 77 | Kachua | 84 | 21:00 | 143 | Rajshahi-230 | 96 | 13:00
12 | Banani | 36 | 13:00 | 78 | Kallyanpur | 96 | 14:00 | 144 | Ramganj | 106 | 22:00
13 | Bangabhaban | 16 | 12:00 | 79 | Kalurghat | 36 | 17:00 | 145 | Rampur | 34 | 23:00
14 | Barapukuria | 60 | 19:30 | 80 | Kamrangirchar | 62.8 | 17:00 | 146 | Rangamati | 17 | 19:00
15 | Barguna | 22 | 01:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 159 | 19:30
16 | Barishal | 118 | 21:00 | 82 | Kasba | 34 | 21:00 | 148 | Ruppur | 8.4 | 16:00
17 | Barishal-230 | 80 | 00:00 | 83 | Kazla | 94 | 13:00 | 149 | SSM | 2 | 23:00
18 | Baroaulia | 54 | 15:00 | 84 | Keranigonj | 73 | 13:00 | 150 | Saidpur | 104 | 19:30
19 | Baroirhat | 59 | 00:00 | 85 | Khagrachori | 26 | 21:00 | 151 | Satkhira | 155 | 01:00
20 | Bashundhara | 175 | 14:00 | 86 | Khulna | 85 | 13:00 | 152 | Satmasjid | 98 | 14:00
21 | BashundharaCement | 9 | 19:30 | 87 | Khulshi | 170 | 18:30 | 153 | Savar | 210 | 15:00
22 | Beanibazar | 64 | 19:00 | 88 | Kishoreganj | 141 | 00:00 | 154 | SevenRings | 16 | 15:00
23 | Benapole | 70 | 21:00 | 89 | Kodda | 309 | 14:00 | 155 | ShahCement | 22 | 00:00
24 | Bhaluka | 163 | 20:00 | 90 | Kulaura | 46 | 22:00 | 156 | Shahjadpur | 84 | 20:00
25 | Bhandaria | 57 | 00:00 | 91 | Kurigram | 64 | 20:00 | 157 | Shahjibazar | 117 | 23:00
26 | Bhangura | 36 | 20:00 | 92 | Kushtia | 161 | 00:00 | 158 | Shahmirpur | 48 | 00:00
27 | Bheramara(GK) | 67 | 21:00 | 93 | Lalbag | 56 | 11:00 | 159 | Shariatpur | 78 | 00:00
28 | Bhulta | 241 | 14:00 | 94 | Lalmonirhat | 64 | 19:30 | 160 | Sherpur | 136 | 23:00
29 | Bog-Sherpur | 70 | 20:00 | 95 | MI_Cement | 18.1 | 17:00 | 161 | Shikalbaha | 19 | 23:00
30 | Bogura | 179 | 21:00 | 96 | Madanganj | 20 | 13:00 | 162 | Shitalakhya | 81.5 | 15:00
31 | Borhanuddin | 90 | 03:00 | 97 | Madaripur | 105 | 00:00 | 163 | Sholosohor | 41 | 18:30
32 | Brahmanbaria | 121 | 22:00 | 98 | Madartek | 80 | 23:00 | 164 | Shyampur | 158 | 12:00
33 | Cantonment | 138 | 13:00 | 99 | Madunaghat | 43 | 19:00 | 165 | Siddhirganj | 112 | 15:00
34 | Chandina | 19.12 | 21:00 | 100 | Magura | 68 | 00:00 | 166 | Sirajganj | 120 | 20:00
35 | Chandpur | 76 | 20:00 | 101 | Mahasthangarh | 84 | 20:00 | 167 | Sonargaon | 105 | 00:00
36 | Chandraghona | 30 | 00:00 | 102 | Manikganj | 125 | 00:00 | 168 | Sreemongol | 70 | 21:00
37 | Chapai | 74 | 22:00 | 103 | Maniknagar | 78 | 13:00 | 169 | Sreepur | 104 | 22:00
38 | Charsaidpur | 44 | 02:00 | 104 | Matarbari | 39 | 00:00 | 170 | Srinagar | 43.17 | 22:00
39 | Chauddagram | 66 | 00:00 | 105 | Matuail | 64 | 12:00 | 171 | Sunamganj | 54 | 00:00
40 | Chhatak | 32 | 19:30 | 106 | Millgate | 87 | 12:00 | 172 | Sylhet | 41 | 00:00
41 | Chowmuhani | 208 | 22:00 | 107 | Mirpur | 112 | 19:00 | 173 | Sylhet-132 | 104 | 21:00
42 | Chuadanga | 125 | 00:00 | 108 | Mirsorai | 10 | 16:00 | 174 | TK | 31 | 19:30
43 | Coxsbazar | 130 | 20:00 | 109 | Mirzapur | 46 | 21:00 | 175 | Tangail | 177 | 20:00
44 | Cumilla(N) | 142 | 01:00 | 110 | Mithapukur | 72 | 20:00 | 176 | Thakurgaon | 118 | 20:00
45 | Cumilla(S) | 172 | 15:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 114 | 00:00
46 | Daudkandi | 142 | 21:00 | 112 | Mogbazar | 137.9 | 15:00 | 178 | Ullahpara | 38 | 20:00
47 | Dhaka | 60 | 13:00 | 113 | Mongla | 44 | 12:00 | 179 | Ullon | 36 | 00:00
48 | Dhamrai | 138 | 19:30 | 114 | Motijheel | 36 | 12:00 | 180 | Uttara | 75 | 13:00
49 | Dhanmondi | 145 | 13:00 | 115 | Muktagacha | 36 | 00:00 | 181 | UttaraNew | 54 | 22:00
50 | Dohazari | 90 | 00:00 | 116 | Munshiganj | 105 | 00:00 | 182 | Zigatola | 64 | 00:00
51 | Faridpur | 162 | 00:00 | 117 | Muradnagar | 27 | 22:00
52 | Fatullah | 96 | 16:00 | 118 | Mymensingh | 186 | 22:00
53 | Fenchuganj | 33 | 01:00 | 119 | Naogaon | 126 | 19:00
54 | Feni | 111 | 19:00 | 120 | Narail | 62 | 00:00
55 | GPH | 27 | 04:00 | 121 | Narinda | 72 | 13:00
56 | Ghatail | 78 | 19:00 | 122 | Narshingdi | 173 | 19:30
57 | Ghorashal | 15 | 00:00 | 123 | Natore | 157 | 19:30
58 | Ghorashal-230 | 87 | 01:00 | 124 | Nawabganj | 56.8 | 22:00
59 | Goalpara | 44 | 01:00 | 125 | Netrakona | 120 | 21:00
60 | Gollamari | 112 | 00:00 | 126 | New | 81 | 12:00
61 | Gopalganj | 107 | 00:00 | 127 | Niamatpur | 79 | 21:00
62 | Gulshan | 114 | 13:00 | 128 | Noapara | 52 | 00:00
63 | Halishahar | 73 | 10:00 | 129 | PHP | 3 | 05:00
64 | HaripurSBU | 183 | 10:00 | 130 | Pabna | 116 | 15:00
65 | Hasnabad | 76 | 13:00 | 131 | Palashbari | 112 | 20:00
66 | Hathazari | 74 | 20:00 | 132 | Panchagarh | 65 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 03-06-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 12440.25 | 0 |  | 12440.25
1:00 | 11775.26 | 0 |  | 11775.26
2:00 | 10991.87 | 0 |  | 10991.87
3:00 | 9973.03 | 0 |  | 9973.03
4:00 | 8908.76 | 0 |  | 8908.76
5:00 | 8827.15 | 0 |  | 8827.15
6:00 | 8911.28 | 0 |  | 8911.28
7:00 | 8984.59 | 0 |  | 8984.59
8:00 | 9413.85 | 0 |  | 9413.85
9:00 | 10086.77 | 0 |  | 10086.77
10:00 | 10823.07 | 0 |  | 10823.07
11:00 | 11415.23 | 0 |  | 11415.23
12:00 | 12043.2 | 0 |  | 12043.2
13:00 | 12560.42 | 0 |  | 12560.42
14:00 | 12799.55 | 0 |  | 12799.55
15:00 | 13020.65 | 0 |  | 13020.65
16:00 | 12860.86 | 0 |  | 12860.86
17:00 | 12399.24 | 27 |  | 12427.24
18:00 | 12083.64 | 28 |  | 12112.64
19:00 | 13448.69 | 26 |  | 13475.86
19:30 | 14104.49 | 0 |  | 14104.49
20:00 | 14193.73 | 0 |  | 14193.73
21:00 | 14306 | 0 |  | 14306
22:00 | 14188.5 | 16 |  | 14205.5
23:00 | 14154 | 15 |  | 14170
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 03-06-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7415.5 | 5024.75 | 12440.25 | DAILY GENERATION CURVE
00:30 | 7187.25 | 4920.505 | 12107.755
01:00 | 6959 | 4816.26 | 11775.26 | 03-06-2025
01:30 | 6642.5 | 4741.065 | 11383.565
02:00 | 6326 | 4665.87 | 10991.87
02:30 | 5946.5 | 4535.95 | 10482.45
03:00 | 5567 | 4406.03 | 9973.03
03:30 | 5180.5 | 4260.395 | 9440.895
04:00 | 4794 | 4114.76 | 8908.76
04:30 | 4744.5 | 4123.455 | 8867.955
05:00 | 4695 | 4132.15 | 8827.15
05:30 | 4829.285 | 4039.93 | 8869.215
06:00 | 4963.57 | 3947.71 | 8911.28
06:30 | 4978.045 | 3969.89 | 8947.935
07:00 | 4992.52 | 3992.07 | 8984.59
07:30 | 5124.85 | 4074.37 | 9199.22
08:00 | 5257.18 | 4156.67 | 9413.85
08:30 | 5333.17 | 4417.14 | 9750.31
09:00 | 5409.16 | 4677.61 | 10086.77
09:30 | 5613.51 | 4841.41 | 10454.92
10:00 | 5817.86 | 5005.21 | 10823.07
10:30 | 6127.925 | 4991.225 | 11119.15
11:00 | 6437.99 | 4977.24 | 11415.23
11:30 | 6622.69 | 5106.525 | 11729.215
12:00 | 6807.39 | 5235.81 | 12043.2
12:30 | 6924.695 | 5377.115 | 12301.81
13:00 | 7042 | 5518.42 | 12560.42
13:30 | 7112.61 | 5567.375 | 12679.985
14:00 | 7183.22 | 5616.33 | 12799.55
14:30 | 7191.325 | 5718.775 | 12910.1
15:00 | 7199.43 | 5821.22 | 13020.65
15:30 | 7176.79 | 5763.965 | 12940.755
16:00 | 7154.15 | 5706.71 | 12860.86
16:30 | 7075.295 | 5554.755 | 12630.05
17:00 | 6996.44 | 5402.8 | 12399.24
17:30 | 6927.02 | 5314.42 | 12241.44
18:00 | 6857.6 | 5226.04 | 12083.64
18:30 | 7247.3 | 5518.865 | 12766.165
19:00 | 7637 | 5811.69 | 13448.69
19:30 | 7888 | 6216.49 | 14104.49
20:00 | 7781 | 6412.73 | 14193.73
20:30 | 7829.5 | 6420.365 | 14249.865 |  | Executive Engineer
21:00 | 7878 | 6428 | 14306 |  | Network Operation Division
21:30 | 7841.25 | 6406 | 14247.25
22:00 | 7804.5 | 6384 | 14188.5
22:30 | 7771.25 | 6400 | 14171.25
23:00 | 7738 | 6416 | 14154

## En-Curve
QF-LDC-12
Date | 03-06-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3607 | 2007.5 | 880 | 0 | 32 | 810.75 | 155 | 3819 | 0 | 308 | 798 | 0 | 0 | 23 | 0 | DAILY ENERGY CURVE
00:30 | 3581 | 2001.75 | 885.5 | 0 | 32 | 811.505 | 155 | 3666.5 | 0 | 281 | 667.5 | 0 | 0 | 26 | 0 | 03-06-2025
01:00 | 3555 | 1996 | 891 | 0 | 32 | 812.26 | 155 | 3514 | 0 | 254 | 537 | 0 | 0 | 29 | 0
01:30 | 3521 | 1917.5 | 891 | 0 | 32 | 816.065 | 155 | 3359.5 | 0 | 155.5 | 509.5 | 0 | 0 | 26.5 | 0 | Energy Generated | 285.0071 |  | MKWHr
02:00 | 3487 | 1839 | 891 | 0 | 32 | 819.87 | 155 | 3205 | 0 | 57 | 482 | 0 | 0 | 24 | 0 | Energy not Served | 0.112 |  | MKWHr
02:30 | 3435.5 | 1715.5 | 890.5 | 0 | 31 | 819.45 | 155 | 2979 | 0 | 28.5 | 405.5 | 0 | 0 | 22.5 | 0 | Total Energy Requirement | 285.1191 |  | MKWHr
03:00 | 3384 | 1592 | 890 | 0 | 30 | 819.03 | 155 | 2753 | 0 | 0 | 329 | 0 | 0 | 21 | 0
03:30 | 3245 | 1471.5 | 822 | 0 | 25 | 819.395 | 97.5 | 2685 | 0 | 12 | 237.5 | 0 | 0 | 26 | 0
04:00 | 3106 | 1351 | 754 | 0 | 20 | 819.76 | 40 | 2617 | 0 | 24 | 146 | 0 | 0 | 31 | 0
04:30 | 3113 | 1366 | 754 | 0 | 19 | 823.955 | 40 | 2593 | 0 | 28.5 | 102.5 | 0 | 0 | 28 | 0
05:00 | 3120 | 1381 | 754 | 0 | 18 | 828.15 | 40 | 2569 | 0 | 33 | 59 | 0 | 0 | 25 | 0
05:30 | 3187 | 1435 | 633 | 0 | 18 | 827.035 | 60 | 2573.5 | 13.18 | 33 | 63 | 0 | 0 | 26.5 | 0
06:00 | 3254 | 1489 | 512 | 0 | 18 | 825.92 | 80 | 2578 | 26.36 | 33 | 67 | 0 | 0 | 28 | 0
06:30 | 3293.5 | 1448 | 512.5 | 0 | 20 | 825.175 | 80 | 2577 | 65.26 | 33 | 79.5 | 0 | 0 | 14 | 0
07:00 | 3333 | 1407 | 513 | 0 | 22 | 824.43 | 80 | 2576 | 104.16 | 33 | 92 | 0 | 0 | 0 | 0
07:30 | 3416.5 | 1469.5 | 489 | 0 | 21 | 824.16 | 100 | 2581.5 | 172.56 | 33 | 92 | 0 | 0 | 0 | 0
08:00 | 3500 | 1532 | 465 | 0 | 20 | 823.89 | 120 | 2587 | 240.96 | 33 | 92 | 0 | 0 | 0 | 0
08:30 | 3522 | 1571.5 | 622 | 0 | 20 | 822.445 | 137.5 | 2587 | 302.365 | 50.5 | 115 | 0 | 0 | 0 | 0
09:00 | 3544 | 1611 | 779 | 0 | 20 | 821 | 155 | 2587 | 363.77 | 68 | 138 | 0 | 0 | 0 | 0
09:30 | 3613.5 | 1664.5 | 834.5 | 0 | 21 | 823 | 155 | 2659 | 424.42 | 89 | 165.5 | 0 | 0 | 5.5 | 0
10:00 | 3683 | 1718 | 890 | 0 | 22 | 825 | 155 | 2731 | 485.07 | 110 | 193 | 0 | 0 | 11 | 0
10:30 | 3633.5 | 1767.5 | 890 | 0 | 32 | 824 | 155.5 | 2890 | 534.15 | 110 | 272.5 | 0 | 0 | 10 | 0
11:00 | 3584 | 1817 | 890 | 0 | 42 | 823 | 156 | 3049 | 583.23 | 110 | 352 | 0 | 0 | 9 | 0
11:30 | 3659.5 | 1863 | 890.5 | 0 | 43 | 836.5 | 155.5 | 3155.5 | 626.715 | 114 | 379.5 | 0 | 0 | 5.5 | 0
12:00 | 3735 | 1909 | 891 | 0 | 44 | 850 | 155 | 3262 | 670.2 | 118 | 407 | 0 | 0 | 2 | 0
12:30 | 3689 | 1923 | 891 | 0 | 46 | 881.5 | 161 | 3442 | 645.31 | 132.5 | 486 | 0 | 0 | 4.5 | 0
13:00 | 3643 | 1937 | 891 | 0 | 48 | 913 | 167 | 3622 | 620.42 | 147 | 565 | 0 | 0 | 7 | 0
13:30 | 3670 | 1946 | 891 | 0 | 49 | 915.27 | 167 | 3766.5 | 590.215 | 155 | 523.5 | 0 | 0 | 6.5 | 0
14:00 | 3697 | 1955 | 891 | 0 | 50 | 917.54 | 167 | 3911 | 560.01 | 163 | 482 | 0 | 0 | 6 | 0
14:30 | 3705 | 1953.5 | 891 | 0 | 49 | 997.005 | 167 | 3968 | 488.095 | 171.5 | 515 | 0 | 0 | 5 | 0
15:00 | 3713 | 1952 | 891 | 0 | 48 | 1076.47 | 167 | 4025 | 416.18 | 180 | 548 | 0 | 0 | 4 | 0
15:30 | 3694.5 | 1986 | 891 | 0 | 48 | 1066.68 | 167 | 4017.5 | 315.575 | 180 | 570.5 | 0 | 0 | 4 | 0
16:00 | 3676 | 2020 | 891 | 0 | 48 | 1056.89 | 167 | 4010 | 214.97 | 180 | 593 | 0 | 0 | 4 | 0
16:30 | 3590 | 1999.5 | 891 | 0 | 47 | 1036.04 | 167 | 3957 | 152.51 | 180 | 598 | 0 | 0 | 12 | 13.5
17:00 | 3504 | 1979 | 891 | 0 | 46 | 1015.19 | 167 | 3904 | 90.05 | 180 | 603 | 0 | 0 | 20 | 27
17:30 | 3544 | 1909 | 842 | 0 | 45 | 988.14 | 167 | 3854 | 61.3 | 179 | 630.5 | 0 | 0 | 21.5 | 27.5
18:00 | 3584 | 1839 | 793 | 0 | 44 | 961.09 | 167 | 3804 | 32.55 | 178 | 658 | 0 | 0 | 23 | 28
18:30 | 3750.5 | 1916 | 769.5 | 0 | 48 | 1057.89 | 167 | 3907 | 16.275 | 299 | 808.5 | 0 | 0 | 26.5 | 27
19:00 | 3917 | 1993 | 746 | 0 | 52 | 1154.69 | 167 | 4010 | 0 | 420 | 959 | 0 | 0 | 30 | 26
19:30 | 3962 | 2002 | 746 | 0 | 52 | 1297.49 | 167 | 4213 | 0 | 453 | 1176 | 0 | 0 | 36 | 0
20:00 | 3919 | 2028 | 807 | 0 | 52 | 1416.73 | 167 | 4171 | 0 | 468 | 1131 | 0 | 0 | 34 | 0
20:30 | 3892.5 | 2067 | 830.5 | 0 | 53 | 1415.865 | 167 | 4207.5 | 0 | 468 | 1114.5 | 0 | 0 | 34 | 0
21:00 | 3866 | 2106 | 854 | 0 | 54 | 1415 | 167 | 4244 | 0 | 468 | 1098 | 0 | 0 | 34 | 0
21:30 | 3856.5 | 2081.25 | 854 | 0 | 54 | 1417.5 | 167 | 4219.5 | 0 | 476.5 | 1089 | 0 | 0 | 32 | 8
22:00 | 3847 | 2056.5 | 854 | 0 | 54 | 1420 | 167 | 4195 | 0 | 485 | 1080 | 0 | 0 | 30 | 16
22:30 | 3834 | 2052.75 | 854.5 | 0 | 54 | 1414.5 | 167 | 4203.5 | 0 | 479.5 | 1086 | 0 | 0 | 25.5 | 15.5
23:00 | 3821 | 2049 | 855 | 0 | 54 | 1409 | 167 | 4212 | 0 | 474 | 1092 | 0 | 0 | 21 | 15
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 03-06-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 392 | 06:00 | 373 | 15:00 | Payra | 419 | 07:00 | 409 | 00:00
Ashuganj | 413 | 3:00 | 377 | 14:00 | Rahanpur | 407 | 00:00 | 382 | 15:00
Bhulta | 408 | 04:00 | 376 | 15:00 | Rampal | 409 | 04:00 | 391 | 15:00
Bibiana | 396 | 04:00 | 384 | 15:00
BIPTC | 406 | 06:00 | 388 | 15:00
Bogura | 400 | 00:00 | 369 | 15:00
Gopalganj | 402 | 04:00 | 386 | 15:00
Kaliakoir | 382 | 06:00 | 363 | 15:00
Madunaghat | 403 | 07:00 | 389 | 00:00
Meghnaghat | 394 | 06:00 | 378 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 231 | 04:00 | 216 | 15:00 | Keranigonj | 229 | 06:00 | 214 | 15:00
AKSML | 234 | 08:00 | 223 | 18:00 | Khulna(S) | 235 | 04:00 | 217 | 15:00
Aminbazar | 233 | 19:30 | 217 | 15:00 | Madunaghat | 238 | 07:00 | 230 | 00:00
Ashuganj | 237 | 06:00 | 221 | 15:00 | Madunaghat-400 | 238 | 07:00 | 229 | 00:00
Ashuganj-400 | 237 | 06:00 | 221 | 15:00 | Maniknagar | 226 | 04:00 | 214 | 16:00
Baghabari | 235 | 01:00 | 223 | 14:00 | Meghnaghat | 235 | 04:00 | 223 | 15:00
Barapukuria | 233 | 00:00 | 218 | 14:00 | Meghnaghat-400 | 229 | 04:00 | 218 | 16:00
Barapukuria-230 | 233 | 00:00 | 218 | 14:00 | Mirsorai | 231 | 07:00 | 222 | 16:00
Barishal | 242 | 04:00 | 228 | 00:00 | Rajshahi | 236 | 06:00 | 220 | 11:00
Bheramara | 235 | 01:00 | 221 | 11:00 | Rampal | 234 | 03:00 | 217 | 15:00
Bhulta | 238 | 04:00 | 215 | 16:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 233 | 07:00 | 225 | 00:00 | Rampura | 236 | 04:00 | 215 | 15:00
BIPTC | 236 | 01:00 | 221 | 11:00 | Shikalbaha | 236 | 06:00 | 227 | 16:00
Bogura | 236 | 00:00 | 218 | 15:00 | Shyampur | 228 | 04:00 | 215 | 15:00
Bogura-400 | 236 | 00:00 | 219 | 15:00 | Siddhirganj | 225 | 05:00 | 216 | 15:00
Borhanuddin | 248 | 04:00 | 233 | 00:00 | Sirajgonj | 240 | 03:00 | 230 | 15:00
BSRM | 231 | 05:00 | 222 | 15:00 | Sreepur | 234 | 04:00 | 218 | 15:00
Cumilla(N) | 229 | 06:00 | 217 | 14:00 | Tongi | 234 | 03:00 | 215 | 15:00
Faridpur | 238 | 05:00 | 224 | 00:00
Fenchuganj | 232 | 09:00 | 225 | 01:00
Ghorashal | 230 | 00:00 | 230 | 00:00
Ghorashal-230 | 234 | 04:00 | 215 | 15:00
Gopalganj | 239 | 06:00 | 228 | 00:00
GPH | 234 | 07:00 | 225 | 16:00
Haripur | 227 | 04:00 | 216 | 15:00
Hasnabad | 226 | 07:00 | 215 | 15:00
Hathazari | 237 | 08:00 | 229 | 00:00
Ishurdi | 236 | 01:00 | 223 | 15:00
Jhenaidah | 234 | 06:00 | 216 | 15:00
Kaliakoir | 236 | 04:00 | 222 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 03:00 | 125 | 12:00 | Madartek | 137 | 04:00 | 124 | 13:00
Agargaon | 140 | 06:00 | 129 | 15:00 | Madunaghat | 137 | 08:00 | 130 | 15:00
Agrabad | 137 | 07:00 | 128 | 00:00 | Magura | 137 | 04:00 | 122 | 23:00
AKS | 134 | 07:00 | 127 | 16:00 | Mahasthangarh | 140 | 00:00 | 126 | 15:00
Aminbazar | 136 | 04:00 | 126 | 15:00 | Manikganj | 134 | 07:00 | 125 | 14:00
Amnura | 137 | 03:00 | 121 | 15:00 | Maniknagar | 137 | 06:00 | 129 | 13:00
Ashuganj | 140 | 04:00 | 133 | 15:00 | Matarbari | 135 | 09:00 | 116 | 00:00
Bagerhat | 138 | 03:00 | 119 | 22:00 | Matuail | 133 | 02:00 | 125 | 15:00
Bajitpur | 131 | 04:00 | 125 | 00:00 | Millgate | 141 | 03:00 | 130 | 15:00
Bakulia | 138 | 06:00 | 130 | 00:00 | Mirpur | 135 | 06:00 | 124 | 15:00
Banani | 138 | 03:00 | 124 | 15:00 | Mirzapur | 138 | 01:00 | 129 | 12:00
Bangabhaban | 137 | 04:00 | 128 | 15:00 | Mithapukur | 139 | 01:00 | 121 | 16:00
Barapukuria | 140 | 01:00 | 125 | 14:00 | MI_Cement | 134 | 04:00 | 125 | 14:00
Barguna | 138 | 06:00 | 130 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 138 | 03:00 | 124 | 00:00 | Mogbazar | 139 | 05:00 | 125 | 13:00
Barishal-230 | 137 | 04:00 | 125 | 00:00 | Mongla | 140 | 03:00 | 121 | 22:00
Baroaulia | 136 | 06:00 | 132 | 00:00 | Motijheel | 137 | 04:00 | 128 | 15:00
Baroirhat | 131 | 06:00 | 121 | 01:00 | Muktagacha | 140 | 01:00 | 130 | 00:00
Bashundhara | 141 | 04:00 | 123 | 14:00 | Munshiganj | 132 | 04:00 | 121 | 15:00
BashundharaCement | 132 | 05:00 | 125 | 00:00 | Muradnagar | 131 | 04:00 | 121 | 15:00
Beanibazar | 135 | 05:00 | 127 | 00:00 | Mymensingh | 147 | 20:00 | 115 | 22:00
Benapole | 138 | 02:00 | 117 | 15:00 | Naogaon | 137 | 05:00 | 122 | 15:00
Bhaluka | 134 | 02:00 | 121 | 15:00 | Narail | 139 | 06:00 | 122 | 23:00
Bhandaria | 136 | 04:00 | 116 | 00:00 | Narinda | 0 | 00:00 | N/A | N/A
Bhangura | 136 | 06:00 | 126 | 15:00 | Narshingdi | 134 | 04:00 | 116 | 00:00
Bheramara | 138 | 01:00 | 127 | 15:00 | Natore | 137 | 01:00 | 125 | 15:00
Bheramara(GK) | 136 | 02:00 | 127 | 11:00 | Nawabganj | 139 | 03:00 | 127 | 14:00
Bhulta | 128 | 04:00 | 119 | 14:00 | Netrakona | 130 | 02:00 | 113 | 22:00
Bog-Sherpur | 139 | 01:00 | 126 | 15:00 | New | 142 | 03:00 | 130 | 15:00
Bogura | 142 | 00:00 | 128 | 15:00 | Niamatpur | 135 | 03:00 | 125 | 14:00
Bogura-230 | 141 | 00:00 | 128 | 15:00 | Noapara | 140 | 03:00 | 122 | 13:00
Brahmanbaria | 136 | 03:00 | 123 | 00:00 | Pabna | 135 | 00:00 | 124 | 13:00
Cantonment | 139 | 03:00 | 128 | 15:00 | Palashbari | 138 | 00:00 | 120 | 15:00
Chandina | 133 | 05:00 | 123 | 15:00 | Panchagarh | 137 | 00:00 | 120 | 14:00
Chandpur | 129 | 12:00 | 119 | 13:00 | Patuakhali | 136 | 04:00 | 130 | 00:00
Chandraghona | 136 | 07:00 | 130 | 00:00 | Payra | 138 | 04:00 | 133 | 00:00
Chapai | 132 | 05:00 | 122 | 14:00 | PHP | 131 | 06:00 | 119 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 133 | 03:00 | 125 | 15:00 | Postogola | 132 | 09:00 | 126 | 15:00
Chauddagram | 131 | 05:00 | 119 | 15:00 | Purbachal | 138 | 03:00 | 123 | 15:00
Chhatak | 132 | 05:00 | 124 | 21:00 | Purbasadipur | 135 | 00:00 | 117 | 13:00
Chowmuhani | 127 | 05:00 | 114 | 03:00 | Rahanpur | 136 | 00:00 | 126 | 15:00
Chuadanga | 136 | 06:00 | 118 | 22:00 | Rahanpur-400 | 136 | 00:00 | 127 | 14:00
Coxsbazar | 135 | 09:00 | 117 | 00:00 | Rahim | 134 | 20:00 | 126 | 00:00
Cumilla(N) | 133 | 06:00 | 123 | 15:00 | Rajbari | 139 | 06:00 | 128 | 00:00
Cumilla(S) | 134 | 04:00 | 121 | 15:00 | Rajendrapur | 135 | 03:00 | 122 | 15:00
Daudkandi | 129 | 05:00 | 120 | 00:00 | Rajshahi | 136 | 03:00 | 126 | 13:00
Dhaka | 136 | 02:00 | 124 | 15:00 | Rajshahi-230 | 136 | 01:00 | 114 | 14:00
Dhamrai | 135 | 06:00 | 129 | 00:00 | Ramganj | 124 | 04:00 | 112 | 23:00
Dhanmondi | 138 | 05:00 | 125 | 15:00 | Rampur | 136 | 07:00 | 130 | 00:00
Dohazari | 136 | 08:00 | 125 | 00:00 | Rampura | 138 | 04:00 | 124 | 15:00
Faridpur | 139 | 06:00 | 130 | 00:00 | Rangamati | 136 | 01:00 | 130 | 00:00
Fatullah | 134 | 04:00 | 125 | 15:00 | Rangpur | 140 | 00:00 | 118 | 19:00
Fenchuganj | 139 | 06:00 | 134 | 00:00 | Ruppur | 138 | 04:00 | 128 | 13:00
Feni | 129 | 05:00 | 118 | 15:00 | Saidpur | 139 | 00:00 | 118 | 19:00
Ghatail | 140 | 01:00 | 127 | 12:00 | Satkhira | 134 | 04:00 | 118 | 15:00
Ghorashal | 137 | 18:30 | 131 | 12:00 | Satmasjid | 139 | 05:00 | 129 | 12:00
Goalpara | 142 | 03:00 | 125 | 00:00 | Savar | 134 | 04:00 | 124 | 00:00
Gollamari | 140 | 03:00 | 126 | 13:00 | SevenRings | 139 | 04:00 | 129 | 15:00
Gopalganj | 139 | 03:00 | 127 | 00:00 | ShahCement | 133 | 03:00 | 125 | 15:00
Gopalganj-400 | 163 | 09:00 | 131 | 00:00 | Shahjadpur | 134 | 04:00 | 132 | 01:00
Gulshan | 138 | 03:00 | 124 | 15:00 | Shahjibazar | 135 | 04:00 | 125 | 23:00
Halishahar | 137 | 07:00 | 129 | 00:00 | Shahmirpur | 137 | 07:00 | 130 | 00:00
Haripur | 133 | 04:00 | 127 | 00:00 | Shariatpur | 138 | 04:00 | 126 | 00:00
HaripurSBU | 133 | 04:00 | 127 | 00:00 | Sherpur | 142 | 01:00 | 121 | 12:00
Hasnabad | 136 | 04:00 | 127 | 15:00 | Shikalbaha | 127 | 07:00 | 119 | 00:00
Hathazari | 138 | 09:00 | 131 | 00:00 | Shikalbaha-230 | 138 | 07:00 | 131 | 00:00
Ishurdi | 139 | 06:00 | 129 | 15:00 | Shitalakhya | 134 | 04:00 | 125 | 14:00
Jaldhaka | 138 | 00:00 | 117 | 19:00 | Sholosohor | 134 | 10:00 | 128 | 00:00
Jamalpur | 142 | 01:00 | 123 | 12:00 | Shyampur | 130 | 22:00 | 124 | 15:00
Jashore | 138 | 03:00 | 118 | 22:00 | Shyampur-230 | 134 | 06:00 | 124 | 15:00
Jhenaidah | 139 | 05:00 | 115 | 15:00 | Siddhirganj | 133 | 03:00 | 125 | 15:00
Jhenaidah-230 | 139 | 06:00 | 125 | 00:00 | Sirajganj | 137 | 00:00 | 124 | 21:00
Joydebpur | 132 | 03:00 | 122 | 15:00 | Sonargaon | 132 | 07:00 | 123 | 03:00
Joypurhat | 135 | 00:00 | 119 | 15:00 | Sreemongol | 137 | 04:00 | 126 | 00:00
Juldah | 136 | 09:00 | 131 | 00:00 | Sreepur | 134 | 01:00 | 126 | 15:00
Kabirpur | 139 | 06:00 | 129 | 15:00 | Srinagar | 160 | 00:00 | 128 | 15:00
Kachua | 128 | 05:00 | 118 | 23:00 | SSM | 138 | 13:00 | 128 | 11:00
Kaliakoir | 140 | 01:00 | 130 | 12:00 | Sunamganj | 132 | 04:00 | 123 | 00:00
Kallyanpur | 136 | 05:00 | 124 | 12:00 | Sylhet | 135 | 06:00 | 128 | 00:00
Kalurghat | 133 | 10:00 | 130 | 00:00 | Sylhet-132 | 133 | 04:00 | 129 | 00:00
Kamrangirchar | 138 | 06:00 | 127 | 15:00 | Tangail | 139 | 01:00 | 126 | 12:00
Kaptai | 136 | 6:00 | 128 | 21:00 | Thakurgaon | 138 | 00:00 | 118 | 14:00
Kasba | 131 | 04:00 | 121 | 00:00 | TK | 135 | 07:00 | 129 | 00:00
Kazla | 136 | 04:00 | 127 | 16:00 | Tongi | 142 | 03:00 | 133 | 11:00
Keranigonj | 138 | 04:00 | 128 | 15:00 | Ullahpara | 137 | 00:00 | 126 | 15:00
Khagrachori | 136 | 07:00 | 129 | 01:00 | Ullon | 139 | 03:00 | 123 | 15:00
Khulna | 139 | 03:00 | 124 | 05:00 | Uttara | 135 | 03:00 | 125 | 12:00
Khulna(S) | 141 | 03:00 | 126 | 15:00 | UttaraNew | 135 | 03:00 | 124 | 15:00
Khulshi | 136 | 07:00 | 128 | 00:00 | Zigatola | 137 | 04:00 | 127 | 16:00
Kishoreganj | 132 | 06:00 | 122 | 19:00
Kodda | 135 | 01:00 | 121 | 14:00
KSRM | 137 | 05:00 | 131 | 02:00
Kulaura | 139 | 04:00 | 132 | 02:00
Kurigram | 140 | 01:00 | 116 | 19:30
Kushtia | 133 | 07:00 | 120 | 15:00
Lalbag | 138 | 06:00 | 127 | 15:00
Lalmonirhat | 137 | 01:00 | 118 | 16:00
Madanganj | 132 | 05:00 | 125 | 00:00
Madaripur | 138 | 07:00 | 128 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division