## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 04-06-2025 | [28 empty] | Date: | 04-06-2025 | [28 empty] | Date: | 04-06-2025 | [28 empty] | Date: | 04-06-2025 | [28 empty] | Date: | 04-06-2025 | [12 empty] | Date: | 04-06-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [12 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 35 | 0 | 51 | 82 | 30 | 0 | 17 | 54 | 32 | 450 | 285 | 350 | 0 | 17 | 281 | 0 | 0 | 0 | 108 | 26.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 33 | 23 | 0 | 36 | 0 | 0 | 167 | 0 | 33 | 470 | 0 | 0 | 6 | 0 | 0 | 223 | 0 | 0 | 0 | 1104 | 0 | 51 | 12 | 0 | 0 | 355 | 340 | 53 | 185 | 32 | 73 | 80 | 97 | 11 | 14 | 98 | 54 | 0 | 0 | 48 | 240 | 320 | 354 | 32 | 30 | 151 | 0 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 95 | 122 | 47 | 0 | 0 | 12 | 7566.5 | 713 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1071 | 52 | 1416 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 13 | 0 | 0 | 30 | 0 | 163 | 0 | 184 | 0 | 0 | 0 | 395 | 0 | 0 | 200 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 11 | 120 | 220 | 0 | 0 | 1110 | 0 | 6272 | 13838.5 | 90.51
01:00 | 0 | 53 | 8 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 17 | 0 | 51 | 146 | 0 | 0 | 0 | 0 | 0 | 450 | 284 | 350 | 0 | 0 | 276 | 0 | 0 | 0 | 108 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 33 | 522 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 0 | 0 | 353 | 340 | 40 | 218 | 32 | 32 | 80 | 165 | 9 | 14 | 95 | 52 | 0 | 0 | 16 | 240 | 320 | 349 | 32 | 30 | 148 | 0 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 48 | 93 | 48 | 0 | 0 | 12 | 7215 | 711 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1033 | 17 | 1425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 177 | 0 | 0 | 0 | 394 | 0 | 0 | 200 | 50 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 11 | 120 | 220 | 0 | 0 | 1115 | 0 | 6042 | 13257 | 90.59
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 34 | 146 | 0 | 0 | 0 | 0 | 0 | 450 | 286 | 350 | 0 | 0 | 283 | 0 | 0 | 0 | 90 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 33 | 501 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 1085 | 0 | 43 | 0 | 0 | 0 | 355 | 340 | 40 | 217 | 32 | 19 | 80 | 200 | 9 | 14 | 114 | 50 | 0 | 0 | 0 | 240 | 320 | 334 | 32 | 30 | 140 | 0 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 48 | 93 | 48 | 0 | 0 | 8 | 7192 | 711 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 939 | 0 | 1224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 175 | 0 | 0 | 0 | 343 | 0 | 0 | 200 | 50 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 10 | 100 | 220 | 0 | 0 | 1005 | 0 | 5531 | 12723 | 90.67
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 17 | 146 | 0 | 0 | 0 | 0 | 0 | 450 | 287 | 350 | 0 | 0 | 284 | 0 | 0 | 0 | 52 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 33 | 484 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1000 | 0 | 43 | 0 | 0 | 0 | 354 | 340 | 40 | 218 | 32 | 16 | 80 | 200 | 9 | 14 | 114 | 48 | 0 | 0 | 0 | 245 | 320 | 320 | 32 | 30 | 131 | 0 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 48 | 93 | 48 | 0 | 0 | 12 | 7013 | 711 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 874 | 0 | 1114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 183 | 0 | 0 | 0 | 342 | 0 | 0 | 200 | 50 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 9 | 100 | 220 | 0 | 0 | 900 | 0 | 5212 | 12225 | 90.75
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 17 | 112 | 0 | 0 | 0 | 0 | 0 | 450 | 282 | 350 | 0 | 0 | 270 | 0 | 0 | 0 | 52 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 34 | 430 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 950 | 0 | 51 | 0 | 0 | 0 | 354 | 340 | 40 | 219 | 32 | 17 | 80 | 200 | 9 | 14 | 114 | 48 | 0 | 0 | 0 | 250 | 320 | 303 | 32 | 30 | 128 | 0 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 48 | 93 | 53 | 0 | 0 | 12 | 6851 | 730 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 840 | 0 | 1025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 177 | 0 | 0 | 0 | 326 | 0 | 0 | 200 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 9 | 92 | 180 | 0 | 0 | 800 | 0 | 4857 | 11708 | 90.83
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 17 | 64 | 0 | 0 | 0 | 0 | 0 | 450 | 273 | 350 | 0 | 0 | 260 | 0 | 0 | 0 | 17 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 34 | 430 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 914 | 0 | 43 | 0 | 0 | 0 | 355 | 340 | 40 | 221 | 32 | 17 | 80 | 200 | 9 | 14 | 110 | 46 | 0 | 0 | 0 | 245 | 320 | 300 | 32 | 30 | 129 | 0 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 48 | 84 | 64 | 0 | 0 | 12 | 6707 | 813 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 774 | 0 | 860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 167 | 0 | 0 | 0 | 250 | 0 | 0 | 200 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 90 | 180 | 0 | 0 | 500 | 0 | 4250 | 10957 | 90.91
06:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 300 | 288 | 250 | 0 | 0 | 287 | 0 | 0 | 1 | 0 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 32 | 390 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 754 | 3 | 5 | 0 | 0 | 0 | 280 | 280 | 40 | 196 | 31 | 17 | 80 | 68 | 9 | 14 | 39 | 44 | 0 | 6 | 0 | 245 | 320 | 332 | 32 | 30 | 130 | 0 | 0 | 50 | 30 | 0 | 18 | 165 | 0 | 48 | 94 | 80 | 0 | 1.42 | 12 | 5855.42 | 814 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 767 | 0 | 847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 1.67 | 150 | 0 | 159 | 0 | 0 | 0 | 250 | 0 | 0.17 | 200 | 49 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 140 | 2 | 100 | 180 | 0 | 0 | 500 | 0 | 4244.14 | 10099.56 | 90.99
07:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 300 | 293 | 250 | 0 | 0 | 300 | 0 | 0 | 7 | 0 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 2 | 167 | 0 | 16 | 408 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 707 | 1 | 5 | 0 | 0 | 0 | 280 | 280 | 40 | 208 | 31 | 0 | 80 | 0 | 7 | 6 | 0 | 34 | 0 | 1 | 0 | 255 | 320 | 335 | 32 | 30 | 138 | 0 | 0 | 52 | 30 | 0 | 18 | 165 | 0 | 55 | 112 | 80 | 0 | 1.94 | 12 | 5718.94 | 814 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 764 | 0 | 846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 6.84 | 161 | 0 | 172 | 0 | 0 | 0 | 351 | 0 | 0.48 | 200 | 50 | 0 | 4 | 0 | 0 | 0 | 0.8 | 3 | 0.03 | 0 | 140 | 4 | 100 | 180 | 0 | 0 | 500 | 0 | 4389.15 | 10108.09 | 91.07
08:00 | 0 | 17 | 4 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 0 | 13 | 32 | 0 | 0 | 0 | 0 | 0 | 340 | 294 | 280 | 0 | 0 | 313 | 0 | 0 | 12 | 0 | 23.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 1 | 167 | 0 | 8 | 426 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 725 | 2 | 16 | 0 | 0 | 0 | 338 | 340 | 40 | 217 | 30 | 0 | 80 | 0 | 9 | 10 | 0 | 46 | 0 | 4 | 0 | 245 | 320 | 387 | 32 | 30 | 148 | 0 | 0 | 70 | 30 | 0 | 18 | 165 | 0 | 45 | 90 | 65 | 0 | 19.73 | 12 | 6088.23 | 767 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 761 | 0 | 844.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 16.23 | 170 | 0 | 181 | 0 | 0 | 0 | 397 | 0 | 1.9 | 200 | 52 | 0 | 9 | 0 | 0 | 0 | 0 | 18 | 0.09 | 0 | 140 | 3 | 110 | 180 | 0 | 0 | 500 | 0 | 4482.18 | 10570.41 | 91.14
09:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 2 | 0 | 20 | 32 | 0 | 0 | 5 | 40 | 0 | 450 | 294 | 84 | 0 | 5 | 295 | 0 | 0 | 8 | 35 | 23.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 10 | 0 | 1 | 167 | 0 | 0 | 515 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1000 | 2 | 51 | 1 | 45 | 0 | 355 | 340 | 46 | 199 | 31 | 1 | 80 | 1 | 9 | 14 | 17 | 46 | 0 | 7 | 0 | 240 | 320 | 385 | 32 | 30 | 156 | 0 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 45 | 75 | 65 | 1 | 4.97 | 11 | 6618.47 | 766 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.72 | 754 | 0 | 835.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 19.83 | 172 | 0 | 189 | 0 | 0 | 0 | 414 | 0 | 2.03 | 200 | 54 | 0 | 23 | 0 | 0 | 0 | 4.7 | 73 | 0.14 | 0 | 140 | 6 | 100 | 180 | 0 | 0 | 500 | 0 | 4616.91 | 11235.38 | 91.21
10:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 17 | 0 | 50 | 34 | 0 | 0 | 17 | 54 | 0 | 450 | 295 | 0 | 0 | 17 | 284 | 0 | 0 | 10 | 35 | 23.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 24 | 0 | 0 | 167 | 0 | 0 | 501 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 980 | 3 | 51 | 20 | 45 | 0 | 355 | 340 | 51 | 196 | 29 | 22 | 80 | 17 | 9 | 14 | 17 | 38 | 0 | 3 | 0 | 240 | 320 | 358 | 32 | 30 | 155 | 0 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 48 | 82 | 32 | 0 | 37.01 | 8 | 6596.51 | 815 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.35 | 750 | 0 | 867.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 15.09 | 185 | 0 | 186 | 0 | 0 | 0 | 414 | 0 | 1.67 | 200 | 54 | 0 | 33 | 0 | 0 | 0 | 4 | 54 | 0.27 | 0 | 150 | 6 | 120 | 220 | 0 | 0 | 510 | 0 | 4776.5 | 11373.01 | 91.28
11:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 17 | 0 | 50 | 48 | 0 | 0 | 17 | 54 | 0 | 450 | 295 | 0 | 0 | 0 | 288 | 0 | 0 | 20 | 17 | 23.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 1 | 167 | 0 | 4 | 510 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 1055 | 3 | 51 | 0 | 61 | 0 | 355 | 340 | 48 | 197 | 29 | 34 | 80 | 17 | 8 | 14 | 17 | 40 | 0 | 27 | 0 | 240 | 320 | 384 | 32 | 30 | 153 | 0 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 67 | 75 | 33 | 0 | 10.6 | 4 | 6705.1 | 815 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.31 | 732 | 0 | 909.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 26.65 | 178 | 0 | 184 | 0 | 0 | 0 | 414 | 0 | 2.43 | 200 | 50 | 0 | 22 | 0 | 0 | 0 | 8 | 154 | 0.24 | 0 | 170 | 5 | 120 | 220 | 0 | 0 | 610 | 0 | 5092.93 | 11798.03 | 91.36
12:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 17 | 0 | 50 | 48 | 0 | 0 | 17 | 54 | 0 | 450 | 287 | 0 | 0 | 0 | 289 | 61 | 0 | 20 | 17 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 26 | 0 | 1 | 167 | 0 | 5 | 525 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1100 | 1 | 51 | 0 | 83 | 0 | 356 | 340 | 51 | 200 | 25 | 50 | 80 | 17 | 6 | 14 | 17 | 44 | 0 | 41 | 0 | 240 | 320 | 374 | 32 | 30 | 156 | 0 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 67 | 104 | 35 | 1 | 6.8 | 6 | 6888.8 | 815 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.63 | 745 | 0 | 915.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 0 | 19.97 | 182 | 0 | 189 | 0 | 0 | 0 | 414 | 0 | 2.4 | 200 | 50 | 0 | 24 | 0 | 0 | 0 | 7.7 | 210 | 0.22 | 0 | 172 | 5 | 120 | 220 | 0 | 0 | 750 | 0 | 5303 | 12191.8 | 91.44
13:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 17 | 0 | 50 | 32 | 0 | 0 | 17 | 17 | 0 | 450 | 296 | 0 | 0 | 0 | 289 | 98 | 0 | 33 | 17 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 48 | 0 | 3 | 167 | 0 | 12 | 510 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1106 | 1 | 51 | 0 | 120 | 0 | 355 | 340 | 52 | 197 | 32 | 63 | 80 | 17 | 10 | 14 | 42 | 46 | 0 | 26 | 0 | 240 | 320 | 386 | 32 | 30 | 155 | 0 | 0 | 81 | 30 | 0 | 18 | 165 | 0 | 45 | 124 | 34 | 2 | 8.6 | 6 | 7002.6 | 816 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.24 | 790 | 0 | 905.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 32.64 | 181 | 0 | 190 | 0 | 0 | 0 | 414 | 0 | 2.38 | 200 | 50 | 35 | 34 | 30 | 0 | 0 | 4 | 168 | 0.29 | 0 | 168 | 4 | 120 | 220 | 0 | 0 | 960 | 0 | 5544.22 | 12546.82 | 91.62
14:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 17 | 0 | 0 | 450 | 293 | 0 | 0 | 0 | 295 | 98 | 0 | 15 | 17 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 48 | 0 | 3 | 167 | 0 | 7 | 532 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1120 | 1 | 51 | 0 | 148 | 0 | 351 | 340 | 53 | 202 | 31 | 59 | 80 | 17 | 9 | 14 | 52 | 48 | 0 | 5 | 0 | 240 | 320 | 388 | 32 | 30 | 143 | 0 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 45 | 124 | 34 | 2 | 31.37 | 6 | 6968.37 | 815 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.83 | 833 | 0 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 22.79 | 183 | 0 | 189 | 0 | 0 | 0 | 366 | 0 | 2.1 | 200 | 50 | 35 | 29 | 34 | 0 | 0 | 4.1 | 128 | 0.11 | 0 | 169 | 5 | 120 | 220 | 0 | 0 | 1000 | 0 | 5510.93 | 12479.3 | 91.6
15:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 0 | 18 | 25 | 0 | 0 | 17 | 0 | 0 | 450 | 298 | 0 | 0 | 0 | 297 | 98 | 0 | 12 | 17 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 48 | 0 | 1 | 167 | 0 | 8 | 524 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1120 | 2 | 51 | 0 | 152 | 0 | 350 | 340 | 53 | 204 | 31 | 55 | 80 | 17 | 9 | 14 | 52 | 46 | 0 | 6 | 0 | 240 | 320 | 388 | 32 | 30 | 146 | 5 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 66.4 | 104 | 34 | 1 | 17.55 | 6 | 6970.95 | 820 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.84 | 850 | 0 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 37.38 | 183 | 0 | 196 | 0 | 0 | 0 | 374 | 0 | 3.72 | 200 | 52 | 35 | 25 | 34 | 0 | 0 | 1.9 | 144 | 0.15 | 0 | 171 | 4 | 120 | 220 | 0 | 0 | 1000 | 0 | 5550.99 | 12521.94 | 91.68
16:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 43 | 32 | 0 | 0 | 17 | 0 | 0 | 450 | 296 | 0 | 0 | 0 | 296 | 98 | 0 | 17 | 17 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 48 | 0 | 1 | 167 | 0 | 10 | 524 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1112 | 2 | 51 | 0 | 157 | 0 | 349 | 340 | 52 | 203 | 29 | 54 | 80 | 18 | 9 | 14 | 56 | 44 | 0 | 25 | 0 | 240 | 320 | 375 | 32 | 30 | 143 | 5 | 0 | 83 | 30 | 0 | 18 | 165 | 0 | 67 | 119 | 34 | 1 | 6.6 | 6 | 6993.6 | 821 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.13 | 824 | 0 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 21.3 | 178 | 0 | 194 | 0 | 0 | 0 | 368 | 0 | 1.75 | 200 | 50 | 35 | 6 | 34 | 0 | 0 | 4.4 | 95 | 0.09 | 0 | 170 | 5 | 120 | 220 | 0 | 0 | 995 | 0 | 5416.67 | 12410.27 | 91.76
17:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 65 | 32 | 0 | 0 | 17 | 0 | 0 | 380 | 294 | 0 | 0 | 0 | 287 | 99 | 0 | 7 | 17 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 48 | 0 | 0 | 167 | 0 | 6 | 524 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 960 | 2 | 51 | 0 | 157 | 0 | 352 | 340 | 49 | 197 | 29 | 55 | 80 | 31 | 9 | 14 | 70 | 42 | 0 | 9 | 0 | 240 | 320 | 370 | 32 | 30 | 134 | 5 | 0 | 83 | 30 | 0 | 18 | 165 | 0 | 67 | 112 | 34 | 0 | 6.75 | 6 | 6735.75 | 820 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.29 | 775 | 0 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 4.29 | 172 | 0 | 188 | 0 | 0 | 0 | 347 | 0 | 0.38 | 200 | 50 | 35 | 8 | 34 | 0 | 0 | 1 | 47 | 0.11 | 0 | 169 | 3 | 120 | 180 | 0 | 0 | 950 | 0 | 5137.07 | 11872.82 | 91.84
18:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 87 | 32 | 0 | 0 | 17 | 0 | 3 | 380 | 294 | 0 | 0 | 0 | 282 | 100 | 0 | 1 | 17 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 48 | 0 | 0 | 167 | 0 | 16 | 500 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 940 | 0 | 51 | 3 | 102 | 0 | 300 | 300 | 47 | 191 | 32 | 56 | 80 | 34 | 26 | 14 | 70 | 42 | 0 | 3 | 0 | 240 | 320 | 355 | 32 | 30 | 133 | 5 | 0 | 61 | 30 | 0 | 18 | 165 | 0 | 79 | 120 | 34 | 0 | 3.41 | 8 | 6546.41 | 820 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.41 | 796 | 0 | 945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 2.68 | 170 | 0 | 186 | 0 | 0 | 0 | 338 | 0 | 0.26 | 200 | 51 | 35 | 2 | 34 | 0 | 0 | 0.5 | 11 | 0.04 | 0 | 165 | 4 | 120 | 180 | 0 | 0 | 942 | 0 | 5104.89 | 11651.3 | 91.92
19:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 0 | 17 | 0 | 91 | 44 | 0 | 0 | 17 | 17 | 10 | 340 | 291 | 0 | 0 | 0 | 314 | 100 | 0 | 0 | 52 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 33 | 0 | 0 | 48 | 0 | 0 | 167 | 0 | 23 | 537 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1135 | 0 | 51 | 12 | 157 | 0 | 347 | 340 | 48 | 216 | 32 | 68 | 80 | 45 | 27 | 14 | 88 | 50 | 8 | 0 | 32 | 240 | 320 | 391 | 32 | 30 | 139 | 5 | 0 | 84 | 30 | 0 | 18 | 165 | 0 | 85 | 127 | 34 | 0 | 0 | 11 | 7306 | 773 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 945 | 17 | 1255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 190 | 0 | 0 | 0 | 414 | 0 | 0 | 200 | 50 | 58 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 211 | 7 | 128 | 220 | 0 | 0 | 968 | 0 | 5764 | 13070 | 92
19:30 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 17 | 0 | 149 | 80 | 0 | 0 | 17 | 54 | 16 | 450 | 290 | 0 | 0 | 0 | 293 | 100 | 0 | 0 | 90 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 33 | 0 | 0 | 100 | 24 | 0 | 167 | 0 | 25 | 520 | 0 | 0 | 3 | 0 | 0 | 220 | 0 | 0 | 0 | 1100 | 0 | 51 | 12 | 157 | 0 | 356 | 340 | 48 | 200 | 32 | 95 | 80 | 117 | 29 | 14 | 96 | 50 | 8 | 0 | 32 | 240 | 320 | 340 | 32 | 30 | 147 | 5 | 0 | 82 | 30 | 0 | 18 | 165 | 0 | 86 | 148 | 44 | 0 | 0 | 11 | 7707 | 773 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 17 | 1387 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 200 | 0 | 0 | 0 | 414 | 0 | 0 | 200 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 7 | 120 | 220 | 0 | 0 | 1110 | 0 | 6414 | 14121 | 92
20:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 17 | 0 | 148 | 80 | 0 | 0 | 17 | 54 | 16 | 450 | 292 | 0 | 0 | 0 | 285 | 101 | 0 | 0 | 90 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 33 | 0 | 0 | 100 | 24 | 0 | 167 | 0 | 27 | 500 | 0 | 0 | 7 | 0 | 0 | 220 | 0 | 0 | 0 | 1070 | 0 | 51 | 12 | 163 | 0 | 356 | 340 | 49 | 193 | 32 | 88 | 80 | 95 | 29 | 14 | 100 | 50 | 8 | 0 | 32 | 240 | 320 | 330 | 32 | 30 | 154 | 0 | 0 | 82 | 30 | 0 | 18 | 165 | 0 | 86 | 158 | 56 | 0 | 0 | 11 | 7650 | 773 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1108 | 17 | 1409 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 193 | 0 | 0 | 0 | 339 | 0 | 0 | 200 | 50 | 115 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 3 | 120 | 220 | 0 | 0 | 1103 | 0 | 6403 | 14053 | 92.08
21:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 17 | 0.36 | 149 | 80 | 0 | 0 | 17 | 54 | 16 | 450 | 296 | 0 | 0 | 0 | 275 | 101 | 0 | 0 | 90 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 33 | 0 | 0 | 70 | 24 | 0 | 127 | 0 | 29 | 500 | 0 | 0 | 14 | 0 | 0 | 220 | 0 | 0 | 0 | 1050 | 0 | 51 | 12 | 157 | 0 | 356 | 340 | 49 | 186 | 32 | 95 | 80 | 106 | 29 | 16 | 94 | 50 | 8 | 0 | 32 | 245 | 320 | 345 | 32 | 30 | 149 | 0 | 0 | 82 | 30 | 0 | 18 | 165 | 0 | 86 | 158 | 67 | 0 | 0 | 11 | 7556.36 | 821 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1106 | 17 | 1405 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 180 | 0 | 0 | 0 | 393 | 0 | 0 | 200 | 50 | 115 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 9 | 120 | 220 | 0 | 0 | 1102 | 0 | 6482 | 14038.36 | 92.18
22:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 32 | 149 | 64 | 0 | 0 | 0 | 17 | 16 | 450 | 295 | 0 | 0 | 0 | 276 | 101 | 0 | 0 | 90 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 33 | 0 | 0 | 70 | 0 | 0 | 127 | 0 | 29 | 500 | 0 | 0 | 19 | 0 | 0 | 222 | 0 | 0 | 0 | 1064 | 0 | 51 | 12 | 173 | 0 | 355 | 340 | 50 | 191 | 32 | 94 | 80 | 103 | 29 | 16 | 98 | 52 | 0 | 0 | 32 | 250 | 320 | 345 | 32 | 30 | 148 | 0 | 0 | 82 | 30 | 0 | 18 | 165 | 0 | 86 | 149 | 63 | 0 | 0 | 11 | 7482 | 820 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1108 | 17 | 1413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 179 | 0 | 0 | 0 | 334 | 0 | 0 | 200 | 50 | 70 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 9 | 114 | 220 | 0 | 0 | 1105 | 0 | 6461 | 13943 | 92.28
23:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 42 | 139 | 64 | 0 | 0 | 0 | 17 | 16 | 450 | 298 | 0 | 0 | 0 | 281 | 101 | 0 | 0 | 90 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 33 | 0 | 0 | 24 | 0 | 0 | 167 | 0 | 32 | 502 | 0 | 0 | 17 | 0 | 0 | 226 | 0 | 0 | 0 | 1070 | 0 | 51 | 0 | 173 | 0 | 355 | 335 | 50 | 192 | 32 | 94 | 80 | 105 | 28 | 17 | 98 | 32 | 0 | 0 | 32 | 255 | 320 | 345 | 32 | 30 | 136 | 0 | 0 | 82 | 30 | 0 | 18 | 165 | 0 | 85 | 150 | 65 | 0 | 0 | 11 | 7456 | 820 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 1410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 168 | 0 | 0 | 0 | 338 | 0 | 0 | 200 | 50 | 35 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 9 | 114 | 220 | 0 | 0 | 1105 | 0 | 6383 | 13839 | 92.36
Total KWH | 0 | 1218240 | 344933 | 0 | 0 | 0 | 0 | 0 | 8647200 | 0 | 0 | 171360 | 129600 | 1410336 | 1460160 | 6524 | 0 | 227147 | 436320 | 94080 | 9981500 | 7020771 | 3139677 | 0 | 39134 | 6926767 | 1224000 | 0 | 153314 | 1068000 | 494400 | 522720 | 0 | 0 | 0 | 0 | 0 | 0 | 570720 | 184752 | 10168 | 0 | 758400 | 47040 | 14039 | 3969620 | 0 | 498240 | 11818181.82 | 0 | 0 | 61920 | 0 | 0 | 5118341 | 0 | 0 | 0 | 24016361 | 22545 | 1074088 | 133818 | 1957091 | 0 | 8541900 | 8028000 | 1124640 | 4935000 | 727488 | 1128000 | 1884310 | 1860000 | 350280 | 315560 | 1600560 | 1085760 | 22282 | 149082 | 206448 | 5872500 | 7701600 | 8883000 | 760000 | 687120 | 3430554.5 | 26712 | 0 | 1930560 | 711936 | 0 | 432000 | 3477890 | 0 | 1506000 | 2635200 | 1147200 | 8200 | 176380 | 232080 | 166549750.32 | 19487273 | 3048480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 483120 | 20974540 | 139200 | 25628120 | 0 | 0 | 0 | 70176 | 0 | 10496 | 0 | 0 | 0 | 606100 | 16503 | 261000 | 4110727 | 0 | 4577427 | 0 | 0 | 0 | 8714909 | 0 | 23802 | 4884000 | 1184290 | 860546 | 216485 | 1021910 | 0 | 0 | 44867.16 | 1116720 | 1945 | 0 | 4189000 | 139562 | 2673000 | 5201260 | 0 | 0 | 21303272.73 | 0 | 130988730.89 | 297538481.21

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 05-06-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-06-2025 | during | 05-06-2025 | during | 05-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0.01 | 0.01 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 363 | 372 | 400.75 | 400.75 | 392 | 392 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 287 | 290 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 61 | 100 | 208.13 | 208.13 | 61 | 61 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 289 | 293 | 335 | 335 | 313 | 313 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 17 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 48 | 80 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 17 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 24 | 20 | 33 | 33 | 28 | 28 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 16 | 52.19 | 52.19 | 24 | 24 | Fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 50 | 149 | 149 | 149 | 149 | 149 | Machine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 105 | 105 | 105 | 100 | 100 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 16 | 104 | 104 | 90 | 90 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 54 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 20 | 0 | 25 | 0 | 25 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 470 | 470 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 90 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6123 | 5939.724 | 1795 | 2091 | 5217.1 | 5286.1 | 3472.38 | 3541.38
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 17 | 17 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 1 | 0 | 17 | 0 | 17 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 3 | 0 | 0 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 167 | 167 | 165 | 165 | 165 | 165 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 222 | 220 | 221 | 221 | 221 | 221 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 56 | 80 | 80 | 80 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 33 | 0 | 0 | 34 | 34 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 26 | 100 | 0 | 0 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 5 | 25 | 0 | 0 | 0 | 0 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1 | 0 | 0 | 0 | 0 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 24 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1100 | 1100 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 6 | 9 | 24 | 4 | 24 | 4 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 525 | 520 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 2053 | 2201 | 3360.72 | 3347.72 | 3560.22 | 3523.22
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 200 | 200 | 221.43 | 221.43 | 221.43 | 221.43 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 356 | 356 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 340 | 340 | 340 | 340 | 340 | machine problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 25 | 32 | 0 | 0 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 51 | 48 | 55 | 55 | 52 | 52 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 83 | 157 | 195 | 195 | 110 | 110 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 12 | 150 | 150 | 135 | 135 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 32 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 80 | 163 | 163 | 97 | 97 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 117 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 44 | 50 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 14 | 17.75 | 17.75 | 15 | 15 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 96 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 6 | 29 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 50 | 95 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 41 | 0 | 35 | 0 | 35 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2891.241 | 1375 | 1717 | 2382.73 | 2347.73 | 2210.98 | 2175.98
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-06-2025 | during | 05-06-2025 | during | 05-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 35 | 44 | 157.5 | 157.5 | 80 | 80 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 104 | 148 | 200 | 200 | 150 | 150 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 67 | 86 | 115 | 115 | 105 | 105 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 6.8 | 0 | 38 | 0 | 38 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 11 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 219.8 | 289 | 589.1 | 549 | 441.6 | 401.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 32 | 32 | 36 | 36 | 36 | 36 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 147 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 82 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 165 | 165 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 5 | 0 | 0 | 7 | 7 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 240 | 240 | 341 | 341 | 270 | 270 | Gas shortage
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 374 | 340 | 385 | 385 | 385 | 385 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2400 | 2325 | 1446 | 1409 | 1407 | 1407 | 1343 | 1343
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 815 | 773 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 84 | 145 | 410 | 410 | 300 | 300 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 90 | 90 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 63.63 | 0 | 88 | 0 | 88 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 745 | 1120 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3699.2 | 1707.63 | 2055 | 3264.2 | 3176.2 | 3139 | 3051
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 5 | 7 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 750 | 1110 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 172 | 202 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.22 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1267.22 | 1659 | 2172 | 2171 | 2162 | 2161
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 182 | 186 | 214 | 214 | 200 | 200 | -
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 189 | 200 | 220 | 220 | 220 | 220 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.4 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 915.08 | 1387 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 19.97 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 114 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3460 | 3452.96 | 1836.45 | 2222 | 3192.47 | 3025.87 | 3178.47 | 3011.87
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 50 | 50 | 50 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 200 | 200 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.7 | 0 | 5.6 | 0 | 5.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 24 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 210 | 0 | 107.47 | 0 | 107.47 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 491.7 | 478 | 653.07 | 512 | 653.07 | 512
System Total |  |  |  |  | 28798.2 | 27044.055 | 12191.8 | 14121 | 22238.39 | 21822.62 | 20160.72 | 19720.95
Forecast Scenario (05-06-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13550 |  | 0 |  | 13550
|  |  |  | 1:00 | 13000 |  | 0 |  | 13000
|  |  |  | 2:00 | 12450 |  | 0 |  | 12450
|  |  |  | 3:00 | 11920 |  | 0 |  | 11920
|  |  |  | 4:00 | 11400 |  | 0 |  | 11400
|  |  |  | 5:00 | 10650 |  | 0 |  | 10650
|  |  |  | 6:00 | 9800 |  | 0 |  | 9800
|  |  |  | 7:00 | 9800 |  | 0 |  | 9800
|  |  |  | 8:00 | 10000 |  | 0 |  | 10000
|  |  |  | 9:00 | 10200 |  | 0 |  | 10200
|  |  |  | 10:00 | 10500 |  | 0 |  | 10500
|  |  |  | 11:00 | 10600 |  | 0 |  | 10600
|  |  |  | 12:00 | 10650 |  | 0 |  | 10650
|  |  |  | 13:00 | 10700 |  | 0 |  | 10700
|  |  |  | 14:00 | 10600 |  | 0 |  | 10600
|  |  |  | 15:00 | 10650 |  | 0 |  | 10650
|  |  |  | 16:00 | 10500 |  | 0 |  | 10500
|  |  |  | 17:00 | 10100 |  | 0 |  | 10100
|  |  |  | 18:00 | 9900 |  | 0 |  | 9900
|  |  |  | 18:30 | 12100 |  | 0 |  | 12100
|  |  |  | 19:00 | 12700 |  | 0 |  | 12700
|  |  |  | 19:30 | 13100 |  | 0 |  | 13100
|  |  |  | 20:00 | 13100 |  | 0 |  | 13100
|  |  |  | 21:00 | 13100 |  | 0 |  | 13100
|  |  |  | 22:00 | 13000 |  | 0 |  | 13000
|  |  |  | 23:00 | 12800 |  | 0 |  | 12800
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 10650.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 13100.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13000.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 270.27 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:29 hrs on 05-06-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 04-06-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12191.8 | MW | 12:00 Hr. | Energy Generated |  |  | 297.5385 |  | MKWHr.
| Day Peak Demand |  |  | 12191.8 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.083 |  | MKWHr.
| Evening Peak Generation |  |  | 14121 | MW | 19:30 Hr. | Energy Demand |  |  | 297.6215 |  | MKWHr.
| Evening Peak Demand |  |  | 14121 | MW | 19:30 Hr. | Maximum Temperature |  |  | 30.4 |  | °C
| Minimum Generation of the Day |  |  | 10099.56 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1019.94 |  | MMCFD
| Maximum Generation of the Day |  |  | 14121 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 5.9448 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 37.957 | 0 | 6.6058 | 0 | 0 | 0.15331 | 0 | 0 | 44.7162 | Gas | 135.6881 | Gas | 491088372.435
| Chattogram Zone |  |  | 5.6166 | 35.8345 | 1.0623 | 0 | 3.9696 | 0.036584 | 0 | 0.57072 | 47.0903 | Coal | 88.3696 | Coal | 612217522.1991
| Cumilla Zone |  |  | 28.5881 | 0 | 5.3014 | 0 | 0 | 0.14908 | 1.0858 | 0 | 35.1243 | HFO | 19.4616 | HFO | 362550329.73
| Mymensingh Zone |  |  | 1.1472 | 0 | 4.3733 | 0 | 0 | 0.18458 | 0 | 0 | 5.7051 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 33.9139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.9139 | Hydro | 3.9696 | Hydro | 396962
| Khulna Zone |  |  | 3.0485 | 20.9745 | 0.1392 | 0 | 0 | 0.48312 | 19.4873 | 0 | 44.1326 | Solar | 3.2776 | Solar | 54632627.5776
| Barishal Zone |  |  | 8.0138 | 25.4923 | 0 | 0 | 0 | 0.001945 | 0 | 0 | 33.508 | Import | 46.2012 | Import | 239573880.34
| Rajshahi Zone |  |  | 17.4031 | 0 | 0.097175 | 0 | 0 | 0.8909 | 25.6281 | 0 | 44.0193 | Wind | 0.57072 | Wind | 8355340.8
| Rangpur Zone |  |  | 0 | 6.0683 | 1.8825 | 0 | 0 | 1.3781 | 0 | 0 | 9.3288
| Total |  |  | 135.6881 | 88.3696 | 19.4616 | 0 | 3.9696 | 3.2776 | 46.2012 | 0.57072 | 297.5385
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 491088372.435 |  | Hydro | 396962
|  |  |  | Coal | 612217522.1991 |  | Solar | 54632627.5776
|  |  |  | HFO | 362550329.73 |  | Import | 239573880.34
|  |  |  | HSD | 0 |  | Wind | 8355340.8
[5 empty] | Total: | 176,88,15,035 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.4873 | Peak Hr Flow | 773.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 7264600.05 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 25.6281 | Peak Hr Flow | 1387.00 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 452 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.0858 | Peak Hr Flow | 50.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 680 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 46.2012 | Peak Hr Flow | 2210.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4568
|  |  |  | Chattogram |  | 0 |  | 1260
|  |  |  | Cumilla |  | 0 |  | 1308
|  |  |  | Mymensingh |  | 0 |  | 1167
|  |  |  | Sylhet |  | 0 |  | 519
|  |  |  | Khulna |  | 0 |  | 1747
|  |  |  | Barishal |  | 0 |  | 410
|  |  |  | Rajshahi |  | 0 |  | 1514
|  |  |  | Rangpur |  | 0 |  | 1001
|  |  |  | Total |  | 0 |  | 13494
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[5 empty] | Total | 300 |  |  |  | Total | 400
|  |  |  | Total Unavailable Capacity |  |  |  | 700
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:10 | 09:28 | Jamalpur 132/33kV S/S T-2 HT Scheduled S/D Due to 33kv bus sections isolalor temperature | [7 empty] | 25.0MW load
|  |  | rediuse | [7 empty] | interrup.
| 08:10 | 09:28 | Jamalpur 132/33kV S/S T-2 LT Scheduled S/D Due to 33kv bus sections isolalor temperature | [7 empty] | 25.0MW load
|  |  | rediuse | [7 empty] | interrup.
| 08:12 | 10:04 | Ramganj 132/33kV S/S Transformer-01 HT Scheduled S/D Due to Temperature Bay Junction | [7 empty] | 10.0MW load
|  |  | Point measurement | [7 empty] | interrup.
| 08:13 | 09:11 | Halishahar 132/33kV S/S 405T(TR-1) HT Tripped showing Transformer relay, relays Due to | [7 empty] | 25.0MW load
|  |  | Birds nest | [7 empty] | interrup.
| 08:13 | 09:12 | Halishahar 132/33kV S/S 405T(TR-1) LT Tripped showing Transformer relay relays Due to | [7 empty] | 25.0MW load
|  |  | Birds nest | [7 empty] | interrup.
| 08:16 | 10:04 | Ramganj 132/33kV S/S Transformer-01 LT Scheduled S/D Due to Temperature Bay Junction | [7 empty] | 10.0MW load
|  |  | Point measurement | [7 empty] | interrup.
|  | 08:45 | Goalpara 132/33kV S/S T-6 LT is restored.
|  | 08:45 | Goalpara 132/33kV S/S T-6 HT is restored.
| 08:45 | 10:30 | Jaldhaka 132/33kV S/S 416T-2 HT Forced S/D Due to 33KV Bus Clamp of Jaldhaka NESCO Red | [7 empty] | 30.0MW load
|  |  | Hot | [7 empty] | interrup.
| 08:45 | 10:30 | Jaldhaka 132/33kV S/S 416T-2 LT Forced S/D Due to 33KV Bus Clamp of Jaldhaka NESCO Red | [7 empty] | 30.0MW load
|  |  | Hot | [7 empty] | interrup.
| 08:52 |  | Meghnaghat CCPP(Summit)-2 Shutdown with remarks:- ST
|  | 08:54 | Bagerhat 132/33kV S/S Transformer-1 (403T) HT is restored.
|  | 08:55 | Bagerhat 132/33kV S/S Transformer-1 (403T) LT is restored.
|  | 08:55 | Goalpara 132/33kV S/S T-5 LT is restored.
|  | 08:55 | Goalpara 132/33kV S/S T-5 HT is restored.
| 09:02 |  | Meghnaghat CCPP(Summit)-2 Shutdown with remarks:- GT
| 09:02 |  | Summit Meghnaghat-2 589 MW CCPP was forced shutdown due to a red-hot at 400kV circuit.
| 09:05 | 18:38 | Lalmonirhat-Rangpur 132 kV Ckt-2 Scheduled S/D from Rangpur 132/33kV end Due to REMOVE
RED HOT
| 09:30 | 10:30 | Bagerhat 132/33kV S/S Transformer-2 (413 T) LT Scheduled S/D Due to 33 kv CT overheat
maintenance work
| 09:31 | 10:28 | Bagerhat 132/33kV S/S Transformer-2 (413 T) HT Scheduled S/D Due to 33 kv CT overheat
maintenance work
| 09:31 | 16:51 | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T LT Project Work S/D Due to T-01 main-1
relay testing
| 09:31 | 16:35 | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T HT Project Work S/D Due to T-01 main-1
relay testing
| 09:34 | 10:30 | Baroirhat-Feni 132 kV Ckt-2 Forced S/D from Baroirhat 132/33kV end Due to Feni ss taken
s/d
|  | 09:45 | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-1 is restored.
| 09:45 | 11:01 | Goalpara 132/33kV S/S Bus 1 Scheduled S/D Due to Third transformer instelation Works.
|  | 09:46 | Aminbazar 400/230/132kV S/S Gopalganj-1 is restored.
| 09:47 | 13:20 | Gopalganj 132/33kV S/S T1 HT Scheduled S/D Due to Hot spot maintenance
| 09:50 | 10:26 | Jamalpur 132/33kV S/S T-4 LT Scheduled S/D Due to 33kv incomming breaker R -phase
temperature rediuse
| 09:50 | 10:26 | Jamalpur 132/33kV S/S T-4 HT Scheduled S/D Due to 33kv incomming breaker R -phase
temperature rediuse
| 09:56 | 12:25 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT Scheduled S/D Due to Red
hot Maintanence
| 09:56 | 12:17 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) HT Scheduled S/D Due to Red
hot Maintanence
|  | 10:10 | Cumilla(S) 132/33kV S/S TR-1 LT is restored.
|  | 10:10 | Cumilla(S) 132/33kV S/S TR-1 HT is restored.
|  | 10:13 | Gopalganj 132/33kV S/S T2 HT is restored.
|  | 10:14 | Gopalganj 132/33kV S/S T2 LT is restored.
|  | 10:16 | Gopalganj(N)-Madaripur 132kV Ckt-1 is restored.
| 10:22 | 13:55 | Gopalganj(N)-Madaripur 132kV Ckt-3 Scheduled S/D from Madaripur 132/33kV end Due to Red
hot maintaining and from Gopalganj 400/132kVend.
| 10:25 |  | Mongla 132/33kV S/S T-2 HT Project Work S/D Due to DS Alignment Problem.
| 10:25 |  | Mongla 132/33kV S/S T-2 LT Project Work S/D Due to DS Alignment problem.
| 10:37 | 18:34 | Bheramara 230/132kV S/S STG (NW) Tripped showing 86B relays.
| 10:46 | 13:20 | Gopalganj 132/33kV S/S T1 LT Scheduled S/D Due to Hot spot maintenance
| 11:17 | 11:59 | Goalpara 132/33kV S/S Bus 2 Scheduled S/D Due to Third Transformer Instaletion Works.
| 11:25 | 11:40 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing WTI Trip ( micon ) , Lockout Relay
relays Due to Rain
| 11:25 | 11:40 | Shahjibazar 132/33kV S/S TR-02 HT Tripped showing WTI Trip ( micon ), Lockout Relay.
relays Due to Rain
| 11:48 | 20:39 | Hathazari 230/132/33kV S/S MT-03 HT Scheduled S/D
| 11:48 | 20:39 | Hathazari 230/132/33kV S/S MT-03 LT Scheduled S/D
| 11:53 |  | Siddhirganj GT-1 was sync.
| 12:00 |  | Day Peak Generation: 12186 MW.
|  | 12:39 | Daudkandi-Sonargaon 132 kV Ckt-2 is restored.
| 13:04 | 14:21 | Khulshi 132/33kV S/S 405T (T1) HT Tripped showing Lockout relays Due to Moisture show
within PRD junction box.
| 13:35 | 16:32 | Meghnaghat 400/230kV S/S Meghnaghat-Summit PP 400KV Ckt-1 Scheduled S/D Due to Summit Bay
Line DS Maintenance
|  | 14:29 | Barishal 230/132kV S/S T-5 HT is restored.
|  | 14:34 | Barishal 230/132kV S/S T-5 LT is restored.
| 15:04 | 16:33 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Forced S/D Due to Jack bus to DS jumper changed | [7 empty] | 40.0MW load
|  |  | of 33kv side of 109 PTR-2 | [7 empty] | interrup.
| 15:04 | 16:31 | Sreepur 230/132/33kV S/S 132/33 kV T-2 HT Forced S/D | [7 empty] | 40.0MW load
interrup.
| 15:39 | 17:55 | Cumilla(S) 132/33kV S/S 53.2MW Lakthanavi Forced S/D Due to work for lakdhanavi end
|  | 15:53 | Jashore 132/33kV S/S Cap. Bank-1 is restored.
| 15:58 | 16:47 | Khulshi-Madunaghat 132kV Ckt-2 Scheduled S/D from Khulshi 132/33kV end Due to Emergency
S/D for nut bolt change at Y -phase at Khulshi S/S end.
| 16:05 | 16:51 | Ashuganj-Brahmanbaria 132kV Ckt-2 Forced S/D from Brahmanbaria 132/33kV end. | [7 empty] | 70.0MW load
interrup.
Brahmanbaria
132/33kV end
|  | 18:23 | Gopalganj 400/132kV S/S 400kV Rooppur is restored.
| 19:02 |  | Bheramara 410 MW CCPP ST was sync.
| 19:30 |  | Evening Peak Gen. 14121 MW
| 20:16 |  | Shahjibazar 132/33kV S/S TR-02 LT Forced S/D Due to HT Bushing oil leakage
| 20:17 |  | Shahjibazar 132/33kV S/S TR-02 HT Forced S/D Due to HT Bushing oil leakage
|  | 21:37 | Ghorashal 230kV S/S TARFO-2 HT is restored.
|  | 21:38 | Ghorashal 230kV S/S TARFO-2 LT is restored.
| 22:56 | 23:53 | Bhangura 132/33kV S/S Tr-2(413T) HT Forced S/D Due to 33 kv incoming bkr red hot
| 22:57 | 23:54 | Bhangura 132/33kV S/S Tr-2(413T) LT Forced S/D Due to Red hot
| 23:54 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- GT
| 00:56 | 02:32 | Ghorashal 230kV S/S TARFO-2 HT Forced S/D Due to Red Hot Maintenance works | [7 empty] | 20.0MW load
interrup.
| 05:18 |  | Bhaluka 132/33kV S/S Transformer- 01 LT Scheduled S/D Due to 33 kv bushing clamp change
| 05:19 |  | Bhaluka 132/33kV S/S Transformer- 01 HT Scheduled S/D Due to 33 kv bushing clamp change
| 05:21 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized with remarks:- GT
| 06:44 | 07:37 | Ramganj 132/33kV S/S Transformer -02 LT Scheduled S/D Due to Red Hot maintenance work. | [7 empty] | 10.0MW load
interrup.
| 06:58 |  | Kishoreganj 132/33kV S/S Tr-3 (424T) HT Scheduled S/D Due to T -3 33 kv bus Section. 33 | [7 empty] | 40.0MW load
|  |  | kv feeder hotspot maintenance work by PBS | [7 empty] | interrup.
| 06:58 |  | Kishoreganj 132/33kV S/S Tr-3 (424T) LT Scheduled S/D Due to 33kv T-3 bus section .33 kv | [7 empty] | 40.0MW load
|  |  | feeder hotspot maintenance work by PBS | [7 empty] | interrup.
| 07:13 |  | Natore 132/33kV S/S TR-2 (415 T) LT Scheduled S/D | [7 empty] | 31.0MW load
interrup.
| 07:13 |  | Natore 132/33kV S/S TR-1 (405 T) LT Scheduled S/D | [7 empty] | 31.0MW load
interrup.
| 07:13 |  | Natore 132/33kV S/S TR-2 (415 T) HT Scheduled S/D | [7 empty] | 31.0MW load
interrup.
| 07:13 |  | Natore 132/33kV S/S TR-1 (405 T) HT Scheduled S/D Due to 33kV bus red hot maintenance. | [7 empty] | 31.0MW load
interrup.
| 07:54 |  | Gopalganj(N)-Madaripur 132kV Ckt-2 Scheduled S/D from Madaripur 132/33kV end Due to Hot
spot maintenance work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 04-06-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 372 | 8647200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9981500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 290 | 7020771 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 100 | 1224000 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 293 | 6926767 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 171360 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 80 | 1460160 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 227147 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 39134 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20 | 494400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 522720 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 344933 | Fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 6524 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1410336 | Machine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1218240 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 94080 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 436320 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 153314 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 129600 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 3139677 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 90 | 1068000 | -
Dhaka Area Total |  |  |  |  | 5939.724 | 2091 | 44716183
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 22545 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 3 | 61920 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 167 | 3969620 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 5118341 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 10168 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 33 | 184752 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 758400 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 25 | 498240 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 14039 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 24 | 47040 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1100 | 24016361 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 9 | 570720 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 520 | 11818181.82 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4895.72 | 2201 | 47090327.82
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 200 | 4935000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 356 | 8541900 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 8028000 | machine problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 32 | 727488 | machine problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 48 | 1124640 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 157 | 1957091 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1074088 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 12 | 133818 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 32 | 206448 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1884310 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 117 | 1860000 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 50 | 1085760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 22282 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 315560 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 96 | 1600560 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 29 | 350280 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 95 | 1128000 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 149082 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1717 | 35124307
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 44 | 1147200 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8200 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 148 | 2635200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 86 | 1506000 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 176380 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 11 | 232080 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 289 | 5705060
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 32 | 760000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 687120 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 147 | 3430554.5 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 711936 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1930560 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 165 | 3477890 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 432000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 5 | 26712 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 240 | 5872500 | Gas shortage
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 340 | 8883000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7701600 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1409 | 33913872.5
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 773 | 19487273 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 145 | 3048480 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 139200 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 483120 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1120 | 20974540 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3699.2 | 2055 | 44132613
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 7 | 139562 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2673000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1110 | 21303272.73 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5201260 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 202 | 4189000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1945 | -
Barishal Area Total |  |  |  |  | 2236 | 1659 | 33508039.73
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 186 | 4110727 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 200 | 4577427 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8714909 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 16503 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 10496 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 70176 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 23802 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1387 | 25628120 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 261000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 606100 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2222 | 44019260
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1184290 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4884000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1021910 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 44867.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 860546 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 216485 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1116720 | -
Rangpur Area Total |  |  |  |  | 950 | 478 | 9328818.16
Eastern Grid Total |  |  |  |  | 16705.895 | 7707 | 166549750.32
Western Grid Total |  |  |  |  | 10338.16 | 6414 | 130988730.89
National Grid Total |  |  |  |  | 27044.055 | 14121 | 297538481.21
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 04-06-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8821.43 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4671.9 | MW
i) Dhaka area |  |  | 4567.75 |  | MW | i) Khulna area |  |  |  | 1747 | MW
ii) Chattogram area |  |  | 1259.9 |  | MW | ii) Barishal area |  |  |  | 409.5 | MW
iii) Cumilla area |  |  | 1307.78 |  | MW | iii) Rajshahi area |  |  |  | 1514.4 | MW
iv) Mymensingh area |  |  | 1167 |  | MW | iv) Rangpur area |  |  |  | 1001 | MW
v) Sylhet area |  |  | 519 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13493.33 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 22 | 21:00 | 67 | Ishurdi | 79 | 21:00 | 133 | Patuakhali | 78 | 23:00
2 | AKSML | 97 | 01:00 | 68 | Jaldhaka | 81 | 19:30 | 134 | Payra | 32 | 22:00
3 | Aftabnagar | 32 | 00:00 | 69 | Jamalpur | 132 | 21:00 | 135 | Postogola | 50 | 13:00
4 | Agargaon | 113 | 13:00 | 70 | Jashore | 140 | 20:00 | 136 | Purbachal | 17 | 00:00
5 | Agrabad | 80 | 20:00 | 71 | Jhenaidah | 132 | 21:00 | 137 | Purbasadipur | 130 | 21:00
6 | Amnura | 39 | 21:00 | 72 | Joydebpur | 135 | 10:00 | 138 | Rahanpur | 31 | 20:00
7 | Ashuganj | 85 | 22:00 | 73 | Joypurhat | 74 | 00:00 | 139 | Rahim | 18 | 18:00
8 | BSRM | 188 | 01:00 | 74 | Juldah | 13 | 00:00 | 140 | Rajbari | 81 | 19:30
9 | Bagerhat | 83 | 00:00 | 75 | KSRM | 26 | 06:00 | 141 | Rajendrapur | 111 | 01:00
10 | Bajitpur | 51 | 00:00 | 76 | Kabirpur | 239 | 09:00 | 142 | Rajshahi | 110 | 00:00
11 | Bakulia | 80 | 15:00 | 77 | Kachua | 87 | 19:30 | 143 | Rajshahi-230 | 90 | 00:00
12 | Banani | 34.2 | 13:00 | 78 | Kallyanpur | 93 | 00:00 | 144 | Ramganj | 110 | 22:00
13 | Bangabhaban | 15 | 10:00 | 79 | Kalurghat | 34 | 10:00 | 145 | Rampur | 36 | 14:00
14 | Barapukuria | 67 | 22:00 | 80 | Kamrangirchar | 59.2 | 13:00 | 146 | Rangamati | 17 | 19:30
15 | Barguna | 16 | 21:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 145 | 19:00
16 | Barishal | 111 | 00:00 | 82 | Kasba | 35 | 22:00 | 148 | Ruppur | 7.8 | 15:00
17 | Barishal-230 | 85 | 23:00 | 83 | Kazla | 91 | 13:00 | 149 | SSM | 16 | 04:00
18 | Baroaulia | 57 | 10:00 | 84 | Keranigonj | 80 | 01:00 | 150 | Saidpur | 115 | 19:30
19 | Baroirhat | 55 | 19:00 | 85 | Khagrachori | 28 | 19:30 | 151 | Satkhira | 144 | 00:00
20 | Bashundhara | 167 | 13:00 | 86 | Khulna | 73 | 08:00 | 152 | Satmasjid | 88 | 13:00
21 | BashundharaCement | 9 | 00:00 | 87 | Khulshi | 171 | 19:30 | 153 | Savar | 186 | 10:00
22 | Beanibazar | 68 | 21:00 | 88 | Kishoreganj | 140 | 21:00 | 154 | SevenRings | 15.73 | 17:00
23 | Benapole | 70 | 00:00 | 89 | Kodda | 287 | 10:00 | 155 | ShahCement | 25 | 19:30
24 | Bhaluka | 152 | 00:00 | 90 | Kulaura | 45 | 21:00 | 156 | Shahjadpur | 84 | 21:00
25 | Bhandaria | 50 | 21:00 | 91 | Kurigram | 66 | 19:30 | 157 | Shahjibazar | 118 | 22:00
26 | Bhangura | 37 | 19:30 | 92 | Kushtia | 162 | 21:00 | 158 | Shahmirpur | 56 | 00:00
27 | Bheramara(GK) | 68 | 00:00 | 93 | Lalbag | 52 | 00:00 | 159 | Shariatpur | 82 | 22:00
28 | Bhulta | 234 | 22:00 | 94 | Lalmonirhat | 60 | 20:00 | 160 | Sherpur | 142 | 00:00
29 | Bog-Sherpur | 68 | 00:00 | 95 | MI_Cement | 15.8 | 15:00 | 161 | Shikalbaha | 25 | 19:00
30 | Bogura | 171 | 00:00 | 96 | Madanganj | 21 | 19:00 | 162 | Shitalakhya | 79.5 | 12:00
31 | Borhanuddin | 80 | 19:30 | 97 | Madaripur | 110 | 22:00 | 163 | Sholosohor | 40 | 11:00
32 | Brahmanbaria | 127 | 22:00 | 98 | Madartek | 78 | 00:00 | 164 | Shyampur | 138 | 10:00
33 | Cantonment | 128 | 12:00 | 99 | Madunaghat | 46 | 19:00 | 165 | Siddhirganj | 111 | 10:00
34 | Chandina | 18.78 | 19:30 | 100 | Magura | 65 | 19:30 | 166 | Sirajganj | 120 | 21:00
35 | Chandpur | 76 | 20:00 | 101 | Mahasthangarh | 80 | 00:00 | 167 | Sonargaon | 169 | 03:00
36 | Chandraghona | 32 | 19:00 | 102 | Manikganj | 121 | 22:00 | 168 | Sreemongol | 69 | 19:30
37 | Chapai | 75 | 19:30 | 103 | Maniknagar | 70 | 13:00 | 169 | Sreepur | 94 | 00:00
38 | Charsaidpur | 32 | 00:00 | 104 | Matarbari | 40 | 00:00 | 170 | Srinagar | 45.3 | 23:00
39 | Chauddagram | 62 | 22:00 | 105 | Matuail | 58 | 12:00 | 171 | Sunamganj | 52 | 21:00
40 | Chhatak | 33 | 00:00 | 106 | Millgate | 80 | 09:00 | 172 | Sylhet | 40 | 19:00
41 | Chowmuhani | 217 | 22:00 | 107 | Mirpur | 103 | 12:00 | 173 | Sylhet-132 | 108 | 21:00
42 | Chuadanga | 118 | 22:00 | 108 | Mirsorai | 9 | 00:00 | 174 | TK | 31 | 23:00
43 | Coxsbazar | 120 | 19:00 | 109 | Mirzapur | 46 | 21:00 | 175 | Tangail | 181 | 19:30
44 | Cumilla(N) | 133 | 23:00 | 110 | Mithapukur | 66 | 19:30 | 176 | Thakurgaon | 110 | 20:00
45 | Cumilla(S) | 166 | 01:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 109 | 11:00
46 | Daudkandi | 139 | 21:00 | 112 | Mogbazar | 124.5 | 13:00 | 178 | Ullahpara | 40 | 21:00
47 | Dhaka | 54 | 12:00 | 113 | Mongla | 42 | 00:00 | 179 | Ullon | 34 | 00:00
48 | Dhamrai | 128 | 00:00 | 114 | Motijheel | 34 | 12:00 | 180 | Uttara | 71 | 12:00
49 | Dhanmondi | 130 | 13:00 | 115 | Muktagacha | 37 | 22:00 | 181 | UttaraNew | 51 | 00:00
50 | Dohazari | 90 | 21:00 | 116 | Munshiganj | 108 | 23:00 | 182 | Zigatola | 62 | 00:00
51 | Faridpur | 155 | 23:00 | 117 | Muradnagar | 27 | 19:30
52 | Fatullah | 84 | 12:00 | 118 | Mymensingh | 195 | 21:00
53 | Fenchuganj | 33 | 00:00 | 119 | Naogaon | 140 | 21:00
54 | Feni | 112 | 19:30 | 120 | Narail | 55 | 20:00
55 | GPH | 29 | 18:00 | 121 | Narinda | 66 | 13:00
56 | Ghatail | 80 | 21:00 | 122 | Narshingdi | 169 | 20:00
57 | Ghorashal | 20 | 11:00 | 123 | Natore | 166 | 22:00
58 | Ghorashal-230 | 53 | 23:00 | 124 | Nawabganj | 55 | 21:00
59 | Goalpara | 40 | 00:00 | 125 | Netrakona | 124 | 20:00
60 | Gollamari | 96 | 00:00 | 126 | New | 73 | 10:00
61 | Gopalganj | 104 | 20:00 | 127 | Niamatpur | 74 | 21:00
62 | Gulshan | 106 | 13:00 | 128 | Noapara | 50 | 00:00
63 | Halishahar | 67 | 10:00 | 129 | PHP | 6 | 14:00
64 | HaripurSBU | 180 | 11:00 | 130 | Pabna | 126 | 21:00
65 | Hasnabad | 62 | 18:30 | 131 | Palashbari | 116 | 19:30
66 | Hathazari | 75 | 19:00 | 132 | Panchagarh | 60 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 04-06-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13838.5 | 16 |  | 13855.5
1:00 | 13257 | 41 |  | 13300
2:00 | 12723 | 26 |  | 12750
3:00 | 12225 | 0 |  | 12225
4:00 | 11708 | 0 |  | 11708
5:00 | 10957 | 0 |  | 10957
6:00 | 10099.56 | 0 |  | 10099.56
7:00 | 10108.09 | 0 |  | 10108.09
8:00 | 10570.41 | 0 |  | 10570.41
9:00 | 11235.38 | 0 |  | 11235.38
10:00 | 11373.01 | 0 |  | 11373.01
11:00 | 11798.03 | 0 |  | 11798.03
12:00 | 12191.8 | 0 |  | 12191.8
13:00 | 12546.82 | 0 |  | 12546.82
14:00 | 12479.3 | 0 |  | 12479.3
15:00 | 12521.94 | 0 |  | 12521.94
16:00 | 12410.27 | 0 |  | 12410.27
17:00 | 11872.82 | 0 |  | 11872.82
18:00 | 11651.3 | 0 |  | 11651.3
19:00 | 13070 | 0 |  | 13070
19:30 | 14121 | 0 |  | 14121
20:00 | 14053 | 0 |  | 14053
21:00 | 14038.36 | 0 |  | 14038.36
22:00 | 13943 | 0 |  | 13943
23:00 | 13839 | 0 |  | 13839
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 04-06-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7566.5 | 6272 | 13838.5 | DAILY GENERATION CURVE
00:30 | 7390.75 | 6157 | 13547.75
01:00 | 7215 | 6042 | 13257 | 04-06-2025
01:30 | 7203.5 | 5786.5 | 12990
02:00 | 7192 | 5531 | 12723
02:30 | 7102.5 | 5371.5 | 12474
03:00 | 7013 | 5212 | 12225
03:30 | 6932 | 5034.5 | 11966.5
04:00 | 6851 | 4857 | 11708
04:30 | 6779 | 4553.5 | 11332.5
05:00 | 6707 | 4250 | 10957
05:30 | 6281.21 | 4247.07 | 10528.28
06:00 | 5855.42 | 4244.14 | 10099.56
06:30 | 5787.18 | 4316.645 | 10103.825
07:00 | 5718.94 | 4389.15 | 10108.09
07:30 | 5903.585 | 4435.665 | 10339.25
08:00 | 6088.23 | 4482.18 | 10570.41
08:30 | 6353.35 | 4549.545 | 10902.895
09:00 | 6618.47 | 4616.91 | 11235.38
09:30 | 6607.49 | 4696.705 | 11304.195
10:00 | 6596.51 | 4776.5 | 11373.01
10:30 | 6650.805 | 4934.715 | 11585.52
11:00 | 6705.1 | 5092.93 | 11798.03
11:30 | 6796.95 | 5197.965 | 11994.915
12:00 | 6888.8 | 5303 | 12191.8
12:30 | 6945.7 | 5423.61 | 12369.31
13:00 | 7002.6 | 5544.22 | 12546.82
13:30 | 6985.485 | 5527.575 | 12513.06
14:00 | 6968.37 | 5510.93 | 12479.3
14:30 | 6969.66 | 5530.96 | 12500.62
15:00 | 6970.95 | 5550.99 | 12521.94
15:30 | 6982.275 | 5483.83 | 12466.105
16:00 | 6993.6 | 5416.67 | 12410.27
16:30 | 6864.675 | 5276.87 | 12141.545
17:00 | 6735.75 | 5137.07 | 11872.82
17:30 | 6641.08 | 5120.98 | 11762.06
18:00 | 6546.41 | 5104.89 | 11651.3
18:30 | 6926.205 | 5434.445 | 12360.65
19:00 | 7306 | 5764 | 13070
19:30 | 7707 | 6414 | 14121
20:00 | 7650 | 6403 | 14053
20:30 | 7603.18 | 6442.5 | 14045.68 |  | Executive Engineer
21:00 | 7556.36 | 6482 | 14038.36 |  | Network Operation Division
21:30 | 7519.18 | 6471.5 | 13990.68
22:00 | 7482 | 6461 | 13943
22:30 | 7469 | 6422 | 13891
23:00 | 7456 | 6383 | 13839

## En-Curve
QF-LDC-12
Date | 04-06-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3780 | 1990.5 | 713 | 0 | 54 | 1416 | 167 | 4198 | 0 | 430 | 1078 | 0 | 0 | 12 | 16 | DAILY ENERGY CURVE
00:30 | 3778 | 1980.75 | 712 | 0 | 53 | 1420.5 | 167 | 4156.5 | 0 | 380.5 | 878.5 | 0 | 0 | 21 | 28.5 | 04-06-2025
01:00 | 3776 | 1971 | 711 | 0 | 52 | 1425 | 167 | 4115 | 0 | 331 | 679 | 0 | 0 | 30 | 41
01:30 | 3735 | 1963.5 | 711 | 0 | 51 | 1324.5 | 167 | 4048 | 0 | 296 | 662 | 0 | 0 | 32 | 33.5 | Energy Generated | 297.5385 |  | MKWHr
02:00 | 3694 | 1956 | 711 | 0 | 50 | 1224 | 167 | 3981 | 0 | 261 | 645 | 0 | 0 | 34 | 26 | Energy not Served | 0.083 |  | MKWHr
02:30 | 3699.5 | 1954 | 711 | 0 | 49 | 1169 | 167 | 3844 | 0 | 242 | 611.5 | 0 | 0 | 27 | 13 | Total Energy Requirement | 297.6215 |  | MKWHr
03:00 | 3705 | 1952 | 711 | 0 | 48 | 1114 | 167 | 3707 | 0 | 223 | 578 | 0 | 0 | 20 | 0
03:30 | 3670 | 1934 | 720.5 | 0 | 48 | 1069.5 | 167 | 3584.5 | 0 | 206 | 544 | 0 | 0 | 23 | 0
04:00 | 3635 | 1916 | 730 | 0 | 48 | 1025 | 167 | 3462 | 0 | 189 | 510 | 0 | 0 | 26 | 0
04:30 | 3586.5 | 1900 | 771.5 | 0 | 47 | 942.5 | 167 | 3234.5 | 0 | 147.5 | 503.5 | 0 | 0 | 32.5 | 0
05:00 | 3538 | 1884 | 813 | 0 | 46 | 860 | 167 | 3007 | 0 | 106 | 497 | 0 | 0 | 39 | 0
05:30 | 3495.5 | 1733.5 | 813.5 | 0 | 45 | 853.5 | 167 | 2903.5 | 9.28 | 77.5 | 392 | 0 | 0 | 38 | 0
06:00 | 3453 | 1583 | 814 | 0 | 44 | 847 | 167 | 2800 | 18.56 | 49 | 287 | 0 | 0 | 37 | 0
06:30 | 3524.5 | 1583.5 | 814 | 0 | 39 | 846.5 | 167 | 2784.5 | 28.325 | 49 | 236.5 | 0 | 0 | 31 | 0
07:00 | 3596 | 1584 | 814 | 0 | 34 | 846 | 167 | 2769 | 38.09 | 49 | 186 | 0 | 0 | 25 | 0
07:30 | 3737.5 | 1631.75 | 790.5 | 0 | 40 | 845.48 | 167 | 2786.5 | 86.02 | 51 | 177.5 | 0 | 0 | 26 | 0
08:00 | 3879 | 1679.5 | 767 | 0 | 46 | 844.96 | 167 | 2804 | 133.95 | 53 | 169 | 0 | 0 | 27 | 0
08:30 | 3887 | 1686 | 766.5 | 0 | 46 | 840.225 | 167 | 2983.5 | 191.67 | 98 | 205.5 | 0 | 0 | 31.5 | 0
09:00 | 3895 | 1692.5 | 766 | 0 | 46 | 835.49 | 167 | 3163 | 249.39 | 143 | 242 | 0 | 0 | 36 | 0
09:30 | 3866.5 | 1673 | 790.5 | 0 | 42 | 851.305 | 167 | 3154 | 260.39 | 144 | 322 | 0 | 0 | 33.5 | 0
10:00 | 3838 | 1653.5 | 815 | 0 | 38 | 867.12 | 167 | 3145 | 271.39 | 145 | 402 | 0 | 0 | 31 | 0
10:30 | 3846 | 1660.5 | 815 | 0 | 39 | 888.21 | 167 | 3236 | 369.31 | 143 | 381 | 0 | 0 | 40.5 | 0
11:00 | 3854 | 1667.5 | 815 | 0 | 40 | 909.3 | 167 | 3327 | 467.23 | 141 | 360 | 0 | 0 | 50 | 0
11:30 | 3891.5 | 1678.25 | 815 | 0 | 42 | 912.19 | 167 | 3434.5 | 489.975 | 141 | 395.5 | 0 | 0 | 28 | 0
12:00 | 3929 | 1689 | 815 | 0 | 44 | 915.08 | 167 | 3542 | 512.72 | 141 | 431 | 0 | 0 | 6 | 0
12:30 | 3952 | 1715 | 815.5 | 0 | 45 | 910.375 | 167 | 3663 | 481.935 | 133 | 476 | 0 | 0 | 10.5 | 0
13:00 | 3975 | 1741 | 816 | 0 | 46 | 905.67 | 167 | 3784 | 451.15 | 125 | 521 | 0 | 0 | 15 | 0
13:30 | 3957 | 1746 | 815.5 | 0 | 47 | 913.335 | 167 | 3844 | 397.725 | 95.5 | 492 | 0 | 0 | 38 | 0
14:00 | 3939 | 1751 | 815 | 0 | 48 | 921 | 167 | 3904 | 344.3 | 66 | 463 | 0 | 0 | 61 | 0
14:30 | 3953.5 | 1759 | 817.5 | 0 | 47 | 918.5 | 167 | 3910.5 | 337.92 | 79 | 462.2 | 0 | 0 | 48.5 | 0
15:00 | 3968 | 1767 | 820 | 0 | 46 | 916 | 167 | 3917 | 331.54 | 92 | 461.4 | 0 | 0 | 36 | 0
15:30 | 3949.5 | 1767.5 | 820.5 | 0 | 45 | 920 | 167 | 3896 | 289.405 | 103.5 | 483.7 | 0 | 0 | 24 | 0
16:00 | 3931 | 1768 | 821 | 0 | 44 | 924 | 167 | 3875 | 247.27 | 115 | 506 | 0 | 0 | 12 | 0
16:30 | 3901 | 1703 | 820.5 | 0 | 43 | 915 | 167 | 3751.5 | 188.045 | 115 | 527.5 | 0 | 0 | 10 | 0
17:00 | 3871 | 1638 | 820 | 0 | 42 | 906 | 167 | 3628 | 128.82 | 115 | 549 | 0 | 0 | 8 | 0
17:30 | 3798 | 1603.5 | 820 | 0 | 42 | 925.5 | 167 | 3611 | 85.56 | 115 | 584.5 | 0 | 0 | 10 | 0
18:00 | 3725 | 1569 | 820 | 0 | 42 | 945 | 167 | 3594 | 42.3 | 115 | 620 | 0 | 0 | 12 | 0
18:30 | 3889.5 | 1615 | 796.5 | 0 | 46 | 1100 | 167 | 3820 | 21.15 | 181 | 718 | 0 | 0 | 6.5 | 0
19:00 | 4054 | 1661 | 773 | 0 | 50 | 1255 | 167 | 4046 | 0 | 247 | 816 | 0 | 0 | 1 | 0
19:30 | 4037 | 1778 | 773 | 0 | 50 | 1387 | 167 | 4302 | 0 | 356 | 1262 | 0 | 0 | 9 | 0
20:00 | 4031 | 1787 | 773 | 0 | 50 | 1409 | 167 | 4228 | 0 | 356 | 1239 | 0 | 0 | 13 | 0
20:30 | 4032.5 | 1791 | 797 | 0 | 50 | 1407 | 147 | 4214 | 0 | 356 | 1239.18 | 0 | 0 | 12 | 0
21:00 | 4034 | 1795 | 821 | 0 | 50 | 1405 | 127 | 4200 | 0 | 356 | 1239.36 | 0 | 0 | 11 | 0
21:30 | 4059 | 1795 | 820.5 | 0 | 51 | 1409 | 127 | 4211 | 0 | 348 | 1159.18 | 0 | 0 | 11 | 0
22:00 | 4084 | 1795 | 820 | 0 | 52 | 1413 | 127 | 4222 | 0 | 340 | 1079 | 0 | 0 | 11 | 0
22:30 | 4072 | 1795 | 820 | 0 | 42 | 1411.5 | 147 | 4229 | 0 | 340 | 1024 | 0 | 0 | 10.5 | 0
23:00 | 4060 | 1795 | 820 | 0 | 32 | 1410 | 167 | 4236 | 0 | 340 | 969 | 0 | 0 | 10 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 04-06-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 390 | 05:00 | 374 | 15:00 | Payra | 421 | 05:00 | 407 | 23:00
Ashuganj | 409 | 5:00 | 387 | 13:00 | Rahanpur | 413 | 09:00 | 395 | 22:00
Bhulta | 403 | 05:00 | 385 | 14:00 | Rampal | 411 | 05:00 | 388 | 23:00
Bibiana | 392 | 05:00 | 385 | 14:00
BIPTC | 406 | 02:00 | 394 | 12:00
Bogura | 403 | 09:00 | 382 | 20:00
Gopalganj | 409 | 05:00 | 387 | 23:00
Kaliakoir | 381 | 05:00 | 366 | 14:00
Madunaghat | 399 | 07:00 | 390 | 12:00
Meghnaghat | 393 | 06:00 | 376 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 230 | 05:00 | 219 | 12:00 | Keranigonj | 229 | 05:00 | 216 | 15:00
AKSML | 234 | 05:00 | 226 | 01:00 | Khulna(S) | 234 | 05:00 | 216 | 22:00
Aminbazar | 229 | 06:00 | 219 | 14:00 | Madunaghat | 235 | 07:00 | 229 | 15:00
Ashuganj | 234 | 05:00 | 227 | 00:00 | Madunaghat-400 | 236 | 07:00 | 230 | 15:00
Ashuganj-400 | 234 | 05:00 | 227 | 00:00 | Maniknagar | 226 | 04:00 | 216 | 15:00
Baghabari | 234 | 08:00 | 224 | 19:30 | Meghnaghat | 233 | 05:00 | 223 | 14:00
Barapukuria | 227 | 10:00 | 217 | 19:30 | Meghnaghat-400 | 229 | 06:00 | 219 | 15:00
Barapukuria-230 | 227 | 10:00 | 217 | 19:30 | Mirsorai | 233 | 07:00 | 223 | 02:00
Barishal | 244 | 05:00 | 229 | 23:00 | Rajshahi | 235 | 05:00 | 220 | 19:30
Bheramara | 234 | 03:00 | 222 | 19:30 | Rampal | 235 | 05:00 | 216 | 23:00
Bhulta | 235 | 05:00 | 217 | 14:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 232 | 07:00 | 225 | 19:00 | Rampura | 236 | 05:00 | 220 | 15:00
BIPTC | 235 | 03:00 | 221 | 19:30 | Shikalbaha | 233 | 06:00 | 226 | 19:00
Bogura | 235 | 05:00 | 223 | 22:00 | Shyampur | 228 | 05:00 | 217 | 15:00
Bogura-400 | 235 | 05:00 | 224 | 22:00 | Siddhirganj | 227 | 07:00 | 219 | 15:00
Borhanuddin | 248 | 05:00 | 237 | 22:00 | Sirajgonj | 239 | 05:00 | 231 | 22:00
BSRM | 233 | 07:00 | 222 | 01:00 | Sreepur | 231 | 05:00 | 223 | 00:00
Cumilla(N) | 229 | 06:00 | 219 | 01:00 | Tongi | 228 | 21:00 | 218 | 15:00
Faridpur | 240 | 05:00 | 225 | 23:00
Fenchuganj | 238 | 04:00 | 227 | 23:00
Ghorashal | 235 | 15:00 | 230 | 00:00
Ghorashal-230 | 234 | 05:00 | 220 | 14:00
Gopalganj | 243 | 05:00 | 227 | 23:00
GPH | 231 | 18:00 | 227 | 01:00
Haripur | 227 | 05:00 | 217 | 15:00
Hasnabad | 226 | 05:00 | 216 | 15:00
Hathazari | 237 | 06:00 | 229 | 14:00
Ishurdi | 235 | 03:00 | 224 | 19:30
Jhenaidah | 232 | 03:00 | 214 | 21:00
Kaliakoir | 236 | 05:00 | 225 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 05:00 | 126 | 15:00 | Madartek | 136 | 05:00 | 126 | 14:00
Agargaon | 139 | 05:00 | 130 | 16:00 | Madunaghat | 133 | 06:00 | 129 | 15:00
Agrabad | 134 | 07:00 | 128 | 14:00 | Magura | 135 | 01:00 | 122 | 13:00
AKS | 132 | 07:00 | 127 | 14:00 | Mahasthangarh | 135 | 05:00 | 127 | 19:30
Aminbazar | 135 | 06:00 | 127 | 15:00 | Manikganj | 136 | 18:00 | 127 | 10:00
Amnura | 136 | 03:00 | 124 | 21:00 | Maniknagar | 137 | 05:00 | 130 | 12:00
Ashuganj | 138 | 05:00 | 134 | 15:00 | Matarbari | 128 | 21:00 | 115 | 09:00
Bagerhat | 139 | 03:00 | 117 | 23:00 | Matuail | 133 | 05:00 | 126.7 | 15:00
Bajitpur | 132 | 09:00 | 125 | 00:00 | Millgate | 141 | 05:00 | 132 | 15:00
Bakulia | 135 | 06:00 | 129 | 15:00 | Mirpur | 134 | 04:00 | 125 | 15:00
Banani | 137 | 05:00 | 126 | 14:00 | Mirzapur | 137 | 04:00 | 130 | 14:00
Bangabhaban | 136 | 05:00 | 129 | 13:00 | Mithapukur | 132 | 06:00 | 123 | 12:00
Barapukuria | 136 | 17:00 | 123 | 12:00 | MI_Cement | 134 | 05:00 | 127 | 15:00
Barguna | 138 | 06:00 | 131 | 23:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 136 | 05:00 | 125 | 21:00 | Mogbazar | 136 | 04:00 | 126 | 15:00
Barishal-230 | 137 | 05:00 | 125 | 23:00 | Mongla | 134 | 04:00 | 116 | 23:00
Baroaulia | 135 | 08:00 | 130 | 15:00 | Motijheel | 136 | 05:00 | 129 | 13:00
Baroirhat | 131 | 07:00 | 120 | 15:00 | Muktagacha | 137 | 06:00 | 132 | 14:00
Bashundhara | 138 | 05:00 | 125 | 15:00 | Munshiganj | 134 | 05:00 | 124 | 15:00
BashundharaCement | 133 | 05:00 | 124 | 21:00 | Muradnagar | 132 | 06:00 | 122 | 01:00
Beanibazar | 131 | 06:00 | 127 | 00:00 | Mymensingh | 138 | 07:00 | 117 | 00:00
Benapole | 136 | 05:00 | 117 | 23:00 | Naogaon | 133 | 05:00 | 124 | 19:30
Bhaluka | 131 | 05:00 | 125 | 00:00 | Narail | 136 | 02:00 | 119 | 21:00
Bhandaria | 132 | 08:00 | 118 | 21:00 | Narinda | 137 | 05:00 | 130 | 12:00
Bhangura | 134 | 02:00 | 127 | 19:30 | Narshingdi | 135 | 17:00 | 119 | 00:00
Bheramara | 136 | 06:00 | 130 | 19:30 | Natore | 135 | 09:00 | 127 | 19:30
Bheramara(GK) | 137 | 06:00 | 129 | 19:30 | Nawabganj | 136 | 06:00 | 128 | 15:00
Bhulta | 123 | 04:00 | 118 | 16:00 | Netrakona | 126 | 16:00 | 115 | 00:00
Bog-Sherpur | 136 | 05:00 | 127 | 22:00 | New | 141 | 05:00 | 133 | 15:00
Bogura | 138 | 06:00 | 129 | 23:00 | Niamatpur | 136 | 04:00 | 129 | 19:30
Bogura-230 | 138 | 05:00 | 130 | 23:00 | Noapara | 139 | 03:00 | 24 | 20:00
Brahmanbaria | 132 | 07:00 | 124 | 00:00 | Pabna | 134 | 05:00 | 127 | 19:30
Cantonment | 138 | 05:00 | 130 | 15:00 | Palashbari | 130 | 09:00 | 121 | 19:30
Chandina | 133 | 07:00 | 124 | 01:00 | Panchagarh | 135 | 02:00 | 119 | 12:00
Chandpur | 130 | 07:00 | 117 | 15:00 | Patuakhali | 138 | 05:00 | 131 | 22:00
Chandraghona | 135 | 06:00 | 130 | 19:00 | Payra | 138 | 05:00 | 133 | 22:00
Chapai | 133 | 02:00 | 125 | 19:30 | PHP | 130 | 07:00 | 118 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 133 | 05:00 | 127 | 15:00 | Postogola | 136 | 04:00 | 129 | 15:00
Chauddagram | 130 | 07:00 | 118 | 15:00 | Purbachal | 135 | 04:00 | 126 | 12:00
Chhatak | 132 | 03:00 | 124 | 21:00 | Purbasadipur | 129 | 18:00 | 116 | 12:00
Chowmuhani | 127 | 06:00 | 109 | 01:00 | Rahanpur | 137 | 06:00 | 131 | 19:30
Chuadanga | 132 | 18:30 | 120 | 21:00 | Rahanpur-400 | 138 | 05:00 | 131 | 20:00
Coxsbazar | 125 | 10:00 | 115 | 19:00 | Rahim | 132 | 07:00 | 127 | 12:00
Cumilla(N) | 133 | 07:00 | 124 | 01:00 | Rajbari | 140 | 05:00 | 127 | 23:00
Cumilla(S) | 132 | 06:00 | 121 | 02:00 | Rajendrapur | 139 | 20:00 | 125 | 15:00
Daudkandi | 132 | 06:00 | 120 | 12:00 | Rajshahi | 135 | 05:00 | 127 | 19:30
Dhaka | 135 | 05:00 | 127 | 12:00 | Rajshahi-230 | 135 | 05:00 | 118 | 20:00
Dhamrai | 135 | 06:00 | 127 | 15:00 | Ramganj | 128 | 07:00 | 112 | 15:00
Dhanmondi | 135 | 04:00 | 127 | 12:00 | Rampur | 135 | 07:00 | 129 | 13:00
Dohazari | 132 | 10:00 | 125 | 01:00 | Rampura | 136 | 05:00 | 126 | 12:00
Faridpur | 140 | 05:00 | 130 | 23:00 | Rangamati | 134 | 06:00 | 129 | 19:00
Fatullah | 134 | 06:00 | 127 | 15:00 | Rangpur | 129 | 05:00 | 119 | 12:00
Fenchuganj | 138 | 07:00 | 134 | 19:30 | Ruppur | 137 | 09:00 | 131 | 19:30
Feni | 126 | 07:00 | 117 | 14:00 | Saidpur | 130 | 18:00 | 118 | 12:00
Ghatail | 134 | 05:00 | 129 | 01:00 | Satkhira | 139 | 05:00 | 116 | 23:00
Ghorashal | 139 | 18:30 | 133 | 00:00 | Satmasjid | 139 | 05:00 | 130 | 15:00
Goalpara | 139 | 06:00 | 126 | 19:30 | Savar | 133 | 05:00 | 124 | 15:00
Gollamari | 139 | 03:00 | 125 | 23:00 | SevenRings | 141 | 05:00 | 131 | 15:00
Gopalganj | 139 | 05:00 | 126 | 23:00 | ShahCement | 133 | 05:00 | 127 | 15:00
Gopalganj-400 | 141 | 05:00 | 131 | 22:00 | Shahjadpur | 135 | 10:00 | 131 | 19:30
Gulshan | 136 | 04:00 | 126 | 14:00 | Shahjibazar | 133 | 07:00 | 126 | 00:00
Halishahar | 135 | 07:00 | 128 | 15:00 | Shahmirpur | 134 | 07:00 | 131 | 14:00
Haripur | 133 | 05:00 | 127 | 14:00 | Shariatpur | 138 | 05:00 | 126 | 22:00
HaripurSBU | 132 | 08:00 | 120 | 14:00 | Sherpur | 139 | 12:00 | 129 | 01:00
Hasnabad | 135 | 07:00 | 129 | 15:00 | Shikalbaha | 124 | 07:00 | 119 | 15:00
Hathazari | 135 | 05:00 | 131 | 14:00 | Shikalbaha-230 | 135 | 07:00 | 131 | 14:00
Ishurdi | 138 | 09:00 | 130 | 19:30 | Shitalakhya | 134 | 05:00 | 127 | 15:00
Jaldhaka | 128 | 18:00 | 116 | 12:00 | Sholosohor | 134 | 07:00 | 129 | 01:00
Jamalpur | 141 | 07:00 | 131 | 01:00 | Shyampur | 132 | 01:00 | 127 | 15:00
Jashore | 134 | 02:00 | 118 | 22:00 | Shyampur-230 | 134 | 05:00 | 127 | 12:00
Jhenaidah | 138 | 04:00 | 119 | 19:30 | Siddhirganj | 132 | 06:00 | 127 | 15:00
Jhenaidah-230 | 137 | 03:00 | 125 | 00:00 | Sirajganj | 132 | 08:00 | 125 | 20:00
Joydebpur | 139 | 20:00 | 126 | 15:00 | Sonargaon | 134 | 04:00 | 124 | 00:00
Joypurhat | 132 | 03:00 | 121 | 19:30 | Sreemongol | 133 | 07:00 | 128 | 00:00
Juldah | 133 | 06:00 | 130 | 12:00 | Sreepur | 134 | 05:00 | 128 | 00:00
Kabirpur | 138 | 05:00 | 130 | 14:00 | Srinagar | 137 | 05:00 | 129 | 14:00
Kachua | 129 | 07:00 | 118 | 15:00 | SSM | 138 | 10:00 | 132 | 00:00
Kaliakoir | 141 | 05:00 | 131 | 14:00 | Sunamganj | 130 | 07:00 | 123 | 01:00
Kallyanpur | 133 | 02:00 | 127 | 13:00 | Sylhet | 132 | 06:00 | 129 | 00:00
Kalurghat | 133 | 06:00 | 129 | 01:00 | Sylhet-132 | 131 | 07:00 | 129 | 00:00
Kamrangirchar | 137 | 06:00 | 129 | 12:00 | Tangail | 132 | 04:00 | 123 | 15:00
Kaptai | 136 | 7:00 | 132 | 23:00 | Thakurgaon | 131 | 02:00 | 116 | 12:00
Kasba | 129 | 05:00 | 121 | 15:00 | TK | 135 | 12:00 | 129 | 15:00
Kazla | 137 | 06:00 | 130 | 12:00 | Tongi | 140 | 07:00 | 135 | 15:00
Keranigonj | 138 | 05:00 | 129 | 15:00 | Ullahpara | 135 | 03:00 | 127 | 19:30
Khagrachori | 134 | 07:00 | 129 | 14:00 | Ullon | 135 | 18:00 | 126 | 15:00
Khulna | 139 | 05:00 | 124 | 23:00 | Uttara | 134 | 05:00 | 125 | 15:00
Khulna(S) | 141 | 03:00 | 125 | 23:00 | UttaraNew | 136 | 05:00 | 125 | 15:00
Khulshi | 133 | 07:00 | 127 | 19:00 | Zigatola | 137 | 06:00 | 129 | 15:00
Kishoreganj | 130 | 05:00 | 123 | 00:00
Kodda | 138 | 19:30 | 127 | 02:00
KSRM | 135 | 18:00 | 130 | 12:00
Kulaura | 136 | 05:00 | 132 | 23:00
Kurigram | 129 | 06:00 | 118 | 12:00
Kushtia | 133 | 05:00 | 124 | 19:30
Lalbag | 138 | 05:00 | 128 | 14:00
Lalmonirhat | 130 | 04:00 | 119 | 12:00
Madanganj | 133 | 05:00 | 124 | 21:00
Madaripur | 138 | 05:00 | 128 | 23:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division