## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 06-06-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-06-2025 | during | 06-06-2025 | during | 06-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 230 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 190 | 190 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 260 | 260 | -
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 97.7 | 97.7 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 376 | 342 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 301 | 298 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 101 | 208.13 | 208.13 | 208.13 | 208.13 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 298 | 282 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 17 | 15 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 11 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 47 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 24 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 71 | 127 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 350 | 583 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 70 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6123 | 5939.724 | 1825 | 2313 | 5222.1 | 5286.1 | 5222.1 | 5286.1
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 13 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 12 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 121 | 167 | 115 | 115 | 115 | 115 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 218 | 221 | 221 | 221 | 221 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 64 | 80 | 64 | 80 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 33 | 68 | 68 | 68 | 68 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 17 | 39 | 30 | 30 | 30 | 30 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0 | 0 | 2.75 | 0 | 2.75 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 800 | 936 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 11 | 6 | 0 | 6 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 402 | 385 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1568 | 1810 | 3454.47 | 3441.72 | 3454.47 | 3441.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 206 | 191 | 221 | 221 | 221.43 | 221.43 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 320 | 354 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 320 | 340 | 330 | 330 | 340 | 340 | machine problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 31 | 32 | 46.7 | 46.7 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 30 | 45 | 55 | 55 | 52 | 52 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 16 | 122 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 5 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 135 | 135 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 47 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 80 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 33 | 135 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 26 | 34 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 9 | 14 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 47 | 97 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 19 | 29 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 42 | 96 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 60 | 0 | 35 | 0 | 35 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2891.241 | 1244 | 1701 | 2425.75 | 2390.75 | 2371.48 | 2336.48
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-06-2025 | during | 06-06-2025 | during | 06-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 102 | 157 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 45 | 70 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 16 | 45 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 50.01 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 0 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 220.01 | 272 | 593.1 | 549 | 593.1 | 549
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 32 | 32 | 33 | 33 | 33 | 33 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 153 | 154 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | -
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 28 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 40 | 80 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 165 | 163 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 6 | 8 | 0 | 0 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 295 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 390 | 362 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2400 | 2325 | 1477 | 1492 | 1558 | 1558 | 1496 | 1496
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 821 | 820 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 320 | 351 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 94.22 | 0 | 65 | 0 | 65 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 784 | 782 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3699.2 | 2019.22 | 1953 | 3577.2 | 3512.2 | 3577 | 3512
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 6 | 8 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 100 | 114 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 600 | 900 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 172 | 168 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.18 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1098.18 | 1410 | 2172 | 2171 | 2172 | 2171
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 35 | 50 | 70 | 70 | 0 | 0 | M/C running
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 177 | 167 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 194 | 184 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 412 | 400 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 | 30 | 30 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.21 | 0 | 5.15 | 0 | 5.15 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 821.79 | 1003.55 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 30.4 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 87 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3460 | 3452.96 | 1760.4 | 1804.55 | 3263.02 | 3096.87 | 3108.24 | 2942.09
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 51 | 50 | 50 | 50 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 200 | 200 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 111 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.8 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 6 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 11 | 0 | 175.36 | 0 | 175.36 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 275.8 | 476 | 723.96 | 512 | 723.96 | 512
System Total |  |  |  |  | 28798.2 | 27044.055 | 11487.61 | 13231.55 | 22989.6 | 22517.64 | 22718.35 | 22246.39
Forecast Scenario (06-06-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12830 |  | 0 |  | 12830
|  |  |  | 1:00 | 12410 |  | 0 |  | 12410
|  |  |  | 2:00 | 12030 |  | 0 |  | 12030
|  |  |  | 3:00 | 11600 |  | 0 |  | 11600
|  |  |  | 4:00 | 11340 |  | 0 |  | 11340
|  |  |  | 5:00 | 11160 |  | 0 |  | 11160
|  |  |  | 6:00 | 10260 |  | 0 |  | 10260
|  |  |  | 7:00 | 10000 |  | 0 |  | 10000
|  |  |  | 8:00 | 9650 |  | 0 |  | 9650
|  |  |  | 9:00 | 9840 |  | 0 |  | 9840
|  |  |  | 10:00 | 10080 |  | 0 |  | 10080
|  |  |  | 11:00 | 10360 |  | 0 |  | 10360
|  |  |  | 12:00 | 10710 |  | 0 |  | 10710
|  |  |  | 13:00 | 11150 |  | 0 |  | 11150
|  |  |  | 14:00 | 10410 |  | 0 |  | 10410
|  |  |  | 15:00 | 10540 |  | 0 |  | 10540
|  |  |  | 16:00 | 10020 |  | 0 |  | 10020
|  |  |  | 17:00 | 9780 |  | 0 |  | 9780
|  |  |  | 18:00 | 9660 |  | 0 |  | 9660
|  |  |  | 18:30 | 10350 |  | 0 |  | 10350
|  |  |  | 19:00 | 11480 |  | 0 |  | 11480
|  |  |  | 19:30 | 12280 |  | 0 |  | 12280
|  |  |  | 20:00 | 12260 |  | 0 |  | 12260
|  |  |  | 21:00 | 12180 |  | 0 |  | 12180
|  |  |  | 22:00 | 12080 |  | 0 |  | 12080
|  |  |  | 23:00 | 12150 |  | 0 |  | 12150
Probable Maximum Temperature: |  |  | 31.10°C
Probable Maximum Demand at Day Peak: |  |  | 10710.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12280.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12280.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 263.98 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:34 hrs on 06-06-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 05-06-2025 | [28 empty] | Date: | 05-06-2025 | [28 empty] | Date: | 05-06-2025 | [28 empty] | Date: | 05-06-2025 | [28 empty] | Date: | 05-06-2025 | [12 empty] | Date: | 05-06-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [12 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 54 | 86 | 81 | 0 | 0 | 0 | 0 | 0 | 450 | 298 | 57 | 0 | 0 | 281 | 101 | 0 | 0 | 90 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 33 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 32 | 502 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1050 | 0 | 51 | 0 | 175 | 0 | 355 | 340 | 51 | 191 | 32 | 95 | 80 | 107 | 27 | 19 | 100 | 18 | 0 | 0 | 32 | 255 | 320 | 325 | 32 | 30 | 129 | 0 | 0 | 82 | 30 | 0 | 18 | 165 | 0 | 86 | 149 | 72 | 0 | 0 | 11 | 7368 | 820 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1090 | 0 | 1420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 163 | 0 | 0 | 0 | 338 | 0 | 0 | 200 | 50 | 35 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 10 | 100 | 220 | 0 | 0 | 1000 | 0 | 6186 | 13554 | 92.48
01:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 54 | 24 | 130 | 0 | 0 | 0 | 0 | 0 | 450 | 300 | 59 | 0 | 0 | 285 | 101 | 0 | 0 | 90 | 16.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 33 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 24 | 505 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 990 | 0 | 51 | 0 | 175 | 0 | 355 | 340 | 51 | 193 | 32 | 84 | 80 | 84 | 9 | 16 | 101 | 30 | 0 | 0 | 32 | 260 | 320 | 334 | 32 | 30 | 133 | 0 | 0 | 83 | 30 | 0 | 18 | 165 | 0 | 48 | 95 | 72 | 0 | 0 | 11 | 7218.5 | 821 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 972 | 0 | 1315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 170 | 0 | 0 | 0 | 342 | 0 | 0 | 200 | 52 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 6 | 100 | 220 | 0 | 0 | 980 | 0 | 5941 | 13159.5 | 92.58
02:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 54 | 16 | 98 | 0 | 0 | 0 | 0 | 0 | 450 | 300 | 95 | 0 | 0 | 285 | 101 | 0 | 0 | 70 | 16.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 33 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 24 | 501 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 920 | 0 | 51 | 0 | 175 | 0 | 355 | 340 | 50 | 195 | 32 | 79 | 80 | 108 | 8 | 20 | 97 | 30 | 0 | 0 | 16 | 260 | 320 | 322 | 32 | 30 | 131 | 0 | 0 | 83 | 30 | 0 | 18 | 165 | 0 | 48 | 95 | 72 | 0 | 0 | 11 | 7069.5 | 821 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 953 | 0 | 1211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 167 | 0 | 0 | 0 | 342 | 0 | 0 | 200 | 52 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 8 | 100 | 220 | 0 | 0 | 952 | 0 | 5790 | 12859.5 | 92.68
03:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 54 | 16 | 82 | 0 | 0 | 0 | 0 | 0 | 450 | 294 | 138 | 0 | 0 | 275 | 101 | 0 | 0 | 70 | 16.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 16 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 30 | 502 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 843 | 0 | 51 | 0 | 177 | 0 | 355 | 340 | 52 | 186 | 32 | 75 | 80 | 105 | 9 | 13 | 97 | 28 | 0 | 0 | 0 | 260 | 320 | 322 | 32 | 30 | 130 | 0 | 0 | 83 | 30 | 0 | 18 | 165 | 0 | 48 | 94 | 73 | 0 | 0 | 11 | 6952.5 | 821 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 901 | 0 | 1156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 165 | 0 | 0 | 0 | 330 | 0 | 0 | 200 | 52 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 9 | 100 | 220 | 0 | 0 | 945 | 0 | 5651 | 12603.5 | 92.48
04:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 54 | 16 | 64 | 0 | 0 | 0 | 0 | 0 | 370 | 295 | 146 | 0 | 0 | 280 | 101 | 0 | 0 | 52 | 16.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 34 | 415 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 860 | 0 | 51 | 0 | 177 | 0 | 355 | 340 | 52 | 191 | 32 | 75 | 80 | 104 | 9 | 14 | 96 | 28 | 0 | 0 | 0 | 260 | 320 | 321 | 32 | 30 | 134 | 0 | 0 | 83 | 30 | 0 | 18 | 165 | 0 | 48 | 94 | 104 | 0 | 0 | 11 | 6799.5 | 821 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 854 | 0 | 1121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 162 | 0 | 0 | 0 | 335 | 0 | 0 | 200 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 9 | 94 | 220 | 0 | 0 | 900 | 0 | 5457 | 12256.5 | 92.88
05:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 35 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 370 | 295 | 210 | 0 | 0 | 270 | 101 | 0 | 0 | 52 | 16.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 34 | 394 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 830 | 0 | 5 | 0 | 78 | 0 | 347 | 330 | 52 | 184 | 32 | 79 | 80 | 107 | 9 | 13 | 94 | 26 | 0 | 0 | 0 | 265 | 320 | 345 | 32 | 30 | 137 | 0 | 0 | 83 | 30 | 0 | 18 | 165 | 0 | 48 | 94 | 104 | 0 | 0 | 11 | 6584.5 | 821 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 790 | 0 | 1121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 166 | 0 | 0 | 0 | 326 | 0 | 0 | 200 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 8 | 98 | 220 | 0 | 0 | 895 | 0 | 5382 | 11966.5 | 92.98
06:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 35 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 300 | 299 | 210 | 0 | 0 | 285 | 41 | 0 | 2 | 35 | 16.5 | 22 | 0 | 72 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 35 | 402 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 778 | 3 | 5 | 0 | 78 | 0 | 280 | 280 | 52 | 193 | 32 | 68 | 80 | 106 | 9 | 13 | 102 | 26 | 0 | 9 | 0 | 270 | 320 | 320 | 32 | 30 | 135 | 0 | 0 | 22 | 30 | 0 | 18 | 165 | 0 | 48 | 75 | 105 | 0 | 1.85 | 11 | 6274.35 | 821 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.66 | 739 | 0 | 827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 2.07 | 166 | 0 | 165 | 0 | 0 | 0 | 342 | 0 | 0.21 | 200 | 50 | 0 | 1 | 0 | 0 | 0 | 0.3 | 7 | 0.03 | 0 | 171 | 8 | 100 | 180 | 0 | 0 | 750 | 0 | 4791.27 | 11065.62 | 93.08
07:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 35 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 210 | 0 | 0 | 290 | 37 | 0 | 8 | 17 | 16.5 | 22 | 0 | 70 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 167 | 0 | 12 | 415 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 800 | 5 | 5 | 0 | 8 | 0 | 280 | 280 | 30 | 198 | 32 | 37 | 80 | 85 | 9 | 13 | 102 | 24 | 0 | 18 | 0 | 240 | 320 | 320 | 32 | 30 | 137 | 0 | 0 | 22 | 30 | 0 | 18 | 165 | 0 | 45 | 75 | 105 | 0 | 3.84 | 11 | 6124.34 | 821 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.86 | 737 | 0 | 828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 9.11 | 158 | 0 | 170 | 0 | 0 | 0 | 346 | 0 | 0.83 | 154 | 50 | 0 | 2 | 0 | 0 | 0 | 1.5 | 41 | 0.14 | 0 | 170 | 6 | 100 | 180 | 0 | 0 | 650 | 0 | 4707.44 | 10831.78 | 93.16
08:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 35 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 210 | 0 | 0 | 285 | 37 | 0 | 8 | 17 | 20 | 22 | 0 | 70 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 2 | 167 | 0 | 15 | 400 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 800 | 8 | 5 | 0 | 8 | 0 | 280 | 280 | 30 | 194 | 32 | 32 | 80 | 51 | 9 | 13 | 102 | 24 | 0 | 34 | 0 | 240 | 320 | 325 | 32 | 30 | 133 | 0 | 0 | 22 | 30 | 0 | 18 | 165 | 0 | 45 | 75 | 104 | 1 | 22.4 | 11 | 6065.4 | 773 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.68 | 741 | 0 | 827.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 18.91 | 158 | 0 | 170 | 0 | 0 | 0 | 342 | 0 | 2.03 | 151 | 52 | 0 | 11 | 0 | 0 | 0 | 3.9 | 49 | 0.28 | 0 | 168 | 7 | 100 | 180 | 0 | 0 | 600 | 0 | 4652.71 | 10718.11 | 93.24
09:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 299 | 210 | 0 | 0 | 290 | 38 | 0 | 16 | 0 | 19 | 22 | 0 | 72 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 7 | 396 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 800 | 9 | 5 | 0 | 8 | 0 | 280 | 280 | 30 | 197 | 32 | 30 | 80 | 17 | 9 | 13 | 20 | 24 | 0 | 15 | 0 | 240 | 320 | 320 | 32 | 30 | 132 | 0 | 0 | 22 | 30 | 0 | 18 | 165 | 0 | 45 | 45 | 104 | 2 | 29.82 | 11 | 5865.82 | 773 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.57 | 738 | 0 | 822.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 22.35 | 157 | 0 | 168 | 0 | 0 | 0 | 343 | 0 | 2.24 | 160 | 52 | 0 | 22 | 0 | 0 | 0 | 5.6 | 71 | 0.46 | 0 | 171 | 7 | 100 | 180 | 0 | 0 | 600 | 0 | 4761.43 | 10627.25 | 93.32
10:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 298 | 210 | 0 | 0 | 306 | 36 | 0 | 19 | 0 | 18.5 | 22 | 0 | 71 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 14 | 442 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 810 | 10 | 5 | 0 | 8 | 0 | 280 | 280 | 30 | 208 | 32 | 16 | 80 | 17 | 9 | 14 | 17 | 28 | 0 | 32 | 0 | 245 | 320 | 348 | 32 | 30 | 136 | 0 | 0 | 22 | 30 | 0 | 18 | 165 | 0 | 16 | 45 | 104 | 2 | 27.53 | 10 | 5918.03 | 821 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.5 | 747 | 0 | 835.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 45.06 | 160 | 0 | 172 | 0 | 0 | 0 | 380 | 0 | 4.53 | 161 | 52 | 0 | 24 | 0 | 0 | 0 | 5.8 | 28 | 0.32 | 0 | 173 | 6 | 100 | 220 | 0 | 0 | 600 | 0 | 4898.63 | 10816.66 | 93.4
11:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 210 | 0 | 0 | 304 | 0 | 0 | 25 | 0 | 18.5 | 22 | 0 | 73 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 8 | 435 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 805 | 19 | 5 | 0 | 8 | 0 | 320 | 320 | 30 | 211 | 32 | 24 | 80 | 29 | 9 | 14 | 34 | 26 | 0 | 33 | 0 | 295 | 320 | 352 | 32 | 30 | 148 | 0 | 0 | 22 | 30 | 0 | 18 | 166 | 0 | 16 | 45 | 103 | 2 | 29.87 | 6 | 6060.37 | 821 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.27 | 810 | 0 | 820.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 27.16 | 169 | 0 | 181 | 0 | 0 | 0 | 385 | 0 | 2.66 | 200 | 51 | 0 | 24 | 0 | 0 | 0 | 7.6 | 38 | 0.59 | 0 | 173 | 7 | 100 | 220 | 0 | 0 | 600 | 0 | 5084.54 | 11144.91 | 93.48
12:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 301 | 350 | 0 | 0 | 298 | 0 | 0 | 24 | 0 | 17 | 22 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 17 | 402 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 800 | 12 | 5 | 0 | 16 | 0 | 320 | 320 | 30 | 206 | 31 | 42 | 80 | 33 | 19 | 9 | 47 | 26 | 0 | 60 | 0 | 295 | 320 | 390 | 32 | 30 | 153 | 6 | 0 | 40 | 28 | 0 | 18 | 165 | 0 | 16 | 45 | 102 | 1 | 50.01 | 6 | 6334.01 | 821 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.22 | 784 | 0 | 821.79 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 30.4 | 177 | 0 | 194 | 0 | 0 | 0 | 412 | 0 | 3.21 | 200 | 51 | 0 | 6 | 0 | 0 | 0 | 7.8 | 11 | 0.18 | 0 | 172 | 6 | 100 | 220 | 0 | 0 | 600 | 0 | 5153.6 | 11487.61 | 93.56
13:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 298 | 450 | 0 | 0 | 300 | 0 | 0 | 8 | 0 | 17 | 14 | 0 | 70 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 17 | 410 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 802 | 14 | 22 | 0 | 45 | 0 | 340 | 335 | 44 | 207 | 31 | 52 | 80 | 32 | 9 | 14 | 65 | 30 | 0 | 51 | 0 | 300 | 320 | 390 | 32 | 30 | 154 | 6 | 0 | 51 | 30 | 0 | 18 | 164 | 0 | 16 | 60 | 119 | 2 | 38.92 | 6 | 6641.92 | 821 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.65 | 745 | 0 | 822.53 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 26.08 | 175 | 0 | 193 | 0 | 0 | 0 | 410 | 0 | 2.14 | 200 | 50 | 0 | 28 | 0 | 0 | 0 | 8 | 76 | 0.18 | 0 | 172 | 6 | 120 | 220 | 0 | 0 | 600 | 0 | 5175.58 | 11817.5 | 93.61
14:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 293 | 500 | 0 | 0 | 267 | 0 | 0 | 2 | 17 | 16.5 | 7 | 0 | 70 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 16 | 382 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 780 | 18 | 43 | 0 | 45 | 0 | 346 | 340 | 46 | 184 | 31 | 76 | 80 | 31 | 9 | 14 | 75 | 30 | 0 | 61 | 0 | 295 | 320 | 363 | 32 | 30 | 151 | 6 | 0 | 81 | 30 | 0 | 18 | 164 | 0 | 0 | 24 | 134 | 2 | 14.75 | 6 | 6581.25 | 821 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.81 | 725 | 0 | 823.17 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 0 | 49.27 | 170 | 0 | 188 | 0 | 0 | 0 | 382 | 0 | 3.18 | 200 | 50 | 0 | 9 | 0 | 0 | 0 | 8 | 110 | 0.21 | 0 | 161 | 8 | 120 | 220 | 0 | 0 | 600 | 0 | 5172.64 | 11753.89 | 93.66
15:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 283 | 450 | 0 | 0 | 274 | 0 | 0 | 10 | 17 | 17 | 7 | 0 | 70 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 16 | 382 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 760 | 10 | 10 | 0 | 40 | 0 | 300 | 340 | 46 | 186 | 30 | 90 | 80 | 39 | 9 | 14 | 72 | 30 | 0 | 49 | 0 | 290 | 320 | 360 | 32 | 30 | 129 | 6 | 0 | 81 | 30 | 0 | 18 | 164 | 0 | 0 | 0 | 130 | 0 | 0.71 | 6 | 6348.71 | 820 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.62 | 733 | 0 | 820.77 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 14.89 | 162 | 0 | 179 | 0 | 0 | 0 | 328 | 0 | 1.76 | 200 | 50 | 0 | 12 | 0 | 0 | 0 | 3.1 | 148 | 0.06 | 0 | 164 | 7 | 120 | 220 | 0 | 0 | 600 | 0 | 5091.2 | 11439.91 | 93.71
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 280 | 400 | 0 | 0 | 265 | 0 | 0 | 5 | 17 | 14 | 7 | 0 | 70 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 2 | 167 | 0 | 34 | 382 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 747 | 4 | 10 | 0 | 8 | 0 | 300 | 280 | 46 | 182 | 30 | 90 | 80 | 76 | 9 | 8 | 72 | 30 | 0 | 32 | 0 | 290 | 320 | 350 | 32 | 30 | 128 | 6 | 0 | 61 | 30 | 0 | 18 | 165 | 0 | 0 | 0 | 139 | 0 | 12.89 | 0 | 6117.89 | 821 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.76 | 733 | 0 | 819.39 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 15.95 | 163 | 0 | 180 | 0 | 0 | 0 | 325 | 0 | 2.34 | 200 | 50 | 0 | 8 | 0 | 0 | 0 | 3 | 102 | 0.15 | 0 | 160 | 4 | 112 | 220 | 0 | 0 | 591 | 0 | 4965.59 | 11083.48 | 93.76
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 283 | 300 | 0 | 0 | 278 | 0 | 0 | 8 | 0 | 17 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 1 | 167 | 0 | 38 | 384 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 760 | 3 | 10 | 0 | 8 | 0 | 300 | 280 | 20 | 190 | 30 | 94 | 80 | 88 | 9 | 14 | 75 | 28 | 0 | 13 | 0 | 290 | 320 | 300 | 32 | 30 | 131 | 6 | 0 | 30 | 30 | 0 | 18 | 164 | 0 | 0 | 0 | 141 | 1 | 9.51 | 0 | 5920.51 | 820 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.89 | 734 | 0 | 820.99 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 9.84 | 150 | 0 | 161 | 0 | 0 | 0 | 330 | 0 | 0.85 | 200 | 50 | 0 | 6 | 0 | 0 | 0 | 1.9 | 51 | 0.03 | 0 | 166 | 6 | 96 | 180 | 0 | 0 | 550 | 0 | 4699.5 | 10620.01 | 93.81
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 286 | 250 | 0 | 0 | 273 | 0 | 0 | 3 | 0 | 17 | 6 | 0 | 114 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 38 | 382 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 735 | 1 | 10 | 0 | 8 | 0 | 300 | 280 | 20 | 187 | 31 | 115 | 80 | 91 | 25 | 14 | 73 | 30 | 0 | 1 | 0 | 295 | 320 | 300 | 32 | 30 | 133 | 6 | 0 | 30 | 30 | 0 | 18 | 164 | 0 | 0 | 0 | 154 | 0 | 4.44 | 0 | 5934.44 | 821 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.13 | 731 | 0 | 819.77 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 5.31 | 146 | 0 | 160 | 0 | 0 | 0 | 329 | 0 | 0.48 | 200 | 50 | 0 | 1 | 0 | 0 | 0 | 0.4 | 13 | 0.06 | 0 | 165 | 7 | 96 | 180 | 0 | 0 | 550 | 0 | 4589.15 | 10523.59 | 93.86
19:00 | 0 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 21 | 350 | 293 | 450 | 0 | 0 | 303 | 0 | 0 | 0 | 70 | 17 | 11 | 0 | 140 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 39 | 443 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1000 | 0 | 10 | 0 | 8 | 0 | 346 | 310 | 20 | 209 | 31 | 102 | 80 | 108 | 27 | 7 | 110 | 34 | 16 | 0 | 0 | 300 | 320 | 371 | 32 | 30 | 138 | 6 | 0 | 51 | 30 | 0 | 18 | 165 | 0 | 43 | 70 | 155 | 0 | 0 | 0 | 7089 | 773 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773 | 0 | 962.99 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 165 | 0 | 0 | 0 | 383 | 0 | 0 | 201 | 50 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 10 | 100 | 220 | 0 | 0 | 591 | 0 | 5002.99 | 12091.99 | 93.91
19:30 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 35 | 420 | 296 | 500 | 0 | 0 | 289 | 38 | 0 | 0 | 70 | 17 | 11 | 0 | 121 | 0 | 0 | 0 | 10 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 39 | 392 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1000 | 0 | 18 | 0 | 40 | 0 | 355 | 340 | 30 | 197 | 31 | 99 | 80 | 140 | 28 | 7 | 104 | 32 | 34 | 0 | 0 | 300 | 320 | 376 | 32 | 30 | 148 | 7 | 0 | 81 | 30 | 0 | 18 | 163 | 0 | 45 | 70 | 156 | 0 | 0 | 0 | 7345 | 773 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 828 | 0 | 1051.82 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 183 | 0 | 0 | 0 | 414 | 0 | 0 | 200 | 50 | 66 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 8 | 120 | 220 | 0 | 0 | 809 | 0 | 5534.82 | 12879.82
20:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 42 | 420 | 295 | 500 | 0 | 0 | 283 | 39 | 0 | 0 | 70 | 17 | 11 | 0 | 126 | 0 | 0 | 0 | 10 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 39 | 394 | 0 | 0 | 0 | 1 | 0 | 218 | 0 | 0 | 0 | 980 | 0 | 28 | 0 | 45 | 0 | 354 | 340 | 30 | 193 | 32 | 101 | 80 | 152 | 29 | 5 | 97 | 34 | 34 | 0 | 25 | 300 | 320 | 362 | 32 | 30 | 155 | 8 | 0 | 82 | 30 | 0 | 18 | 163 | 0 | 45 | 70 | 157 | 0 | 0 | 0 | 7361 | 773 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 767 | 0 | 1050.95 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 185 | 0 | 0 | 0 | 400 | 0 | 0 | 200 | 50 | 110 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 6 | 120 | 220 | 0 | 0 | 866 | 0 | 5594.95 | 12955.95 | 93.96
21:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 420 | 298 | 583 | 0 | 0 | 282 | 101 | 0 | 0 | 70 | 15 | 11 | 0 | 127 | 0 | 0 | 0 | 13 | 11 | 33 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 39 | 385 | 0 | 0 | 0 | 8 | 0 | 218 | 0 | 0 | 0 | 936 | 0 | 51 | 0 | 122 | 0 | 354 | 340 | 45 | 191 | 32 | 96 | 80 | 135 | 29 | 14 | 97 | 34 | 34 | 0 | 47 | 295 | 320 | 362 | 32 | 30 | 154 | 8 | 0 | 80 | 30 | 0 | 18 | 163 | 0 | 45 | 70 | 157 | 0 | 0 | 0 | 7588 | 820 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 782 | 0 | 1003.55 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 184 | 0 | 0 | 0 | 400 | 0 | 0 | 200 | 50 | 115 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 8 | 114 | 220 | 0 | 0 | 900 | 0 | 5643.55 | 13231.55 | 94.01
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 420 | 300 | 583 | 0 | 0 | 287 | 101 | 0 | 0 | 70 | 15 | 11 | 0 | 127 | 0 | 0 | 0 | 50 | 15 | 33 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 42 | 398 | 0 | 0 | 0 | 8 | 0 | 218 | 0 | 0 | 0 | 900 | 0 | 43 | 0 | 120 | 0 | 354 | 340 | 44 | 197 | 32 | 96 | 80 | 134 | 28 | 14 | 102 | 40 | 16 | 0 | 47 | 300 | 320 | 381 | 32 | 30 | 150 | 8 | 0 | 82 | 30 | 0 | 18 | 163 | 0 | 45 | 70 | 157 | 0 | 0 | 0 | 7619 | 820 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757 | 0 | 909.95 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 185 | 0 | 0 | 0 | 414 | 0 | 0 | 200 | 50 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 11 | 120 | 220 | 0 | 0 | 890 | 0 | 5504.95 | 13123.95 | 94.06
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 420 | 298 | 583 | 0 | 0 | 287 | 101 | 0 | 0 | 70 | 15 | 11 | 0 | 358 | 0 | 0 | 0 | 70 | 5 | 33 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 42 | 394 | 0 | 0 | 0 | 8 | 0 | 218 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 120 | 0 | 354 | 340 | 46 | 194 | 32 | 97 | 80 | 138 | 29 | 14 | 102 | 42 | 0 | 0 | 47 | 300 | 320 | 372 | 33 | 30 | 141 | 8 | 0 | 82 | 30 | 0 | 18 | 164 | 0 | 45 | 70 | 157 | 0 | 0 | 0 | 7808 | 820 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754 | 0 | 859.87 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 185 | 0 | 0 | 0 | 343 | 0 | 0 | 200 | 50 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 9 | 120 | 220 | 0 | 0 | 850 | 0 | 5337.87 | 13145.87 | 94.11
Total KWH | 0 | 586704 | 253920 | 0 | 0 | 0 | 0 | 46000 | 8506800 | 0 | 0 | 0 | 434160 | 119664 | 465600 | 0 | 0 | 0 | 0 | 249600 | 9056000 | 7068276 | 7616818 | 0 | 0 | 6894148 | 1219000 | 0 | 129847 | 938400 | 368400 | 382680 | 0 | 2071818.18 | 0 | 0 | 0 | 200000 | 284160 | 214834 | 0 | 0 | 0 | 0 | 9359 | 3761600 | 0 | 645600 | 10014545.46 | 0 | 0 | 0 | 34462.8 | 0 | 4949774 | 0 | 0 | 0 | 20089089 | 117180 | 711264 | 0 | 1589091 | 0 | 8180600 | 7720000 | 952800 | 4763000 | 764640 | 1759680 | 1914680 | 2058720 | 348600 | 300760 | 1977900 | 719040 | 110842 | 389745 | 253280 | 6716500 | 7644800 | 8564000 | 762000 | 682560 | 3347754.5 | 88200 | 0 | 1333440 | 717984 | 0 | 432000 | 4455970 | 0 | 795600 | 1449600 | 2792640 | 12950 | 281840 | 144960 | 161465879.94 | 19670545 | 7486848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 432000 | 18763637 | 0 | 21669818 | 0 | 0 | 605000 | 0 | 0 | 0 | 0 | 0 | 0 | 737245 | 0 | 278248 | 3983182 | 0 | 4397236 | 0 | 0 | 0 | 8668909 | 0 | 28500 | 4695000 | 1184291 | 591143 | 138680 | 682646 | 0 | 0 | 51315.24 | 812880 | 3075 | 0 | 4254000 | 179994 | 2521000 | 5252860 | 0 | 0 | 18436363.64 | 0 | 125524415.88 | 286990295.82

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 05-06-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11487.61 | MW | 12:00 Hr. | Energy Generated |  |  | 286.9903 |  | MKWHr.
| Day Peak Demand |  |  | 11487.61 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 13231.55 | MW | 21:00 Hr. | Energy Demand |  |  | 286.9903 |  | MKWHr.
| Evening Peak Demand |  |  | 13231.55 | MW | 21:00 Hr. | Maximum Temperature |  |  | 31 |  | °C
| Minimum Generation of the Day |  |  | 10620.01 | MW | 17:00 Hr. | Total Gas Supplied |  |  | 1082.3 |  | MMCFD
| Maximum Generation of the Day |  |  | 13554 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.5108 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 43.2299 | 0 | 3.048 | 0 | 0 | 0.12985 | 0 | 0 | 46.4078 | Gas | 146.555 | Gas | 526996594.8056
| Chattogram Zone |  |  | 5.7954 | 30.1036 | 0.2493 | 0 | 3.7616 | 0.12654 | 0 | 0.28416 | 40.3206 | Coal | 77.4369 | Coal | 536378550.6888
| Cumilla Zone |  |  | 26.8968 | 0 | 6.509 | 0 | 0 | 0.38975 | 0.71904 | 0 | 34.5146 | HFO | 13.4703 | HFO | 249769286.736
| Mymensingh Zone |  |  | 2.7926 | 0 | 2.3902 | 0 | 0 | 0.29479 | 0 | 0 | 5.4776 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 34.7452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.7452 | Hydro | 3.7616 | Hydro | 376160
| Khulna Zone |  |  | 7.4868 | 18.7636 | 0 | 0 | 0 | 0.432 | 19.6705 | 0 | 46.353 | Solar | 3.4229 | Solar | 54976465.6664
| Barishal Zone |  |  | 7.9539 | 22.6904 | 0 | 0 | 0 | 0.003075 | 0 | 0 | 30.6473 | Import | 42.0594 | Import | 208900929.34
| Rajshahi Zone |  |  | 17.6543 | 0 | 0 | 0 | 0 | 1.044 | 21.6698 | 0 | 40.3681 | Wind | 0.28416 | Wind | 4160102.4
| Rangpur Zone |  |  | 0 | 5.8793 | 1.2738 | 0 | 0 | 1.0029 | 0 | 0 | 8.156
| Total |  |  | 146.555 | 77.4369 | 13.4703 | 0 | 3.7616 | 3.4229 | 42.0594 | 0.28416 | 286.9903
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 526996594.8056 |  | Hydro | 376160
|  |  |  | Coal | 536378550.6888 |  | Solar | 54976465.6664
|  |  |  | HFO | 249769286.736 |  | Import | 208900929.34
|  |  |  | HSD | 0 |  | Wind | 4160102.4
[5 empty] | Total: | 158,15,58,089 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.6705 | Peak Hr Flow | 820.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 21659472.76 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 21.6698 | Peak Hr Flow | 1003.55 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 336 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.71904 | Peak Hr Flow | 34.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 602 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 42.0594 | Peak Hr Flow | 1857.55 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3617
|  |  |  | Chattogram |  | 0 |  | 1184
|  |  |  | Cumilla |  | 0 |  | 1433
|  |  |  | Mymensingh |  | 0 |  | 1129
|  |  |  | Sylhet |  | 0 |  | 584
|  |  |  | Khulna |  | 0 |  | 1743
|  |  |  | Barishal |  | 0 |  | 452
|  |  |  | Rajshahi |  | 0 |  | 1469
|  |  |  | Rangpur |  | 0 |  | 989
|  |  |  | Total |  | 0 |  | 12600
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Meghnaghat CCPP(Summit) GT-2 |  |  | 110
[5 empty] | Total | 300 |  |  |  | Total | 510
|  |  |  | Total Unavailable Capacity |  |  |  | 810
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:25 | 10:05 | Bogura 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Puran bogura-1 (NESCO) Isolator | [7 empty] | 25.0MW load
|  |  | work. | [7 empty] | interrup.
| 08:26 | 10:05 | Bogura 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Puran bogura-1 (NESCO) Isolator | [7 empty] | 25.0MW load
|  |  | work. | [7 empty] | interrup.
| 08:48 | 14:15 | Gopalganj(N)-Madaripur 132kV Ckt-2 Scheduled S/D from Gopalganj 400/132kV end.
| 08:54 | 09:39 | Chowmuhani 132/33kV S/S TR2-425T LT Scheduled S/D Due to 33KV Incoming CB to DS R Phase | [7 empty] | 20.0MW load
|  |  | Loop Maintenance. | [7 empty] | interrup.
| 08:54 | 09:39 | Chowmuhani 132/33kV S/S TR2-425T HT Scheduled S/D Due to 33KV Incoming CB to DS R Phase | [7 empty] | 20.0MW load
|  |  | Loop Maintenance. | [7 empty] | interrup.
| 09:06 | 12:20 | BIPTC S/S 10CF25 Forced S/D Due to Shutdown is taken for emergency maintenance work.
| 09:10 | 11:20 | Jaldhaka 132/33kV S/S 406T-1 LT Forced S/D Due to ৫০/৭৫ এমভিএ ট্রান্সফরমার-০১ এর ৩৩ কেভি | [7 empty] | 7.0MW load
|  |  | সিটি’র Y-ফেজে তাপমাত্রা বেশি রাইজ করায় (১৬৫ ডিগ্রি সে.) সংরক্ষণ কাজ । | [7 empty] | interrup.
| 09:11 | 11:19 | Jaldhaka 132/33kV S/S 406T-1 HT Forced S/D Due to ৫০/৭৫ এমভিএ ট্রান্সফরমার-০১ এর ৩৩ কেভি | [7 empty] | 7.0MW load
|  |  | সিটি’র Y-ফেজে তাপমাত্রা বেশি রাইজ করায় (১৬৫ ডিগ্রি সে.) সংরক্ষণ কাজ | [7 empty] | interrup.
| 09:20 | 09:35 | Panchagarh 132/33kV S/S T-1(407T) LT Forced S/D Due to 33 kv capacitor bank-02 Bus DS | [7 empty] | 6.0MW load
|  |  | Open due to no working of CB tripping signal | [7 empty] | interrup.
| 09:26 | 14:27 | GPH 230/33kV S/S Transformer-01(D05) HT Scheduled S/D Due to General maintenance
|  | 09:26 | Natore 132/33kV S/S TR-1 (405 T) HT is restored.
| 09:27 | 12:55 | Fenchuganj 230/132/33kV S/S AT-02 LT Scheduled S/D Due to Hot spot problem
| 09:28 | 13:00 | Fenchuganj 230/132/33kV S/S AT-02 HT Scheduled S/D Due to Hot spot problem
|  | 09:36 | Natore 132/33kV S/S TR-2 (415 T) HT is restored.
|  | 09:37 | Natore 132/33kV S/S TR-2 (415 T) LT is restored.
|  | 09:40 | Natore 132/33kV S/S TR-1 (405 T) LT is restored.
|  | 09:54 | Bhaluka 132/33kV S/S Transformer- 01 HT is restored.
|  | 09:56 | Bhaluka 132/33kV S/S Transformer- 01 LT is restored.
| 09:58 | 13:06 | Bhaluka 132/33kV S/S Transformer- 02 LT Scheduled S/D
| 09:59 | 13:04 | Bhaluka 132/33kV S/S Transformer- 02 HT Scheduled S/D
| 10:27 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized with remarks:- ST
| 11:28 |  | Unique Meghnaghat Power Limited (UMPL) Shutdown with remarks:- ST
| 11:30 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized
| 12:00 |  | Day peak generation: 11485 MW
| 12:06 | 22:49 | Gopalganj 400/132kV S/S 400kV Rooppur Scheduled S/D
|  | 12:18 | Kishoreganj 132/33kV S/S Tr-3 (424T) LT is restored.
|  | 12:18 | Kishoreganj 132/33kV S/S Tr-3 (424T) HT is restored.
|  | 13:02 | Shahjibazar 132/33kV S/S TR-02 HT is restored.
|  | 13:06 | Shahjibazar 132/33kV S/S TR-02 LT is restored.
|  | 14:16 | Gopalganj(N)-Madaripur 132kV Ckt-2 is restored.
| 14:32 | 16:11 | Patuakhali 132/33kV S/S 425T (T-3) LT Scheduled S/D Due to Hot spot maintenance
| 14:32 | 16:11 | Patuakhali 132/33kV S/S 425T (T-3) HT Scheduled S/D Due to Hot spot maintenance
| 15:05 | 18:49 | GPH 230/33kV S/S Transformer -2 (D07) HT Forced S/D Due to Emergency Maintenance.
| 16:05 |  | Haripur-Sonargaon 132kV Ckt-2 Tripped from Haripur 230/132kV end showing
Opimho Zone-1, BN(Y-phase) relays Due to Thunderstorm and from Sonargaon 132/33kV end
showing Line Distance relay (General trip, Z-1, Y-ph fault, A/R operated, carrier send.
relays Due to Bed weather and thunderstorm.
| 16:27 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized with remarks:- ST
| 18:57 | 02:59 | Siddhirganj 132/33kV S/S T-1 LT Tripped showing 51,51N,67,67N relays Due to O/C,E/F 33kv
Side trip for DPDC side trip
| 19:12 |  | Raozan unit-2 was sync.
| 19:14 |  | Siddhirganj GT-1 was sync.
| 19:36 | 02:58 | Siddhirganj 132/33kV S/S T-1 HT Forced S/D Due to 33 kv CB Fault DPDC side
| 19:51 | 02:59 | Siddhirganj 132/33kV S/S T-1 LT Forced S/D Due to 33 kv CB Fault DPDC side
| 21:00 |  | Evening Peak Generation: 13231 MW.
| 21:02 | 23:58 | Chowmuhani 132/33kV S/S TR2-425T LT Forced S/D Due to 132/33 KV Tr-02 X-former & | [7 empty] | 40.0MW load
|  |  | associate 33 KV BUS R-phase Isulator Nut Red-Hot Maintn. | [7 empty] | interrup.
| 00:30 |  | Meghnaghat Summit CCPP 335MW GT-2 was forced shutdown due to HRG leakage.
| 00:30 |  | Meghnaghat CCPP(Summit) Shutdown with remarks:- GT2
| 00:30 |  | Meghnaghat CCPP(Summit) GT-2 Forced Shutdown with remarks:- HRSG-2 leakage
| 00:31 |  | Sirajgonj 225MW CCPP Unit-3 Synchronized with remarks:- GT
| 00:31 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- Gt 2 (False SMS), / GT 2 S/D & GT 1
Running
| 00:40 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- Gt 2 (False SMS)
| 00:40 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- Gt-2 sd-00:30
| 01:07 | 03:00 | Shahjibazar-Sreemangal 132kV Ckt-1 Forced S/D from Shahjibazar 132/33kV end Due to
Sreemongol circuit 1 bus loop B phase maintenance work. and from Sreemongol 132/33kV end
Due to Redhot removing work at Shahjibazar SS.
| 03:24 |  | Sirajgonj Unit-3 ST was sync.
| 03:24 |  | Sirajgonj 225MW CCPP Unit-3 Synchronized with remarks:- ST
| 07:00 |  | Min. Gen. 10008 MW
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 05-06-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 46000 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 342 | 8506800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9056000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 298 | 7068276 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 101 | 1219000 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 282 | 6894148 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 0 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 465600 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 15 | 368400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 11 | 382680 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 253920 | Fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 119664 | Machine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 586704 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 47 | 249600 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 129847 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 434160 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 127 | 2071818.18 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 583 | 7616818 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 70 | 938400 | -
Dhaka Area Total |  |  |  |  | 5939.724 | 2313 | 46407835.18
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 13 | 200000 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 34462.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 117180 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 167 | 3761600 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 4949774 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 33 | 214834 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 39 | 645600 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 9359 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 936 | 20089089 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 11 | 284160 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 385 | 10014545.46 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4895.72 | 1810 | 40320604.26
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 191 | 4763000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 354 | 8180600 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 7720000 | machine problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 32 | 764640 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 45 | 952800 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 122 | 1589091 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 711264 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 47 | 253280 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1914680 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 135 | 2058720 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 34 | 719040 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 34 | 110842 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 300760 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 97 | 1977900 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 29 | 348600 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 96 | 1759680 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 389745 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1701 | 34514642
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 157 | 2792640 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12950 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 70 | 1449600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 45 | 795600 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 281840 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 144960 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 272 | 5477590
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 32 | 762000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 682560 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 154 | 3347754.5 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 717984 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1333440 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 163 | 4455970 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 432000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 88200 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 6716500 | Gas shortage
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 362 | 8564000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7644800 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1492 | 34745208.5
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 820 | 19670545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 351 | 7486848 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 432000 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 782 | 18763637 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3699.2 | 1953 | 46353030
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 8 | 179994 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 114 | 2521000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 900 | 18436363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5252860 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 168 | 4254000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3075 | -
Barishal Area Total |  |  |  |  | 2236 | 1410 | 30647292.64
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 50 | 605000 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 167 | 3983182 | -
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 184 | 4397236 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 400 | 8668909 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 28500 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1003.55 | 21669818 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 278248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 737245 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 1804.55 | 40368138
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1184291 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4695000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 111 | 682646 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 51315.24 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 591143 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 138680 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 812880 | -
Rangpur Area Total |  |  |  |  | 950 | 476 | 8155955.24
Eastern Grid Total |  |  |  |  | 16705.895 | 7588 | 161465879.94
Western Grid Total |  |  |  |  | 10338.16 | 5643.55 | 125524415.88
National Grid Total |  |  |  |  | 27044.055 | 13231.55 | 286990295.82
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 05-06-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7947.05 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4653.3 | MW
i) Dhaka area |  |  | 3616.76 |  | MW | i) Khulna area |  |  |  | 1742.8 | MW
ii) Chattogram area |  |  | 1184 |  | MW | ii) Barishal area |  |  |  | 452.5 | MW
iii) Cumilla area |  |  | 1433.29 |  | MW | iii) Rajshahi area |  |  |  | 1469 | MW
iv) Mymensingh area |  |  | 1129 |  | MW | iv) Rangpur area |  |  |  | 989 | MW
v) Sylhet area |  |  | 584 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12600.35 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 20 | 07:00 | 67 | Ishurdi | 75 | 00:00 | 133 | Patuakhali | 89 | 23:00
2 | AKSML | 152 | 03:00 | 68 | Jaldhaka | 87 | 21:00 | 134 | Payra | 34 | 22:00
3 | Aftabnagar | 30 | 00:00 | 69 | Jamalpur | 136 | 20:00 | 135 | Postogola | 44 | 00:00
4 | Agargaon | 94 | 13:00 | 70 | Jashore | 136 | 00:00 | 136 | Purbachal | 17 | 00:00
5 | Agrabad | 78 | 18:30 | 71 | Jhenaidah | 132 | 19:30 | 137 | Purbasadipur | 135 | 20:00
6 | Amnura | 48 | 15:00 | 72 | Joydebpur | 110 | 00:00 | 138 | Rahanpur | 34 | 21:00
7 | Ashuganj | 90 | 00:00 | 73 | Joypurhat | 65 | 21:00 | 139 | Rahim | 14 | 04:00
8 | BSRM | 111 | 02:00 | 74 | Juldah | 13 | 00:00 | 140 | Rajbari | 78 | 00:00
9 | Bagerhat | 86 | 20:00 | 75 | KSRM | 14 | 11:00 | 141 | Rajendrapur | 107 | 00:00
10 | Bajitpur | 50 | 00:00 | 76 | Kabirpur | 186 | 00:00 | 142 | Rajshahi | 103 | 23:00
11 | Bakulia | 81 | 14:00 | 77 | Kachua | 97 | 23:00 | 143 | Rajshahi-230 | 89 | 23:00
12 | Banani | 24 | 14:00 | 78 | Kallyanpur | 90 | 00:00 | 144 | Ramganj | 116 | 22:00
13 | Bangabhaban | 5 | 10:00 | 79 | Kalurghat | 28 | 00:00 | 145 | Rampur | 36 | 23:00
14 | Barapukuria | 68 | 22:00 | 80 | Kamrangirchar | 53 | 00:00 | 146 | Rangamati | 18 | 20:00
15 | Barguna | 16 | 19:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 147 | 21:00
16 | Barishal | 106 | 21:00 | 82 | Kasba | 38 | 21:00 | 148 | Ruppur | 7.6 | 11:00
17 | Barishal-230 | 89 | 23:00 | 83 | Kazla | 78 | 01:00 | 149 | SSM | 0 | 00:00
18 | Baroaulia | 54 | 21:00 | 84 | Keranigonj | 79 | 00:00 | 150 | Saidpur | 110 | 21:00
19 | Baroirhat | 65 | 15:00 | 85 | Khagrachori | 30 | 20:00 | 151 | Satkhira | 147 | 21:00
20 | Bashundhara | 143 | 14:00 | 86 | Khulna | 64 | 13:00 | 152 | Satmasjid | 78 | 13:00
21 | BashundharaCement | 10 | 16:00 | 87 | Khulshi | 165 | 19:00 | 153 | Savar | 134 | 00:00
22 | Beanibazar | 84 | 22:00 | 88 | Kishoreganj | 142 | 22:00 | 154 | SevenRings | 10.69 | 02:00
23 | Benapole | 66 | 23:00 | 89 | Kodda | 221 | 00:00 | 155 | ShahCement | 24 | 00:00
24 | Bhaluka | 128 | 00:00 | 90 | Kulaura | 52 | 19:00 | 156 | Shahjadpur | 79 | 19:30
25 | Bhandaria | 59 | 22:00 | 91 | Kurigram | 68 | 20:00 | 157 | Shahjibazar | 114 | 21:00
26 | Bhangura | 41 | 00:00 | 92 | Kushtia | 146 | 00:00 | 158 | Shahmirpur | 45 | 19:00
27 | Bheramara(GK) | 70 | 22:00 | 93 | Lalbag | 46 | 00:00 | 159 | Shariatpur | 88 | 22:00
28 | Bhulta | 236 | 01:00 | 94 | Lalmonirhat | 67 | 19:30 | 160 | Sherpur | 142 | 00:00
29 | Bog-Sherpur | 66 | 00:00 | 95 | MI_Cement | 2.7 | 00:00 | 161 | Shikalbaha | 21 | 20:00
30 | Bogura | 164 | 22:00 | 96 | Madanganj | 31 | 23:00 | 162 | Shitalakhya | 67.8 | 11:00
31 | Borhanuddin | 90 | 21:00 | 97 | Madaripur | 108 | 23:00 | 163 | Sholosohor | 35 | 23:00
32 | Brahmanbaria | 136 | 22:00 | 98 | Madartek | 76 | 00:00 | 164 | Shyampur | 122 | 00:00
33 | Cantonment | 112 | 13:00 | 99 | Madunaghat | 48 | 22:00 | 165 | Siddhirganj | 94 | 00:00
34 | Chandina | 26.66 | 19:30 | 100 | Magura | 64 | 19:30 | 166 | Sirajganj | 106 | 00:00
35 | Chandpur | 82 | 22:00 | 101 | Mahasthangarh | 80 | 00:00 | 167 | Sonargaon | 84 | 00:00
36 | Chandraghona | 37 | 20:00 | 102 | Manikganj | 117 | 00:00 | 168 | Sreemongol | 68 | 20:00
37 | Chapai | 72 | 22:00 | 103 | Maniknagar | 58 | 00:00 | 169 | Sreepur | 85 | 00:00
38 | Charsaidpur | 28 | 00:00 | 104 | Matarbari | 48 | 19:00 | 170 | Srinagar | 45.69 | 23:00
39 | Chauddagram | 73 | 22:00 | 105 | Matuail | 48 | 00:00 | 171 | Sunamganj | 61 | 23:00
40 | Chhatak | 37 | 23:00 | 106 | Millgate | 62 | 18:30 | 172 | Sylhet | 46 | 23:00
41 | Chowmuhani | 233 | 19:30 | 107 | Mirpur | 95 | 14:00 | 173 | Sylhet-132 | 107 | 20:00
42 | Chuadanga | 118 | 22:00 | 108 | Mirsorai | 8 | 15:00 | 174 | TK | 59 | 04:00
43 | Coxsbazar | 128 | 19:30 | 109 | Mirzapur | 43 | 00:00 | 175 | Tangail | 167 | 00:00
44 | Cumilla(N) | 164 | 22:00 | 110 | Mithapukur | 64 | 20:00 | 176 | Thakurgaon | 110 | 20:00
45 | Cumilla(S) | 161 | 22:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 94 | 00:00
46 | Daudkandi | 138 | 00:00 | 112 | Mogbazar | 100.4 | 13:00 | 178 | Ullahpara | 41 | 19:30
47 | Dhaka | 32 | 13:00 | 113 | Mongla | 30 | 07:00 | 179 | Ullon | 34 | 00:00
48 | Dhamrai | 120 | 00:00 | 114 | Motijheel | 26 | 13:00 | 180 | Uttara | 62 | 13:00
49 | Dhanmondi | 98 | 13:00 | 115 | Muktagacha | 36 | 21:00 | 181 | UttaraNew | 47 | 00:00
50 | Dohazari | 106 | 19:30 | 116 | Munshiganj | 110 | 00:00 | 182 | Zigatola | 56 | 00:00
51 | Faridpur | 152 | 00:00 | 117 | Muradnagar | 32 | 22:00
52 | Fatullah | 72 | 00:00 | 118 | Mymensingh | 200 | 19:30
53 | Fenchuganj | 37 | 23:00 | 119 | Naogaon | 135 | 19:30
54 | Feni | 127 | 23:00 | 120 | Narail | 57.5 | 20:00
55 | GPH | 36 | 03:00 | 121 | Narinda | 50 | 13:00
56 | Ghatail | 78 | 00:00 | 122 | Narshingdi | 164 | 02:00
57 | Ghorashal | 15 | 22:00 | 123 | Natore | 160 | 20:00
58 | Ghorashal-230 | 66 | 14:00 | 124 | Nawabganj | 54.4 | 22:00
59 | Goalpara | 38 | 00:00 | 125 | Netrakona | 126 | 22:00
60 | Gollamari | 90 | 00:00 | 126 | New | 55 | 00:00
61 | Gopalganj | 101.3 | 23:00 | 127 | Niamatpur | 77 | 22:00
62 | Gulshan | 78 | 14:00 | 128 | Noapara | 44 | 00:00
63 | Halishahar | 56 | 21:00 | 129 | PHP | 5 | 05:00
64 | HaripurSBU | 141 | 00:00 | 130 | Pabna | 122 | 21:00
65 | Hasnabad | 58 | 00:00 | 131 | Palashbari | 122 | 21:00
66 | Hathazari | 85 | 19:00 | 132 | Panchagarh | 61 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 05-06-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13554 | 0 |  | 13554
1:00 | 13159.5 | 0 |  | 13159.5
2:00 | 12859.5 | 0 |  | 12859.5
3:00 | 12603.5 | 0 |  | 12603.5
4:00 | 12256.5 | 0 |  | 12256.5
5:00 | 11966.5 | 0 |  | 11966.5
6:00 | 11065.62 | 0 |  | 11065.62
7:00 | 10831.78 | 0 |  | 10831.78
8:00 | 10718.11 | 0 |  | 10718.11
9:00 | 10627.25 | 0 |  | 10627.25
10:00 | 10816.66 | 0 |  | 10816.66
11:00 | 11144.91 | 0 |  | 11144.91
12:00 | 11487.61 | 0 |  | 11487.61
13:00 | 11817.5 | 0 |  | 11817.5
14:00 | 11753.89 | 0 |  | 11753.89
15:00 | 11439.91 | 0 |  | 11439.91
16:00 | 11083.48 | 0 |  | 11083.48
17:00 | 10620.01 | 0 |  | 10620.01
18:00 | 10523.59 | 0 |  | 10523.59
19:00 | 12091.99 | 0 |  | 12091.99
19:30 | 12879.82 | 0 |  | 12879.82
20:00 | 12955.95 | 0 |  | 12955.95
21:00 | 13231.55 | 0 |  | 13231.55
22:00 | 13123.95 | 0 |  | 13123.95
23:00 | 13145.87 | 0 |  | 13145.87
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 05-06-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7368 | 6186 | 13554 | DAILY GENERATION CURVE
00:30 | 7293.25 | 6063.5 | 13356.75
01:00 | 7218.5 | 5941 | 13159.5 | 05-06-2025
01:30 | 7144 | 5865.5 | 13009.5
02:00 | 7069.5 | 5790 | 12859.5
02:30 | 7011 | 5720.5 | 12731.5
03:00 | 6952.5 | 5651 | 12603.5
03:30 | 6876 | 5554 | 12430
04:00 | 6799.5 | 5457 | 12256.5
04:30 | 6692 | 5419.5 | 12111.5
05:00 | 6584.5 | 5382 | 11966.5
05:30 | 6429.425 | 5086.635 | 11516.06
06:00 | 6274.35 | 4791.27 | 11065.62
06:30 | 6199.345 | 4749.355 | 10948.7
07:00 | 6124.34 | 4707.44 | 10831.78
07:30 | 6094.87 | 4680.075 | 10774.945
08:00 | 6065.4 | 4652.71 | 10718.11
08:30 | 5965.61 | 4707.07 | 10672.68
09:00 | 5865.82 | 4761.43 | 10627.25
09:30 | 5891.925 | 4830.03 | 10721.955
10:00 | 5918.03 | 4898.63 | 10816.66
10:30 | 5989.2 | 4991.585 | 10980.785
11:00 | 6060.37 | 5084.54 | 11144.91
11:30 | 6197.19 | 5119.07 | 11316.26
12:00 | 6334.01 | 5153.6 | 11487.61
12:30 | 6487.965 | 5164.59 | 11652.555
13:00 | 6641.92 | 5175.58 | 11817.5
13:30 | 6611.585 | 5174.11 | 11785.695
14:00 | 6581.25 | 5172.64 | 11753.89
14:30 | 6464.98 | 5131.92 | 11596.9
15:00 | 6348.71 | 5091.2 | 11439.91
15:30 | 6233.3 | 5028.395 | 11261.695
16:00 | 6117.89 | 4965.59 | 11083.48
16:30 | 6019.2 | 4832.545 | 10851.745
17:00 | 5920.51 | 4699.5 | 10620.01
17:30 | 5927.475 | 4644.325 | 10571.8
18:00 | 5934.44 | 4589.15 | 10523.59
18:30 | 6511.72 | 4796.07 | 11307.79
19:00 | 7089 | 5002.99 | 12091.99
19:30 | 7345 | 5534.82 | 12879.82
20:00 | 7361 | 5594.95 | 12955.95
20:30 | 7474.5 | 5619.25 | 13093.75 |  | Executive Engineer
21:00 | 7588 | 5643.55 | 13231.55 |  | Network Operation Division
21:30 | 7603.5 | 5574.25 | 13177.75
22:00 | 7619 | 5504.95 | 13123.95
22:30 | 7713.5 | 5421.41 | 13134.91
23:00 | 7808 | 5337.87 | 13145.87

## En-Curve
QF-LDC-12
Date | 05-06-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4030 | 1851 | 820 | 0 | 18 | 1420 | 167 | 4089 | 0 | 357 | 800 | 0 | 0 | 2 | 0 | DAILY ENERGY CURVE
00:30 | 4053 | 1858.75 | 820.5 | 0 | 24 | 1367.5 | 167 | 3993 | 0 | 381.5 | 690 | 0 | 0 | 1.5 | 0 | 05-06-2025
01:00 | 4076 | 1866.5 | 821 | 0 | 30 | 1315 | 167 | 3897 | 0 | 406 | 580 | 0 | 0 | 1 | 0
01:30 | 4063 | 1886 | 821 | 0 | 30 | 1263 | 167 | 3838 | 0 | 354.5 | 583 | 0 | 0 | 4 | 0 | Energy Generated | 286.9903 |  | MKWHr
02:00 | 4050 | 1905.5 | 821 | 0 | 30 | 1211 | 167 | 3779 | 0 | 303 | 586 | 0 | 0 | 7 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 4027.5 | 1925.5 | 821 | 0 | 29 | 1183.5 | 167 | 3708 | 0 | 278.5 | 582.5 | 0 | 0 | 9 | 0 | Total Energy Requirement | 286.9903 |  | MKWHr
03:00 | 4005 | 1945.5 | 821 | 0 | 28 | 1156 | 167 | 3637 | 0 | 254 | 579 | 0 | 0 | 11 | 0
03:30 | 4026 | 1914.5 | 821 | 0 | 28 | 1138.5 | 167 | 3557 | 0 | 219 | 543 | 0 | 0 | 16 | 0
04:00 | 4047 | 1883.5 | 821 | 0 | 28 | 1121 | 167 | 3477 | 0 | 184 | 507 | 0 | 0 | 21 | 0
04:30 | 4047.5 | 1846 | 821 | 0 | 27 | 1121 | 167 | 3413 | 0 | 151.5 | 500 | 0 | 0 | 17.5 | 0
05:00 | 4048 | 1808.5 | 821 | 0 | 26 | 1121 | 167 | 3349 | 0 | 119 | 493 | 0 | 0 | 14 | 0
05:30 | 3925.5 | 1763 | 821 | 0 | 26 | 974 | 167 | 3219.5 | 19.06 | 110.5 | 473.5 | 0 | 0 | 17 | 0
06:00 | 3803 | 1717.5 | 821 | 0 | 26 | 827 | 167 | 3090 | 38.12 | 102 | 454 | 0 | 0 | 20 | 0
06:30 | 3812.5 | 1644.5 | 821 | 0 | 25 | 827.5 | 167 | 3033 | 80.7 | 93 | 426.5 | 0 | 0 | 18 | 0
07:00 | 3822 | 1571.5 | 821 | 0 | 24 | 828 | 167 | 2976 | 123.28 | 84 | 399 | 0 | 0 | 16 | 0
07:30 | 3802.5 | 1573.25 | 797 | 0 | 24 | 827.955 | 167 | 2944 | 165.74 | 84 | 379.5 | 0 | 0 | 10 | 0
08:00 | 3783 | 1575 | 773 | 0 | 24 | 827.91 | 167 | 2912 | 208.2 | 84 | 360 | 0 | 0 | 4 | 0
08:30 | 3795 | 1570.5 | 773 | 0 | 24 | 825.06 | 167 | 2914.5 | 260.12 | 58.5 | 277 | 0 | 0 | 8 | 0
09:00 | 3807 | 1566 | 773 | 0 | 24 | 822.21 | 167 | 2917 | 312.04 | 33 | 194 | 0 | 0 | 12 | 0
09:30 | 3858 | 1592.75 | 797 | 0 | 26 | 828.815 | 144 | 2951 | 311.89 | 33 | 170.5 | 0 | 0 | 9 | 0
10:00 | 3909 | 1619.5 | 821 | 0 | 28 | 835.42 | 121 | 2985 | 311.74 | 33 | 147 | 0 | 0 | 6 | 0
10:30 | 3979 | 1650 | 821 | 0 | 27 | 827.84 | 121 | 3029.5 | 333.945 | 24.5 | 163.5 | 0 | 0 | 3.5 | 0
11:00 | 4049 | 1680.5 | 821 | 0 | 26 | 820.26 | 121 | 3074 | 356.15 | 16 | 180 | 0 | 0 | 1 | 0
11:30 | 4109.5 | 1794.25 | 821 | 0 | 26 | 821.025 | 121 | 3041.5 | 371.485 | 16 | 194 | 0 | 0 | 0.5 | 0
12:00 | 4170 | 1908 | 821 | 0 | 26 | 821.79 | 121 | 3009 | 386.82 | 16 | 208 | 0 | 0 | 0 | 0
12:30 | 4213 | 2028 | 821 | 0 | 28 | 822.16 | 121 | 2994 | 379.895 | 16 | 224 | 0 | 0 | 5.5 | 0
13:00 | 4256 | 2148 | 821 | 0 | 30 | 822.53 | 121 | 2979 | 372.97 | 16 | 240 | 0 | 0 | 11 | 0
13:30 | 4215 | 2189.75 | 821 | 0 | 30 | 822.85 | 121 | 2938.5 | 385.595 | 20.5 | 230.5 | 0 | 0 | 11 | 0
14:00 | 4174 | 2231.5 | 821 | 0 | 30 | 823.17 | 121 | 2898 | 398.22 | 25 | 221 | 0 | 0 | 11 | 0
14:30 | 4105 | 2143.75 | 820.5 | 0 | 30 | 821.97 | 144 | 2893.5 | 375.68 | 25 | 218.5 | 0 | 0 | 19 | 0
15:00 | 4036 | 2056 | 820 | 0 | 30 | 820.77 | 167 | 2889 | 353.14 | 25 | 216 | 0 | 0 | 27 | 0
15:30 | 3968.5 | 1981 | 820.5 | 0 | 30 | 820.08 | 167 | 2876 | 323.115 | 21 | 231.5 | 0 | 0 | 23 | 0
16:00 | 3901 | 1906 | 821 | 0 | 30 | 819.39 | 167 | 2863 | 293.09 | 17 | 247 | 0 | 0 | 19 | 0
16:30 | 3840.5 | 1804.5 | 820.5 | 0 | 29 | 820.19 | 167 | 2853.5 | 232.055 | 8.5 | 256.5 | 0 | 0 | 19.5 | 0
17:00 | 3780 | 1703 | 820 | 0 | 28 | 820.99 | 167 | 2844 | 171.02 | 0 | 266 | 0 | 0 | 20 | 0
17:30 | 3780.5 | 1708.5 | 820.5 | 0 | 29 | 820.38 | 167 | 2828.5 | 107.42 | 0 | 293.5 | 0 | 0 | 16.5 | 0
18:00 | 3781 | 1714 | 821 | 0 | 30 | 819.77 | 167 | 2813 | 43.82 | 0 | 321 | 0 | 0 | 13 | 0
18:30 | 3965 | 1892 | 797 | 0 | 32 | 891.38 | 167 | 3022.5 | 21.91 | 43 | 461.5 | 0 | 0 | 14.5 | 0
19:00 | 4149 | 2070 | 773 | 0 | 34 | 962.99 | 167 | 3232 | 0 | 86 | 602 | 0 | 0 | 16 | 0
19:30 | 4327 | 2263 | 773 | 0 | 32 | 1051.82 | 167 | 3450 | 0 | 95 | 708 | 0 | 0 | 13 | 0
20:00 | 4293 | 2287 | 773 | 0 | 34 | 1050.95 | 167 | 3426 | 0 | 112 | 801 | 0 | 0 | 12 | 0
20:30 | 4312 | 2388.5 | 796.5 | 0 | 34 | 1027.25 | 167 | 3423.5 | 0 | 139.5 | 794 | 0 | 0 | 11.5 | 0
21:00 | 4331 | 2490 | 820 | 0 | 34 | 1003.55 | 167 | 3421 | 0 | 167 | 787 | 0 | 0 | 11 | 0
21:30 | 4379.5 | 2492.5 | 820 | 0 | 37 | 956.75 | 167 | 3393.5 | 0 | 158.5 | 760 | 0 | 0 | 13 | 0
22:00 | 4428 | 2495 | 820 | 0 | 40 | 909.95 | 167 | 3366 | 0 | 150 | 733 | 0 | 0 | 15 | 0
22:30 | 4399.5 | 2618 | 820 | 0 | 41 | 884.91 | 167 | 3316.5 | 0 | 150 | 728 | 0 | 0 | 10 | 0
23:00 | 4371 | 2741 | 820 | 0 | 42 | 859.87 | 167 | 3267 | 0 | 150 | 723 | 0 | 0 | 5 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 05-06-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 395 | 18:30 | 379 | 00:00 | Payra | 419 | 08:00 | 410 | 00:00
Ashuganj | 410 | 4:00 | 387 | 13:00 | Rahanpur | 414 | 09:00 | 397 | 00:00
Bhulta | 404 | 04:00 | 391 | 12:00 | Rampal | 404 | 06:00 | 390 | 00:00
Bibiana | 393 | 16:00 | 386 | 00:00
BIPTC | 404 | 08:00 | 394 | 00:00
Bogura | 401 | 09:00 | 382 | 00:00
Gopalganj | 403 | 08:00 | 390 | 00:00
Kaliakoir | 385 | 18:00 | 372 | 00:00
Madunaghat | 401 | 07:00 | 391 | 01:00
Meghnaghat | 397 | 16:00 | 381 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 233 | 18:30 | 222 | 00:00 | Keranigonj | 231 | 18:30 | 220 | 00:00
AKSML | 234 | 06:00 | 227 | 00:00 | Khulna(S) | 231 | 08:00 | 218 | 00:00
Aminbazar | 233 | 18:00 | 223 | 00:00 | Madunaghat | 236 | 07:00 | 230 | 00:00
Ashuganj | 233 | 02:00 | 229 | 12:00 | Madunaghat-400 | 237 | 07:00 | 230 | 01:00
Ashuganj-400 | 233 | 02:00 | 229 | 12:00 | Maniknagar | 229 | 17:00 | 220 | 00:00
Baghabari | 235 | 09:00 | 225 | 00:00 | Meghnaghat | 235 | 07:00 | 225 | 00:00
Barapukuria | 224 | 10:00 | 216 | 00:00 | Meghnaghat-400 | 232 | 18:00 | 222 | 00:00
Barapukuria-230 | 224 | 10:00 | 216 | 00:00 | Mirsorai | 234 | 06:00 | 226 | 00:00
Barishal | 239 | 07:00 | 231 | 00:00 | Rajshahi | 235 | 09:00 | 222 | 23:00
Bheramara | 234 | 05:00 | 223 | 00:00 | Rampal | 230 | 06:00 | 219 | 00:00
Bhulta | 236 | 05:00 | 222 | 02:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 233 | 18:30 | 226 | 01:00 | Rampura | 235 | 05:00 | 227 | 12:00
BIPTC | 236 | 05:00 | 224 | 00:00 | Shikalbaha | 234 | 07:00 | 227 | 00:00
Bogura | 235 | 09:00 | 224 | 00:00 | Shyampur | 231 | 18:30 | 220 | 00:00
Bogura-400 | 234 | 09:00 | 224 | 00:00 | Siddhirganj | 233 | 18:00 | 222 | 00:00
Borhanuddin | 243 | 08:00 | 237 | 01:00 | Sirajgonj | 240 | 08:00 | 233 | 00:00
BSRM | 233 | 06:00 | 225 | 00:00 | Sreepur | 232 | 05:00 | 225 | 00:00
Cumilla(N) | 229 | 18:00 | 220 | 00:00 | Tongi | 235 | 18:00 | 226 | 00:00
Faridpur | 236 | 18:00 | 226 | 00:00
Fenchuganj | 233 | 08:00 | 223 | 02:00
Ghorashal | 240 | 20:00 | 235 | 00:00
Ghorashal-230 | 234 | 04:00 | 226 | 00:00
Gopalganj | 237 | 06:00 | 228 | 00:00
GPH | 234 | 07:00 | 228 | 00:00
Haripur | 230 | 17:00 | 221 | 00:00
Hasnabad | 232 | 18:00 | 221 | 00:00
Hathazari | 236 | 08:00 | 229 | 19:00
Ishurdi | 236 | 05:00 | 226 | 23:00
Jhenaidah | 231 | 09:00 | 219 | 00:00
Kaliakoir | 238 | 18:00 | 229 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 03:00 | 131 | 00:00 | Madartek | 135 | 04:00 | 130 | 12:00
Agargaon | 139 | 06:00 | 132 | 19:30 | Madunaghat | 133 | 06:00 | 130 | 00:00
Agrabad | 135 | 06:00 | 129 | 18:30 | Magura | 134 | 07:00 | 124 | 23:00
AKS | 132 | 06:00 | 129 | 08:00 | Mahasthangarh | 134 | 06:00 | 127 | 00:00
Aminbazar | 137 | 18:00 | 130 | 00:00 | Manikganj | 136 | 18:00 | 130 | 00:00
Amnura | 137 | 08:00 | 125 | 00:00 | Maniknagar | 139 | 17:00 | 129 | 19:00
Ashuganj | 138 | 04:00 | 136 | 00:00 | Matarbari | 126 | 09:00 | 111 | 19:30
Bagerhat | 133 | 16:00 | 118 | 00:00 | Matuail | 135 | 18:00 | 129 | 00:00
Bajitpur | 132 | 06:00 | 127 | 23:00 | Millgate | 138 | 16:00 | 132 | 19:00
Bakulia | 133 | 07:00 | 130 | 00:00 | Mirpur | 136 | 18:00 | 129 | 00:00
Banani | 135 | 03:00 | 131 | 12:00 | Mirzapur | 137 | 18:30 | 132 | 12:00
Bangabhaban | 139 | 17:00 | 130 | 19:00 | Mithapukur | 131 | 06:00 | 123 | 00:00
Barapukuria | 134 | 06:00 | 126 | 19:30 | MI_Cement | 135 | 19:00 | 130 | 00:00
Barguna | 136 | 06:00 | 132 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 132 | 18:00 | 126 | 00:00 | Mogbazar | 136 | 03:00 | 132 | 00:00
Barishal-230 | 132 | 07:00 | 126 | 00:00 | Mongla | 132 | 09:00 | 120 | 00:00
Baroaulia | 135 | 07:00 | 131 | 00:00 | Motijheel | 139 | 17:00 | 130 | 19:00
Baroirhat | 128 | 07:00 | 120 | 15:00 | Muktagacha | 137 | 08:00 | 130 | 15:00
Bashundhara | 138 | 04:00 | 131 | 11:00 | Munshiganj | 134 | 16:00 | 127 | 00:00
BashundharaCement | 135 | 18:00 | 128 | 00:00 | Muradnagar | 128 | 06:00 | 122 | 00:00
Beanibazar | 131 | 07:00 | 126 | 19:00 | Mymensingh | 138 | 08:00 | 118 | 22:00
Benapole | 131 | 09:00 | 118 | 00:00 | Naogaon | 134 | 09:00 | 125 | 00:00
Bhaluka | 133 | 18:30 | 125 | 13:00 | Narail | 133 | 06:00 | 122 | 19:30
Bhandaria | 127 | 17:00 | 118 | 22:00 | Narinda | 139 | 17:00 | 129 | 19:00
Bhangura | 134 | 06:00 | 127 | 00:00 | Narshingdi | 133 | 18:30 | 120 | 00:00
Bheramara | 138 | 08:00 | 132 | 00:00 | Natore | 136 | 09:00 | 128 | 23:00
Bheramara(GK) | 137 | 06:00 | 132 | 22:00 | Nawabganj | 139 | 16:00 | 130 | 00:00
Bhulta | 128 | 17:00 | 121 | 01:00 | Netrakona | 127 | 16:00 | 116 | 22:00
Bog-Sherpur | 136 | 08:00 | 128 | 00:00 | New | 139 | 03:00 | 133 | 19:00
Bogura | 138 | 09:00 | 131 | 00:00 | Niamatpur | 137 | 18:00 | 130 | 00:00
Bogura-230 | 138 | 06:00 | 131 | 00:00 | Noapara | 134 | 09:00 | 122 | 00:00
Brahmanbaria | 130 | 18:00 | 125 | 00:00 | Pabna | 135 | 08:00 | 128 | 23:00
Cantonment | 139 | 05:00 | 132 | 19:00 | Palashbari | 129 | 11:00 | 121 | 00:00
Chandina | 130 | 06:00 | 124 | 00:00 | Panchagarh | 135 | 21:00 | 118 | 19:30
Chandpur | 127 | 18:00 | 118 | 10:00 | Patuakhali | 136 | 17:00 | 131 | 00:00
Chandraghona | 135 | 05:00 | 131 | 00:00 | Payra | 137 | 08:00 | 133 | 00:00
Chapai | 133 | 05:00 | 125 | 00:00 | PHP | 126 | 07:00 | 118 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 136 | 18:00 | 124 | 0:00 | Postogola | 139 | 18:00 | 132 | 00:00
Chauddagram | 127 | 04:00 | 118 | 00:00 | Purbachal | 136 | 05:00 | 130 | 13:00
Chhatak | 130 | 06:00 | 123 | 21:00 | Purbasadipur | 127 | 16:00 | 118 | 00:00
Chowmuhani | 120 | 07:00 | 108 | 00:00 | Rahanpur | 137 | 06:00 | 132 | 00:00
Chuadanga | 133 | 14:00 | 120 | 19:30 | Rahanpur-400 | 138 | 09:00 | 132 | 00:00
Coxsbazar | 127 | 07:00 | 113 | 19:00 | Rahim | 135 | 17:00 | 129 | 00:00
Cumilla(N) | 130 | 06:00 | 124 | 00:00 | Rajbari | 137 | 18:00 | 128 | 00:00
Cumilla(S) | 133 | 00:00 | 121 | 00:00 | Rajendrapur | 136 | 18:30 | 128 | 00:00
Daudkandi | 126 | 05:00 | 121 | 00:00 | Rajshahi | 136 | 09:00 | 128 | 00:00
Dhaka | 136 | 04:00 | 131 | 12:00 | Rajshahi-230 | 136 | 09:00 | 121 | 00:00
Dhamrai | 139 | 18:30 | 132 | 00:00 | Ramganj | 123 | 07:00 | 111 | 00:00
Dhanmondi | 136 | 04:00 | 131 | 13:00 | Rampur | 134 | 06:00 | 130 | 00:00
Dohazari | 133 | 07:00 | 123 | 19:30 | Rampura | 136 | 04:00 | 130 | 13:00
Faridpur | 138 | 18:00 | 131 | 00:00 | Rangamati | 134 | 06:00 | 130 | 00:00
Fatullah | 137 | 18:00 | 129 | 00:00 | Rangpur | 128 | 16:00 | 120 | 00:00
Fenchuganj | 138 | 18:00 | 133 | 12:00 | Ruppur | 139 | 09:00 | 132 | 23:00
Feni | 124 | 08:00 | 116 | 13:00 | Saidpur | 131 | 21:00 | 120 | 00:00
Ghatail | 135 | 06:00 | 130 | 12:00 | Satkhira | 132 | 18:00 | 118 | 00:00
Ghorashal | 139 | 05:00 | 136 | 01:00 | Satmasjid | 139 | 06:00 | 132 | 21:00
Goalpara | 136 | 14:00 | 125 | 00:00 | Savar | 135 | 18:00 | 128 | 00:00
Gollamari | 136 | 07:00 | 127 | 00:00 | SevenRings | 140 | 05:00 | 135 | 12:00
Gopalganj | 136 | 14:00 | 128 | 00:00 | ShahCement | 136 | 18:00 | 129 | 00:00
Gopalganj-400 | 138 | 06:00 | 132 | 00:00 | Shahjadpur | 136 | 13:00 | 132 | 00:00
Gulshan | 136 | 03:00 | 131 | 00:00 | Shahjibazar | 131 | 14:00 | 126 | 11:00
Halishahar | 135 | 06:00 | 130 | 00:00 | Shahmirpur | 134 | 09:00 | 131 | 01:00
Haripur | 135 | 17:00 | 129 | 00:00 | Shariatpur | 134 | 06:00 | 127 | 00:00
HaripurSBU | 135 | 18:00 | 129 | 00:00 | Sherpur | 136 | 00:00 | 118 | 18:00
Hasnabad | 139 | 18:00 | 131 | 00:00 | Shikalbaha | 125 | 06:00 | 119 | 00:00
Hathazari | 137 | 05:00 | 131 | 19:00 | Shikalbaha-230 | 136 | 07:00 | 131 | 00:00
Ishurdi | 139 | 08:00 | 133 | 00:00 | Shitalakhya | 135 | 19:00 | 130 | 00:00
Jaldhaka | 127 | 06:00 | 121 | 0:00 | Sholosohor | 135 | 06:00 | 129 | 00:00
Jamalpur | 138 | 00:00 | 123 | 18:00 | Shyampur | 137 | 18:30 | 128 | 00:00
Jashore | 134 | 08:00 | 125 | 00:00 | Shyampur-230 | 136 | 18:00 | 129 | 00:00
Jhenaidah | 136 | 08:00 | 122 | 23:00 | Siddhirganj | 135 | 17:00 | 130 | 00:00
Jhenaidah-230 | 136 | 08:00 | 128 | 19:30 | Sirajganj | 134 | 09:00 | 126 | 00:00
Joydebpur | 137 | 18:30 | 129 | 10:00 | Sonargaon | 133 | 20:00 | 126 | 00:00
Joypurhat | 132 | 05:00 | 123 | 01:00 | Sreemongol | 132 | 05:00 | 128 | 00:00
Juldah | 134 | 05:00 | 130 | 00:00 | Sreepur | 135 | 06:00 | 124 | 13:00
Kabirpur | 138 | 08:00 | 132 | 00:00 | Srinagar | 140 | 16:00 | 131 | 00:00
Kachua | 126 | 07:00 | 118 | 00:00 | SSM | 140 | 06:00 | 132 | 15:00
Kaliakoir | 141 | 06:00 | 136 | 11:00 | Sunamganj | 130 | 07:00 | 122 | 21:00
Kallyanpur | 136 | 16:00 | 130 | 00:00 | Sylhet | 132 | 07:00 | 128 | 11:00
Kalurghat | 133 | 06:00 | 130 | 00:00 | Sylhet-132 | 131 | 05:00 | 129 | 00:00
Kamrangirchar | 139 | 16:00 | 131 | 00:00 | Tangail | 134 | 18:30 | 129 | 12:00
Kaptai | 137 | 8:00 | 134 | 1:00 | Thakurgaon | 133 | 21:00 | 117 | 00:00
Kasba | 127 | 06:00 | 121 | 00:00 | TK | 133 | 08:00 | 129 | 00:00
Kazla | 139 | 18:00 | 130 | 19:30 | Tongi | 140 | 18:00 | 134 | 23:00
Keranigonj | 139 | 16:00 | 132 | 00:00 | Ullahpara | 135 | 17:00 | 128 | 00:00
Khagrachori | 134 | 06:00 | 129 | 01:00 | Ullon | 135 | 04:00 | 131 | 00:00
Khulna | 136 | 14:00 | 126 | 00:00 | Uttara | 136 | 17:00 | 129 | 00:00
Khulna(S) | 136 | 06:00 | 126 | 00:00 | UttaraNew | 135 | 16:00 | 129 | 00:00
Khulshi | 133 | 07:00 | 129 | 00:00 | Zigatola | 138 | 16:00 | 132 | 00:00
Kishoreganj | 131 | 09:00 | 125 | 00:00
Kodda | 139 | 00:00 | 128 | 10:00
KSRM | 135 | 07:00 | 130 | 19:00
Kulaura | 135 | 04:00 | 131 | 12:00
Kurigram | 130 | 06:00 | 116 | 19:30
Kushtia | 135 | 09:00 | 128 | 00:00
Lalbag | 139 | 16:00 | 131 | 00:00
Lalmonirhat | 128 | 10:00 | 118 | 19:30
Madanganj | 135 | 18:00 | 128 | 00:00
Madaripur | 135 | 06:00 | 130 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division