## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 07-06-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-06-2025 | during | 07-06-2025 | during | 07-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 210 | 230 | 230 | 230 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 260 | 260 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 51 | 97.7 | 97.7 | 97.7 | 97.7 | Allocation limit by Titas, instructed by DS(Gen)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 292 | 359 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 136 | 147 | 150 | 150 | 116.5 | 116.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 202 | 208.13 | 208.13 | 208.13 | 208.13 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 305 | 0 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 17 | 17 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 7 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 16 | 16 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 36 | 0 | 20 | 0 | 20 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 360 | 65 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 350 | 150 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 35 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6123 | 5939.724 | 1862 | 2437 | 5027.1 | 5039.1 | 4803.6 | 4815.6
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 120 | 150 | 120 | 120 | 120 | 120 | U#1 Under maintenance, U#2 Running
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 8 | 0 | 12 | 0 | 12 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 132 | 167 | 115 | 115 | 115 | 115 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 188 | 221 | 221 | 221 | 221 | 221 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 64 | 80 | 64 | 80 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 68 | 68 | 68 | 68 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 35 | 41 | 38 | 40 | 38 | 40 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 5 | 0 | 4 | 0 | 4 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 622 | 802 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 2 | 0 | 2 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 379 | 0 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1489 | 1389 | 3669.72 | 3673.72 | 3669.72 | 3673.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 212 | 199 | 221.43 | 221.43 | 205.43 | 205.43 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 300 | 354 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 295 | 340 | 340 | 340 | 340 | 340 | machine problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 26 | 46.7 | 46.7 | 32 | 32 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 48 | 55 | 55 | 52 | 52 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 158 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 0 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 50 | 163 | 163 | 80 | 80 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 69 | 120 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 28 | 34 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 20 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 54 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 22 | 29 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 16 | 113 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 49 | 0 | 30 | 0 | 30 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2891.241 | 1139 | 1664 | 2431.18 | 2401.18 | 2314.48 | 2284.48
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-06-2025 | during | 07-06-2025 | during | 07-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 150 | 156 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.2 | 0 | 1.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 53 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 0 | 16 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 42.7 | 0 | 37.65 | 0 | 37.65 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 202.7 | 225 | 587.85 | 549 | 587.85 | 549
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 32 | 32 | 33 | 33 | 33 | 33 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 148 | 154 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 15 | 20 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 82 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 163 | 164 | 160 | 100 | 160 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 5 | 8 | 0 | 0 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 175 | 320 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 320 | 365 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | -
Sylhet Area Total |  |  |  |  | 2400 | 2325 | 1198 | 1495 | 1565 | 1505 | 1487 | 1427
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 820 | 861 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 220 | 357 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 102.72 | 0 | 48 | 0 | 48 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 384 | 422 | 1234.2 | 1234.2 | 1234 | 1234 | U#1 Reserve shut down as per NLDC Communication
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3699.2 | 1526.72 | 1640 | 3560.2 | 3512.2 | 3560 | 3512
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 8 | 11 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 100 | 120 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 500 | 800 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 210 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.79 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 818.79 | 1151 | 2172 | 2171 | 2172 | 2171
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 40 | 50 | 50 | 50 | 50 | 50 | M/C running
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 130 | 170 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 195 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 130 | 193 | 220 | 220 | 198 | 198 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 391 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 | 30 | 30 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.61 | 0 | 3 | 0 | 3 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 840.93 | 928.27 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 58.12 | 0 | 35 | 0 | 35 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 43 | 0 | 50 | 0 | 50 | 0 | -
Rajshahi Area Total |  |  |  |  | 3460 | 3452.96 | 1765.66 | 1950.27 | 3164.87 | 3076.87 | 3058.09 | 2970.09
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 50 | 50 | 50 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 160 | 200 | 200 | 200 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 111 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.1 | 0 | 3.8 | 0 | 3.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 16 | 0 | 20 | 0 | 20 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 203 | 0 | 110.87 | 0 | 110.87 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 433.1 | 476 | 646.67 | 512 | 646.67 | 512
System Total |  |  |  |  | 28798.2 | 27044.055 | 10434.97 | 12427.27 | 22824.59 | 22440.07 | 22299.41 | 21914.89
Forecast Scenario (07-06-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12100 |  | 0 |  | 12100
|  |  |  | 1:00 | 12000 |  | 0 |  | 12000
|  |  |  | 2:00 | 11880 |  | 0 |  | 11880
|  |  |  | 3:00 | 11380 |  | 0 |  | 11380
|  |  |  | 4:00 | 11060 |  | 0 |  | 11060
|  |  |  | 5:00 | 11030 |  | 0 |  | 11030
|  |  |  | 6:00 | 10430 |  | 0 |  | 10430
|  |  |  | 7:00 | 10240 |  | 0 |  | 10240
|  |  |  | 8:00 | 9310 |  | 0 |  | 9310
|  |  |  | 9:00 | 8930 |  | 0 |  | 8930
|  |  |  | 10:00 | 8580 |  | 0 |  | 8580
|  |  |  | 11:00 | 8610 |  | 0 |  | 8610
|  |  |  | 12:00 | 8790 |  | 0 |  | 8790
|  |  |  | 13:00 | 9160 |  | 0 |  | 9160
|  |  |  | 14:00 | 9780 |  | 0 |  | 9780
|  |  |  | 15:00 | 10010 |  | 0 |  | 10010
|  |  |  | 16:00 | 10340 |  | 0 |  | 10340
|  |  |  | 17:00 | 10310 |  | 0 |  | 10310
|  |  |  | 18:00 | 10210 |  | 0 |  | 10210
|  |  |  | 18:30 | 10800 |  | 0 |  | 10800
|  |  |  | 19:00 | 11410 |  | 0 |  | 11410
|  |  |  | 19:30 | 12430 |  | 0 |  | 12430
|  |  |  | 20:00 | 12340 |  | 0 |  | 12340
|  |  |  | 21:00 | 12660 |  | 0 |  | 12660
|  |  |  | 22:00 | 12650 |  | 0 |  | 12650
|  |  |  | 23:00 | 12690 |  | 0 |  | 12690
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 8930.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12660.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12660.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 252.50 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:06 hrs on 07-06-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 06-06-2025 | [28 empty] | Date: | 06-06-2025 | [28 empty] | Date: | 06-06-2025 | [28 empty] | Date: | 06-06-2025 | [28 empty] | Date: | 06-06-2025 | [12 empty] | Date: | 06-06-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [12 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 380 | 295 | 583 | 0 | 0 | 275 | 101 | 0 | 0 | 70 | 15 | 11 | 0 | 550 | 0 | 0 | 0 | 80 | 7 | 33 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 42 | 390 | 0 | 0 | 0 | 8 | 0 | 218 | 0 | 0 | 0 | 788 | 0 | 5 | 0 | 120 | 0 | 354 | 340 | 51 | 186 | 32 | 96 | 80 | 138 | 12 | 14 | 94 | 42 | 0 | 0 | 47 | 300 | 320 | 357 | 33 | 30 | 133 | 8 | 0 | 62 | 30 | 0 | 18 | 164 | 0 | 45 | 63 | 157 | 0 | 0 | 0 | 7792 | 820 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 743 | 0 | 860.82 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 168 | 0 | 0 | 0 | 328 | 0 | 0 | 200 | 50 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 11 | 120 | 220 | 0 | 0 | 700 | 0 | 5139.82 | 12931.82 | 94.16
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 380 | 140 | 583 | 0 | 0 | 280 | 101 | 0 | 0 | 52 | 15 | 11 | 0 | 593 | 0 | 0 | 0 | 80 | 8 | 33 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 34 | 387 | 0 | 0 | 0 | 8 | 0 | 218 | 0 | 0 | 0 | 794 | 0 | 5 | 0 | 120 | 0 | 354 | 340 | 51 | 192 | 32 | 96 | 80 | 137 | 17 | 14 | 96 | 30 | 0 | 0 | 47 | 295 | 320 | 358 | 33 | 30 | 133 | 8 | 0 | 62 | 30 | 0 | 18 | 163 | 0 | 35 | 55 | 157 | 0 | 0 | 0 | 7648 | 680 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 742 | 0 | 854.91 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 167 | 0 | 2 | 0 | 336 | 0 | 0 | 201 | 50 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 10 | 120 | 220 | 0 | 0 | 700 | 0 | 4980.91 | 12628.91 | 94.19
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 380 | 140 | 583 | 0 | 0 | 275 | 38 | 0 | 0 | 35 | 15 | 11 | 0 | 593 | 0 | 0 | 0 | 100 | 5 | 33 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 42 | 386 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 792 | 0 | 5 | 0 | 8 | 0 | 354 | 340 | 52 | 188 | 32 | 95 | 80 | 132 | 9 | 14 | 98 | 38 | 0 | 0 | 47 | 300 | 320 | 359 | 33 | 30 | 131 | 8 | 0 | 62 | 30 | 0 | 18 | 164 | 0 | 16 | 35 | 157 | 0 | 0 | 0 | 7403 | 680 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 820.94 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 164 | 0 | 2 | 0 | 332 | 0 | 0 | 200 | 50 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 10 | 120 | 220 | 0 | 0 | 602 | 0 | 4798.94 | 12201.94 | 94.22
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 330 | 140 | 500 | 0 | 0 | 272 | 38 | 0 | 0 | 35 | 15 | 11 | 0 | 592 | 0 | 0 | 0 | 100 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 42 | 381 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 780 | 0 | 5 | 0 | 8 | 0 | 300 | 340 | 52 | 186 | 32 | 94 | 80 | 132 | 9 | 14 | 98 | 38 | 0 | 0 | 47 | 295 | 320 | 359 | 33 | 30 | 131 | 6 | 0 | 62 | 30 | 0 | 18 | 164 | 0 | 8 | 24 | 157 | 0 | 0 | 0 | 7137 | 679 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 745 | 0 | 819.62 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 163 | 0 | 2 | 0 | 328 | 0 | 0 | 200 | 50 | 32 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 114 | 220 | 0 | 0 | 600 | 0 | 4701.62 | 11838.62 | 94.25
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 330 | 140 | 400 | 0 | 0 | 272 | 38 | 0 | 0 | 17 | 15 | 11 | 0 | 400 | 0 | 0 | 0 | 100 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 42 | 410 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 800 | 0 | 5 | 0 | 8 | 0 | 300 | 330 | 52 | 185 | 32 | 94 | 80 | 132 | 9 | 14 | 94 | 36 | 0 | 0 | 16 | 295 | 320 | 339 | 33 | 30 | 131 | 6 | 0 | 22 | 30 | 0 | 18 | 165 | 0 | 0 | 24 | 157 | 0 | 0 | 0 | 6709 | 820 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 745 | 0 | 820.57 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 163 | 0 | 12 | 0 | 327 | 0 | 0 | 151 | 50 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 9 | 100 | 180 | 0 | 0 | 600 | 0 | 4701.57 | 11410.57 | 94.28
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 330 | 140 | 400 | 0 | 0 | 278 | 38 | 0 | 0 | 0 | 15 | 11 | 0 | 400 | 0 | 0 | 0 | 100 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 42 | 410 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 656 | 0 | 5 | 0 | 8 | 0 | 280 | 280 | 43 | 181 | 32 | 68 | 80 | 133 | 9 | 14 | 98 | 36 | 0 | 0 | 16 | 285 | 320 | 325 | 33 | 30 | 132 | 6 | 0 | 22 | 30 | 0 | 18 | 165 | 0 | 0 | 8 | 157 | 0 | 0 | 0 | 6375 | 820 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 748 | 0 | 818.93 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 163 | 0 | 41 | 0 | 332 | 0 | 0 | 153 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 10 | 98 | 180 | 0 | 0 | 520 | 0 | 4623.93 | 10998.93 | 94.31
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 330 | 140 | 300 | 0 | 0 | 271 | 0 | 0 | 2 | 0 | 15 | 11 | 0 | 300 | 0 | 0 | 0 | 100 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 35 | 360 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 614 | 2 | 5 | 0 | 8 | 0 | 280 | 280 | 4 | 186 | 5 | 34 | 70 | 99 | 9 | 14 | 42 | 32 | 0 | 6 | 0 | 275 | 300 | 261 | 33 | 30 | 132 | 6 | 0 | 5 | 20 | 0 | 18 | 165 | 0 | 0 | 0 | 157 | 0 | 3.46 | 0 | 5667.46 | 820 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.91 | 750 | 0 | 818.79 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 3.17 | 151 | 0 | 164 | 0 | 97 | 0 | 328 | 0 | 0.28 | 155 | 50 | 0 | 1 | 0 | 0 | 0 | 0.3 | 40 | 0.02 | 0 | 140 | 9 | 96 | 180 | 0 | 0 | 500 | 0 | 4615.47 | 10282.93 | 94.34
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 300 | 140 | 250 | 0 | 0 | 279 | 0 | 0 | 7 | 0 | 15 | 11 | 0 | 280 | 0 | 0 | 0 | 100 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 167 | 0 | 37 | 365 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 615 | 8 | 5 | 0 | 8 | 0 | 280 | 280 | 3 | 154 | 5 | 16 | 70 | 77 | 6 | 14 | 29 | 34 | 0 | 14 | 0 | 240 | 300 | 230 | 33 | 30 | 131 | 6 | 0 | 5 | 30 | 0 | 18 | 164 | 0 | 0 | 0 | 127 | 1 | 12.3 | 0 | 5433.3 | 820 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.97 | 750 | 0 | 810.34 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 11.44 | 152 | 0 | 164 | 0 | 131 | 0 | 250 | 0 | 1.06 | 153 | 50 | 0 | 1 | 0 | 0 | 0 | 0 | 16 | 0.11 | 0 | 140 | 9 | 96 | 180 | 0 | 0 | 502 | 0 | 4574.92 | 10008.22 | 94.37
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 300 | 142 | 250 | 0 | 0 | 230 | 0 | 0 | 14 | 0 | 17 | 11 | 0 | 280 | 0 | 0 | 0 | 100 | 5 | 0 | 0 | 0 | 0 | 0 | 2 | 132 | 0 | 40 | 367 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 615 | 6 | 5 | 0 | 0 | 0 | 280 | 280 | 0 | 154 | 5 | 16 | 70 | 77 | 12 | 14 | 29 | 32 | 0 | 6 | 0 | 215 | 300 | 230 | 33 | 30 | 125 | 6 | 0 | 0 | 30 | 0 | 18 | 164 | 0 | 0 | 0 | 127 | 1 | 25.06 | 0 | 5303.06 | 820 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.32 | 763 | 0 | 823.3 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 21.65 | 130 | 0 | 140 | 0 | 130 | 0 | 250 | 0 | 1.2 | 175 | 51 | 0 | 14 | 0 | 0 | 0 | 2.3 | 100 | 0.34 | 0 | 140 | 8 | 90 | 180 | 0 | 0 | 500 | 0 | 4651.11 | 9954.17 | 94.4
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 300 | 136 | 250 | 0 | 0 | 230 | 0 | 0 | 21 | 0 | 17 | 7 | 0 | 280 | 0 | 0 | 0 | 100 | 4 | 0 | 0 | 0 | 0 | 0 | 3 | 132 | 0 | 35 | 377 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 615 | 5 | 0 | 0 | 0 | 0 | 280 | 280 | 0 | 154 | 0 | 16 | 70 | 75 | 19 | 14 | 31 | 26 | 0 | 56 | 0 | 175 | 300 | 230 | 32 | 20 | 110 | 0 | 0 | 0 | 8 | 0 | 0 | 164 | 0 | 0 | 0 | 108 | 2 | 39.71 | 0 | 5192.71 | 770 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.04 | 731 | 0 | 820.35 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 32.66 | 130 | 0 | 130 | 0 | 130 | 0 | 220 | 0 | 3.39 | 154 | 51 | 0 | 23 | 0 | 0 | 0 | 2.3 | 160 | 0.2 | 0 | 138 | 8 | 90 | 180 | 0 | 0 | 500 | 0 | 4651.94 | 9844.65 | 94.45
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 300 | 142 | 250 | 0 | 0 | 230 | 0 | 0 | 23 | 0 | 17 | 0 | 0 | 280 | 0 | 0 | 0 | 100 | 11 | 0 | 0 | 0 | 0 | 0 | 1 | 132 | 0 | 35 | 377 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 617 | 10 | 0 | 0 | 0 | 0 | 280 | 280 | 0 | 154 | 0 | 16 | 70 | 68 | 18 | 14 | 34 | 28 | 0 | 10 | 0 | 175 | 300 | 230 | 32 | 20 | 110 | 0 | 0 | 0 | 8 | 0 | 0 | 163 | 0 | 0 | 0 | 108 | 1 | 44.74 | 0 | 5146.74 | 704 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.99 | 726 | 0 | 844.76 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 37.15 | 130 | 0 | 130 | 0 | 130 | 0 | 200 | 0 | 3.07 | 160 | 50 | 0 | 29 | 0 | 0 | 0 | 2.8 | 183 | 0.67 | 0 | 143 | 8 | 100 | 180 | 0 | 0 | 500 | 0 | 4630.44 | 9777.18 | 94.5
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 350 | 139 | 330 | 0 | 0 | 280 | 0 | 0 | 32 | 0 | 17 | 0 | 0 | 280 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 132 | 0 | 35 | 377 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 610 | 8 | 0 | 0 | 0 | 0 | 280 | 280 | 0 | 173 | 0 | 16 | 70 | 68 | 18 | 14 | 33 | 22 | 0 | 68 | 0 | 175 | 300 | 277 | 32 | 20 | 130 | 5 | 0 | 0 | 8 | 0 | 0 | 163 | 0 | 0 | 0 | 108 | 2 | 33.79 | 0 | 5489.79 | 820 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.82 | 497 | 0 | 816.27 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 55.16 | 130 | 0 | 130 | 0 | 130 | 0 | 260 | 0 | 1.7 | 160 | 50 | 0 | 24 | 0 | 0 | 0 | 7.6 | 207 | 0.74 | 0 | 84 | 8 | 100 | 180 | 0 | 0 | 500 | 0 | 4578.29 | 10068.08 | 94.55
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 350 | 136 | 350 | 0 | 0 | 305 | 0 | 0 | 36 | 0 | 17 | 0 | 0 | 360 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 132 | 0 | 35 | 379 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 622 | 8 | 0 | 0 | 0 | 0 | 300 | 295 | 0 | 212 | 0 | 16 | 80 | 69 | 22 | 14 | 54 | 28 | 0 | 49 | 0 | 175 | 320 | 320 | 32 | 20 | 148 | 5 | 0 | 0 | 15 | 0 | 0 | 163 | 0 | 0 | 8 | 150 | 2 | 42.7 | 0 | 5890.7 | 820 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.72 | 384 | 0 | 840.93 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 58.12 | 130 | 0 | 130 | 0 | 130 | 0 | 391 | 0 | 2.61 | 160 | 50 | 0 | 16 | 0 | 0 | 0 | 4.1 | 203 | 0.79 | 0 | 0 | 8 | 100 | 210 | 0 | 0 | 500 | 0 | 4544.27 | 10434.97 | 94.6
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 420 | 146 | 480 | 0 | 0 | 0 | 0 | 0 | 27 | 30 | 17 | 7 | 0 | 450 | 0 | 0 | 0 | 120 | 12 | 0 | 0 | 0 | 0 | 0 | 5 | 132 | 0 | 35 | 298 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 704 | 13 | 5 | 0 | 8 | 0 | 352 | 340 | 3 | 204 | 10 | 18 | 80 | 98 | 18 | 14 | 66 | 32 | 0 | 33 | 0 | 285 | 320 | 390 | 32 | 30 | 156 | 6 | 0 | 11 | 30 | 0 | 0 | 164 | 0 | 8 | 24 | 150 | 1 | 49 | 0 | 6437 | 821 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.48 | 408 | 0 | 813.59 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 55.33 | 165 | 0 | 166 | 0 | 163 | 0 | 399 | 0 | 5.06 | 162 | 50 | 0 | 29 | 0 | 0 | 0 | 7.7 | 159 | 0.71 | 0 | 0 | 8 | 120 | 220 | 0 | 0 | 570 | 0 | 4884.87 | 11321.87 | 94.65
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 380 | 148 | 400 | 0 | 0 | 0 | 0 | 0 | 14 | 52 | 17 | 7 | 0 | 400 | 0 | 0 | 0 | 120 | 4 | 0 | 0 | 0 | 0 | 0 | 3 | 132 | 0 | 35 | 225 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 710 | 16 | 10 | 0 | 8 | 0 | 354 | 340 | 10 | 197 | 10 | 31 | 50 | 123 | 18 | 18 | 77 | 32 | 0 | 48 | 0 | 315 | 320 | 374 | 32 | 30 | 153 | 6 | 0 | 11 | 30 | 0 | 0 | 164 | 0 | 24 | 24 | 150 | 1 | 23.7 | 0 | 6247.7 | 820 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.77 | 383 | 0 | 823 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 47.23 | 168 | 0 | 180 | 0 | 191 | 0 | 347 | 0 | 4.13 | 190 | 50 | 0 | 29 | 0 | 0 | 0 | 4.5 | 30 | 0.42 | 0 | 0 | 9 | 120 | 220 | 0 | 0 | 650 | 0 | 4841.05 | 11088.75 | 94.7
15:00 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 340 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 320 | 138 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 7 | 0 | 400 | 0 | 0 | 0 | 130 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 132 | 0 | 35 | 215 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 652 | 6 | 10 | 0 | 8 | 0 | 320 | 280 | 10 | 190 | 10 | 34 | 50 | 136 | 18 | 20 | 88 | 32 | 0 | 48 | 0 | 310 | 320 | 354 | 32 | 30 | 143 | 6 | 0 | 11 | 20 | 0 | 0 | 164 | 0 | 8 | 24 | 150 | 1 | 39.17 | 0 | 6054.17 | 821 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.91 | 370 | 0 | 820 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 38.42 | 157 | 0 | 178 | 0 | 178 | 0 | 335 | 0 | 3.56 | 200 | 50 | 0 | 24 | 0 | 0 | 0 | 5.6 | 158 | 0.24 | 0 | 0 | 9 | 120 | 220 | 0 | 0 | 500 | 0 | 4621.73 | 10675.9 | 94.75
16:00 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 330 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 320 | 132 | 400 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 19 | 7 | 0 | 400 | 0 | 0 | 0 | 150 | 4 | 0 | 0 | 0 | 0 | 0 | 2 | 132 | 0 | 35 | 220 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 607 | 7 | 10 | 0 | 8 | 0 | 320 | 280 | 10 | 186 | 10 | 34 | 50 | 85 | 18 | 8 | 88 | 28 | 0 | 32 | 0 | 300 | 320 | 354 | 32 | 30 | 132 | 6 | 0 | 11 | 20 | 0 | 0 | 164 | 0 | 8 | 16 | 150 | 1 | 29.28 | 0 | 5897.28 | 821 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.31 | 357 | 0 | 820 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 24.71 | 146 | 0 | 163 | 0 | 160 | 0 | 328 | 0 | 2.35 | 200 | 50 | 0 | 16 | 0 | 0 | 0 | 1.4 | 98 | 0 | 0 | 0 | 6 | 92 | 180 | 0 | 0 | 502 | 0 | 4428.77 | 10326.05 | 94.8
17:00 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 331 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 280 | 134 | 300 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 19 | 7 | 0 | 400 | 0 | 0 | 0 | 150 | 6 | 0 | 0 | 0 | 0 | 0 | 1 | 132 | 0 | 35 | 220 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 606 | 4 | 10 | 0 | 8 | 0 | 280 | 280 | 10 | 193 | 10 | 34 | 50 | 17 | 18 | 8 | 88 | 30 | 0 | 14 | 0 | 295 | 320 | 305 | 32 | 30 | 132 | 6 | 0 | 11 | 20 | 0 | 0 | 164 | 0 | 9 | 19 | 150 | 1 | 7.63 | 0 | 5552.63 | 861 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.21 | 355 | 0 | 826 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 11.27 | 147 | 0 | 162 | 0 | 161 | 0 | 338 | 0 | 1.19 | 200 | 50 | 0 | 7 | 0 | 0 | 0 | 0.4 | 50 | 0.05 | 0 | 0 | 8 | 92 | 180 | 0 | 0 | 500 | 0 | 4386.12 | 9938.75 | 94.85
18:00 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 333 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 280 | 138 | 250 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 17 | 7 | 0 | 300 | 0 | 0 | 0 | 150 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 35 | 145 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 606 | 1 | 10 | 0 | 8 | 0 | 280 | 280 | 10 | 188 | 10 | 34 | 50 | 17 | 27 | 16 | 88 | 28 | 0 | 1 | 0 | 305 | 320 | 321 | 32 | 30 | 132 | 6 | 0 | 11 | 20 | 0 | 0 | 164 | 0 | 16 | 32 | 151 | 0 | 3.72 | 0 | 5480.72 | 861 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.89 | 345 | 0 | 826 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 3.27 | 151 | 0 | 166 | 0 | 165 | 0 | 330 | 0 | 0.29 | 201 | 50 | 0 | 1 | 0 | 0 | 0 | 0.2 | 13 | 0.05 | 0 | 0 | 8 | 100 | 180 | 0 | 0 | 500 | 0 | 4291.7 | 9772.42 | 94.9
19:00 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 12 | 395 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 420 | 143 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 17 | 7 | 0 | 450 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 35 | 153 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 725 | 0 | 15 | 0 | 12 | 0 | 345 | 345 | 11 | 215 | 24 | 41 | 50 | 24 | 29 | 20 | 114 | 34 | 8 | 0 | 0 | 315 | 320 | 376 | 32 | 30 | 142 | 8 | 0 | 65 | 20 | 0 | 0 | 164 | 0 | 45 | 65 | 153 | 0 | 0 | 0 | 6857 | 860 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 875 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 179 | 0 | 179 | 0 | 414 | 0 | 0 | 200 | 50 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 120 | 220 | 0 | 0 | 520 | 0 | 4690 | 11547 | 94.95
19:30 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 43 | 335 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 420 | 145 | 583 | 0 | 0 | 0 | 101 | 0 | 0 | 70 | 17 | 7 | 0 | 370 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 35 | 128 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 790 | 0 | 22 | 0 | 45 | 0 | 355 | 340 | 20 | 190 | 26 | 80 | 50 | 120 | 29 | 20 | 114 | 24 | 52.2 | 0 | 0 | 305 | 320 | 341 | 32 | 30 | 152 | 8 | 0 | 82 | 20 | 0 | 0 | 164 | 0 | 45 | 63 | 155 | 0 | 0 | 0 | 7448.2 | 812 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 901 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 196 | 0 | 181 | 0 | 393 | 0 | 0 | 201 | 50 | 100 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 120 | 220 | 0 | 0 | 670 | 0 | 4903 | 12351.2
20:00 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 44 | 357 | 0 | 607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 420 | 145 | 200 | 0 | 0 | 0 | 140 | 0 | 0 | 52 | 17 | 7 | 0 | 350 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 35 | 10 | 0 | 0 | 0 | 1 | 0 | 219 | 0 | 0 | 0 | 780 | 0 | 32 | 0 | 83 | 0 | 354 | 340 | 25 | 193 | 26 | 80 | 50 | 104 | 29 | 20 | 114 | 30 | 25 | 0 | 0 | 310 | 320 | 386 | 32 | 30 | 152 | 8 | 0 | 82 | 20 | 0 | 0 | 164 | 0 | 45 | 70 | 155 | 0 | 0 | 0 | 7230 | 813 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 923 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 190 | 0 | 190 | 0 | 398 | 0 | 0 | 201 | 50 | 110 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 720 | 0 | 4989 | 12219 | 95
21:00 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 51 | 359 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 420 | 147 | 150 | 0 | 0 | 0 | 202 | 0 | 0 | 35 | 17 | 7 | 0 | 65 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 41 | 0 | 0 | 0 | 0 | 8 | 0 | 221 | 0 | 0 | 0 | 802 | 0 | 51 | 0 | 158 | 0 | 354 | 340 | 48 | 199 | 26 | 113 | 50 | 120 | 29 | 20 | 114 | 34 | 8 | 0 | 0 | 320 | 320 | 365 | 32 | 30 | 154 | 8 | 0 | 82 | 20 | 0 | 0 | 164 | 0 | 16 | 53 | 156 | 0 | 0 | 0 | 7210 | 861 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 422 | 0 | 928.27 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 195 | 0 | 193 | 0 | 414 | 0 | 0 | 200 | 50 | 115 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 800 | 0 | 5217.27 | 12427.27 | 95.05
22:00 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 60 | 358 | 0 | 760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 420 | 145 | 60 | 0 | 0 | 0 | 203 | 0 | 0 | 35 | 17 | 7 | 0 | 140 | 0 | 0 | 0 | 150 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 221 | 0 | 0 | 0 | 805 | 0 | 51 | 0 | 175 | 0 | 354 | 340 | 50 | 199 | 26 | 115 | 50 | 100 | 29 | 20 | 114 | 34 | 8 | 0 | 0 | 310 | 320 | 388 | 32 | 30 | 154 | 8 | 0 | 82 | 20 | 0 | 0 | 164 | 0 | 16 | 53 | 156 | 0 | 0 | 0 | 7223 | 861 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 931.95 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 194 | 0 | 191 | 0 | 414 | 0 | 0 | 200 | 50 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 802 | 0 | 5167.95 | 12390.95 | 95.1
23:00 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 67 | 365 | 0 | 710 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 420 | 147 | 60 | 0 | 0 | 0 | 202 | 0 | 0 | 35 | 17 | 7 | 0 | 300 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 28 | 0 | 0 | 0 | 0 | 8 | 0 | 220 | 0 | 0 | 0 | 806 | 0 | 51 | 0 | 175 | 0 | 350 | 340 | 53 | 204 | 26 | 115 | 50 | 100 | 29 | 19 | 114 | 34 | 9 | 0 | 0 | 315 | 320 | 390 | 32 | 30 | 156 | 8 | 0 | 82 | 20 | 0 | 0 | 164 | 0 | 35 | 73 | 156 | 0 | 0 | 0 | 7385 | 861 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 429 | 0 | 930.52 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 199 | 0 | 197 | 0 | 414 | 0 | 0 | 200 | 50 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 803 | 0 | 5211.52 | 12596.52 | 95.15
Total KWH | 0 | 0 | 0 | 0 | 0 | 1547750 | 0 | 287500 | 8161200 | 0 | 1407900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574080 | 8651000 | 3452509 | 7955000 | 0 | 0 | 3265583 | 1269000 | 0 | 205934 | 512400 | 379200 | 191160 | 0 | 8706818.18 | 0 | 0 | 0 | 2900000 | 112320 | 87191 | 0 | 0 | 0 | 0 | 23160 | 3707140 | 0 | 964320 | 6290909.09 | 0 | 0 | 0 | 48151.8 | 0 | 4847443 | 0 | 0 | 0 | 16707271 | 91665 | 398008 | 0 | 1037091 | 0 | 7972100 | 7548000 | 554880 | 4586000 | 392544 | 1403520 | 1520500 | 2338080 | 442680 | 344830 | 1914060 | 772800 | 103310 | 434073 | 202224 | 6634000 | 7540600 | 8155000 | 769000 | 643080 | 3323291 | 146256 | 0 | 715200 | 521568 | 0 | 162000 | 3451100 | 0 | 344400 | 693600 | 3425280 | 13850 | 326030 | 0 | 151175560.07 | 19466181 | 7639488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 573840 | 13243636 | 0 | 20702182 | 0 | 0 | 1105000 | 0 | 0 | 0 | 0 | 0 | 0 | 605474 | 0 | 390752 | 3732273 | 0 | 4243582 | 0 | 3207455 | 0 | 8135309 | 0 | 32520 | 4416000 | 1164218 | 569197 | 223706 | 858470 | 0 | 0 | 44032.32 | 1365120 | 4374 | 0 | 1746000 | 211374 | 2589000 | 5138690 | 0 | 0 | 14935272.73 | 0 | 116343146.05 | 267518706.12

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 06-06-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10434.97 | MW | 12:00 Hr. | Energy Generated |  |  | 267.5187 |  | MKWHr.
| Day Peak Demand |  |  | 10434.97 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 12427.27 | MW | 21:00 Hr. | Energy Demand |  |  | 267.5187 |  | MKWHr.
| Evening Peak Demand |  |  | 12427.27 | MW | 21:00 Hr. | Maximum Temperature |  |  | 34.5 |  | °C
| Minimum Generation of the Day |  |  | 9777.18 | MW | 10:00 Hr. | Total Gas Supplied |  |  | 1201.76 |  | MMCFD
| Maximum Generation of the Day |  |  | 12931.82 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.2428 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 45.2746 | 0 | 1.0865 | 0 | 0 | 0.20593 | 0 | 0 | 46.567 | Gas | 149.8289 | Gas | 537689703.4606
| Chattogram Zone |  |  | 8.7118 | 22.9982 | 0.13534 | 0 | 3.7071 | 0.11482 | 0 | 0.11232 | 35.7796 | Coal | 58.5033 | Coal | 404065377.7091
| Cumilla Zone |  |  | 24.354 | 0 | 6.4039 | 0 | 0 | 0.43407 | 0.7728 | 0 | 31.9647 | HFO | 10.0914 | HFO | 185579133.896
| Mymensingh Zone |  |  | 3.4253 | 0 | 1.038 | 0 | 0 | 0.33988 | 0 | 0 | 4.8032 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 32.0611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.0611 | Hydro | 3.7071 | Hydro | 370714
| Khulna Zone |  |  | 7.6395 | 13.2436 | 0 | 0 | 0 | 0.57384 | 19.4662 | 0 | 40.9231 | Solar | 4.3345 | Solar | 71060848.9952
| Barishal Zone |  |  | 7.9391 | 16.6813 | 0 | 0 | 0 | 0.004374 | 0 | 0 | 24.6247 | Import | 40.9412 | Import | 202135129.34
| Rajshahi Zone |  |  | 20.4236 | 0 | 0 | 0 | 0 | 1.0287 | 20.7022 | 0 | 42.1545 | Wind | 0.11232 | Wind | 1644364.8
| Rangpur Zone |  |  | 0 | 5.5802 | 1.4277 | 0 | 0 | 1.6329 | 0 | 0 | 8.6407
| Total |  |  | 149.8289 | 58.5033 | 10.0914 | 0 | 3.7071 | 4.3345 | 40.9412 | 0.11232 | 267.5187
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 537689703.4606 |  | Hydro | 370714
|  |  |  | Coal | 404065377.7091 |  | Solar | 71060848.9952
|  |  |  | HFO | 185579133.896 |  | Import | 202135129.34
|  |  |  | HSD | 0 |  | Wind | 1644364.8
[5 empty] | Total: | 140,25,45,272 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.4662 | Peak Hr Flow | 861.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 11362018.21 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 20.7022 | Peak Hr Flow | 928.27 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 570 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.7728 | Peak Hr Flow | 34.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 666 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 40.9412 | Peak Hr Flow | 1823.27 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3225
|  |  |  | Chattogram |  | 0 |  | 1099
|  |  |  | Cumilla |  | 0 |  | 1360
|  |  |  | Mymensingh |  | 0 |  | 1127
|  |  |  | Sylhet |  | 0 |  | 577
|  |  |  | Khulna |  | 0 |  | 1647
|  |  |  | Barishal |  | 0 |  | 440
|  |  |  | Rajshahi |  | 0 |  | 1304
|  |  |  | Rangpur |  | 0 |  | 1000
|  |  |  | Total |  | 0 |  | 11779
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Meghnaghat CCPP(Summit) GT-2 |  |  | 110
[5 empty] | Total | 300 |  |  |  | Total | 510
|  |  |  | Total Unavailable Capacity |  |  |  | 810
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:24 | Coxsbazar 132/33kV S/S 415T-T2 HT is restored.
| 08:37 | 08:58 | BIPTC S/S 10CF14 Scheduled S/D
| 08:45 |  | Unique Meghnaghat Power Limited (UMPL) GT Synchronized with remarks:- 5-6-2025 at 05:21
GT Sync. as per NLDC requirement.
| 08:46 |  | Unique Meghnaghat Power Limited (UMPL) ST Synchronized with remarks:- 5-6-2025 at 16:27
ST sync. as per NLDC requirement.
| 09:16 |  | Madunaghat 400/230kV S/S ATR-2 7106T HT Scheduled S/D Due to Fire system installation,
testing & commissioning.
| 09:16 |  | Madunaghat 400/230kV S/S ATR-2 7106T LT Scheduled S/D Due to Fire system installation,
testing & commissioning.
| 10:07 | 11:59 | Barishal 230/132kV S/S T-4 LT Scheduled S/D Due to Emergency maintenance | [7 empty] | 8.0MW load
interrup.
| 10:07 | 11:56 | Barishal 230/132kV S/S T-4 HT Scheduled S/D Due to Emergency maintenance | [7 empty] | 8.0MW load
interrup.
| 10:24 | 11:44 | Gopalganj 400/132kV S/S 132kV Bus-01 Scheduled S/D Due to Hotpot maintenance
| 10:30 | 12:39 | Gopalganj- Gopalganj(N) 132kV Ckt-2 Scheduled S/D from Gopalganj 400/132kV end Due to
Hotspot maintenance
| 10:31 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U1 sd-10:31 on 06-06-25
| 10:31 |  | Rampal 1320 MW (BIFPCL) Shutdown with remarks:- U1
| 10:40 | 11:34 | Barguna 132/33kV S/S Transformer-1 HT Scheduled S/D Due to WZPDCL-2 ফিডারে ৩৩ কেভি Bus
Section-1 Y-phase এর লুপে Redhot Maintenance
| 10:40 | 11:35 | Barguna 132/33kV S/S Transformer-1 LT Scheduled S/D Due to WZPDCL-2 ফিডারে ৩৩ কেভি Bus
Section-1 Y-phase এর লুপে Redhot maintenance
| 10:44 | 11:44 | Brahmanbaria 132/33kV S/S 402T LT Forced S/D Due to PBS 33KV Nabinagar feeder bus D/S red | [7 empty] | 40.0MW load
|  |  | hot maintenance | [7 empty] | interrup.
| 10:44 | 11:44 | Brahmanbaria 132/33kV S/S 402T HT Forced S/D | [7 empty] | 40.0MW load
interrup.
| 11:08 | 12:00 | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to Maintenance work. | [7 empty] | 24.0MW load
interrup.
| 11:09 | 11:59 | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to Maintenance work. | [7 empty] | 24.0MW load
interrup.
| 11:50 |  | Barisal 307 MW Shutdown
| 12:00 |  | Day peak Generation is 10431 MW
| 13:43 | 15:34 | Aminbazar-Kaliakoir 230kV Ckt-2 Tripped from Kaliakoir 400/230/132kV end showing REL-670
relays Due to Fault. and from Aminbazar 400/230/132kV end showing ABB REL 316*4 relays
Due to Unknown
| 14:24 |  | Ghorasal Repowered CCPP Unit-4 Synchronized
| 16:46 | 18:19 | Noapara 132/33kV S/S T-1 LT Scheduled S/D Due to REB -4 Redhot Maintenance | [7 empty] | 20.0MW load
interrup.
| 16:47 | 18:19 | Noapara 132/33kV S/S T-1 HT Scheduled S/D Due to None | [7 empty] | 20.0MW load
interrup.
| 19:15 |  | Unique Meghnaghat Power Limited (UMPL) record a general event:- ST Tripped.
| 19:15 |  | Unique Meghnaghat Power Limited (UMPL) ST Tripped with remarks:- Condenser Hotwell level
High High.
| 19:15 |  | Unique Meghnaghat Power Limited (UMPL) Tripped with remarks:- ST
| 19:20 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized
| 19:40 |  | Meghnaghat CCPP(Summit)-2 Shutdown with remarks:- ST
| 20:04 |  | Matarbari 2*600 MW (CPGCBL) Shutdown
| 21:00 |  | Evening peak generation: 12427 MW
|  | 21:10 | Chandpur 132/33kV S/S 402T LT is restored.
| 21:10 |  | Chandpur 132/33kV S/S 412T LT Scheduled S/D Due to Load alternate to T-1 Power
Transformer
| 21:26 |  | Unique Meghnaghat Power Limited (UMPL) ST Synchronized with remarks:- ST synchronized
with grid as per NLDC requirement.
| 21:26 |  | Unique Meghnaghat Power Limited (UMPL) record a general event:- ST synchronized with
grid.
| 21:26 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized with remarks:- ST
| 21:55 |  | Meghnaghat CCPP(Summit)-2 Synchronized
| 22:04 |  | Sirajgonj 225MW CCPP Unit-3, FGMO is ON with remarks:-
| 22:18 | 23:08 | Naogaon 132/33kV S/S T-3 HT Forced S/D Due to Baludanga 33 kv feeder(NESCO) B phase Bus
side isolator red hot maintenance which is connected to T-3 33kV bus in Naogaon
Grid Substation.
| 22:18 | 23:08 | Naogaon 132/33kV S/S T-3 LT Forced S/D Due to Baludanga 33 kv feeder(NESCO) B phase Bus
side isolator red hot maintenance which is connected to T-3 33kV bus in Naogaon
Grid Substation.
| 22:36 |  | Daudkandi-Sonargaon 132 kV Ckt-2 Tripped from Daudkandi 132/33kV end showing distance
relay relays Due to sonargaon-2 line conductor breakdown
|  | 23:40 | Daudkandi-Sonargaon 132 kV Ckt-1 is restored.
| 23:40 |  | Daudkandi-Sonargaon 132 kV Ckt-2 Tripped from Sonargaon 132/33kV end showing Line
distance relay. relays Due to line tripped
|  | 02:34 | Haripur-Sonargaon 132kV Ckt-2 is restored.
| 03:25 |  | Sirajgonj 225MW CCPP Unit-3 GT Synchronized with remarks:- None
| 03:25 |  | Sirajgonj 225MW CCPP Unit-3 ST Synchronized with remarks:- None
| 05:13 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- ST
| 07:00 |  | Minimum generation 10544 MW
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 06-06-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 210 | 1547750 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 51 | 287500 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 359 | 8161200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8651000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 147 | 3452509 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 202 | 1269000 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 3265583 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 0 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17 | 379200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 7 | 191160 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 0 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 0 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 574080 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 205934 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 65 | 8706818.18 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 150 | 7955000 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 758 | 1407900 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 35 | 512400 | -
Dhaka Area Total |  |  |  |  | 5939.724 | 2437 | 46567034.18
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 150 | 2900000 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 48151.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 91665 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 167 | 3707140 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 221 | 4847443 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 87191 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 41 | 964320 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 23160 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 802 | 16707271 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 112320 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 0 | 6290909.09 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4895.72 | 1389 | 35779570.89
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 199 | 4586000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 354 | 7972100 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 7548000 | machine problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 26 | 392544 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 48 | 554880 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 158 | 1037091 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 398008 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 202224 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1520500 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 120 | 2338080 | -
| Import (Tripura) |  | Import | 0 | 160 | 34 | 772800 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 103310 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 344830 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1914060 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 29 | 442680 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 113 | 1403520 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 434073 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1664 | 31964700
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 156 | 3425280 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13850 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 53 | 693600 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 16 | 344400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 326030 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 225 | 4803160
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 32 | 769000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 643080 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 154 | 3323291 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 20 | 521568 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 715200 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 164 | 3451100 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 162000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 146256 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 6634000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 365 | 8155000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7540600 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1495 | 32061095
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 861 | 19466181 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 357 | 7639488 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 573840 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 422 | 13243636 | U#1 Reserve shut down as per NLDC Communication
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3699.2 | 1640 | 40923145
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 11 | 211374 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2589000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 800 | 14935272.73 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5138690 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 1746000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4374 | -
Barishal Area Total |  |  |  |  | 2236 | 1151 | 24624710.73
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 50 | 1105000 | M/C running
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 170 | 3732273 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 195 | 4243582 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 193 | 3207455 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8135309 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 32520 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 928.27 | 20702182 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 390752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 605474 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 1950.27 | 42154547
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1164218 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4416000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 111 | 858470 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 44032.32 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 569197 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 223706 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1365120 | -
Rangpur Area Total |  |  |  |  | 950 | 476 | 8640743.32
Eastern Grid Total |  |  |  |  | 16705.895 | 7210 | 151175560.07
Western Grid Total |  |  |  |  | 10338.16 | 5217.27 | 116343146.05
National Grid Total |  |  |  |  | 27044.055 | 12427.27 | 267518706.12
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 06-06-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7388.18 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4391.7 | MW
i) Dhaka area |  |  | 3225.23 |  | MW | i) Khulna area |  |  |  | 1647 | MW
ii) Chattogram area |  |  | 1098.6 |  | MW | ii) Barishal area |  |  |  | 440.3 | MW
iii) Cumilla area |  |  | 1360.35 |  | MW | iii) Rajshahi area |  |  |  | 1304.4 | MW
iv) Mymensingh area |  |  | 1127 |  | MW | iv) Rangpur area |  |  |  | 1000 | MW
v) Sylhet area |  |  | 577 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11779.88 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 18 | 02:00 | 67 | Ishurdi | 72 | 00:00 | 133 | Patuakhali | 91 | 00:00
2 | AKSML | 21 | 02:00 | 68 | Jaldhaka | 92 | 21:00 | 134 | Payra | 36 | 22:00
3 | Aftabnagar | 28 | 00:00 | 69 | Jamalpur | 141 | 20:00 | 135 | Postogola | 42 | 13:00
4 | Agargaon | 92 | 13:00 | 70 | Jashore | 138 | 21:00 | 136 | Purbachal | 16 | 00:00
5 | Agrabad | 76 | 20:00 | 71 | Jhenaidah | 133 | 19:30 | 137 | Purbasadipur | 132 | 00:00
6 | Amnura | 37 | 02:00 | 72 | Joydebpur | 80 | 20:00 | 138 | Rahanpur | 35 | 00:00
7 | Ashuganj | 88 | 23:00 | 73 | Joypurhat | 68 | 23:00 | 139 | Rahim | 2 | 01:00
8 | BSRM | 13 | 01:00 | 74 | Juldah | 13 | 00:00 | 140 | Rajbari | 82 | 00:00
9 | Bagerhat | 86 | 00:00 | 75 | KSRM | 9 | 03:00 | 141 | Rajendrapur | 99 | 01:00
10 | Bajitpur | 55 | 23:00 | 76 | Kabirpur | 114 | 00:00 | 142 | Rajshahi | 103 | 00:00
11 | Bakulia | 76 | 00:00 | 77 | Kachua | 96 | 22:00 | 143 | Rajshahi-230 | 86 | 13:00
12 | Banani | 24 | 19:00 | 78 | Kallyanpur | 84 | 00:00 | 144 | Ramganj | 120 | 23:00
13 | Bangabhaban | 3 | 00:00 | 79 | Kalurghat | 26 | 00:00 | 145 | Rampur | 37 | 01:00
14 | Barapukuria | 67 | 21:00 | 80 | Kamrangirchar | 38.4 | 01:00 | 146 | Rangamati | 16 | 20:00
15 | Barguna | 24 | 22:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 147 | 20:00
16 | Barishal | 111 | 12:00 | 82 | Kasba | 39 | 23:00 | 148 | Ruppur | 6.6 | 10:00
17 | Barishal-230 | 90 | 23:00 | 83 | Kazla | 62 | 00:00 | 149 | SSM | 0 | 00:00
18 | Baroaulia | 51 | 00:00 | 84 | Keranigonj | 68 | 13:00 | 150 | Saidpur | 99 | 00:00
19 | Baroirhat | 70 | 15:00 | 85 | Khagrachori | 36 | 19:00 | 151 | Satkhira | 146 | 20:00
20 | Bashundhara | 139 | 13:00 | 86 | Khulna | 65 | 00:00 | 152 | Satmasjid | 72 | 12:00
21 | BashundharaCement | 2 | 00:00 | 87 | Khulshi | 149 | 00:00 | 153 | Savar | 108 | 00:00
22 | Beanibazar | 82 | 00:00 | 88 | Kishoreganj | 150 | 00:00 | 154 | SevenRings | 0.47 | 03:00
23 | Benapole | 66 | 21:00 | 89 | Kodda | 148 | 00:00 | 155 | ShahCement | 16 | 19:30
24 | Bhaluka | 110 | 00:00 | 90 | Kulaura | 53 | 19:00 | 156 | Shahjadpur | 82 | 20:00
25 | Bhandaria | 57 | 01:00 | 91 | Kurigram | 72 | 20:00 | 157 | Shahjibazar | 118 | 23:00
26 | Bhangura | 42 | 21:00 | 92 | Kushtia | 140 | 00:00 | 158 | Shahmirpur | 45 | 00:00
27 | Bheramara(GK) | 69 | 19:30 | 93 | Lalbag | 27 | 00:00 | 159 | Shariatpur | 88 | 00:00
28 | Bhulta | 147 | 00:00 | 94 | Lalmonirhat | 70 | 19:30 | 160 | Sherpur | 140 | 00:00
29 | Bog-Sherpur | 64 | 00:00 | 95 | MI_Cement | 1.3 | 04:00 | 161 | Shikalbaha | 22 | 03:00
30 | Bogura | 162 | 00:00 | 96 | Madanganj | 31 | 00:00 | 162 | Shitalakhya | 57.6 | 13:00
31 | Borhanuddin | 91 | 23:00 | 97 | Madaripur | 112 | 23:00 | 163 | Sholosohor | 35 | 23:00
32 | Brahmanbaria | 137 | 22:00 | 98 | Madartek | 72 | 23:00 | 164 | Shyampur | 54 | 13:00
33 | Cantonment | 102 | 12:00 | 99 | Madunaghat | 53 | 20:00 | 165 | Siddhirganj | 75 | 13:00
34 | Chandina | 22.58 | 17:00 | 100 | Magura | 69 | 23:00 | 166 | Sirajganj | 110 | 19:30
35 | Chandpur | 78 | 00:00 | 101 | Mahasthangarh | 80 | 00:00 | 167 | Sonargaon | 54 | 01:00
36 | Chandraghona | 38 | 19:00 | 102 | Manikganj | 93 | 20:00 | 168 | Sreemongol | 70 | 23:00
37 | Chapai | 73 | 00:00 | 103 | Maniknagar | 58 | 13:00 | 169 | Sreepur | 65 | 00:00
38 | Charsaidpur | 11 | 00:00 | 104 | Matarbari | 52 | 22:00 | 170 | Srinagar | 48.74 | 23:00
39 | Chauddagram | 75 | 23:00 | 105 | Matuail | 36 | 00:00 | 171 | Sunamganj | 61 | 00:00
40 | Chhatak | 37 | 23:00 | 106 | Millgate | 42 | 00:00 | 172 | Sylhet | 46 | 00:00
41 | Chowmuhani | 221 | 03:00 | 107 | Mirpur | 93 | 13:00 | 173 | Sylhet-132 | 104 | 19:30
42 | Chuadanga | 118 | 00:00 | 108 | Mirsorai | 8 | 00:00 | 174 | TK | 36.6 | 23:00
43 | Coxsbazar | 131 | 23:00 | 109 | Mirzapur | 41 | 22:00 | 175 | Tangail | 174 | 19:30
44 | Cumilla(N) | 150 | 23:00 | 110 | Mithapukur | 60 | 23:00 | 176 | Thakurgaon | 119 | 20:00
45 | Cumilla(S) | 160 | 00:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 71 | 11:00
46 | Daudkandi | 122 | 00:00 | 112 | Mogbazar | 90.4 | 13:00 | 178 | Ullahpara | 40 | 19:30
47 | Dhaka | 24 | 12:00 | 113 | Mongla | 24 | 00:00 | 179 | Ullon | 32 | 00:00
48 | Dhamrai | 92 | 00:00 | 114 | Motijheel | 26 | 13:00 | 180 | Uttara | 57 | 12:00
49 | Dhanmondi | 96 | 14:00 | 115 | Muktagacha | 39 | 19:30 | 181 | UttaraNew | 45 | 00:00
50 | Dohazari | 110 | 20:00 | 116 | Munshiganj | 106 | 00:00 | 182 | Zigatola | 56 | 13:00
51 | Faridpur | 157 | 22:00 | 117 | Muradnagar | 30 | 20:00
52 | Fatullah | 49 | 00:00 | 118 | Mymensingh | 202 | 20:00
53 | Fenchuganj | 37 | 22:00 | 119 | Naogaon | 132 | 01:00
54 | Feni | 124 | 00:00 | 120 | Narail | 60 | 22:00
55 | GPH | 2 | 00:00 | 121 | Narinda | 42 | 00:00
56 | Ghatail | 78 | 23:00 | 122 | Narshingdi | 149 | 00:00
57 | Ghorashal | 14 | 00:00 | 123 | Natore | 156 | 00:00
58 | Ghorashal-230 | 61 | 00:00 | 124 | Nawabganj | 59.4 | 22:00
59 | Goalpara | 38 | 00:00 | 125 | Netrakona | 137 | 19:30
60 | Gollamari | 86 | 00:00 | 126 | New | 39.8 | 13:00
61 | Gopalganj | 105.6 | 22:00 | 127 | Niamatpur | 77 | 23:00
62 | Gulshan | 68 | 12:00 | 128 | Noapara | 42 | 19:30
63 | Halishahar | 36 | 01:00 | 129 | PHP | 6 | 02:00
64 | HaripurSBU | 88 | 00:00 | 130 | Pabna | 122 | 19:30
65 | Hasnabad | 52 | 01:00 | 131 | Palashbari | 124 | 21:00
66 | Hathazari | 83 | 00:00 | 132 | Panchagarh | 62 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 06-06-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 12931.82 | 0 |  | 12931.82
1:00 | 12628.91 | 0 |  | 12628.91
2:00 | 12201.94 | 0 |  | 12201.94
3:00 | 11838.62 | 0 |  | 11838.62
4:00 | 11410.57 | 0 |  | 11410.57
5:00 | 10998.93 | 0 |  | 10998.93
6:00 | 10282.93 | 0 |  | 10282.93
7:00 | 10008.22 | 0 |  | 10008.22
8:00 | 9954.17 | 0 |  | 9954.17
9:00 | 9844.65 | 0 |  | 9844.65
10:00 | 9777.18 | 0 |  | 9777.18
11:00 | 10068.08 | 0 |  | 10068.08
12:00 | 10434.97 | 0 |  | 10434.97
13:00 | 11321.87 | 0 |  | 11321.87
14:00 | 11088.75 | 0 |  | 11088.75
15:00 | 10675.9 | 0 |  | 10675.9
16:00 | 10326.05 | 0 |  | 10326.05
17:00 | 9938.75 | 0 |  | 9938.75
18:00 | 9772.42 | 0 |  | 9772.42
19:00 | 11547 | 0 |  | 11547
19:30 | 12351.2 | 0 |  | 12351.2
20:00 | 12219 | 0 |  | 12219
21:00 | 12427.27 | 0 |  | 12427.27
22:00 | 12390.95 | 0 |  | 12390.95
23:00 | 12596.52 | 0 |  | 12596.52
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 06-06-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7792 | 5139.82 | 12931.82 | DAILY GENERATION CURVE
00:30 | 7720 | 5060.365 | 12780.365
01:00 | 7648 | 4980.91 | 12628.91 | 06-06-2025
01:30 | 7525.5 | 4889.925 | 12415.425
02:00 | 7403 | 4798.94 | 12201.94
02:30 | 7270 | 4750.28 | 12020.28
03:00 | 7137 | 4701.62 | 11838.62
03:30 | 6923 | 4701.595 | 11624.595
04:00 | 6709 | 4701.57 | 11410.57
04:30 | 6542 | 4662.75 | 11204.75
05:00 | 6375 | 4623.93 | 10998.93
05:30 | 6021.23 | 4619.7 | 10640.93
06:00 | 5667.46 | 4615.47 | 10282.93
06:30 | 5550.38 | 4595.195 | 10145.575
07:00 | 5433.3 | 4574.92 | 10008.22
07:30 | 5368.18 | 4613.015 | 9981.195
08:00 | 5303.06 | 4651.11 | 9954.17
08:30 | 5247.885 | 4651.525 | 9899.41
09:00 | 5192.71 | 4651.94 | 9844.65
09:30 | 5169.725 | 4641.19 | 9810.915
10:00 | 5146.74 | 4630.44 | 9777.18
10:30 | 5318.265 | 4604.365 | 9922.63
11:00 | 5489.79 | 4578.29 | 10068.08
11:30 | 5690.245 | 4561.28 | 10251.525
12:00 | 5890.7 | 4544.27 | 10434.97
12:30 | 6163.85 | 4714.57 | 10878.42
13:00 | 6437 | 4884.87 | 11321.87
13:30 | 6342.35 | 4862.96 | 11205.31
14:00 | 6247.7 | 4841.05 | 11088.75
14:30 | 6150.935 | 4731.39 | 10882.325
15:00 | 6054.17 | 4621.73 | 10675.9
15:30 | 5975.725 | 4525.25 | 10500.975
16:00 | 5897.28 | 4428.77 | 10326.05
16:30 | 5724.955 | 4407.445 | 10132.4
17:00 | 5552.63 | 4386.12 | 9938.75
17:30 | 5516.675 | 4338.91 | 9855.585
18:00 | 5480.72 | 4291.7 | 9772.42
18:30 | 6168.86 | 4490.85 | 10659.71
19:00 | 6857 | 4690 | 11547
19:30 | 7448.2 | 4903 | 12351.2
20:00 | 7230 | 4989 | 12219
20:30 | 7220 | 5103.135 | 12323.135 |  | Executive Engineer
21:00 | 7210 | 5217.27 | 12427.27 |  | Network Operation Division
21:30 | 7216.5 | 5192.61 | 12409.11
22:00 | 7223 | 5167.95 | 12390.95
22:30 | 7304 | 5189.735 | 12493.735
23:00 | 7385 | 5211.52 | 12596.52

## En-Curve
QF-LDC-12
Date | 06-06-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4305 | 2855 | 820 | 0 | 42 | 860.82 | 167 | 3035 | 0 | 150 | 690 | 0 | 0 | 7 | 0 | DAILY ENERGY CURVE
00:30 | 4320.5 | 2796 | 750 | 0 | 36 | 857.865 | 167 | 3038 | 0 | 141 | 666.5 | 0 | 0 | 7.5 | 0 | 06-06-2025
01:00 | 4336 | 2737 | 680 | 0 | 30 | 854.91 | 167 | 3041 | 0 | 132 | 643 | 0 | 0 | 8 | 0
01:30 | 4305.5 | 2687 | 680 | 0 | 34 | 837.925 | 167 | 2990.5 | 0 | 123.5 | 583.5 | 0 | 0 | 6.5 | 0 | Energy Generated | 267.5187 |  | MKWHr
02:00 | 4275 | 2637 | 680 | 0 | 38 | 820.94 | 167 | 2940 | 0 | 115 | 524 | 0 | 0 | 5 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 4224 | 2561.5 | 679.5 | 0 | 38 | 820.28 | 167 | 2929.5 | 0 | 98.5 | 495 | 0 | 0 | 7 | 0 | Total Energy Requirement | 267.5187 |  | MKWHr
03:00 | 4173 | 2486 | 679 | 0 | 38 | 819.62 | 167 | 2919 | 0 | 82 | 466 | 0 | 0 | 9 | 0
03:30 | 4154 | 2279 | 749.5 | 0 | 37 | 820.095 | 167 | 2907.5 | 0 | 57.5 | 443 | 0 | 0 | 10 | 0
04:00 | 4135 | 2072 | 820 | 0 | 36 | 820.57 | 167 | 2896 | 0 | 33 | 420 | 0 | 0 | 11 | 0
04:30 | 4095 | 2063.5 | 820 | 0 | 36 | 819.75 | 167 | 2786.5 | 0 | 24.5 | 384 | 0 | 0 | 8.5 | 0
05:00 | 4055 | 2055 | 820 | 0 | 36 | 818.93 | 167 | 2677 | 0 | 16 | 348 | 0 | 0 | 6 | 0
05:30 | 3938 | 1918 | 820 | 0 | 34 | 818.86 | 167 | 2623 | 35.07 | 8 | 274 | 0 | 0 | 5 | 0
06:00 | 3821 | 1781 | 820 | 0 | 32 | 818.79 | 167 | 2569 | 70.14 | 0 | 200 | 0 | 0 | 4 | 0
06:30 | 3755 | 1713.5 | 820 | 0 | 33 | 814.565 | 167 | 2572 | 95.51 | 0 | 172 | 0 | 0 | 3 | 0
07:00 | 3689 | 1646 | 820 | 0 | 34 | 810.34 | 167 | 2575 | 120.88 | 0 | 144 | 0 | 0 | 2 | 0
07:30 | 3606 | 1619.5 | 820 | 0 | 33 | 816.82 | 149.5 | 2593 | 192.875 | 0 | 147 | 0 | 0 | 3.5 | 0
08:00 | 3523 | 1593 | 820 | 0 | 32 | 823.3 | 132 | 2611 | 264.87 | 0 | 150 | 0 | 0 | 5 | 0
08:30 | 3447 | 1552.5 | 795 | 0 | 29 | 821.825 | 132 | 2588.5 | 375.585 | 0 | 153.5 | 0 | 0 | 4.5 | 0
09:00 | 3371 | 1512 | 770 | 0 | 26 | 820.35 | 132 | 2566 | 486.3 | 0 | 157 | 0 | 0 | 4 | 0
09:30 | 3359 | 1511.5 | 737 | 0 | 27 | 832.555 | 132 | 2569.5 | 480.36 | 0 | 154.5 | 0 | 0 | 7.5 | 0
10:00 | 3347 | 1511 | 704 | 0 | 28 | 844.76 | 132 | 2573 | 474.42 | 0 | 152 | 0 | 0 | 11 | 0
10:30 | 3455.5 | 1587 | 762 | 0 | 25 | 830.515 | 132 | 2425.5 | 548.115 | 0 | 151.5 | 0 | 0 | 5.5 | 0
11:00 | 3564 | 1663 | 820 | 0 | 22 | 816.27 | 132 | 2278 | 621.81 | 0 | 151 | 0 | 0 | 0 | 0
11:30 | 3758.5 | 1735.5 | 820 | 0 | 25 | 828.6 | 132 | 2186.5 | 597.425 | 0 | 168 | 0 | 0 | 0 | 0
12:00 | 3953 | 1808 | 820 | 0 | 28 | 840.93 | 132 | 2095 | 573.04 | 0 | 185 | 0 | 0 | 0 | 0
12:30 | 4099.5 | 2039.5 | 820.5 | 0 | 30 | 827.26 | 132 | 2143.5 | 548.66 | 15 | 216.5 | 0 | 0 | 6 | 0
13:00 | 4246 | 2271 | 821 | 0 | 32 | 813.59 | 132 | 2192 | 524.28 | 30 | 248 | 0 | 0 | 12 | 0
13:30 | 4200.5 | 2211.5 | 820.5 | 0 | 32 | 818.295 | 132 | 2200 | 457.015 | 41 | 284.5 | 0 | 0 | 8 | 0
14:00 | 4155 | 2152 | 820 | 0 | 32 | 823 | 132 | 2208 | 389.75 | 52 | 321 | 0 | 0 | 4 | 0
14:30 | 4116.5 | 2111.5 | 820.5 | 0 | 32 | 821.5 | 132 | 2097.5 | 382.325 | 43.5 | 322.5 | 0 | 0 | 2.5 | 0
15:00 | 4078 | 2071 | 821 | 0 | 32 | 820 | 132 | 1987 | 374.9 | 35 | 324 | 0 | 0 | 1 | 0
15:30 | 4035.5 | 2043 | 821 | 0 | 30 | 820 | 132 | 1961.5 | 343.475 | 17.5 | 294.5 | 0 | 0 | 2.5 | 0
16:00 | 3993 | 2015 | 821 | 0 | 28 | 820 | 132 | 1936 | 312.05 | 0 | 265 | 0 | 0 | 4 | 0
16:30 | 3961 | 1944.5 | 841 | 0 | 29 | 823 | 132 | 1933.5 | 230.4 | 0 | 233 | 0 | 0 | 5 | 0
17:00 | 3929 | 1874 | 861 | 0 | 30 | 826 | 132 | 1931 | 148.75 | 0 | 201 | 0 | 0 | 6 | 0
17:30 | 3935.5 | 1847 | 861 | 0 | 29 | 826 | 149.5 | 1889 | 93.085 | 0 | 220.5 | 0 | 0 | 5 | 0
18:00 | 3942 | 1820 | 861 | 0 | 28 | 826 | 167 | 1847 | 37.42 | 0 | 240 | 0 | 0 | 4 | 0
18:30 | 4234.5 | 2188 | 860.5 | 0 | 31 | 850.5 | 167 | 1945 | 18.71 | 26 | 336.5 | 0 | 0 | 2 | 0
19:00 | 4527 | 2556 | 860 | 0 | 34 | 875 | 167 | 2043 | 0 | 52 | 433 | 0 | 0 | 0 | 0
19:30 | 4483 | 2915 | 812 | 0 | 24 | 901 | 167 | 2237 | 0 | 70 | 742.2 | 0 | 0 | 0 | 0
20:00 | 4607 | 2768 | 813 | 0 | 30 | 923 | 167 | 2141 | 0 | 52 | 718 | 0 | 0 | 0 | 0
20:30 | 4652 | 2748 | 837 | 0 | 32 | 925.635 | 167 | 2207.5 | 0 | 43.5 | 710.5 | 0 | 0 | 0 | 0
21:00 | 4697 | 2728 | 861 | 0 | 34 | 928.27 | 167 | 2274 | 0 | 35 | 703 | 0 | 0 | 0 | 0
21:30 | 4710 | 2730 | 861 | 0 | 34 | 930.11 | 167 | 2269 | 0 | 35 | 672.5 | 0 | 0 | 0.5 | 0
22:00 | 4723 | 2732 | 861 | 0 | 34 | 931.95 | 167 | 2264 | 0 | 35 | 642 | 0 | 0 | 1 | 0
22:30 | 4738 | 2789 | 861 | 0 | 34 | 931.235 | 167 | 2276 | 0 | 35 | 662 | 0 | 0 | 0.5 | 0
23:00 | 4753 | 2846 | 861 | 0 | 34 | 930.52 | 167 | 2288 | 0 | 35 | 682 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 06-06-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 399 | 16:00 | 390 | 23:00 | Payra | 419 | 06:00 | 411 | 22:00
Ashuganj | 421 | 5:00 | 400 | 12:00 | Rahanpur | 414 | 18:00 | 404 | 00:00
Bhulta | 409 | 20:00 | 398 | 13:00 | Rampal | 408 | 09:00 | 391 | 23:00
Bibiana | 395 | 09:00 | 390 | 01:00
BIPTC | 404 | 09:00 | 393 | 00:00
Bogura | 402 | 10:00 | 391 | 00:00
Gopalganj | 407 | 06:00 | 394 | 23:00
Kaliakoir | 389 | 15:00 | 372 | 00:00
Madunaghat | 404 | 17:00 | 398 | 01:00
Meghnaghat | 403 | 16:00 | 395 | 23:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 236 | 18:00 | 223 | 18:30 | Keranigonj | 234 | 16:00 | 228 | 13:00
AKSML | 234 | 06:00 | 229 | 19:00 | Khulna(S) | 233 | 09:00 | 218 | 23:00
Aminbazar | 236 | 09:00 | 231 | 23:00 | Madunaghat | 236 | 06:00 | 231 | 19:00
Ashuganj | 238 | 20:00 | 232 | 13:00 | Madunaghat-400 | 237 | 09:00 | 232 | 21:00
Ashuganj-400 | 238 | 20:00 | 232 | 13:00 | Maniknagar | 232 | 16:00 | 227 | 13:00
Baghabari | 236 | 09:00 | 228 | 00:00 | Meghnaghat | 240 | 17:00 | 234 | 01:00
Barapukuria | 224 | 06:00 | 219 | 00:00 | Meghnaghat-400 | 234 | 16:00 | 230 | 13:00
Barapukuria-230 | 224 | 06:00 | 219 | 00:00 | Mirsorai | 234 | 09:00 | 230 | 01:00
Barishal | 241 | 09:00 | 232 | 23:00 | Rajshahi | 234 | 06:00 | 222 | 00:00
Bheramara | 234 | 06:00 | 223 | 23:00 | Rampal | 233 | 08:00 | 219 | 23:00
Bhulta | 238 | 06:00 | 228 | 13:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 234 | 07:00 | 228 | 23:00 | Rampura | 238 | 15:00 | 230 | 13:00
BIPTC | 236 | 08:00 | 222 | 23:00 | Shikalbaha | 233 | 07:00 | 227 | 19:00
Bogura | 235 | 06:00 | 228 | 00:00 | Shyampur | 234 | 18:00 | 228 | 13:00
Bogura-400 | 235 | 10:00 | 227 | 00:00 | Siddhirganj | 234 | 15:00 | 230 | 13:00
Borhanuddin | 244 | 17:00 | 237 | 02:00 | Sirajgonj | 241 | 08:00 | 235 | 00:00
BSRM | 233 | 08:00 | 230 | 01:00 | Sreepur | 233 | 20:00 | 226 | 00:00
Cumilla(N) | 229 | 15:00 | 224 | 13:00 | Tongi | 238 | 17:00 | 232 | 00:00
Faridpur | 238 | 18:00 | 228 | 23:00
Fenchuganj | 233 | 07:00 | 230 | 00:00
Ghorashal | 240 | 00:00 | 235 | 01:00
Ghorashal-230 | 237 | 15:00 | 230 | 13:00
Gopalganj | 239 | 07:00 | 229 | 11:00
GPH | 234 | 05:00 | 230 | 23:00
Haripur | 233 | 18:00 | 228 | 13:00
Hasnabad | 235 | 18:00 | 229 | 12:00
Hathazari | 235 | 08:00 | 227 | 12:00
Ishurdi | 236 | 06:00 | 225 | 23:00
Jhenaidah | 231 | 06:00 | 216 | 23:00
Kaliakoir | 243 | 15:00 | 229 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 06:00 | 128 | 13:00 | Madartek | 136 | 06:00 | 127 | 13:00
Agargaon | 136 | 06:00 | 128 | 14:00 | Madunaghat | 133 | 05:00 | 130 | 19:00
Agrabad | 134 | 08:00 | 130 | 19:00 | Magura | 134 | 06:00 | 123 | 23:00
AKS | 132 | 05:00 | 128 | 13:00 | Mahasthangarh | 135 | 09:00 | 128 | 00:00
Aminbazar | 139 | 05:00 | 131 | 22:00 | Manikganj | 137 | 14:00 | 129 | 23:00
Amnura | 136 | 10:00 | 126 | 02:00 | Maniknagar | 132 | 16:00 | 128 | 13:00
Ashuganj | 140 | 16:00 | 137 | 00:00 | Matarbari | 122 | 08:00 | 110 | 19:00
Bagerhat | 133 | 08:00 | 117 | 23:00 | Matuail | 137 | 16:00 | 134 | 00:00
Bajitpur | 134 | 20:00 | 128 | 00:00 | Millgate | 136 | 05:00 | 132 | 13:00
Bakulia | 135 | 08:00 | 130 | 13:00 | Mirpur | 138 | 07:00 | 129 | 13:00
Banani | 137 | 06:00 | 128 | 13:00 | Mirzapur | 136 | 05:00 | 127 | 22:00
Bangabhaban | 132 | 04:00 | 129 | 13:00 | Mithapukur | 131 | 06:00 | 125 | 14:00
Barapukuria | 135 | 06:00 | 129 | 00:00 | MI_Cement | 137 | 16:00 | 131 | 02:00
Barguna | 136 | 07:00 | 129 | 22:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 135 | 18:00 | 127 | 00:00 | Mogbazar | 137 | 03:00 | 129 | 13:00
Barishal-230 | 134 | 11:00 | 127 | 00:00 | Mongla | 133 | 09:00 | 120 | 22:00
Baroaulia | 135 | 07:00 | 132 | 13:00 | Motijheel | 132 | 03:00 | 129 | 13:00
Baroirhat | 126 | 18:00 | 119 | 13:00 | Muktagacha | 135 | 00:00 | 120 | 23:00
Bashundhara | 137 | 07:00 | 128 | 13:00 | Munshiganj | 136 | 16:00 | 132 | 00:00
BashundharaCement | 137 | 18:00 | 133 | 01:00 | Muradnagar | 130 | 16:00 | 124 | 13:00
Beanibazar | 131 | 08:00 | 126 | 00:00 | Mymensingh | 135 | 00:00 | 119 | 00:00
Benapole | 133 | 09:00 | 120 | 22:00 | Naogaon | 134 | 05:00 | 126 | 00:00
Bhaluka | 133 | 15:00 | 127 | 19:00 | Narail | 133 | 06:00 | 119 | 23:00
Bhandaria | 129 | 17:00 | 118 | 00:00 | Narinda | 0 | 00:00 | N/A | N/A
Bhangura | 134 | 07:00 | 128 | 00:00 | Narshingdi | 135 | 17:00 | 123 | 00:00
Bheramara | 138 | 05:00 | 133 | 22:00 | Natore | 136 | 09:00 | 129 | 00:00
Bheramara(GK) | 138 | 08:00 | 133 | 00:00 | Nawabganj | 138 | 17:00 | 133 | 13:00
Bhulta | 130 | 10:00 | 126 | 00:00 | Netrakona | 126 | 05:00 | 118 | 00:00
Bog-Sherpur | 137 | 09:00 | 130 | 00:00 | New | 137 | 15:00 | 132 | 13:00
Bogura | 138 | 09:00 | 131 | 00:00 | Niamatpur | 137 | 18:00 | 132 | 00:00
Bogura-230 | 139 | 08:00 | 133 | 00:00 | Noapara | 136 | 09:00 | 123 | 23:00
Brahmanbaria | 132 | 16:00 | 126 | 00:00 | Pabna | 136 | 09:00 | 129 | 00:00
Cantonment | 136 | 06:00 | 132 | 13:00 | Palashbari | 131 | 09:00 | 125 | 00:00
Chandina | 131 | 16:00 | 126 | 01:00 | Panchagarh | 133 | 21:00 | 122 | 00:00
Chandpur | 126 | 20:00 | 110 | 08:00 | Patuakhali | 135 | 05:00 | 131 | 22:00
Chandraghona | 134 | 06:00 | 131 | 13:00 | Payra | 137 | 04:00 | 134 | 21:00
Chapai | 134 | 18:00 | 128 | 00:00 | PHP | 124 | 18:00 | 117 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 137 | 15:00 | 134 | 00:00 | Postogola | 139 | 17:00 | 127 | 13:00
Chauddagram | 125 | 19:30 | 118 | 13:00 | Purbachal | 137 | 05:00 | 127 | 13:00
Chhatak | 129 | 06:00 | 123 | 00:00 | Purbasadipur | 129 | 21:00 | 119 | 19:00
Chowmuhani | 120 | 19:30 | 110 | 13:00 | Rahanpur | 138 | 18:00 | 133 | 00:00
Chuadanga | 134 | 10:00 | 119 | 23:00 | Rahanpur-400 | 138 | 18:00 | 134 | 00:00
Coxsbazar | 123 | 10:00 | 110 | 22:00 | Rahim | 136 | 15:00 | 133 | 13:00
Cumilla(N) | 130 | 09:00 | 126 | 13:00 | Rajbari | 138 | 11:00 | 130 | 23:00
Cumilla(S) | 132 | 04:00 | 123 | 13:00 | Rajendrapur | 138 | 16:00 | 130 | 00:00
Daudkandi | 129 | 15:00 | 122 | 13:00 | Rajshahi | 136 | 08:00 | 128 | 00:00
Dhaka | 138 | 06:00 | 128 | 13:00 | Rajshahi-230 | 136 | 08:00 | 123 | 00:00
Dhamrai | 141 | 06:00 | 133 | 22:00 | Ramganj | 118 | 00:00 | 111 | 13:00
Dhanmondi | 137 | 06:00 | 135 | 00:00 | Rampur | 134 | 08:00 | 130 | 19:00
Dohazari | 131 | 08:00 | 121 | 23:00 | Rampura | 137 | 06:00 | 127 | 13:00
Faridpur | 139 | 17:00 | 133 | 23:00 | Rangamati | 133 | 05:00 | 130 | 13:00
Fatullah | 138 | 18:00 | 134 | 13:00 | Rangpur | 130 | 11:00 | 124 | 00:00
Fenchuganj | 138 | 19:00 | 135 | 00:00 | Ruppur | 138 | 07:00 | 133 | 00:00
Feni | 122 | 00:00 | 116 | 13:00 | Saidpur | 129 | 06:00 | 122 | 00:00
Ghatail | 133 | 00:00 | 120 | 22:00 | Satkhira | 133 | 06:00 | 118 | 22:00
Ghorashal | 141 | 14:00 | 136 | 00:00 | Satmasjid | 136 | 07:00 | 132 | 13:00
Goalpara | 139 | 08:00 | 127 | 22:00 | Savar | 138 | 07:00 | 129 | 13:00
Gollamari | 138 | 06:00 | 128 | 23:00 | SevenRings | 143 | 15:00 | 137 | 13:00
Gopalganj | 137 | 06:00 | 129 | 22:00 | ShahCement | 137 | 15:00 | 134 | 00:00
Gopalganj-400 | 139 | 06:00 | 133 | 23:00 | Shahjadpur | 138 | 10:00 | 132 | 00:00
Gulshan | 137 | 06:00 | 127 | 13:00 | Shahjibazar | 131 | 11:00 | 127 | 03:00
Halishahar | 134 | 07:00 | 130 | 19:00 | Shahmirpur | 134 | 04:00 | 130 | 19:00
Haripur | 136 | 08:00 | 134 | 00:00 | Shariatpur | 136 | 18:00 | 128 | 23:00
HaripurSBU | 137 | 18:00 | 134 | 00:00 | Sherpur | 129 | 00:00 | 109 | 15:00
Hasnabad | 139 | 16:00 | 135 | 15:00 | Shikalbaha | 123 | 04:00 | 119 | 19:00
Hathazari | 136 | 08:00 | 131 | 23:00 | Shikalbaha-230 | 135 | 07:00 | 130 | 18:30
Ishurdi | 139 | 08:00 | 133 | 00:00 | Shitalakhya | 137 | 16:00 | 132 | 01:00
Jaldhaka | 128 | 10:00 | 116 | 19:00 | Sholosohor | 135 | 08:00 | 130 | 13:00
Jamalpur | 132 | 00:00 | 113 | 22:00 | Shyampur | 137 | 16:00 | 135 | 00:00
Jashore | 134 | 06:00 | 122 | 23:00 | Shyampur-230 | 138 | 18:00 | 134 | 01:00
Jhenaidah | 136 | 06:00 | 123 | 00:00 | Siddhirganj | 137 | 15:00 | 134 | 00:00
Jhenaidah-230 | 136 | 06:00 | 125 | 23:00 | Sirajganj | 135 | 09:00 | 127 | 00:00
Joydebpur | 140 | 19:00 | 133 | 12:00 | Sonargaon | 136 | 15:00 | 132 | 00:00
Joypurhat | 133 | 08:00 | 124 | 00:00 | Sreemongol | 132 | 09:00 | 128 | 04:00
Juldah | 133 | 07:00 | 130 | 19:00 | Sreepur | 135 | 15:00 | 131 | 00:00
Kabirpur | 141 | 14:00 | 131 | 23:00 | Srinagar | 138 | 17:00 | 134 | 00:00
Kachua | 126 | 16:00 | 119 | 06:00 | SSM | 138 | 08:00 | 132 | 00:00
Kaliakoir | 143 | 14:00 | 134 | 00:00 | Sunamganj | 128 | 11:00 | 122 | 00:00
Kallyanpur | 139 | 03:00 | 131 | 13:00 | Sylhet | 132 | 06:00 | 128 | 00:00
Kalurghat | 133 | 07:00 | 130 | 19:00 | Sylhet-132 | 131 | 06:00 | 129 | 00:00
Kamrangirchar | 139 | 18:00 | 134 | 00:00 | Tangail | 132 | 04:00 | 121 | 23:00
Kaptai | 136 | 18:00 | 134 | 22:00 | Thakurgaon | 132 | 21:00 | 119 | 13:00
Kasba | 129 | 15:00 | 123 | 13:00 | TK | 133 | 08:00 | 129 | 19:00
Kazla | 132 | 18:00 | 129 | 14:00 | Tongi | 138 | 15:00 | 134 | 00:00
Keranigonj | 138 | 16:00 | 134 | 13:00 | Ullahpara | 136 | 08:00 | 129 | 00:00
Khagrachori | 132 | 07:00 | 128 | 19:00 | Ullon | 136 | 02:00 | 127 | 13:00
Khulna | 137 | 06:00 | 126 | 22:00 | Uttara | 138 | 06:00 | 129 | 13:00
Khulna(S) | 138 | 06:00 | 127 | 22:00 | UttaraNew | 137 | 06:00 | 129 | 13:00
Khulshi | 133 | 05:00 | 129 | 19:00 | Zigatola | 138 | 06:00 | 135 | 00:00
Kishoreganj | 131 | 05:00 | 125 | 19:00
Kodda | 138 | 05:00 | 130 | 00:00
KSRM | 134 | 03:00 | 131 | 19:00
Kulaura | 136 | 08:00 | 133 | 01:00
Kurigram | 128 | 06:00 | 117 | 19:00
Kushtia | 134 | 05:00 | 128 | 00:00
Lalbag | 139 | 04:00 | 134 | 13:00
Lalmonirhat | 127 | 05:00 | 121 | 13:00
Madanganj | 137 | 18:00 | 133 | 01:00
Madaripur | 136 | 09:00 | 130 | 23:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division