## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-02-08 | Friday
|  | Date (day): | 2019-02-08 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10578 | MW |  |  | (b) At Evening Peak Hour : |  | 11640 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-02-07 | 2019-02-08 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit #1 Under maint.
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  |  | On test.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 380 | 300 | 380 | 380
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 290 | 290 | 300 | 300 |  | 139 | ST under maint. & FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 26 | 0 | 95 | 95 |  | 15 | Engine problem
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 357 | 328 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 400 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 8 | 100 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 |  | 305 | Reserve
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 48 | 100 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 30 | 48 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 105 | 105 | 210 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 50 | 50 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 0 | 0 | 0 | 217 |  | Gas shortage
0 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
21 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 102 | 102 | 102
22 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 47 | 40 | 47 | 47
23 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
24 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
25 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 37 | 37 | 37 | 37 |  | 18 | Engine problem
26 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
27 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 48 | 48 | 49 | 49 |  | 59 | Engine problem
28 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 51 | 58 | 58 | 58 |  | 22 | Engine problem
29 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
30 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
31 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 51 | 51 | 52 | 52
32 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
33 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 180 | 300 | 300
34 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
37 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 15 | 84 | 149 | 149
| Dhaka area Total |  |  |  |  | 6034 | 5798 | 2061 | 2447 | 3720 | 3920 | 873 | 968
38 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 100 | 110 | 110 | 70 |  | Gas shortage
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
40 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 47 | 46 | 50 | 50
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 70 | 72 | 72 |  | 158 | Low water lavel
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  |  | Under maint.
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint.
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 0 | 51 | 51 | 51
47 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 56 | 60 | 65
48 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 68 | 68
49 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 68 | 70 | 68 | 68 |  | 32 | Engine problem
50 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 74 | 74 | 84 | 84 |  | 16 | Engine problem
51 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 19 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 32 | 15 | 25
52 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 93 | 100 | 90 | 106
| Chattogram area Total |  |  |  |  | 1761 | 1681 | 379 | 711 | 735 | 746 | 250 | 396
53 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 20 | 80 | 80 | 130 | 135 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 60 | 0 | 0 | 0 | 29 |  | Under maint.
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under Maint.
54 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 125 | 186 | 221 | 221
55 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 305 | 360 | 360
56 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 257 | 264 | 360 | 360 |  |  | FGMO
57 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 10 | 33 | 33 |  | 8 | Engine problem
58 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
59 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
60 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas Shortage
61 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 21 | 21 | 45 | 45 |  | 6 | Engine problem
62 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 115 | 133 | 150 | 150
63 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 85 | 85 | 85 | 85
64 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 100 | 100 |  | 57 | ST under maint.
66 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 98 | 85 | 200 | 200
67 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
68 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 104 | 124 | 105 | 130
69 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
70 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 34 | 52 | 52
71 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 22 | 22
72 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1361 | 1521 | 1997 | 2222 | 449 | 205
73 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 66 | 75 | 85 | 85 | 117 |  | Gas shortage
74 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
75 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 87 | 87 | 87 | 87 |  | 8 | Enjgine problem
76 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 1.9 | 0 | 2 | 0
77 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 80 | 200 | 100 | 200
| United Jamalpur PPL |  | HFO | IPP | 115 MW | 0 | 0 | 58 | 67 | 57 | 57
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 314.9 | 451 | 353 | 451 | 117 | 8
78 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 28 | 30 | 30 | 30 |  | 40 | GT-1 under maint.
79 | Fenchugonj CCPP-2 |  | Gas | PDB | !F71 | 104 | 90 | 49 | 60 | 60 | 60
80 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
81 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 244 | 301 | 308 | 280 |  | 110 | ST under maint.
82 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 49 | 53 | 51 | 51
83 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 49 | 44 | 44
84 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
85 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 60 | 66 | 66
86 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 60 | 84 | 86 | 86
87 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 46 | 46 | 50 | 50
88 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 85 | 112 | 100 | 130
89 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 19 | 20 | 20
90 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 23 | 23 | 23 | 23 |  | 27 | Engine problem
91 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25
92 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 305 | 341 | 341 |  |  | FGMO
| Bibiyana-3 285MW |  | Gas | PDB | 285 MW | 0 | 0 | 180 | 0 | 0 | 0 |  |  | On test
93 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1333 | 1309 | 1388 | 1390 | 0 | 177
94 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 603 | 702 | 509 | 705
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
95 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 99 | 115 | 115
96 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 44 | 0 | 40
97 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 |  |  | Reserve
98 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 60 | 0 | 80
99 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 360 | 300 | 410 | 410
100 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
0 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 100 | 100
102 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 90 | 105 | 105 | 105
| Khulna Area Total |  |  |  |  | 2223 | 2209 | 1109 | 1350 | 1279 | 1641 | 0 | 0
103 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 100 | 100
104 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
105 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 26 | 25 | 26 |  | 7 | Engine problem
106 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 189 | 187 | 194 | 194
107 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 96 | 95 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 303 | 356 | 414 | 445 | 0 | 7
108 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage.
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Gas shortage.
109 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 0 | 43
110 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 42
111 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 40 | 40 | 40 | 40 |  | 10 | Engine problem
112 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 43 | 50 | 50 | 50
113 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 15 | 40 | 40
114 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
115 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
116 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 141 | 141 | 201 | 186 | 200 | 200
117 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282 | 282 | 282 | 0 | 0 | 0 | 0 | 282 |  | Gas shortage
118 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 0 | 31
119 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
120 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 16 | 16 | 17 | 17
121 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
122 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 52 | 43 | 43 |  | 9 | Engine problem
123 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 50 | 102 | 100 | 100
| Paramount Baghabari |  | HSD | IPP | 200 MW | 0 | 0 | 30 | 0 | 0 | 0 |  |  | On Test
| Confidence CPBL-2 |  | HFO | IPP | 113 MW | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 1556 | 1546 | 456 | 568 | 523 | 639 | 783 | 119
124 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
125 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 149 | 150 | 150 | 124 |  | Coal shortage
126 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
127 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 17 | 18 | 19 | 19
| Rangpur Area Total |  |  |  |  | 564 | 484 | 166 | 167 | 169 | 186 | 124 | 170
| Total |  |  |  |  | 17685 | 17142 | 7482.9 | 8880 | 10578 | 11640 | 2596 | 2050
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7103.699 | 8430 | 10041.9527 | 11050.1351
A. |  | 2019-02-07 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 8880 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 5403 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8880 | MW
3 | Day peak Generation : |  |  | 7482.9 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8430 | MW
4 | Evening peak Generation : |  |  | 8880 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 170.6608 | MKWHr | By Solar | 0.13492 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 119.6087 | MKWHr |  | By Oil: | 30.139 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.6489 | MKWHr |  | By Hydro: | 0.79862 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2596 | MW | Dhaka | 2948 | 2948 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2050 | MW | Chittagong | 898 | 898 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 4646 | MW | Khulna | 1022 | 1022 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 973.87 | MMCFD |  |  | Rajshahi | 958 | 958 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 81569408.392 | ii) Oil : | Taka | 208925942.53 | Comilla | 742 | 742 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 14084754 | Total | Taka | 304580104.922 | Mymensingh | 718 | 718 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 5.458 | MKWHr. | Sylhet | 331 | 331 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -610 | MW (E to W) at | 19:30 | hrs | Barisal | 198 | 198 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -640 | MW at | 20:00 | hrs | Rangpur | 615 | 615 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 29.5° C |  |  | Total | 8430 | 8430 |  | 0
B. |  | 2019-02-08 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 29.5° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 11640 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6200 | MW
4 | Reserve(Generation end) |  |  |  | 3440 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 157.5922 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5547 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 14.0015 | MKWHr. | ii) HVDC Flow at Peak Time |  | 702 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.3292 | MKWHr. | iii) Maximum HVDC Flow : |  | 703 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 94.94 |  | (b) Today: | 94.79 |  | (c) Rule Curve: |  | 96.2
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-02-07
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285MW | United Jamalpur PPL | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | Paramount Baghabari | Confidence CPBL-2 | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 0 | 0 | 320 | 0 | 0 | 308 | 331 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 33 | 33 | 33 | 0 | 0 | 41 | 30 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 40 | 0 | 80 | 0 | 270 | 287 | 185 | 8 | 100 | 10 | 5 | 5 | 45 | 85 | 0 | 0 | 22 | 11 | 25 | 21 | 92 | 95 | 0 | 22 | 0 | 30 | 61 | 51 | 50 | 130 | 100 | 57 | 70 | 49 | 107 | 20 | 23 | 10 | 260 | 17 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 28 |  | 363 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 196 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 17 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 187 | 0 | 0 | 0 | 0 | 0 |  | 4604 | 1426 | 6030 | 3595 | 363 | 1676 | 84 | 149 | 71 | 0 | 92 | 0 | 0 | 94.96
2:00 | 35 | 0 | 0 | 0 | 320 | 0 | 0 | 308 | 331 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 33 | 33 | 33 | 0 | 0 | 41 | 30 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 40 | 0 | 80 | 0 | 270 | 290 | 185 | 8 | 100 | 10 | 5 | 5 | 45 | 85 | 0 | 0 | 22 | 8 | 0 | 21 | 90 | 94 | 0 | 22 | 0 | 30 | 61 | 51 | 50 | 130 | 82 | 58 | 5 | 49 | 108 | 0 | 23 | 0 | 270 | 17 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 28 |  | 363 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 187 | 0 | 0 | 0 | 0 | 0 |  | 4458 | 1313 | 5771 | 3530 | 363 | 1533 | 35 | 149 | 71 | 0 | 90 | 0 | 0 | 94.96
3:00 | 35 | 0 | 0 | 0 | 320 | 0 | 0 | 309 | 332 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 33 | 33 | 33 | 0 | 0 | 40 | 30 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 40 | 0 | 80 | 0 | 270 | 287 | 185 | 8 | 100 | 10 | 5 | 5 | 7 | 5 | 0 | 0 | 22 | 8 | 0 | 21 | 86 | 97 | 0 | 22 | 0 | 29 | 61 | 7 | 50 | 130 | 100 | 61 | 5 | 49 | 84 | 0 | 23 | 0 | 265 | 17 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 28 |  | 363 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 185 | 0 | 0 | 0 | 0 | 0 |  | 4286 | 1301 | 5587 | 3524 | 363 | 1360 | 35 | 149 | 70 | 0 | 86 | 0 | 0 | 94.95
4:00 | 35 | 0 | 0 | 0 | 320 | 0 | 0 | 310 | 311 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 33 | 33 | 33 | 0 | 0 | 40 | 30 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 40 | 0 | 80 | 0 | 270 | 272 | 185 | 8 | 100 | 10 | 5 | 5 | 7 | 5 | 0 | 0 | 22 | 8 | 0 | 20 | 84 | 97 | 0 | 22 | 0 | 29 | 61 | 5 | 5 | 130 | 160 | 60 | 5 | 5 | 82 | 0 | 5 | 0 | 260 | 17 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 28 |  | 363 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 17 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 183 | 0 | 0 | 0 | 0 | 0 |  | 4155 | 1283 | 5438 | 3555 | 363 | 1182 | 35 | 149 | 70 | 0 | 84 | 0 | 0 | 94.95
5:00 | 35 | 0 | 0 | 0 | 320 | 0 | 0 | 307 | 309 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 33 | 33 | 33 | 0 | 0 | 39 | 30 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 40 | 0 | 80 | 0 | 270 | 264 | 185 | 8 | 100 | 10 | 5 | 5 | 7 | 5 | 0 | 0 | 22 | 8 | 0 | 20 | 80 | 99 | 0 | 22 | 0 | 30 | 61 | 5 | 5 | 130 | 200 | 66 | 5 | 5 | 84 | 0 | 5 | 0 | 250 | 17 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 28 |  | 364 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 17 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 153 | 0 | 0 | 0 | 0 | 0 |  | 4175 | 1228 | 5403 | 3537 | 364 | 1169 | 35 | 149 | 69 | 0 | 80 | 0 | 0 | 94.94
6:00 | 35 | 0 | 0 | 0 | 320 | 0 | 0 | 306 | 308 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 6 | 0 | 0 | 0 | 25 | 33 | 33 | 33 | 0 | 0 | 39 | 30 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 40 | 0 | 80 | 0 | 270 | 276 | 191 | 8 | 100 | 10 | 5 | 5 | 7 | 5 | 0 | 0 | 22 | 8 | 0 | 20 | 84 | 99 | 4 | 22 | 0 | 30 | 61 | 11 | 14 | 130 | 207 | 68 | 40 | 5 | 83 | 0 | 23 | 0 | 240 | 17 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 28 |  | 607 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 195 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 29 | 0 | 22 | 17 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 159 | 0 | 0 | 21 | 0 | 0 |  | 4291 | 1606 | 5897 | 3606 | 607 | 1258 | 124 | 149 | 69 | 0 | 84 | 0 | 0 | 94.94
7:00 | 35 | 0 | 0 | 0 | 320 | 0 | 0 | 310 | 292 | 0 | 0 | 350 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 6 | 54 | 18 | 0 | 19 | 25 | 33 | 33 | 33 | 2 | 0 | 40 | 30 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 22 | 38 | 0 | 80 | 0 | 270 | 264 | 186 | 8 | 100 | 33 | 5 | 5 | 22 | 85 | 0 | 0 | 22 | 11 | 25 | 20 | 88 | 98 | 28 | 22 | 0.1 | 28 | 61 | 48 | 50 | 130 | 212 | 63 | 81 | 49 | 82 | 0 | 23 | 10 | 230 | 17 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 1.2 | 30 | 19 | 6 | 329 | 26 |  | 606 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 193 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 8 | 0 | 43 | 0 | 22 | 17 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 155 | 0 | 0 | 70 | 0 | 0 |  | 4797.3 | 1739 | 6536.3 | 3661 | 606 | 1500 | 461 | 149 | 70 | 0 | 88 | 1.3 | 0 | 94.93
8:00 | 35 | 0 | 0 | 0 | 380 | 0 | 0 | 307 | 291 | 0 | 0 | 330 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 47 | 54 | 36 | 0 | 19 | 25 | 33 | 33 | 33 | 38 | 0 | 40 | 30 | 0 | 0 | 9 | 51 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 7 | 30 | 18 | 22 | 12 | 0 | 80 | 0 | 270 | 287 | 197 | 8 | 100 | 33 | 5 | 5 | 45 | 85 | 0 | 0 | 22 | 11 | 25 | 20 | 94 | 74 | 80 | 22 | 0.5 | 30 | 62 | 50 | 50 | 100 | 208 | 70 | 81 | 49 | 92 | 0 | 23 | 10 | 240 | 17 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 4 | 6 | 74 | 50 | 35 | 330 | 28 |  | 607 | 0 | 300 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 40 | 195 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 40 | 24 | 0 | 43 | 0 | 18 | 17 | 11 | 0 | 0 | 148 | 0 | 19 | 0 | 0 | 0 | 0 | 93 | 0 | 176 | 0 | 0 | 105 | 0 | 0 |  | 5071.5 | 1936 | 7007.5 | 3570 | 607 | 1529 | 913 | 148 | 70 | 70 | 94 | 6.5 | 0 | 95.16
9:00 | 35 | 0 | 0 | 0 | 380 | 0 | 0 | 305 | 300 | 0 | 0 | 425 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 46 | 54 | 37 | 0 | 19 | 25 | 10 | 33 | 25 | 51 | 0 | 42 | 30 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 52 | 46 | 22 | 3 | 0 | 80 | 0 | 360 | 320 | 193 | 8 | 96 | 36 | 5 | 5 | 45 | 85 | 0 | 0 | 19 | 11 | 25 | 21 | 94 | 72 | 80 | 22 | 1 | 30 | 61 | 48 | 50 | 130 | 189 | 67 | 81 | 49 | 100 | 0 | 23 | 10 | 270 | 17 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 17 | 11.5 | 74 | 54 | 50 | 160 | 48 |  | 607 | 0 | 340 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 40 | 191 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 40 | 43 | 0 | 43 | 0 | 18 | 17 | 8 | 0 | 0 | 149 | 0 | 19 | 0 | 0 | 0 | 0 | 95 | 0 | 200 | 0 | 0 | 105 | 0 | 0 |  | 5270.5 | 2049 | 7319.5 | 3472 | 607 | 1684 | 1125 | 149 | 72 | 104 | 94 | 12.5 | 0 | 95.16
10:00 | 35 | 0 | 0 | 0 | 380 | 0 | 0 | 302 | 362 | 13 | 0 | 430 | 0 | 1 | 0 | 25 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 49 | 0 | 46 | 54 | 37 | 0 | 19 | 25 | 32 | 33 | 25 | 51 | 0 | 26 | 30 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 53 | 48 | 22 | 4 | 0 | 80 | 0 | 360 | 305 | 162 | 8 | 100 | 36 | 5 | 5 | 45 | 85 | 0 | 0 | 19 | 11 | 25 | 21 | 98 | 65 | 87 | 22 | 1.5 | 29 | 61 | 48 | 50 | 130 | 188 | 64 | 50 | 49 | 85 | 0 | 23 | 10 | 260 | 17 | 8 | 0 | 0 | 0 | 0 | 80 | 0 | 15 | 13.5 | 74 | 76 | 80 | 149 | 58 |  | 607 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 189 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 43 | 0 | 43 | 0 | 18 | 17 | 8 | 0 | 0 | 149 | 0 | 18 | 0 | 0 | 0 | 0 | 96 | 0 | 186 | 0 | 0 | 72 | 18 | 0 |  | 5361 | 1960 | 7321 | 3403 | 607 | 1705 | 1220 | 149 | 56 | 68 | 98 | 15 | 0 | 95.16
11:00 | 35 | 0 | 0 | 0 | 380 | 0 | 0 | 295 | 361 | 13 | 0 | 450 | 0 | 7 | 25 | 30 | 0 | 0 | 0 | 0 | 40 | 7 | 0 | 0 | 48 | 0 | 47 | 54 | 37 | 0 | 19 | 25 | 26 | 33 | 25 | 51 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 78 | 48 | 21 | 2 | 0 | 70 | 0 | 300 | 279 | 154 | 8 | 100 | 10 | 5 | 5 | 45 | 85 | 0 | 0 | 19 | 11 | 25 | 21 | 98 | 66 | 87 | 22 | 1.8 | 29 | 49 | 48 | 50 | 130 | 245 | 67 | 50 | 46 | 92 | 0 | 23 | 10 | 280 | 17 | 8 | 0 | 0 | 0 | 0 | 80 | 0 | 15 | 17.6 | 74 | 87 | 100 | 150 | 58 |  | 607 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 190 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 43 | 0 | 43 | 0 | 18 | 16 | 8 | 0 | 0 | 149 | 0 | 18 | 0 | 0 | 0 | 0 | 98 | 0 | 192 | 0 | 0 | 70 | 25 | 0 |  | 5387.4 | 1973 | 7360.4 | 3323 | 607 | 1740 | 1356 | 149 | 0 | 68 | 98 | 19.4 | 0 | 95.16
12:00 | 35 | 0 | 0 | 0 | 380 | 0 | 0 | 290 | 357 | 26 | 0 | 450 | 0 | 8 | 48 | 30 | 0 | 0 | 0 | 0 | 50 | 7 | 0 | 0 | 48 | 0 | 47 | 54 | 37 | 0 | 19 | 25 | 26 | 33 | 25 | 51 | 0 | 0 | 30 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 93 | 47 | 22 | 2 | 20 | 60 | 0 | 280 | 257 | 125 | 8 | 100 | 5 | 5 | 5 | 21 | 85 | 0 | 0 | 19 | 8 | 25 | 21 | 104 | 66 | 87 | 22 | 1.9 | 28 | 49 | 49 | 50 | 130 | 244 | 60 | 60 | 46 | 85 | 0 | 23 | 10 | 295 | 16 | 8 | 0 | 0 | 0 | 0 | 80 | 0 | 15 | 18 | 74 | 98 | 115 | 180 | 58 |  | 603 | 0 | 360 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 189 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 43 | 0 | 43 | 0 | 22 | 16 | 11 | 0 | 0 | 149 | 0 | 17 | 0 | 0 | 0 | 0 | 96 | 0 | 201 | 0 | 0 | 90 | 30 | 0 |  | 5448.9 | 2034 | 7482.9 | 3294 | 603 | 1748 | 1468 | 149 | 30 | 67 | 104 | 19.9 | 0 | 95.15
13:00 | 35 | 0 | 0 | 0 | 380 | 0 | 0 | 290 | 341 | 26 | 0 | 370 | 0 | 50 | 50 | 48 | 0 | 0 | 0 | 0 | 50 | 32 | 0 | 0 | 46 | 0 | 47 | 54 | 37 | 0 | 19 | 25 | 22 | 33 | 25 | 19 | 0 | 35 | 30 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 68 | 93 | 46 | 22 | 9 | 50 | 60 | 0 | 280 | 257 | 128 | 8 | 95 | 5 | 5 | 5 | 21 | 85 | 0 | 0 | 22 | 8 | 25 | 21 | 104 | 67 | 87 | 22 | 1.9 | 28 | 49 | 50 | 50 | 100 | 243 | 55 | 60 | 46 | 85 | 0 | 23 | 10 | 270 | 16 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 15 | 17.5 | 74 | 140 | 145 | 180 | 41 |  | 603 | 0 | 260 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 159 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 50 | 0 | 43 | 0 | 22 | 14 | 11 | 0 | 0 | 149 | 0 | 17 | 0 | 0 | 0 | 0 | 98 | 0 | 201 | 0 | 0 | 105 | 28 | 0 |  | 5491.4 | 1925 | 7416.4 | 3189 | 603 | 1606 | 1614 | 149 | 65 | 67 | 104 | 19.4 | 0 | 95.14
14:00 | 35 | 0 | 0 | 0 | 300 | 0 | 0 | 292 | 266 | 27 | 0 | 340 | 0 | 40 | 64 | 48 | 0 | 0 | 0 | 0 | 50 | 64 | 0 | 5 | 45 | 0 | 47 | 54 | 37 | 0 | 16 | 25 | 22 | 33 | 25 | 51 | 0 | 40 | 30 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 68 | 87 | 46 | 19 | 8 | 70 | 0 | 0 | 280 | 253 | 184 | 8 | 100 | 5 | 5 | 5 | 21 | 40 | 0 | 0 | 22 | 8 | 25 | 15 | 102 | 67 | 87 | 22 | 1.7 | 30 | 28 | 10 | 50 | 100 | 150 | 51 | 60 | 46 | 85 | 0 | 23 | 10 | 260 | 17 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 15 | 15.3 | 74 | 140 | 150 | 99 | 58 |  | 603 | 0 | 260 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 171 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 24 | 0 | 43 | 0 | 22 | 13 | 11 | 0 | 0 | 149 | 0 | 17 | 0 | 0 | 0 | 0 | 94 | 0 | 187 | 0 | 0 | 105 | 32 | 0 |  | 5117 | 1897 | 7014 | 2918 | 603 | 1401 | 1687 | 149 | 70 | 67 | 102 | 17 | 0 | 95.13
15:00 | 35 | 0 | 0 | 0 | 300 | 0 | 0 | 288 | 271 | 19 | 0 | 340 | 0 | 16 | 64 | 48 | 0 | 0 | 0 | 0 | 50 | 102 | 0 | 10 | 45 | 0 | 47 | 54 | 37 | 17 | 16 | 25 | 22 | 33 | 25 | 51 | 0 | 40 | 30 | 0 | 10 | 25 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 68 | 87 | 46 | 19 | 2 | 70 | 0 | 0 | 280 | 253 | 210 | 8 | 100 | 5 | 5 | 5 | 21 | 40 | 0 | 0 | 22 | 8 | 25 | 21 | 102 | 66 | 87 | 0 | 1.2 | 28 | 48 | 11 | 49 | 100 | 147 | 64 | 60 | 46 | 84 | 0 | 23 | 10 | 270 | 16 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 28 | 11.5 | 74 | 105 | 150 | 130 | 48 |  | 603 | 0 | 260 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 193 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 12 | 24 | 0 | 43 | 0 | 22 | 14 | 11 | 0 | 0 | 149 | 0 | 17 | 0 | 0 | 0 | 0 | 93 | 0 | 185 | 0 | 0 | 105 | 28 | 0 |  | 5189.7 | 1881 | 7070.7 | 3010 | 603 | 1406 | 1651 | 149 | 70 | 67 | 102 | 12.7 | 0 | 95.13
16:00 | 35 | 0 | 0 | 0 | 300 | 0 | 0 | 290 | 313 | 13 | 0 | 370 | 0 | 16 | 64 | 48 | 0 | 0 | 0 | 0 | 7 | 102 | 0 | 10 | 45 | 0 | 47 | 54 | 37 | 17 | 19 | 25 | 22 | 33 | 25 | 51 | 0 | 40 | 30 | 0 | 40 | 25 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 68 | 92 | 46 | 19 | 2 | 70 | 0 | 0 | 280 | 257 | 218 | 8 | 100 | 5 | 5 | 5 | 21 | 40 | 0 | 0 | 22 | 8 | 25 | 15 | 88 | 69 | 87 | 22 | 0.8 | 28 | 48 | 11 | 50 | 100 | 147 | 58 | 30 | 46 | 84 | 0 | 23 | 10 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 28 | 6.6 | 74 | 50 | 87 | 128 | 58 |  | 602 | 0 | 260 | 0 | 16 | 0 | 0 | 0 | 0 | 3 | 40 | 190 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 12 | 24 | 0 | 25 | 20 | 22 | 15 | 11 | 0 | 0 | 149 | 0 | 17 | 0 | 0 | 0 | 0 | 96 | 0 | 146 | 0 | 0 | 53 | 0 | 0 |  | 5129.4 | 1769 | 6898.4 | 3026 | 602 | 1464 | 1401 | 149 | 70 | 91 | 88 | 7.4 | 0 | 95.12
17:00 | 35 | 0 | 0 | 0 | 296 | 0 | 0 | 288 | 308 | 13 | 0 | 370 | 0 | 16 | 64 | 48 | 0 | 0 | 0 | 0 | 7 | 102 | 0 | 10 | 45 | 0 | 18 | 54 | 37 | 17 | 19 | 25 | 22 | 33 | 25 | 51 | 0 | 40 | 30 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 68 | 95 | 46 | 19 | 14 | 80 | 0 | 0 | 280 | 257 | 217 | 8 | 100 | 5 | 5 | 5 | 21 | 40 | 0 | 0 | 22 | 8 | 25 | 15 | 92 | 71 | 87 | 22 | 0.1 | 30 | 48 | 11 | 50 | 100 | 161 | 60 | 30 | 46 | 84 | 0 | 23 | 10 | 285 | 16 | 11 | 0 | 2 | 0 | 0 | 80 | 0 | 14 | 1.7 | 74 | 50 | 83 | 0 | 58 |  | 602 | 0 | 260 | 0 | 16 | 0 | 0 | 0 | 6 | 18 | 40 | 186 | 17 | 0 | 0 | 0 | 0 | 0 | 10 | 51 | 12 | 8 | 7 | 25 | 31 | 22 | 15 | 11 | 0 | 0 | 149 | 0 | 17 | 0 | 0 | 0 | 0 | 98 | 0 | 195 | 0 | 0 | 35 | 0 | 0 |  | 5022.8 | 1831 | 6853.8 | 2996 | 602 | 1478 | 1325 | 149 | 70 | 140 | 92 | 1.8 | 0 | 95.12
18:00 | 35 | 0 | 0 | 0 | 300 | 0 | 0 | 295 | 278 | 13 | 0 | 370 | 0 | 18 | 64 | 48 | 0 | 0 | 0 | 0 | 8 | 102 | 0 | 10 | 45 | 0 | 18 | 54 | 37 | 50 | 19 | 25 | 6 | 33 | 25 | 51 | 0 | 40 | 30 | 0 | 90 | 25 | 0 | 0 | 0 | 0 | 0 | 51 | 56 | 68 | 68 | 100 | 46 | 19 | 21 | 80 | 0 | 0 | 280 | 257 | 204 | 8 | 100 | 10 | 5 | 5 | 21 | 40 | 4 | 5 | 22 | 8 | 25 | 16 | 124 | 74 | 87 | 22 | 0 | 28 | 60 | 11 | 49 | 100 | 195 | 67 | 30 | 46 | 96 | 0 | 23 | 10 | 285 | 16 | 11 | 0 | 40 | 0 | 0 | 125 | 0 | 28 | 0 | 74 | 74 | 85 | 0 | 58 |  | 703 | 0 | 300 | 0 | 101 | 0 | 0 | 0 | 38 | 36 | 40 | 186 | 23 | 20 | 0 | 0 | 0 | 43 | 0 | 102 | 40 | 24 | 34 | 36 | 31 | 22 | 13 | 11 | 0 | 0 | 149 | 0 | 17 | 0 | 0 | 0 | 0 | 77 | 0 | 185 | 0 | 0 | 35 | 0 | 0 |  | 5426 | 2266 | 7692 | 3100 | 703 | 1437 | 1680 | 149 | 70 | 429 | 124 | 0 | 0 | 95.11
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 0 | 0 | 300 | 0 | 0 | 291 | 328 | 13 | 0 | 400 | 0 | 80 | 80 | 48 | 0 | 0 | 0 | 0 | 45 | 102 | 0 | 10 | 47 | 0 | 40 | 54 | 37 | 55 | 19 | 25 | 33 | 28 | 25 | 51 | 0 | 40 | 30 | 0 | 100 | 25 | 0 | 0 | 0 | 0 | 0 | 51 | 51 | 68 | 70 | 100 | 46 | 19 | 32 | 80 | 0 | 0 | 305 | 257 | 186 | 8 | 100 | 10 | 5 | 5 | 21 | 85 | 8 | 27 | 22 | 8 | 25 | 21 | 124 | 74 | 87 | 22 | 0 | 28 | 60 | 53 | 49 | 130 | 296 | 65 | 84 | 46 | 112 | 19 | 23 | 10 | 300 | 16 | 11 | 0 | 168 | 0 | 0 | 192 | 0 | 72 | 0 | 74 | 120 | 121 | 0 | 67 |  | 702 | 0 | 300 | 0 | 99 | 0 | 0 | 0 | 40 | 60 | 40 | 186 | 26 | 48 | 0 | 0 | 0 | 43 | 0 | 102 | 40 | 50 | 39 | 52 | 31 | 22 | 14 | 11 | 0 | 0 | 149 | 0 | 18 | 0 | 0 | 0 | 0 | 96 | 0 | 193 | 0 | 0 | 105 | 0 | 0 |  | 6374 | 2466 | 8840 | 3282 | 702 | 1737 | 2316 | 149 | 70 | 460 | 124 | 0 | 0 | 95.11
19:30 | 35 | 0 | 0 | 0 | 300 | 0 | 0 | 290 | 328 | 0 | 0 | 400 | 0 | 100 | 100 | 48 | 0 | 0 | 0 | 0 | 50 | 102 | 0 | 10 | 48 | 0 | 40 | 54 | 37 | 55 | 19 | 25 | 33 | 33 | 25 | 51 | 0 | 40 | 30 | 0 | 100 | 25 | 0 | 0 | 0 | 0 | 0 | 51 | 56 | 68 | 70 | 100 | 46 | 19 | 32 | 80 | 0 | 0 | 305 | 264 | 186 | 8 | 100 | 10 | 5 | 5 | 21 | 85 | 0 | 34 | 22 | 8 | 25 | 21 | 124 | 75 | 87 | 22 | 0 | 30 | 60 | 53 | 49 | 130 | 301 | 60 | 84 | 46 | 112 | 19 | 23 | 10 | 305 | 16 | 11 | 0 | 180 | 0 | 0 | 200 | 0 | 84 | 0 | 74 | 85 | 133 | 0 | 67 |  | 702 | 0 | 300 | 0 | 99 | 0 | 0 | 0 | 44 | 60 | 40 | 187 | 26 | 48 | 0 | 0 | 0 | 43 | 0 | 102 | 40 | 50 | 15 | 52 | 31 | 22 | 16 | 11 | 0 | 0 | 149 | 0 | 18 | 0 | 0 | 0 | 0 | 95 | 0 | 186 | 0 | 0 | 105 | 0 | 0 |  | 6439 | 2441 | 8880 | 3290 | 702 | 1743 | 2365 | 149 | 70 | 437 | 124 | 0 | 0 | 95.11
20:00 | 35 | 0 | 0 | 0 | 300 | 0 | 0 | 296 | 328 | 0 | 0 | 400 | 0 | 80 | 80 | 48 | 0 | 0 | 0 | 0 | 24 | 102 | 0 | 0 | 48 | 0 | 47 | 54 | 37 | 55 | 19 | 25 | 33 | 33 | 25 | 51 | 0 | 40 | 30 | 0 | 100 | 25 | 0 | 0 | 0 | 0 | 0 | 51 | 31 | 68 | 70 | 100 | 46 | 19 | 36 | 80 | 0 | 0 | 305 | 264 | 188 | 8 | 100 | 10 | 5 | 5 | 21 | 85 | 0 | 32 | 22 | 8 | 25 | 21 | 126 | 74 | 87 | 22 | 0 | 28 | 60 | 53 | 49 | 130 | 301 | 66 | 84 | 46 | 115 | 19 | 23 | 10 | 280 | 16 | 11 | 0 | 198 | 0 | 0 | 200 | 0 | 82 | 0 | 74 | 85 | 133 | 0 | 48 |  | 703 | 0 | 300 | 0 | 99 | 0 | 0 | 0 | 44 | 60 | 40 | 187 | 19 | 48 | 0 | 0 | 0 | 43 | 0 | 102 | 40 | 50 | 0 | 52 | 31 | 22 | 15 | 11 | 0 | 0 | 149 | 0 | 18 | 0 | 0 | 0 | 0 | 95 | 0 | 186 | 0 | 0 | 105 | 0 | 0 |  | 6335 | 2419 | 8754 | 3304 | 703 | 1714 | 2291 | 149 | 70 | 397 | 126 | 0 | 0 | 95.1
21:00 | 35 | 0 | 0 | 0 | 300 | 0 | 0 | 297 | 330 | 0 | 0 | 400 | 0 | 40 | 80 | 48 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 48 | 0 | 46 | 54 | 37 | 55 | 19 | 25 | 33 | 33 | 25 | 51 | 0 | 40 | 30 | 0 | 100 | 25 | 0 | 0 | 0 | 0 | 0 | 51 | 24 | 34 | 70 | 100 | 46 | 19 | 38 | 80 | 0 | 0 | 305 | 283 | 196 | 8 | 100 | 10 | 5 | 5 | 21 | 85 | 0 | 32 | 22 | 11 | 25 | 21 | 124 | 75 | 87 | 22 | 0 | 28 | 60 | 53 | 49 | 130 | 307 | 69 | 84 | 47 | 114 | 20 | 23 | 10 | 295 | 17 | 11 | 0 | 188 | 0 | 0 | 160 | 0 | 43 | 0 | 74 | 85 | 138 | 0 | 52 |  | 698 | 0 | 300 | 0 | 99 | 0 | 0 | 0 | 44 | 60 | 40 | 188 | 27 | 48 | 0 | 0 | 0 | 43 | 0 | 102 | 40 | 50 | 0 | 52 | 31 | 22 | 17 | 11 | 0 | 0 | 149 | 0 | 19 | 0 | 0 | 0 | 0 | 96 | 0 | 190 | 0 | 0 | 105 | 0 | 0 |  | 6209 | 2431 | 8640 | 3351 | 698 | 1745 | 2146 | 149 | 70 | 357 | 124 | 0 | 0 | 95.1
22:00 | 35 | 0 | 0 | 0 | 300 | 0 | 0 | 299 | 330 | 0 | 0 | 400 | 0 | 0 | 15 | 48 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 48 | 0 | 46 | 54 | 37 | 17 | 19 | 25 | 33 | 33 | 25 | 51 | 0 | 40 | 30 | 0 | 100 | 25 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 70 | 60 | 46 | 19 | 41 | 80 | 0 | 0 | 305 | 264 | 185 | 8 | 100 | 10 | 5 | 5 | 21 | 85 | 0 | 0 | 22 | 11 | 25 | 21 | 114 | 73 | 87 | 22 | 0 | 30 | 60 | 50 | 49 | 130 | 305 | 63 | 84 | 48 | 112 | 20 | 23 | 10 | 275 | 17 | 8 | 0 | 124 | 0 | 0 | 100 | 0 | 28 | 0 | 74 | 85 | 141 | 0 | 48 |  | 697 | 0 | 300 | 0 | 99 | 0 | 0 | 0 | 38 | 0 | 40 | 186 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 102 | 40 | 0 | 0 | 52 | 31 | 22 | 17 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 186 | 0 | 0 | 105 | 0 | 0 |  | 5671 | 2243 | 7914 | 3304 | 697 | 1723 | 1686 | 149 | 70 | 171 | 114 | 0 | 0 | 94.98
23:00 | 35 | 0 | 0 | 0 | 300 | 0 | 0 | 299 | 330 | 0 | 0 | 400 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 48 | 0 | 46 | 54 | 37 | 0 | 19 | 0 | 33 | 33 | 25 | 25 | 0 | 40 | 30 | 0 | 100 | 25 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 46 | 19 | 41 | 80 | 0 | 0 | 305 | 287 | 192 | 8 | 100 | 10 | 5 | 5 | 21 | 85 | 0 | 0 | 22 | 11 | 25 | 21 | 104 | 75 | 87 | 22 | 0 | 29 | 60 | 53 | 49 | 130 | 312 | 69 | 84 | 48 | 118 | 20 | 23 | 10 | 280 | 17 | 8 | 0 | 14 | 0 | 0 | 100 | 0 | 0 | 0 | 74 | 90 | 141 | 0 | 46 |  | 698 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 32 | 188 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 52 | 0 | 22 | 16 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 190 | 0 | 0 | 105 | 0 | 0 |  | 5330 | 1955 | 7285 | 3335 | 698 | 1730 | 1199 | 149 | 70 | 0 | 104 | 0 | 0 | 94.97
24:00 | 35 | 0 | 0 | 0 | 300 | 0 | 0 | 300 | 330 | 0 | 0 | 400 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 48 | 0 | 6 | 54 | 18 | 0 | 19 | 25 | 33 | 33 | 25 | 25 | 0 | 40 | 30 | 0 | 100 | 25 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 19 | 19 | 41 | 80 | 0 | 0 | 305 | 264 | 185 | 8 | 95 | 10 | 5 | 5 | 21 | 85 | 0 | 0 | 22 | 11 | 25 | 21 | 96 | 96 | 87 | 22 | 0 | 28 | 60 | 53 | 49 | 130 | 300 | 52 | 81 | 48 | 113 | 20 | 23 | 10 | 250 | 17 | 8 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 74 | 87 | 141 | 0 | 36 |  | 641 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 190 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 52 | 0 | 22 | 16 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 188 | 0 | 0 | 0 | 0 | 0 |  | 5045 | 1736 | 6781 | 3284 | 641 | 1695 | 846 | 149 | 70 | 0 | 96 | 0 | 0 | 94.97
KWH | 710000 | 0 | 0 | 0 | 7929709 | 0 | 0 | 7275520 | 7645000 | 145200 | 0 | 9015625 | 0 | 418560 | 783096 | 695067 | 0 | 0 | 0 | 0 | 443520 | 966672 | 0 | 73527 | 813120 | 0 | 764016 | 988560 | 624321 | 301000 | 416448 | 575000 | 662760 | 811800 | 658800 | 787704 | 0 | 798616 | 0 | 0 | 800000 | 412380 | 1471566 | 0 | 0 | 0 | 0 | 511680 | 152920 | 212088 | 939840 | 1233600 | 745920 | 494928 | 589440 | 889740 | 1009290 | 0 | 7313900 | 6744000 | 4502000 | 200727 | 2361890 | 288360 | 156480 | 120000 | 672092 | 1524477 | 7528 | 127176 | 499212 | 208800 | 496800 | 494670 | 2329160 | 1853180 | 1472640 | 500400 | 12200 | 690000 | 1348120 | 861600 | 1066000 | 3331946 | 4639000 | 1485984 | 1396800 | 1005480 | 2402950 | 145000 | 525280 | 200700 | 6767250 | 395760 | 226896 | 0 | 757750 | 0 | 0 | 1948800 | 0 | 388800 | 122715 | 1253760 | 1588800 | 1973818 | 3879800 | 1094400 |  | 14001455 | 0 | 7900416 | 0 | 667200 | 0 | 0 | 0 | 197760 | 245248 | 720000 | 4515402 | 447300 | 248640 | 0 | 0 | 0 | 155439 | 6706 | 1042268 | 661610 | 520599 | 68241 | 790080 | 195408 | 504000 | 377712 | 213426 | 0 | 0 | 3648900 | 0 | 254000 | 0 | 0 | 0 | 0 | 1798475 | 0 | 4590818 | 0 | 0 | 1579680 | 159900 | 0 |  | 125150134 | 45510683 | 170660817 | 81402345 | 14001455 | 38206384 | 27601436 | 3648900 | 798616 | 2537606 | 2329160 | 134915 | 0
Fuel Cost | 610600 | 0 | 0 | 0 | 5075013.76 | 0 | 0 | 4438067.2 | 4663450 | 1395372 | 0 | 6040468.75 | 0 | 2628556.8 | 5231081.28 | 4246859.37 | 0 | 0 | 0 | 0 | 2772000 | 6370368.48 | 0 | 468366.99 | 4870588.8 | 0 | 5095986.72 | 7048432.8 | 3902006.25 | 1887270 | 312336 | 431250 | 0 | 0 | 0 | 7451679.84 | 0 | 0 | 0 | 0 | 880000 | 3905238.6 | 971233.56 | 0 | 0 | 0 | 0 | 4497667.2 | 1646948.4 | 2063616.24 | 5817609.6 | 7969056 | 4878316.8 | 420688.8 | 0 | 809663.4 | 918453.9 | 0 | 4534618 | 4653360 | 3151400 | 138501.63 | 2267414.4 | 193201.2 | 134572.8 | 110400 | 551115.44 | 1448253.15 | 81603.52 | 943645.92 | 384393.24 | 156600 | 382536 | 371002.5 | 15931454.4 | 1389885 | 13533561.6 | 385308 | 0 | 717600 | 1402044.8 | 827136 | 959400 | 2598917.88 | 3247300 | 1694021.76 | 1494576 | 1106028 | 2739363 | 185600 | 488510.4 | 186651 | 4331040 | 296820 | 172440.96 | 0 | 5501265 | 0 | 0 | 13933920 | 0 | 0 | 0 | 0 | 14839392 | 18435460.12 | 3375426 | 0 |  | 71407420.5 | 0 | 5293278.72 | 0 | 5531088 | 0 | 0 | 0 | 2226777.6 | 2889021.44 | 5673600 | 3115627.38 | 442827 | 1839936 | 0 | 0 | 0 | 1779776.55 | 71888.32 | 9338721.28 | 5722926.5 | 4633331.1 | 726766.65 | 7837593.6 | 2299952.16 | 554400 | 355049.28 | 161563.482 | 0 | 0 | 14084754 | 0 | 6799580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139113 | 0 |  | 238993987.26 | 152924992.562 | 391918979.822 | 55138111.062 | 71407420.5 | 26431297.33 | 179001290.37 | 14084754 | 0 | 29924652.16 | 15931454.4 | 0 | 0
Yesterday Day Peak | 35 | 0 | 0 | 0 | 380 | 0 | 0 | 290 | 357 | 26 | 0 | 450 | 0 | 8 | 48 | 30 | 0 | 0 | 0 | 0 | 50 | 7 | 0 | 0 | 48 | 0 | 47 | 54 | 37 | 0 | 19 | 25 | 26 | 33 | 25 | 51 | 0 | 0 | 30 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 93 | 47 | 22 | 2 | 20 | 60 | 0 | 280 | 257 | 125 | 8 | 100 | 5 | 5 | 5 | 21 | 85 | 0 | 0 | 19 | 8 | 25 | 21 | 104 | 66 | 87 | 22 | 1.9 | 28 | 49 | 49 | 50 | 130 | 244 | 60 | 60 | 46 | 85 | 0 | 23 | 10 | 295 | 16 | 8 | 0 | 0 | 0 | 0 | 80 | 0 | 15 | 18 | 74 | 98 | 115 | 180 | 58 |  | 603 | 0 | 360 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 189 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 43 | 0 | 43 | 0 | 22 | 16 | 11 | 0 | 0 | 149 | 0 | 17 | 0 | 0 | 0 | 0 | 96 | 0 | 201 | 0 | 0 | 90 | 30 | 0 |  | 7482.9 | DayPeak
Yesterday Evening Peak | 35 | 0 | 0 | 0 | 300 | 0 | 0 | 290 | 328 | 0 | 0 | 400 | 0 | 100 | 100 | 48 | 0 | 0 | 0 | 0 | 50 | 102 | 0 | 10 | 48 | 0 | 40 | 54 | 37 | 55 | 19 | 25 | 33 | 33 | 25 | 51 | 0 | 40 | 30 | 0 | 100 | 25 | 0 | 0 | 0 | 0 | 0 | 51 | 56 | 68 | 70 | 100 | 46 | 19 | 32 | 80 | 0 | 0 | 305 | 264 | 186 | 8 | 100 | 10 | 5 | 5 | 21 | 85 | 0 | 34 | 22 | 8 | 25 | 21 | 124 | 75 | 87 | 22 | 0 | 30 | 60 | 53 | 49 | 130 | 301 | 60 | 84 | 46 | 112 | 19 | 23 | 10 | 305 | 16 | 11 | 0 | 180 | 0 | 0 | 200 | 0 | 84 | 0 | 74 | 85 | 133 | 0 | 67 |  | 702 | 0 | 300 | 0 | 99 | 0 | 0 | 0 | 44 | 60 | 40 | 187 | 26 | 48 | 0 | 0 | 0 | 43 | 0 | 102 | 40 | 50 | 15 | 52 | 31 | 22 | 16 | 11 | 0 | 0 | 149 | 0 | 18 | 0 | 0 | 0 | 0 | 95 | 0 | 186 | 0 | 0 | 105 | 0 | 0 |  | 8880 | EvPeak
Forecast for Evening | 35 | 0 | 0 | 0 | 380 | 0 | 0 | 300 | 360 | 95 | 0 | 450 | 0 | 100 | 100 | 55 | 0 | 0 | 105 | 100 | 100 | 102 | 149 | 100 | 49 | 0 | 47 | 54 | 37 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 42 | 30 | 0 | 110 | 25 | 0 | 0 | 0 | 0 | 0 | 51 | 65 | 68 | 68 | 106 | 50 | 22 | 25 | 130 | 0 | 0 | 360 | 360 | 221 | 8 | 100 | 33 | 5 | 5 | 45 | 85 | 50 | 52 | 22 | 11 | 33 | 22 | 130 | 85 | 87 | 22 | 0 | 30 | 60 | 51 | 44 | 163 | 280 | 66 | 86 | 50 | 130 | 20 | 23 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 84 | 200 | 150 | 0 | 57 |  | 705 | 46 | 410 | 0 | 115 | 0 | 0 | 0 | 40 | 80 | 40 | 194 | 26 | 100 | 30 | 0 | 0 | 43 | 42 | 100 | 40 | 50 | 40 | 43 | 31 | 22 | 17 | 11 | 0 | 0 | 150 | 17 | 19 | 0 | 0 | 0 | 0 | 95 | 100 | 200 | 0 | 0 | 105 | 0
Forecast for Day | 35 | 0 | 0 | 0 | 380 | 0 | 0 | 300 | 360 | 95 | 0 | 450 | 0 | 100 | 100 | 55 | 0 | 0 | 105 | 100 | 100 | 102 | 149 | 100 | 49 | 0 | 47 | 54 | 37 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 42 | 30 | 0 | 110 | 25 | 0 | 0 | 0 | 0 | 0 | 51 | 60 | 68 | 68 | 90 | 50 | 22 | 15 | 80 | 0 | 0 | 360 | 360 | 221 | 8 | 100 | 33 | 5 | 5 | 45 | 85 | 0 | 52 | 22 | 11 | 33 | 22 | 105 | 85 | 87 | 22 | 2 | 30 | 60 | 51 | 44 | 163 | 308 | 66 | 86 | 50 | 100 | 20 | 23 | 10 | 341 | 25 | 11 | 100 | 300 | 300 | 0 | 100 | 0 | 149 | 20 | 84 | 200 | 150 | 0 | 57 |  | 509 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 194 | 25 | 100 | 0 | 0 | 0 | 0 | 0 | 100 | 40 | 50 | 40 | 43 | 0 | 22 | 17 | 11 | 0 | 0 | 150 |  | 19 | 0 | 0 | 0 | 0 | 95 | 100 | 200 | 0 | 0 | 105
Generation at 08:00(Today) | 35 | 0 | 0 | 0 | 280 | 0 | 0 | 305 | 280 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 0 | 33 | 33 | 25 | 8 | 0 | 39 | 30 | 0 | 110 | 26 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 45 | 19 | 40 | 80 | 0 | 0 | 300 | 264 | 187 | 8 | 95 | 10 | 5 | 5 | 33 | 5 | 0 | 0 | 22 | 8 | 25 | 21 | 0 | 112 | 58 | 22 | 0.2 | 28 | 60 | 53 | 49 | 100 | 308 | 71 | 5 | 48 | 114 | 20 | 23 | 10 | 341 | 17 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7.5 | 74 | 0 | 0 | 0 | 19 | 0 | 503 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 32 | 0 | 0 | 52 | 0 | 22 | 14 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 190 | 0 | 0 | 90 | 0 | 0 | 0
199
| Minimum Generation |  | 5403 | 5:00
| Highest Generation |  | 8880 | 19:30
| Day Peak Generation |  | 7482.9 | 12:00
| Evening Peak Generation |  | 8880 | 19:30
| HVDC Max Flow |  | 703 | 18:00
| HVDC EvPeak Flow |  | 702 | 19:30
| Load factor L.F |  | 80.08%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-02-08
Till now the maximum generation is : - |  |  | 11623 MW | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2019-02-07 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7482.9 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5547 | MW
Evening Peak Generation : |  | 8880 | MW Hour : | 19:30 | Available Max Generation : |  | 11640 | MW
E.P. Demand (at gen end) : |  | 8880 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 8200 | MW
Maximum Generation : |  | 8880 | MW Hour : | 19:30 | Reserve(Generation end) |  | 3440 | MW
Total Gen. (MKWH) : |  | 170.6608 | System Load Factor : | 80.08% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -640 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-02-08
Actual : | 94.79 | Ft.(MSL) , | Rule curve : | 96.2 | Ft.( MSL )
Gas Consumed : | Total = | 973.87 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 81569408.392
|  | Coal : | 14084754 | Oil : | 208925942.53 | Total : | 304580104.922
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 2912.815 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 983.0136 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 879.4103 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 794.1466 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 717.9206 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 579.3176 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 333.5833 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 149.4143 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 446.7523 |  |  | 0 | 0%
Total | 0 |  | 7796.3737 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 09) Ashuganj #4 & 5
| Nil |  |  | 2) Khulna ST 110 MW |  | 10) Haripur-412 MW CCPP ST
|  |  |  | 3) Ghorasal Unit-1,3,4,5 |  | 11) Siddhirganj Peaking 210 MW
|  |  |  | 4) Tongi GT |  | 12) Sikalbaha 225 MW
5) Haripur GT-1,2
6) Siddhirganj ST 210 MW
7) Bhagabari 71 MW,100 MW
8) Sikalbaha 150MW Peaking
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Aminbazar-Kaliakoir 230 kV Ckt-2 was under shut down from 09:24 to 17:24 for A/M.
b) Kaliakoir-Summit 300 MW 230 kV Ckt was under shut down from 09:23 to 17:25 for A/M.
c) Tongi-Kaliakoir 230 kV Ckt was switched on at 09:20.
d) Haripur 230/132 kV transformer T03 was under shut down from 10:26 to 15:29 for A/M.
e) Haripur-Sonargaon 132 kV Ckt-1 & 2 were under shut down from 09:33 to 15:54 for A/M.
f) Khulshi-Baraulia 132 kV Ckt-2 was under shut down from 09:05 to 11:56 for A/M.
g) Tangail 132/33 kV T3 transformer was under shut down from 09:45 to 13:06 for C/M.
h) Comilla (N)-Shahjibazar 230 kV Ckt-2 was under shut down from 10:30 to 17:32 for A/M.
i) Comilla (N) 132/33 kV T4 transformer was under shut down from 10:47 to 14:08 for C/M.
j) Sikalbaha S/S (old)-Sikalbaha 55 MW (Rental) 132 kV Ckt was under shut down from 08:55 to 10:36 for red hot
maintenance.
k) Khulshi-AK Steel 132 kV Ckt was under shut down from 12:00 to 14:45 for A/M.
l) Ashuganj Unit-3 was synchronized at 11:18.
m) Ashuganj Unit-4 was shut down at 13:14 due to low gas pressure.
n) Naogaon-Bogra 132 kV Ckt-1 was under shut down from 13:28 to 18:35 for D/W.
o) Aminbazar-Hasnabad 230 kV Ckt-1 was shut down from 13:56 to 17:22 for D/W.
p) Tangail-Kaliakoir 132 kV Ckt-1 was under shut down from 13:47 to 14:21 for C/M.
q) Chandraghona-Rangamati 132 kV Ckt-2 was under shut down from 13:59 to 17:20 for D/W.
r) Hasnabad-Keraniganj 230 kV was switched on at 17:41.
s) Shahjibazar 330 MW GT-1 was switched on at 16:53.
t) Raozan Unit-2 was synchronized at 14:31.
u) Cox's Bazar 132/33 kV T2 transformer was shut down at 05:45 (08/02/2019) for A/M.
v) Natore 33 kV bus of 132/33 kV T1 & T2 transformer was shut down at 07:04 (08/02/2019) for development work. |  |  |  | About 50 MW Power interruption occurred under Natore S/S area from
from 07:04 (08/02/2019) to till now.
w) G.K 33 kV Bus was shut down at 07:12 (08/02/2019) for C/M. |  |  |  | About 20 MW Power interruption occurred under G.K S/S area from
from 07:12 (08/02/2019) to till now.
x) Barisal-Bhandaria 132 kV Ckt was shut down at 07:12 (08/02/2019) for C/M.
y) Noapara 33 kV Bus was shut down at 07:31 (08/02/2019) for D/W. |  |  |  | About 15 MW Power interruption occurred under Noapara S/S area from
z) Comilla (N) -Feni 132 kV CKt-1 was shut down at 07:11 (08/02/2019) for D/W. |  |  |  | from 07:31(08/02/2019) to till now.
aa) Shyampur (N)-Shyampur 132 kV Ckt-1 & 2 were under shut down from 07:42 to 11:20 (08/02/2019) for D/W. |  |  |  | About 120 MW Power interruption occurred under Shyampur S/S area from
from 07:42 to 11:20 (08/02/2019).
ab) Bogura-Naogaon 132 kV Ckt-1 was shut down at 07:18 (08/02/2019) for D/W. |  |  |  | About 60 MW Power interruption occurred under Naogaon S/S area from
from 07:18 (08/02/2019) to till now.
ac) Comilla (S)-Surjamoninagar 132 kV Ckt-1 & 2 were shut down at 07:03 & 07:05 (08/02/2019) respectively for D/W. |  |  |  | About 40 MW Power interruption occurred under Comilla (S) S/S area from
from 07:03 (08/02/2019) to till now.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-02-07 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 35 | 710000 | #1 Under maint.
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | On test
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7929709 | FGMO
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 290 | 7275520 | ST under maint.
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 145200 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 328 | 7645000 | Frequency control
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 400 | 9015625 | Frequency control
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 100 | 418560
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Reserve
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 100 | 783096
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 48 | 695067 | Engine problem
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 10 | 73527 | Low demand
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 416448
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 50 | 443520 | Low demand
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 0 | 0 | Gas shortage
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 102 | 966672
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 40 | 764016 | Engine problem
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 988560
25 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 37 | 624321 | Engine problem
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 301000
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 48 | 813120 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 58 | 1237760 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 811800
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 25 | 658800
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 51 | 787704
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
34 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 180 | 757750 | Low demand
35 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
38 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 84 | 388800 | Low demand
| Dhaka area Total |  |  |  | 5798 | 2447 | 44651575
39 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 100 | 800000 | Gas shortage
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 412380
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 122715
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 46 | 745920
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 798616 | Low water lavel
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 1471566 | Under maint.
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 511680
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 56 | 152920
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 68 | 212088
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 70 | 939840 | Engine problem
| Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 74 | 1253760 | Engine problem
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 494928
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 32 | 589440
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 100 | 1233600
| Chattogram area Total |  |  |  | 1681 | 711 | 9739453
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 889740 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 1009290 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Under maint.
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 186 | 4502000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 305 | 7313900 | Gas shortage
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 264 | 6744000 | FGMO
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 10 | 288360 | Engine problem
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 5 | 156480 | Gas shortage
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 21 | 672092 | Engine problem
| Midland 150MW |  | IPP | 23*7.015 | 150 | 133 | 1973818
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 1524477
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 7528 | Reserve
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2361890
| Chandpur Desh 200MW |  | IPP | 0 | 200 | 85 | 1588800 | Low demand
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 499212
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 208800
** | Tripura |  | Imported power | 0 | 160 | 124 | 2329160
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 25 | 496800 | Engine problem
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 34 | 127176 | Low demand
68 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 494670
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1521 | 33508920
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 75 | 1853180 | Gas shortage
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 500400
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 87 | 1472640 | Engine problem
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 12200
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 200 | 1948800
| United Jamalpur PPL |  | IPP | 115 MW | 0 | 67 | 1094400 | On test
| Mymensingh Area Total |  |  |  | 522 | 451 | 6881620
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 30 | 690000 | GT-1 under maint.
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1348120
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 130 | 3331946 | High voltage
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 301 | 4639000 | FGMO
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 861600
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 49 | 1066000
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 226896
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 60 | 1485984 | FGMO
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 84 | 1396800
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 46 | 1005480
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 112 | 2402950 | FGMO
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 19 | 145000
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 23 | 525280 | Engine problem
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 16 | 395760 | Engine problem
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 305 | 6767250 | FGMO
| Bibiyana-3 285MW |  | PDB | 285 MW | 0 | 0 | 3879800 | On test
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 200700
| Sylhet Area Total |  |  |  | 1549 | 1309 | 30368566
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 702 | 14001455
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 667200 | Engine problem
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 44 | 197760
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 60 | 245248
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 300 | 7900416 | Gas shortage
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 720000
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
| Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 105 | 1579680
| Khulna Area Total |  |  |  | 2209 | 1350 | 25311759
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 48 | 248640 | High voltage
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 26 | 447300 | Engine problem
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 187 | 4515402
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 95 | 1798475
| Barisal Area Total |  |  |  | 462 | 356 | 7009817
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 43 | 155439
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 0 | 6706
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 40 | 661610 | Engine problem
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 520599
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 15 | 68241
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 141 | 186 | 4590818 | FGMO
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282 | 282 | 0 | 0 | Gas shortage
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 31 | 195408
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 504000
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 16 | 377712 | Engine problem
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 213426
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 52 | 790080
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 102 | 1042268
| Paramount Baghabari |  | IPP | 200 MW | 0 | 0 | 159900 | On test
| Confidence CPBL-2 |  | IPP | 113 MW | 0 | 0 | 0 | On test
| Rajshahi Area Total |  |  |  | 1546 | 568 | 9286207
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 149 | 3648900
122 | Rangpur GT |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
123 | Saidpur GT |  | PDB | 1*20 | 20 | 18 | 254000
| Rangpur Area Total |  |  |  | 484 | 167 | 3902900
| Total |  |  |  | 17142 | 8880 | 170660817
| Eastern Grid Total |  |  |  | 12441 | 6439 | 125150134
| Western Grid Total |  |  |  | 4701 | 2441 | 45510683
| National Grid Total |  |  |  | 17142 | 8880 | 170660817
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2019-02-07 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 5637 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2793 | MW
i) Dhaka area |  |  | 2948 | MW | i) Khulna area |  |  | 1022 | MW
ii) Chittagong area |  |  | 898 | MW | ii) Rajshahi area |  |  | 958 | MW
iii) Comilla area |  |  | 742 | MW | iii) Barisal area |  |  | 198 | MW
iv) Mymensingh area |  |  | 718 | MW | iv) Rangpur area |  |  | 615 | MW
v) Sylhet area |  |  | 331 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 8430 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 90 | 1600 | Netrokona | 90 | 1830 | Central s/s | 60 | 1900
Munsiganj | 66 | 2000 | Jamalpur | 103 | 1900 | Noapara | 79 | 1830
Sonargaon | 40 | 1830 | Sherpur | 86 | 800 | Jessore | 112 | 1900
Shyampur | 160 | 1200 | Srimongal | 22 | 1930 | Jhenida | 78 | 1830
Bhulta | 145 | 1000 | Shahjibazar | 86 | 1830 | Bottail | 90 | 1830
Madanganj | 53 | 1600 | Fenchuganj | 28 | 1930 | G.K Project | 36 | 1830
Shitalakhya | 95 | 1600 | Kulawara | 27 | 1830 | Faridpur | 120 | 1930
Rahim steel | 8 | 1700 | Sylhet | 98 | 1900 | Madaripur | 93 | 2100
Matuail | 84 | 1000 | Chatak | 20 | 1900 | Gopalganj | 58 | 1830
Ghorasal | 62 | 1900 | Sunamganj | 25 | 1930 | Bagerhat | 66 | 1930
Narsingdi | 103 | 1900 | Biani Bazar | 28 | 1900 | Mongla | 36 | 100
Haripur (SBU) | 90 | 2000 | Comilla (S) | 126 | 1830 | Satkhira | 69 | 1930
Ullon | 56 | 1900 | Comilla(N) | 89 | 1830 | Gallamari | 34 | 1300
Hasnabad | 151 | 1900 | Chandpur | 81 | 1900 | Magura | 41 | 1900
Magbazar | 100 | 1300 | Feni | 90 | 1800 | Chuadanga | 56 | 1830
Maniknagar | 80 | 1300 | Chowmuhani | 126 | 1830 | Barisal | 78 | 1830
Bangabhaban | 18 | 1300 | Ashuganj | 41 | 1830 | Patuakhali | 64 | 2100
Narinda | 80 | 1200 | Daudkandi | 90 | 1930 | Bhandaria | 38 | 1900
Dhanmondi | 77 | 1400 | B.Baria | 88 | 1830 | Ishurdi | 38 | 2000
Lalbag | 55 | 1830 | Ramganj | 24 | 1800 | Ruppur Paromanobik | 1 | 100
Madartek | 34 | 2000 | Madunaghat | 43 | 1800 | Natore | 94 | 1930
Mirpur | 78 | 1800 | Hathazari | 67 | 1930 | Bogra | 176 | 2000
Kalyanpur | 60 | 1800 | Khulshi | 136 | 1000 | Noagaon | 110 | 2000
Gulshan | 86 | 1300 | Halishahar | 97 | 1900 | Rajshahi | 100 | 2000
Uttara | 32 | 1300 | Baraulia | 128 | 1900 | C.Nawabganj | 60 | 1200
Uttara(New) | 6 | 1400 | Sikalbaha | 26 | 1830 | Amnura | 32 | 1830
Kamrangirchar | 58 | 1830 | Dohazari | 68 | 1830 | Pabna | 83 | 1900
Savar | 100 | 1830 | Cox'sbazar | 71 | 1930 | Shahjadpur | 72 | 2000
Bhasantec | 100 | 1830 | Chandraghona | 23 | 1900 | Serajganj | 76 | 1100
Agargaon | 39 | 1800 | Kaptai | 0 | 0 | Niyamatpur | 92 | 2000
Satmosjid | 68 | 1300 | A. Khaer Stl. | 0 | 0 | Joypurhat | 48 | 2000
Tongi | 107 | 1500 | Bakulia | 74 | 1800 | Mohastangor | 0 | 0
Kabirpur | 152 | 1500 | Julda | 19 | 900 | Rangpur | 106 | 1830
Basundhara | 82 | 1800 | TK chemical | 6 | 1100 | Lalmonirhat | 78 | 1930
Manikganj | 68 | 1830 | Modern Steel | 16 | 1100 | Saidpur | 94 | 1830
Joydevpur | 160 | 2000 | Shahmirpur | 21 | 1800 | Purbasadipur | 95 | 1100
New Tongi | 90 | 1200 | Khagrachhari | 16 | 1830 | Thakurgaon | 66 | 1900
Kodda | 193 | 1000 | Matarbari | 20 | 1830 | Palashbari | 94 | 2000
Dhamrai | 40 | 1830 | Baroiar Hat | 16 | 1800 | Barapukuria | 50 | 800
Valuka | 52 | 900 | Rangamati | 8 | 1800 | Panchagar | 38 | 1830
Tangail | 153 | 1800 | Abul Khair 230 | 151 | 1800 | Joldhaka | 16 | 1830
Mymensing | 183 | 1830 | BSRM | 107 | 1800
Kishorganj | 80 | 1830 | Goalpara | 32 | 1900
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-02-07
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 407 | 3:00 | 399 | 11:00 | Kaliakoir | 394 | 3:00 | 381 | 12:00
Bheramara | 405 | 3:00 | 393 | 10:00 | Bhulta | 405 | 1:00 | 395 | 12:00
Ashuganj(N) | 407 | 24:00 | 395 | 12:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 230 | 19:30 | 212 | 12:00
Ishurdi | 237 | 22:00 | 226 | 12:00 | Megnaghat | 234 | 18:30 | 228 | 10:00
Ashuganj | 244 | 14:00 | 235 | 11:00 | Fenchuganj | 242 | 4:00 | 238 | 9:00
Serajganj | 228 | 24:00 | 216 | 8:00 | Siddhirganj | 232 | 2:00 | 225 | 11:00
Baghabari | 230 | 1:00 | 220 | 9:00 | Maniknagar | 230 | 5:00 | 223 | 15:00
Barapukuria | 231 | 1:00 | 221 | 18:30 | Old Airport | 230 | 4:00 | 220 | 11:00
Bogra | 222 | 24:00 | 206 | 8:00 | Barisal | 240 | 15:00 | 232 | 3:00
Khulna South | 239 | 14:00 | 224 | 8:00 | AKSML | 228 | 20:00 | 211 | 15:00
Rampura | 230 | 5:00 | 223 | 11:00 | BSRM | 230 | 19:30 | 213 | 11:00
Haripur | 230 | 18:00 | 224 | 11:00 | Bibiyana | 242 | 4:00 | 234 | 13:00
Hasnabad | 230 | 1:00 | 220 | 12:00 | Bhulta | 231 | 2:00 | 225 | 11:00
Aminbazar | 231 | 3:00 | 220 | 11:00 | Ashuganj (S) | 241 | 24:00 | 234 | 12:00
Tongi | 230 | 19:30 | 221 | 9:00 | Kaliakoir | 235 | 20:00 | 227 | 11:00
Comilla (N) | 241 | 24:00 | 230 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 134 | 1800 | 129 | 1100 | Madanhat | 139 | 2100 | 126 | 1100
Munsiganj | 139 | 1830 | 132 | 300 | Hathazari | 137 | 1900 | 127 | 1100
Megnaghat | 142 | 1300 | 131 | 700 | Khulshi | 135 | 1900 | 134 | 1000
Shyampur | 132 | 300 | 124 | 1100 | Halishahar | 139 | 2000 | 128 | 1100
Bhulta | 130 | 400 | 123 | 1100 | Baraulia | 136 | 1800 | 125 | 1100
Madanganj | 136 | 200 | 130 | 1100 | Sikalbaha | 137 | 1830 | 125 | 1100
Shitalakhya | 141 | 1800 | 129 | 1200 | Dohazari | 139 | 2000 | 125 | 1100
Rahim steal | 135 | 1800 | 130 | 1100 | Cox'sbazar | 132 | 1800 | 120 | 1100
Matuail | 133 | 300 | 128 | 1100 | Chandraghona | 137 | 1800 | 126 | 1100
Ghorasal | 138 | 100 | 138 | 200 | Kaptai | 0 | 0 | 0 | 0
Narsinghdi | 137 | 100 | 133 | 1830 | A. Khaer Stl. | 134 | 1830 | 127 | 1300
Haripur (SBU) | 135 | 1900 | 129 | 1200 | Bakulia | 136 | 1930 | 123 | 1100
Ullon | 132 | 100 | 127 | 1000 | Julda | 137 | 1900 | 126 | 1100
Hasnabad | 136 | 400 | 128 | 1100 | TK Chemical | 140 | 1900 | 126 | 1100
Magbazar | 133 | 200 | 127 | 1100 | Modern Steel | 137 | 1930 | 121 | 1100
Maniknagar | 131 | 300 | 130 | 1000 | Shahmirpur | 137 | 1900 | 126 | 1100
Bangabhaban | 135 | 300 | 128 | 1100 | Khagrachhari | 136 | 1900 | 125 | 1100
Narinda | 133 | 400 | 126 | 1200 | Matarbari | 132 | 1830 | 118 | 1200
Dhanmondi | 132 | 100 | 127 | 1000 | Baroiar Hat | 136 | 1800 | 133 | 1000
Lalbag | 135 | 300 | 128 | 1100 | Rangamati | 136 | 1930 | 124 | 1100
Madartek | 133 | 400 | 126 | 1200 | Goalpara | 138 | 1500 | 127 | 700
Mirpur | 136 | 700 | 129 | 1200 | Central s/s | 138 | 1500 | 127 | 700
Kalyanpur | 137 | 200 | 128 | 1200 | Noapara | 135 | 1500 | 124 | 1200
Gulshan | 131 | 300 | 126 | 1100 | Jessore | 134 | 1500 | 120 | 800
Uttara | 133 | 800 | 124 | 1200 | Jhenida | 132 | 1500 | 120 | 800
Uttara New | 132 | 200 | 125 | 1100 | Bottail | 139 | 200 | 132 | 800
Kamrangirchar | 134 | 400 | 126 | 1100 | G.K.Project | 142 | 100 | 137 | 1200
Savar | 132 | 700 | 125 | 1100 | Faridpur | 135 | 200 | 132 | 800
Bhasantec | 134 | 300 | 126 | 1100 | Madaripur | 135 | 100 | 132 | 700
Agargaon | 135 | 400 | 126 | 1200 | Gopalganj | 140 | 2100 | 131 | 1200
Satmosjid | 134 | 300 | 126 | 1200 | Bagerhat | 136 | 2200 | 126 | 1200
Tongi | 136 | 1400 | 131 | 1100 | Mongla | 135 | 2100 | 124 | 1100
Kabirpur | 135 | 100 | 129 | 1200 | Satkhira | 136 | 1400 | 126 | 700
Basundhara | 128 | 400 | 123 | 1300 | Gallamari | 138 | 1500 | 127 | 1200
Manikganj | 139 | 200 | 134 | 800 | Magura | 136 | 300 | 125 | 700
Joydevpur | 141 | 1800 | 136 | 1100 | Chuadanga | 134 | 200 | 121 | 800
New Tongi | 136 | 400 | 130 | 1100 | Barisal | 139 | 1400 | 135 | 1200
Kodda | 138 | 1830 | 134 | 2100 | Patuakhali | 140 | 1700 | 135 | 200
Dhamrai | 135 | 300 | 129 | 1500 | Bhandaria | 136 | 400 | 127 | 700
Valuka | 129 | 400 | 120 | 1000 | Ishurdi | 139 | 1500 | 134 | 1100
Tangail | 135 | 200 | 125 | 700 | Ruppur Paromanobik | 141 | 500 | 135 | 1100
Mymensing | 134 | 2300 | 122 | 800 | Natore | 138 | 1400 | 128 | 800
Kishorganj | 134 | 200 | 128 | 700 | Bogra | 134 | 100 | 120 | 800
Netrokona | 133 | 2300 | 121 | 700 | Noagaon | 129 | 100 | 115 | 1200
Jamalpur | 137 | 1300 | 121 | 700 | Rajshahi | 136 | 1400 | 127 | 700
Sherpur | 136 | 1300 | 118 | 700 | C.Nawabganj | 136 | 1800 | 125 | 700
Srimongal | 140 | 100 | 139 | 900 | Amnura | 139 | 1800 | 128 | 200
Shahjibazar | 140 | 100 | 138 | 400 | Pabna | 135 | 100 | 126 | 800
Fenchuganj | 139 | 400 | 136 | 900 | Shahjadpur | 140 | 100 | 131 | 1200
Khulawara | 137 | 100 | 136 | 1800 | Serajganj | 136 | 300 | 124 | 1200
Sylhet | 136 | 100 | 134 | 1800 | Niyamatpur | 127 | 1400 | 110 | 1930
Chatak | 137 | 200 | 134 | 1800 | Joypurhat | 130 | 200 | 112 | 800
Sunamganj | 136 | 200 | 133 | 1900 | Mohastangor | 133 | 400 | 118 | 800
Biani Bazar | 137 | 100 | 134 | 1200 | Rangpur | 131 | 500 | 114 | 800
Comilla(s) | 129 | 100 | 124 | 1800 | Lalmonirhat | 124 | 600 | 107 | 1900
Comilla(n) | 144 | 2100 | 138 | 700 | Saidpur | 126 | 500 | 109 | 1830
Chandpur | 141 | 1500 | 138 | 1100 | Purbasadipur | 127 | 100 | 110 | 900
Feni | 135 | 1800 | 130 | 1000 | Thakurgaon | 126 | 600 | 102 | 1900
Chowmuhani | 133 | 900 | 132 | 2100 | Palashbari | 131 | 500 | 114 | 1200
Ashuganj | 140 | 700 | 139 | 1200 | Barapukuria | 131 | 500 | 121 | 1900
Daudkandi | 140 | 1400 | 132 | 1000 | Panchagar | 121 | 100 | 98 | 1830
B.Baria | 139 | 2300 | 137 | 1100 | Joldhaka | 129 | 400 | 109 | 1830

## L-Curve
Date | 2019-02-07
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 460 | 5045 | 1736 | 6781 |  |  |  | QF-LDC-12
0:30 | 520 | 4824.5 | 1581 | 6405.5 | Date: | 2019-02-07
1:00 | 580 | 4604 | 1426 | 6030
1:30 | 570 | 4531 | 1369.5 | 5900.5
2:00 | 560 | 4458 | 1313 | 5771
2:30 | 520 | 4372 | 1307 | 5679 | [5 empty] | Gen. at Eve. Peak | 8880 | 8880 MW (19:30 )
3:00 | 480 | 4286 | 1301 | 5587 | [6 empty] | 19:30
3:30 | 460 | 4220.5 | 1292 | 5512.5 | [5 empty] | Gen. at Day Peak | 7482.9 | 7482.9 MW (12:00 )
4:00 | 440 | 4155 | 1283 | 5438 | [6 empty] | 12:00
4:30 | 420 | 4165 | 1255.5 | 5420.5 | [5 empty] | Highest Generation | 8880
5:00 | 400 | 4175 | 1228 | 5403 | [6 empty] | 19:30
5:30 | 390 | 4233 | 1417 | 5650
6:00 | 380 | 4291 | 1606 | 5897
6:30 | 495 | 4544.15 | 1672.5 | 6216.65
7:00 | 610 | 4797.3 | 1739 | 6536.3
7:30 | 600 | 4934.4 | 1837.5 | 6771.9
8:00 | 590 | 5071.5 | 1936 | 7007.5
8:30 | 490 | 5171 | 1992.5 | 7163.5
9:00 | 390 | 5270.5 | 2049 | 7319.5
9:30 | 375 | 5315.75 | 2004.5 | 7320.25
10:00 | 360 | 5361 | 1960 | 7321
10:30 | 345 | 5374.2 | 1966.5 | 7340.7
11:00 | 330 | 5387.4 | 1973 | 7360.4
11:30 | 345 | 5418.15 | 2003.5 | 7421.65
12:00 | 360 | 5448.9 | 2034 | 7482.9
12:30 | 430 | 5470.15 | 1979.5 | 7449.65
13:00 | 500 | 5491.4 | 1925 | 7416.4
13:30 | 370 | 5304.2 | 1911 | 7215.2
14:00 | 240 | 5117 | 1897 | 7014
14:30 | 220 | 5153.35 | 1889 | 7042.35
15:00 | 200 | 5189.7 | 1881 | 7070.7
15:30 | 220 | 5159.55 | 1825 | 6984.55
16:00 | 240 | 5129.4 | 1769 | 6898.4
16:30 | 225 | 5076.1 | 1800 | 6876.1
17:00 | 210 | 5022.8 | 1831 | 6853.8
17:30 | 245 | 5224.4 | 2048.5 | 7272.9
18:00 | 280 | 5426 | 2266 | 7692
18:30 | 415 | 5900 | 2366 | 8266
19:00 | 550 | 6374 | 2466 | 8840
19:30 | 610 | 6439 | 2441 | 8880
20:00 | 640 | 6335 | 2419 | 8754 |  |  |  | Executive Engineer
20:30 | 575 | 6272 | 2425 | 8697 |  |  |  | Network Operation Division
21:00 | 510 | 6209 | 2431 | 8640
21:30 | 465 | 5940 | 2337 | 8277
22:00 | 420 | 5671 | 2243 | 7914 |  |  |  |  | Page 6 of 7
22:30 | 400 | 5500.5 | 2099 | 7599.5
23:00 | 380 | 5330 | 1955 | 7285
23:30 | 420 | 5187.5 | 1845.5 | 7033
24:00 | 460 | 5045 | 1736 | 6781
8880 MW (19:30 )
7482.9 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-02-07 |  | Energy | 170660817
[10 empty] | 2019-02-07 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3284 | 641 | 1695 | 846 | 149 | 70 | 0 | 0 | 96
0:30 | 3439.5 | 502 | 1685.5 | 465 | 149 | 70.5 | 0 | 0 | 94 | Date: | 2019-02-07
1:00 | 3595 | 363 | 1676 | 84 | 149 | 71 | 0 | 0 | 92
1:30 | 3562.5 | 363 | 1604.5 | 59.5 | 149 | 71 | 0 | 0 | 91 | [7 empty] | Total Energy | 170.6608 | Total Energy Gen 170.661 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 170.661 MKWHr
2:00 | 3530 | 363 | 1533 | 35 | 149 | 71 | 0 | 0 | 90 | [7 empty] | Energy not Served | 0
2:30 | 3527 | 363 | 1446.5 | 35 | 149 | 70.5 | 0 | 0 | 88 | [7 empty] | Energy Requirement | 170.6608
3:00 | 3524 | 363 | 1360 | 35 | 149 | 70 | 0 | 0 | 86
3:30 | 3539.5 | 363 | 1271 | 35 | 149 | 70 | 0 | 0 | 85 | [6 empty] | Shortage
4:00 | 3555 | 363 | 1182 | 35 | 149 | 70 | 0 | 0 | 84
4:30 | 3546 | 363.5 | 1175.5 | 35 | 149 | 69.5 | 0 | 0 | 82
5:00 | 3537 | 364 | 1169 | 35 | 149 | 69 | 0 | 0 | 80
5:30 | 3571.5 | 485.5 | 1213.5 | 79.5 | 149 | 69 | 0 | 0 | 82
6:00 | 3606 | 607 | 1258 | 124 | 149 | 69 | 0 | 0 | 84
6:30 | 3633.5 | 606.5 | 1379 | 292.5 | 149 | 69.5 | 0 | 0 | 86 |  |  |  |  | Coal
7:00 | 3661 | 606 | 1500 | 461 | 149 | 70 | 0 | 0 | 88
7:30 | 3615.5 | 606.5 | 1514.5 | 687 | 148.5 | 70 | 35 | 0 | 91 |  |  |  | Oil |  |  |  | ,
8:00 | 3570 | 607 | 1529 | 913 | 148 | 70 | 70 | 0 | 94
8:30 | 3521 | 607 | 1606.5 | 1019 | 148.5 | 71 | 87 | 0 | 94
9:00 | 3472 | 607 | 1684 | 1125 | 149 | 72 | 104 | 0 | 94
9:30 | 3437.5 | 607 | 1694.5 | 1172.5 | 149 | 64 | 86 | 0 | 96
10:00 | 3403 | 607 | 1705 | 1220 | 149 | 56 | 68 | 0 | 98
10:30 | 3363 | 607 | 1722.5 | 1288 | 149 | 28 | 68 | 0 | 98
11:00 | 3323 | 607 | 1740 | 1356 | 149 | 0 | 68 | 0 | 98
11:30 | 3308.5 | 605 | 1744 | 1412 | 149 | 15 | 67.5 | 0 | 101
12:00 | 3294 | 603 | 1748 | 1468 | 149 | 30 | 67 | 0 | 104
12:30 | 3241.5 | 603 | 1677 | 1541 | 149 | 47.5 | 67 | 0 | 104
13:00 | 3189 | 603 | 1606 | 1614 | 149 | 65 | 67 | 0 | 104
13:30 | 3189 | 603 | 1606 | 1614 | 149 | 65 | 67 | 0 | 104
14:00 | 3189 | 603 | 1606 | 1614 | 149 | 65 | 67 | 0 | 104
14:30 | 3099.5 | 603 | 1506 | 1632.5 | 149 | 67.5 | 67 | 0 | 103
15:00 | 3010 | 603 | 1406 | 1651 | 149 | 70 | 67 | 0 | 102
15:30 | 3018 | 602.5 | 1435 | 1526 | 149 | 70 | 79 | 0 | 95
16:00 | 3026 | 602 | 1464 | 1401 | 149 | 70 | 91 | 0 | 88
16:30 | 3011 | 602 | 1471 | 1363 | 149 | 70 | 115.5 | 0 | 90
17:00 | 2996 | 602 | 1478 | 1325 | 149 | 70 | 140 | 0 | 92
17:30 | 3048 | 652.5 | 1457.5 | 1502.5 | 149 | 70 | 284.5 | 0 | 108
18:00 | 3100 | 703 | 1437 | 1680 | 149 | 70 | 429 | 0 | 124
18:30 | 3191 | 702.5 | 1587 | 1998 | 149 | 70 | 444.5 | 0 | 124
19:00 | 3282 | 702 | 1737 | 2316 | 149 | 70 | 460 | 0 | 124
19:30 | 3290 | 702 | 1743 | 2365 | 149 | 70 | 437 | 0 | 124
20:00 | 3304 | 703 | 1714 | 2291 | 149 | 70 | 397 | 0 | 126
20:30 | 3327.5 | 700.5 | 1729.5 | 2218.5 | 149 | 70 | 377 | 0 | 125
21:00 | 3351 | 698 | 1745 | 2146 | 149 | 70 | 357 | 0 | 124
21:30 | 3327.5 | 697.5 | 1734 | 1916 | 149 | 70 | 264 | 0 | 119
22:00 | 3304 | 697 | 1723 | 1686 | 149 | 70 | 171 | 0 | 114
22:30 | 3319.5 | 697.5 | 1726.5 | 1442.5 | 149 | 70 | 85.5 | 0 | 109
23:00 | 3335 | 698 | 1730 | 1199 | 149 | 70 | 0 | 0 | 104
23:30 | 3309.5 | 669.5 | 1712.5 | 1022.5 | 149 | 70 | 0 | 0 | 100 | Max Temp. in Dhaka |  | 29.5° C
24:00 | 3284 | 641 | 1695 | 846 | 149 | 70 | 0 | 0 | 96
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 170.661 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 170.661 MKWHr
Note on W13: Author:

## Generation
2019-02-07
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 41 | 41 | 40 | 40 | 39 | 39 | 40 | 40 | 42 | 26 | 0 | 0 | 35 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 798616
2 | Kaptai Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 664000
3 | Chattogram ST-1 (Raozan)
4 | Chittgong ST-2 (Raozan) | [14 empty] | 10 | 40 | 70 | 90 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 800000
5 | Raozan 25 MW (RPCL) | [7 empty] | 9 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 412380
| Teknaf Solartech 20MW | [5 empty] | 0 | 1.2 | 6 | 11.5 | 13.5 | 17.6 | 18 | 17.5 | 15.3 | 11.5 | 6.6 | 1.7 | 0 |  | 0 | 0 | 0 |  |  |  |  | 122715
6 | Sikalbaha 225MW (Gas) | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 51 | 0 | 0 | [16 empty] | 1471566
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | [17 empty] | 68 |  | 68 | 68 | 68 | 34 | 0 |  |  | 212088
12 | Hathazari peaking | [17 empty] | 56 |  | 51 | 56 | 31 | 24 | 0 |  |  | 152920
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | [17 empty] | 4 |  | 8 | 0 | 0 |  |  |  |  | 7528
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2
17 | Siddhirganj CCPP-335 MW
18 | Summit Gazipur -2 | [15 empty] | 0 | 2 | 40 |  | 168 | 180 | 198 | 188 | 124 | 14 | 0 | 757750
19 | Ashuganj 195MW Modular | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal ST: Unit-1,2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 710000
21 | Ghorasal GT: Unit-3
22 | Ghorasal GT: Unit-4
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 380 | 380 | 380 | 380 | 380 | 380 | 300 | 300 | 300 | 296 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7929709
26
28 | Ashuganj ST: Unit- 3 | [11 empty] | 20 | 50 | 70 | 70 | 70 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 889740
29 | Ashuganj ST: Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 70 | 60 | 60 | 0 | 0 | [11 empty] | 1009290
30 | Ashuganj ST: Unit- 5
32 | Ashuganj Engines TSK | 10 | 10 | 10 | 10 | 10 | 10 | 33 | 33 | 36 | 36 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 288360
33 | Ashuganj CCPP 225 MW | 185 | 185 | 185 | 185 | 185 | 191 | 186 | 197 | 193 | 162 | 154 | 125 | 128 | 184 | 210 | 218 | 217 | 204 |  | 186 | 186 | 188 | 196 | 185 | 192 | 185 | 4502000
34 | Ashuganj CCPP(South) | 287 | 290 | 287 | 272 | 264 | 276 | 264 | 287 | 320 | 305 | 279 | 257 | 257 | 253 | 253 | 257 | 257 | 257 |  | 257 | 264 | 264 | 283 | 264 | 287 | 264 | 6744000
| Ashuganj CCPP(North) | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 360 | 360 | 300 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 7313900
35 | Ashuganj (Precision) 55MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 156480
36 | Chandpur CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 96 | 100 | 100 | 100 | 95 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 95 | 2361890
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 308 | 308 | 309 | 310 | 307 | 306 | 310 | 307 | 305 | 302 | 295 | 290 | 290 | 292 | 288 | 290 | 288 | 295 |  | 291 | 290 | 296 | 297 | 299 | 299 | 300 | 7275520
40 | Meghnaghat CCPP 450MW | 360 | 360 | 360 | 320 | 320 | 350 | 350 | 330 | 425 | 430 | 450 | 450 | 370 | 340 | 340 | 370 | 370 | 370 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 9015625
41 | Haripur Power CCPP 360MW | 331 | 331 | 332 | 311 | 309 | 308 | 292 | 291 | 300 | 362 | 361 | 357 | 341 | 266 | 271 | 313 | 308 | 278 |  | 328 | 328 | 328 | 330 | 330 | 330 | 330 | 7645000
42 | Mymensingh RPCL 210MW | 95 | 94 | 97 | 97 | 99 | 99 | 98 | 74 | 72 | 65 | 66 | 66 | 67 | 67 | 66 | 69 | 71 | 74 |  | 74 | 75 | 74 | 75 | 73 | 75 | 96 | 1853180
43 | Haripur NEPC 110MW | [9 empty] | 13 | 13 | 26 | 26 | 27 | 19 | 13 | 13 | 13 |  | 13 | 0 | 0 |  |  |  |  | 145200
44 | Fenchugonj CCPP-1 | 30 | 30 | 29 | 29 | 30 | 30 | 28 | 30 | 30 | 29 | 29 | 28 | 28 | 30 | 28 | 28 | 30 | 28 |  | 28 | 30 | 28 | 28 | 30 | 29 | 28 | 690000
45 | Fenchugonj CCPP-2 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 62 | 61 | 61 | 49 | 49 | 49 | 28 | 48 | 48 | 48 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1348120
46 | Shajibazar 330 MW | 100 | 82 | 100 | 160 | 200 | 207 | 212 | 208 | 189 | 188 | 245 | 244 | 243 | 150 | 147 | 147 | 161 | 195 |  | 296 | 301 | 301 | 307 | 305 | 312 | 300 | 4639000
47 | Shahjibazar GT: Unit- 8, 9 | 57 | 58 | 61 | 60 | 66 | 68 | 63 | 70 | 67 | 64 | 67 | 60 | 55 | 51 | 64 | 58 | 60 | 67 |  | 65 | 60 | 66 | 69 | 63 | 69 | 52 | 1485984
48 | Shahjibazar 86MW | 70 | 5 | 5 | 5 | 5 | 40 | 81 | 81 | 81 | 50 | 50 | 60 | 60 | 60 | 60 | 30 | 30 | 30 |  | 84 | 84 | 84 | 84 | 84 | 84 | 81 | 1396800
49 | Shahjibazar (EPL) 50MW | 49 | 49 | 49 | 5 | 5 | 5 | 49 | 49 | 49 | 49 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 47 | 48 | 48 | 48 | 1005480
50 | Sylhet GT 150 MW | 107 | 108 | 84 | 82 | 84 | 83 | 82 | 92 | 100 | 85 | 92 | 85 | 85 | 85 | 84 | 84 | 84 | 96 |  | 112 | 112 | 115 | 114 | 112 | 118 | 113 | 2402950
51 | Sylhet GT 20 MW | 20 | 0 | [17 empty] | 19 | 19 | 19 | 20 | 20 | 20 | 20 | 145000
52 | Sylhet (EPL) 50MW | 23 | 23 | 23 | 5 | 5 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 525280
53 | Sylhet (Desh) 10MW | 10 | 0 |  |  |  | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 200700
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 0 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 226896
55 | Fenchugonj (Barakatullah) 51MW | 51 | 51 | 7 | 5 | 5 | 11 | 48 | 50 | 48 | 48 | 48 | 49 | 50 | 10 | 11 | 11 | 11 | 11 |  | 53 | 53 | 53 | 53 | 50 | 53 | 53 | 861600
56 | Shahjahanulla 25 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 17 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 17 | 17 | 17 | 17 | 395760
57 | Summit Bibiana- 2 | 260 | 270 | 265 | 260 | 250 | 240 | 230 | 240 | 270 | 260 | 280 | 295 | 270 | 260 | 270 | 280 | 285 | 285 |  | 300 | 305 | 280 | 295 | 275 | 280 | 250 | 6767250
58 | Southern 55MW | [13 empty] | 0 | 17 | 17 | 17 | 50 |  | 55 | 55 | 55 | 55 | 17 | 0 |  | 301000
59 | Sikalbaha (Energis) | [5 empty] | 0 | 15 | 25 | 0 | 0 |  | 0 | 19 | 25 | 25 | 25 | 25 | 51 |  | 51 | 51 | 51 | 51 | 50 | 50 | 50 | 511680
60 | Barabkunda (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 22 | 22 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 494928
61 | Narshingdi (Doreen) | 19 | 19 | 19 | 19 | 19 | 0 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 416448
62 | Tangail (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 500400
63 | Tripura | 92 | 90 | 86 | 84 | 80 | 84 | 88 | 94 | 94 | 98 | 98 | 104 | 104 | 102 | 102 | 88 | 92 | 124 |  | 124 | 124 | 126 | 124 | 114 | 104 | 96 | 2329160
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 40 | 40 | 38 | 12 | 3 | 4 | 2 | 2 | 9 | 8 | 2 | 2 | 14 | 21 |  | 32 | 32 | 36 | 38 | 41 | 41 | 41 | 589440
65 | Feni (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 499212
66 | Feni, Mohipal (Doreen) | 11 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 208800
67 | Jangalia (Summit) 33MW | 25 | 0 |  |  |  | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 496800
68 | Summit Cumilla 25MW | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 15 | 21 | 15 | 15 | 16 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 494670
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 0 |  | 575000
70 | Summit Madhabdi | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 10 | 32 | 26 | 26 | 22 | 22 | 22 | 22 | 22 | 6 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 662760
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 28 | 33 | 33 | 33 | 33 | 33 | 33 | 811800
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 658800
73 | Ghorashal (Regent)
76 | Siddhirganj (Desh)
77 | Siddhirganj (Dutch Bangla) | [8 empty] | 0 | 5 | 40 | 50 | 50 | 50 | 50 | 7 | 7 | 8 |  | 45 | 50 | 24 | 0 |  |  | 0 | 443520
78 | Gazipur (RPCL) | [5 empty] | 0 | 2 | 38 | 51 | 51 | 51 | 51 | 19 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 25 | 25 | 787704
79 | Kodda 149MW
80 | Jamalpur 95MW |  |  |  |  | 0 | 4 | 28 | 80 | 80 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 |  | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 1472640
81 | Lakdhanvi 52 MW | [17 empty] | 5 |  | 27 | 34 | 32 | 32 | 0 | 0 |  | 127176
82 | Madanganj 102MW | [10 empty] | 25 | 48 | 50 | 64 | 64 | 64 | 64 | 64 |  | 80 | 100 | 80 | 80 | 15 | 0 |  | 783096
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW | 85 | 85 | 5 | 5 | 5 | 5 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 40 | 40 | 40 | 40 | 40 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1524477
85 | Keraniganj (Powerpac) 100MW | [12 empty] | 0 | 5 | 10 | 10 | 10 | 10 |  | 10 | 10 | 0 | 0 |  |  |  | 73527
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat (IEL) | [9 empty] | 1 | 7 | 8 | 50 | 40 | 16 | 16 | 16 | 18 |  | 80 | 100 | 80 | 40 | 0 |  |  | 418560
88 | Ghorashal 78MW (MAX)
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | [7 empty] | 7 | 54 | 66 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 |  | 70 | 70 | 70 | 70 | 70 | 0 |  | 939840
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 5 | 5 | 14 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 49 | 50 | 50 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1066000
93 | Ashuganj (Midland) 51MW | 45 | 45 | 7 | 7 | 7 | 7 | 22 | 45 | 45 | 45 | 45 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 672092
94 | Gagnagar (Orion) | [9 empty] | 5 | 7 | 7 | 32 | 64 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 48 | 7 | 7 | 966672
95 | Patenga 50MW | [6 empty] | 0 | 18 | 46 | 48 | 48 | 47 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 19 | 745920
96 | Chattogram ECPV 108 MW | [7 empty] | 30 | 52 | 53 | 78 | 93 | 93 | 87 | 87 | 92 | 95 | 100 |  | 100 | 100 | 100 | 100 | 60 | 0 |  | 1233600
97 | Katpotti 51 MW | [5 empty] | 0 | 6 | 47 | 46 | 46 | 47 | 47 | 47 | 47 | 47 | 47 | 18 | 18 |  | 40 | 40 | 47 | 46 | 46 | 46 | 6 | 764016
98 | Bosila 108MW |  |  |  |  | 0 | 5 | 41 | 49 | 49 | 49 | 48 | 48 | 46 | 45 | 45 | 45 | 45 | 45 |  | 47 | 48 | 48 | 48 | 48 | 48 | 48 | 813120
99 | Madanganj-55 MW | [5 empty] | 0 | 8 | 15 | 15 | 25 | 30 | 30 | 48 | 48 | 48 | 48 | 48 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 15 | 695067
100 | Northern 55 MW | [5 empty] | 0 | 18 | 36 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 18 | 624321
101 | Kushiara 163 MW CCPP GT | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 100 | 130 | 130 | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 100 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3331946
102 | Sarishabari (Solar) | [5 empty] | 0 | 0.1 | 0.5 | 1 | 1.5 | 1.8 | 1.9 | 1.9 | 1.7 | 1.2 | 0.8 | 0.1 | 0 |  | 0 | [6 empty] | 12200
103 | Banco Energy 54MW | 17 | 0 |  |  | 0 | 6 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 988560
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 30 | 70 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 125 |  | 192 | 200 | 200 | 160 | 100 | 100 | 50 | 1948800
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | [7 empty] | 4 | 17 | 15 | 15 | 15 | 15 | 15 | 28 | 28 | 14 | 28 |  | 72 | 84 | 82 | 43 | 28 | 0 |  | 388800
115 | Juldah 100 MW Unit-3 | [5 empty] | 0 | 30 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 |  | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 1253760
116 | Chandpur Desh 200MW | [5 empty] | 0 | 19 | 50 | 54 | 76 | 87 | 98 | 140 | 140 | 105 | 50 | 50 | 74 |  | 120 | 85 | 85 | 85 | 85 | 90 | 87 | 1588800
117 | Midland 150MW | [5 empty] | 0 | 6 | 35 | 50 | 80 | 100 | 115 | 145 | 150 | 150 | 87 | 83 | 85 |  | 121 | 133 | 133 | 138 | 141 | 141 | 141 | 1973818
118 | Bibiyana-3 285MW | 320 | 320 | 322 | 326 | 323 | 327 | 329 | 330 | 160 | 149 | 150 | 180 | 180 | 99 | 130 | 128 | 0 | 0 | [8 empty] | 3879800
| United Jamalpur PPL | 28 | 28 | 28 | 28 | 28 | 28 | 26 | 28 | 48 | 58 | 58 | 58 | 41 | 58 | 48 | 58 | 58 | 58 |  | 67 | 67 | 48 | 52 | 48 | 46 | 36 | 1094400
120 | Eastern Zone Total | 4604 | 4458 | 4286 | 4155 | 4175 | 4291 | 4797.3 | 5071.5 | 5270.5 | 5361 | 5387.4 | 5448.9 | 5491.4 | 5117 | 5189.7 | 5129.4 | 5020.8 | 5426 |  | 6374 | 6439 | 6335 | 6249 | 5671 | 5330 | 5045 | 125814134
121
122 | o
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | [6 empty] | 0 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 101 |  | 99 | 99 | 99 | 99 | 99 | 16 | 0 | 667200
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | [16 empty] | 6 | 38 |  | 40 | 44 | 44 | 44 | 38 | 0 |  | 197760
Khulna CCPP 225MW
129 | Labon Chora 105 MW |  |  |  |  | 0 | 21 | 70 | 105 | 105 | 72 | 70 | 90 | 105 | 105 | 105 | 53 | 35 | 35 |  | 105 | 105 | 105 | 105 | 105 | 105 | 0 | 1579680
130
131
132
133
| Summit Barisal 110 MW | [17 empty] | 20 |  | 48 | 48 | 48 | 48 | 48 | 16 | 0 | 248640
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 96 | 20 | 12 | 11 | 11 | 11 | 16 | 93 | 95 | 96 | 98 | 96 | 98 | 94 | 93 | 96 | 98 | 77 |  | 96 | 95 | 95 | 96 | 95 | 96 | 95 | 1798475
| Bhola CCPP 194MW | 196 | 193 | 190 | 177 | 192 | 195 | 193 | 195 | 191 | 189 | 190 | 189 | 159 | 171 | 193 | 190 | 186 | 186 |  | 186 | 187 | 187 | 188 | 186 | 188 | 190 | 4515402
140 | Bhola (Venture) 33MW | 19 | 17 | 18 | 17 | 16 | 17 | 19 | 17 | 17 | 10 | 10 | 18 | 19 | 20 | 16 | 17 | 17 | 23 |  | 26 | 26 | 19 | 27 | 25 | 24 | 23 | 447300
141 | Bangla Trak Noapara
142 | Noapara (KZA) 40MW | 16 | 0 |  |  | 0 | 8 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 32 | 40 | 720000
143 | Gopalganj Peaking | [14 empty] | 0 | 3 | 18 | 36 |  | 60 | 60 | 60 | 60 | 0 |  |  | 245248
144 | Bheramara GT-1,2,3
145
146 | Bheramara HVDC | 363 | 363 | 363 | 363 | 364 | 607 | 606 | 607 | 607 | 607 | 607 | 603 | 603 | 603 | 603 | 602 | 602 | 703 |  | 702 | 702 | 703 | 698 | 697 | 698 | 641 | 14001455
147 | Bheramara 360 MW | 340 | 340 | 340 | 340 | 300 | 350 | 350 | 300 | 340 | 340 | 340 | 360 | 260 | 260 | 260 | 260 | 260 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7900416
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 148 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3648900
153 | Baghabari GT 71MW
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | [16 empty] | 0 | 43 |  | 43 | 43 | 43 | 43 | 0 |  |  | 155439
157 | Sirajgonj Unit-1 225MW (Gas)
158 | Sirajgonj Unit-1 225MW (Oil)
Sirajgonj Unit-2 225MW (Gas)
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas) | 187 | 187 | 185 | 183 | 153 | 159 | 155 | 176 | 200 | 186 | 192 | 201 | 201 | 187 | 185 | 146 | 195 | 185 |  | 193 | 186 | 186 | 190 | 186 | 190 | 188 | 4590818
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas)
161 | Bera Peaking | [16 empty] | 10 | 0 |  | 0 | [6 empty] | 6706
162 | Bogra (GBB) | 22 | 22 | 22 | 21 | 21 | 22 | 22 | 18 | 18 | 18 | 18 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 504000
163 | Bogra (EPL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 14 | 13 | 14 | 15 | 15 | 13 |  | 14 | 16 | 15 | 17 | 17 | 16 | 16 | 377712
164 | Ullapara (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 213426
165 | Amnura 50MW |  |  |  |  | 0 | 16 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 12 | 12 | 12 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 12 | 661610
166 | Katakhali (Northern) | [5 empty] | 0 | 8 | 24 | 43 | 43 | 43 | 43 | 50 | 24 | 24 | 24 | 8 | 24 |  | 50 | 50 | 50 | 50 | 0 |  |  | 520599
167 | Katakhali Peaking | [15 empty] | 0 | 7 | 34 |  | 39 | 15 | 0 | 0 |  |  |  | 68241
168 | Santahar Peaking | [15 empty] | 20 | 31 | 31 |  | 31 | 31 | 31 | 31 | 31 | 0 |  | 195408
169 | Rajlanka 52 MW | 16 | 0 |  |  | 0 | 29 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 25 | 25 | 36 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 790080
170 | Chapainawabganj-100 MW | [6 empty] | 0 | 51 | 85 | 50 | 50 | 50 | 50 | 50 | 50 | 51 | 51 | 102 |  | 102 | 102 | 102 | 102 | 102 | 0 |  | 1042268
171 | Paramount Baghabari | [9 empty] | 18 | 25 | 30 | 28 | 32 | 28 | 0 | 0 | [9 empty] | 159900
172 | Confidence CPBL-2
173 | Rangpur GT
175 | Saidpur GT | [7 empty] | 19 | 19 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 18 | 18 | 18 | 19 | 0 |  |  | 254000
176
177
178
178 | Western Zone Total | 1426 | 1313 | 1301 | 1283 | 1228 | 1606 | 1739 | 1936 | 2049 | 1960 | 1973 | 2034 | 1925 | 1897 | 1881 | 1769 | 1831 | 2266 |  | 2466 | 2441 | 2419 | 2431 | 2243 | 1955 | 1736 | 45510683