## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 09-06-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-06-2025 | during | 09-06-2025 | during | 09-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 120 | 120 | 120 | 120 | 120 | 120 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 240 | 260 | 260 | 260 | 260 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 69 | 83 | 97.7 | 97.7 | 97.7 | 97.7 | Allocation limit by Titas, instructed by DS(Gen)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 314 | 357 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 144 | 147 | 150 | 150 | 133.5 | 133.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 79 | 0 | 208.13 | 208.13 | 208.13 | 208.13 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 16.5 | 17 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 7 | 7 | 22 | 22 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 16 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 13 | 0 | 20 | 0 | 20 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 450 | 556 | 584 | 584 | 584 | 584 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 450 | 583 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 745 | 348 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 35 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2757.5 | 2976 | 4582.1 | 4594.1 | 4353.6 | 4365.6
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 180 | 180 | 150 | 150 | 150 | 150 | Unit #1 Under Maintenance, Unit#2 Running at 150MW
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 13 | 0 | 13 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 167 | 167 | 0 | 0 | 0 | 0 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 218 | 215 | 221 | 221 | 221 | 221 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 72 | 72 | 72 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 68 | 68 | 68 | 68 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 48 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 16 | 42 | 38 | 40 | 38 | 40 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4 | 0 | 3.59 | 0 | 3.59 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 611 | 932 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 2 | 0 | 2 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 0 | 0 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25 & U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1213 | 1643 | 3593.31 | 3580.72 | 3593.31 | 3580.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 185 | 196 | 221.43 | 221.43 | 205.43 | 205.43 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 320 | 344 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 280 | 340 | 340 | 340 | 340 | 340 | machine problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 18 | 17 | 46.7 | 46.7 | 32 | 32 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 49 | 48 | 55 | 55 | 52 | 52 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 147 | 180 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 10 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 37 | 43 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 80 | 80 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 85 | 170 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 30 | 36 | 0 | 0 | 0 | 0 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 19 | 17.75 | 17.75 | 17.75 | 17.75 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 29 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 115 | 105 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 41 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1510 | 1794.2 | 2284.43 | 2234.43 | 2167.73 | 2117.73
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-06-2025 | during | 09-06-2025 | during | 09-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 103 | 155 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.3 | 0 | 1.3 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 63 | 85 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 35 | 45 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 44.61 | 0 | 37.65 | 0 | 37.65 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 247.61 | 285 | 587.95 | 549 | 587.95 | 549
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 33 | 32 | 32 | 32 | 32 | 32 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 129 | 151 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 41 | 81 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 162 | 100 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 10 | 10 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 303 | 373 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1356 | 1440 | 1587 | 1587 | 1476 | 1476
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 402 | 917 | 0 | 0 | 0 | 0 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 348 | 358 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 87.76 | 0 | 67 | 0 | 67 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 354 | 438 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | U#1 Reserve shut down as per NLDC Communication
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3699.2 | 1191.76 | 1713 | 2579.2 | 2512.2 | 2579.2 | 2512.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 8 | 11 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 96 | 120 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 500 | 964 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.61 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 824.61 | 1315 | 2172 | 2171 | 2132 | 2131
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 153 | 171 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 163 | 193 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 162 | 192 | 220 | 220 | 198 | 198 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 333 | 408 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 | 30 | 30 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.21 | 0 | 3 | 0 | 3 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 420.4 | 615 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 46.62 | 0 | 35 | 0 | 35 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 83 | 0 | 50 | 0 | 50 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 1365.23 | 1579 | 3113.87 | 3025.87 | 3007.09 | 2919.09
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 49 | 50 | 50 | 50 | 50 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 201 | 201 | 200 | 200 | 200 | 200 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6 | 0 | 3.8 | 0 | 3.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 27 | 0 | 20 | 0 | 20 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 98 | 0 | 113.93 | 0 | 113.93 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 382 | 478 | 649.73 | 512 | 649.73 | 512
System Total |  |  |  |  | 28565.2 | 27044.055 | 10847.71 | 13223.2 | 21149.59 | 20766.32 | 20546.61 | 20163.34
Forecast Scenario (09-06-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13040 |  | 0 |  | 13040
|  |  |  | 1:00 | 12660 |  | 0 |  | 12660
|  |  |  | 2:00 | 12370 |  | 0 |  | 12370
|  |  |  | 3:00 | 12010 |  | 0 |  | 12010
|  |  |  | 4:00 | 11670 |  | 0 |  | 11670
|  |  |  | 5:00 | 11400 |  | 0 |  | 11400
|  |  |  | 6:00 | 10830 |  | 0 |  | 10830
|  |  |  | 7:00 | 10830 |  | 0 |  | 10830
|  |  |  | 8:00 | 10720 |  | 0 |  | 10720
|  |  |  | 9:00 | 10840 |  | 0 |  | 10840
|  |  |  | 10:00 | 10840 |  | 0 |  | 10840
|  |  |  | 11:00 | 10840 |  | 0 |  | 10840
|  |  |  | 12:00 | 10610 |  | 0 |  | 10610
|  |  |  | 13:00 | 11560 |  | 0 |  | 11560
|  |  |  | 14:00 | 12130 |  | 0 |  | 12130
|  |  |  | 15:00 | 12100 |  | 0 |  | 12100
|  |  |  | 16:00 | 11860 |  | 0 |  | 11860
|  |  |  | 17:00 | 11270 |  | 0 |  | 11270
|  |  |  | 18:00 | 10540 |  | 0 |  | 10540
|  |  |  | 18:30 | 11200 |  | 0 |  | 11200
|  |  |  | 19:00 | 11850 |  | 0 |  | 11850
|  |  |  | 19:30 | 12720 |  | 0 |  | 12720
|  |  |  | 20:00 | 12840 |  | 0 |  | 12840
|  |  |  | 21:00 | 13220 |  | 0 |  | 13220
|  |  |  | 22:00 | 13340 |  | 0 |  | 13340
|  |  |  | 23:00 | 13490 |  | 0 |  | 13490
Probable Maximum Temperature: |  |  | 35.30°C
Probable Maximum Demand at Day Peak: |  |  | 10840.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13220.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13220.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 282.86 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:12 hrs on 09-06-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 08-06-2025 | [28 empty] | Date: | 08-06-2025 | [28 empty] | Date: | 08-06-2025 | [28 empty] | Date: | 08-06-2025 | [28 empty] | Date: | 08-06-2025 | [12 empty] | Date: | 08-06-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [12 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 83 | 373 | 0 | 752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 143 | 583 | 0 | 0 | 0 | 200 | 0 | 0 | 35 | 15.5 | 7 | 0 | 584 | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 217 | 0 | 0 | 0 | 805 | 0 | 51 | 0 | 182 | 0 | 351 | 340 | 49 | 198 | 19 | 115 | 50 | 170 | 11 | 19 | 114 | 38 | 52.2 | 0 | 46 | 325 | 320 | 387 | 33 | 30 | 154 | 8 | 0 | 82 | 30 | 0 | 0 | 162 | 0 | 55 | 100 | 157 | 0 | 0 | 0 | 8479.7 | 861 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 470 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 201 | 0 | 199 | 0 | 414 | 0 | 0 | 200 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 600 | 0 | 4565 | 13044.7 | 95.44
01:00 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 82 | 343 | 0 | 750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 141 | 583 | 0 | 0 | 0 | 199 | 0 | 0 | 17 | 15.5 | 7 | 0 | 584 | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 218 | 0 | 0 | 0 | 780 | 0 | 51 | 0 | 182 | 0 | 352 | 340 | 50 | 198 | 19 | 115 | 50 | 170 | 8 | 19 | 114 | 36 | 34 | 0 | 46 | 310 | 320 | 316 | 33 | 30 | 152 | 8 | 0 | 82 | 30 | 0 | 0 | 162 | 0 | 55 | 100 | 157 | 0 | 0 | 0 | 8292.5 | 861 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 462 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 190 | 0 | 188 | 0 | 338 | 0 | 0 | 200 | 50 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 120 | 220 | 0 | 0 | 600 | 0 | 4373 | 12665.5 | 95.45
02:00 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 79 | 310 | 0 | 750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 136 | 583 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 15.5 | 7 | 0 | 584 | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 219 | 0 | 0 | 0 | 750 | 0 | 51 | 0 | 182 | 0 | 355 | 340 | 50 | 185 | 19 | 115 | 50 | 170 | 9 | 19 | 114 | 38 | 34 | 0 | 46 | 300 | 320 | 303 | 33 | 30 | 132 | 8 | 0 | 82 | 30 | 0 | 0 | 163 | 0 | 55 | 100 | 157 | 0 | 0 | 0 | 8159.5 | 860 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 417 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 180 | 0 | 180 | 0 | 326 | 0 | 0 | 200 | 50 | 70 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 96 | 220 | 0 | 0 | 600 | 0 | 4219 | 12378.5 | 95.46
03:00 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 79 | 306 | 0 | 751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 137 | 583 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 16 | 7 | 0 | 584 | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 219 | 0 | 0 | 0 | 750 | 0 | 51 | 0 | 182 | 0 | 354 | 340 | 49 | 187 | 19 | 115 | 50 | 136 | 8 | 19 | 114 | 37 | 25 | 0 | 46 | 300 | 320 | 303 | 33 | 30 | 128 | 0 | 0 | 82 | 30 | 0 | 0 | 161 | 0 | 45 | 80 | 157 | 0 | 0 | 0 | 8007 | 861 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 414 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 161 | 0 | 159 | 0 | 328 | 0 | 0 | 200 | 50 | 61 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 96 | 220 | 0 | 0 | 500 | 0 | 4008 | 12015 | 95.47
04:00 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 79 | 308 | 0 | 751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 137 | 500 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 16 | 7 | 0 | 584 | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 221 | 0 | 0 | 0 | 660 | 0 | 51 | 0 | 180 | 0 | 354 | 340 | 49 | 190 | 19 | 115 | 50 | 136 | 10 | 19 | 114 | 34 | 25 | 0 | 39 | 305 | 320 | 310 | 33 | 30 | 128 | 0 | 0 | 41 | 30 | 0 | 0 | 161 | 0 | 24 | 80 | 105 | 0 | 0 | 0 | 7669 | 861 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 415 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 163 | 0 | 161 | 0 | 336 | 0 | 0 | 200 | 50 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 96 | 220 | 0 | 0 | 500 | 0 | 4008 | 11677 | 95.48
05:00 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 76 | 320 | 0 | 751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 134 | 500 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 15.5 | 7 | 0 | 584 | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 221 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 182 | 0 | 353 | 340 | 50 | 195 | 19 | 109 | 51 | 136 | 18 | 19 | 114 | 34 | 25 | 0 | 39 | 305 | 320 | 316 | 33 | 30 | 130 | 0 | 0 | 41 | 30 | 0 | 0 | 162 | 0 | 24 | 80 | 105 | 0 | 0 | 0 | 7645.5 | 641 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 168 | 0 | 166 | 0 | 344 | 0 | 0 | 200 | 50 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 220 | 0 | 0 | 500 | 0 | 3755 | 11400.5 | 95.49
06:00 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 76 | 314 | 0 | 751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 143 | 500 | 0 | 0 | 0 | 79 | 0 | 2 | 0 | 15.5 | 7 | 0 | 536 | 0 | 0 | 0 | 180 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 221 | 0 | 0 | 0 | 607 | 1 | 51 | 0 | 182 | 0 | 320 | 295 | 50 | 191 | 19 | 115 | 51 | 136 | 17 | 19 | 114 | 30 | 8 | 4 | 38 | 305 | 320 | 306 | 33 | 30 | 129 | 0 | 0 | 41 | 30 | 0 | 0 | 163 | 0 | 8 | 64 | 105 | 0 | 3.39 | 0 | 7380.89 | 387 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.72 | 372 | 0 | 419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 2.65 | 152 | 0 | 166 | 0 | 164 | 0 | 338 | 0 | 0.25 | 200 | 50 | 0 | 2 | 0 | 0 | 0 | 0.5 | 13 | 0.03 | 0 | 0 | 8 | 96 | 220 | 0 | 0 | 500 | 0 | 3449.15 | 10830.04 | 95.5
07:00 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 74 | 322 | 0 | 752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 142 | 500 | 0 | 0 | 0 | 79 | 0 | 5 | 0 | 15.5 | 7 | 0 | 500 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 221 | 0 | 0 | 0 | 605 | 5 | 51 | 0 | 182 | 0 | 320 | 280 | 51 | 195 | 19 | 115 | 50 | 100 | 18 | 19 | 114 | 30 | 8 | 13 | 38 | 310 | 320 | 316 | 33 | 30 | 131 | 0 | 0 | 41 | 30 | 0 | 0 | 161 | 0 | 8 | 64 | 105 | 1 | 12.42 | 0 | 7310.92 | 386 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.09 | 355 | 0 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 9.24 | 155 | 0 | 170 | 0 | 158 | 0 | 343 | 0 | 0 | 195 | 50 | 0 | 7 | 0 | 0 | 0 | 1.7 | 47 | 0.16 | 0 | 0 | 8 | 96 | 220 | 0 | 0 | 500 | 0 | 3522.19 | 10833.11 | 95.51
08:00 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 71 | 321 | 0 | 751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 142 | 450 | 0 | 0 | 0 | 80 | 0 | 11 | 0 | 15.5 | 7 | 0 | 450 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 167 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 606 | 10 | 10 | 0 | 140 | 0 | 320 | 280 | 51 | 194 | 18 | 115 | 50 | 85 | 10 | 19 | 114 | 30 | 0 | 27 | 38 | 310 | 320 | 320 | 33 | 30 | 132 | 0 | 0 | 41 | 30 | 0 | 0 | 161 | 0 | 12 | 64 | 104 | 1 | 24.86 | 0 | 7060.36 | 392 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.17 | 354 | 0 | 425.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 25.89 | 156 | 0 | 170 | 0 | 155 | 0 | 345 | 0 | 0 | 200 | 51 | 0 | 14 | 0 | 0 | 0 | 3.4 | 93 | 0.21 | 0 | 0 | 8 | 98 | 220 | 0 | 0 | 500 | 0 | 3661.69 | 10722.05 | 95.52
09:00 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 69 | 323 | 0 | 751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 142 | 450 | 0 | 0 | 0 | 75 | 0 | 17 | 0 | 16.5 | 7 | 0 | 450 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 606 | 15 | 10 | 0 | 147 | 0 | 320 | 280 | 50 | 195 | 18 | 115 | 50 | 85 | 9 | 19 | 114 | 30 | 0 | 55 | 38 | 310 | 320 | 310 | 33 | 30 | 132 | 8 | 0 | 41 | 30 | 0 | 0 | 162 | 0 | 35 | 64 | 103 | 2 | 35.71 | 0 | 7110.21 | 392 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.11 | 354 | 0 | 424.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 35.84 | 156 | 0 | 170 | 0 | 166 | 0 | 342 | 0 | 3.16 | 200 | 50 | 0 | 21 | 0 | 0 | 0 | 5 | 97 | 0.49 | 0 | 0 | 8 | 96 | 220 | 0 | 0 | 500 | 0 | 3729.63 | 10839.84 | 95.53
10:00 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 69 | 314 | 0 | 745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 144 | 450 | 0 | 0 | 0 | 79 | 0 | 13 | 0 | 16.5 | 7 | 0 | 450 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 167 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 611 | 17 | 10 | 0 | 147 | 0 | 320 | 280 | 49 | 185 | 18 | 115 | 50 | 85 | 9 | 20 | 114 | 30 | 0 | 41 | 37 | 300 | 320 | 303 | 33 | 30 | 129 | 8 | 0 | 41 | 30 | 0 | 0 | 162 | 0 | 35 | 63 | 103 | 2 | 44.61 | 0 | 7084.11 | 402 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.76 | 354 | 0 | 420.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 46.62 | 153 | 0 | 163 | 0 | 162 | 0 | 333 | 0 | 4.21 | 201 | 50 | 0 | 27 | 0 | 0 | 0 | 6 | 98 | 0.61 | 0 | 0 | 8 | 96 | 220 | 0 | 0 | 500 | 0 | 3763.6 | 10847.71 | 95.53
11:00 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 71 | 318 | 0 | 734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 140 | 400 | 0 | 0 | 0 | 79 | 0 | 26 | 0 | 17 | 0 | 0 | 450 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 167 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 608 | 17 | 10 | 0 | 155 | 0 | 320 | 280 | 48 | 191 | 17 | 101 | 50 | 85 | 9 | 20 | 114 | 30 | 0 | 59 | 37 | 305 | 320 | 304 | 32 | 30 | 130 | 8 | 0 | 41 | 30 | 0 | 0 | 165 | 0 | 35 | 45 | 102 | 2 | 48.29 | 0 | 7058.29 | 402 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.91 | 360 | 0 | 423.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 52.85 | 154 | 0 | 161 | 0 | 161 | 0 | 334 | 0 | 4.72 | 201 | 50 | 0 | 31 | 0 | 0 | 0 | 6.9 | 98 | 0.72 | 0 | 0 | 9 | 98 | 220 | 0 | 0 | 500 | 0 | 3784.61 | 10842.9 | 95.54
12:00 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 76 | 334 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 143 | 400 | 0 | 0 | 0 | 40 | 0 | 26 | 0 | 17 | 7 | 0 | 450 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 167 | 0 | 38 | 0 | 0 | 0 | 0 | 4 | 0 | 215 | 0 | 0 | 0 | 608 | 10 | 10 | 0 | 145 | 0 | 320 | 280 | 48 | 206 | 17 | 94 | 50 | 85 | 9 | 20 | 114 | 32 | 0 | 53 | 37 | 305 | 320 | 380 | 32 | 30 | 139 | 8 | 0 | 41 | 30 | 0 | 0 | 0 | 0 | 24 | 45 | 99 | 2 | 49.95 | 0 | 6599.95 | 559 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.69 | 355 | 0 | 423.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 53.49 | 161 | 0 | 172 | 0 | 171 | 0 | 386 | 0 | 4.93 | 200 | 50 | 0 | 20 | 0 | 0 | 0 | 2.9 | 98 | 0.75 | 0 | 0 | 9 | 110 | 220 | 0 | 0 | 500 | 0 | 4012.12 | 10612.07 | 95.54
13:00 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 361 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 142 | 500 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 17 | 7 | 0 | 500 | 0 | 0 | 0 | 180 | 6 | 0 | 0 | 0 | 0 | 0 | 4 | 127 | 0 | 38 | 0 | 0 | 0 | 0 | 8 | 0 | 214 | 0 | 0 | 0 | 728 | 17 | 32 | 0 | 184 | 0 | 329 | 335 | 45 | 208 | 17 | 84 | 50 | 99 | 9 | 18 | 114 | 34 | 0 | 73 | 39 | 310 | 320 | 384 | 32 | 29 | 151 | 8 | 0 | 81 | 30 | 0 | 0 | 0 | 0 | 24 | 55 | 105 | 2 | 48.28 | 0 | 7099.28 | 876 | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.1 | 359 | 0 | 433.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 54.39 | 174 | 0 | 194 | 0 | 197 | 0 | 414 | 0 | 4.65 | 198 | 50 | 0 | 32 | 0 | 0 | 0 | 5.6 | 60 | 0.29 | 0 | 0 | 10 | 120 | 220 | 0 | 0 | 555 | 0 | 4466.89 | 11566.17 | 95.55
14:00 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 366 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 144 | 500 | 0 | 0 | 0 | 0 | 0 | 28 | 17 | 17 | 7 | 0 | 490 | 0 | 0 | 0 | 180 | 8 | 0 | 0 | 0 | 0 | 0 | 4 | 167 | 0 | 38 | 0 | 0 | 0 | 0 | 8 | 0 | 212 | 0 | 0 | 0 | 782 | 11 | 51 | 0 | 184 | 0 | 335 | 340 | 46 | 194 | 15 | 94 | 50 | 113 | 10 | 17 | 114 | 34 | 6 | 59 | 41 | 315 | 320 | 367 | 32 | 30 | 151 | 8 | 0 | 80 | 30 | 0 | 0 | 0 | 0 | 24 | 55 | 149 | 2 | 45.23 | 0 | 7290.23 | 876 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.05 | 464 | 0 | 513.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 44.18 | 167 | 0 | 195 | 0 | 195 | 0 | 390 | 0 | 4.42 | 200 | 50 | 35 | 28 | 0 | 0 | 0 | 6.2 | 94 | 0.3 | 0 | 0 | 10 | 116 | 218 | 0 | 0 | 765 | 0 | 4840.71 | 12130.94 | 95.55
15:00 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 342 | 0 | 438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 143 | 450 | 0 | 0 | 0 | 0 | 0 | 21 | 17 | 17 | 7 | 0 | 480 | 0 | 0 | 0 | 180 | 6 | 0 | 0 | 0 | 0 | 0 | 2 | 167 | 0 | 29 | 0 | 0 | 0 | 0 | 8 | 0 | 212 | 0 | 0 | 0 | 755 | 13 | 51 | 0 | 184 | 0 | 334 | 340 | 44 | 190 | 17 | 96 | 50 | 131 | 18 | 17 | 114 | 34 | 52.2 | 46 | 33 | 305 | 320 | 365 | 32 | 30 | 146 | 8 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 24 | 55 | 147 | 2 | 34.71 | 0 | 7265.91 | 910 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.31 | 460 | 0 | 519.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 36.39 | 163 | 0 | 186 | 0 | 185 | 0 | 338 | 0 | 3.52 | 201 | 50 | 35 | 22 | 0 | 0 | 0 | 3.5 | 93 | 0.49 | 0 | 0 | 10 | 116 | 218 | 0 | 0 | 790 | 0 | 4836.88 | 12102.79 | 95.55
16:00 | 0 | 0 | 0 | 120 | 0 | 120 | 0 | 80 | 336 | 0 | 523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 142 | 400 | 0 | 0 | 0 | 0 | 0 | 14 | 17 | 17 | 7 | 0 | 435 | 0 | 0 | 0 | 180 | 8 | 0 | 0 | 0 | 0 | 0 | 2 | 167 | 0 | 37 | 0 | 0 | 0 | 0 | 8 | 0 | 213 | 0 | 0 | 0 | 667 | 8 | 51 | 0 | 133 | 0 | 336 | 340 | 45 | 185 | 17 | 115 | 50 | 120 | 18 | 17 | 114 | 32 | 52.2 | 31 | 33 | 300 | 320 | 350 | 32 | 30 | 129 | 8 | 0 | 79 | 30 | 0 | 0 | 100 | 0 | 24 | 55 | 147 | 1 | 23.43 | 0 | 7218.63 | 917 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.03 | 432 | 0 | 516.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 24.84 | 160 | 0 | 158 | 0 | 160 | 0 | 328 | 0 | 2.21 | 201 | 50 | 35 | 15 | 0 | 0 | 0 | 3.6 | 94 | 0.34 | 0 | 0 | 10 | 112 | 218 | 0 | 0 | 758 | 0 | 4643.69 | 11862.32 | 95.56
17:00 | 0 | 0 | 0 | 120 | 0 | 120 | 0 | 76 | 337 | 0 | 529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 140 | 350 | 0 | 0 | 0 | 0 | 0 | 4 | 17 | 17 | 7 | 0 | 390 | 0 | 0 | 0 | 180 | 5 | 0 | 0 | 0 | 0 | 0 | 1 | 167 | 0 | 37 | 0 | 0 | 0 | 0 | 8 | 0 | 215 | 0 | 0 | 0 | 753 | 5 | 51 | 0 | 88 | 0 | 335 | 300 | 45 | 190 | 17 | 115 | 50 | 120 | 18 | 17 | 114 | 32 | 25 | 14 | 33 | 305 | 320 | 355 | 32 | 30 | 129 | 8 | 0 | 51 | 30 | 0 | 0 | 100 | 0 | 8 | 45 | 146 | 1 | 11.63 | 0 | 6963.63 | 917 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.39 | 381 | 0 | 415.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 8.35 | 161 | 0 | 158 | 0 | 160 | 0 | 333 | 0 | 1.07 | 200 | 50 | 35 | 7 | 0 | 0 | 0 | 1.8 | 46 | 0.17 | 0 | 0 | 10 | 112 | 218 | 0 | 0 | 702 | 0 | 4310.34 | 11273.97 | 95.56
18:00 | 0 | 0 | 0 | 120 | 0 | 120 | 0 | 80 | 330 | 0 | 401 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 140 | 320 | 0 | 0 | 0 | 0 | 0 | 1 | 17 | 17 | 7 | 0 | 375 | 0 | 0 | 0 | 180 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 36 | 0 | 0 | 0 | 0 | 8 | 0 | 214 | 0 | 0 | 0 | 707 | 1 | 51 | 0 | 88 | 0 | 300 | 300 | 45 | 184 | 17 | 103 | 50 | 100 | 24 | 17 | 114 | 30 | 16 | 3 | 33 | 295 | 320 | 353 | 32 | 30 | 128 | 8 | 0 | 51 | 30 | 0 | 0 | 100 | 0 | 8 | 45 | 120 | 0 | 2.72 | 0 | 6543.72 | 917 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.26 | 377 | 0 | 417.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 2.93 | 155 | 0 | 153 | 0 | 154 | 0 | 280 | 0 | 0.27 | 201 | 50 | 35 | 2 | 0 | 0 | 0 | 0.5 | 13 | 0.03 | 0 | 0 | 6 | 90 | 180 | 0 | 0 | 670 | 0 | 3997.36 | 10541.08 | 95.56
19:00 | 0 | 0 | 0 | 120 | 0 | 120 | 0 | 83 | 362 | 0 | 500 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 5 | 380 | 143 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 17 | 7 | 0 | 512 | 0 | 0 | 0 | 180 | 0 | 32 | 0 | 0 | 10 | 0 | 0 | 167 | 0 | 36 | 0 | 0 | 0 | 0 | 8 | 0 | 214 | 0 | 0 | 0 | 822 | 0 | 51 | 0 | 140 | 0 | 336 | 335 | 45 | 202 | 17 | 93 | 50 | 108 | 28 | 17 | 114 | 38 | 16 | 0 | 33 | 305 | 320 | 390 | 32 | 30 | 133 | 0 | 0 | 77 | 30 | 0 | 0 | 100 | 0 | 12 | 65 | 149 | 0 | 0 | 0 | 7491 | 869 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 493.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 162 | 0 | 164 | 0 | 406 | 0 | 0 | 200 | 51 | 52 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 100 | 190 | 0 | 0 | 680 | 0 | 4359.45 | 11850.45 | 95.57
19:30 | 0 | 0 | 0 | 160 | 0 | 120 | 0 | 83 | 346 | 0 | 507 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 16 | 450 | 140 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 17 | 7 | 0 | 495 | 0 | 0 | 0 | 180 | 0 | 43 | 0 | 0 | 34 | 0 | 0 | 167 | 0 | 36 | 0 | 0 | 0 | 0 | 8 | 0 | 214 | 0 | 0 | 0 | 905 | 0 | 51 | 0 | 143 | 0 | 336 | 335 | 46 | 196 | 17 | 94 | 50 | 200 | 28 | 17 | 114 | 34 | 52.2 | 0 | 35 | 315 | 320 | 370 | 32 | 30 | 143 | 8 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 55 | 84 | 149 | 0 | 0 | 0 | 7911.2 | 869 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 432 | 0 | 583.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 186 | 0 | 185 | 0 | 400 | 0 | 0 | 200 | 50 | 70 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 860 | 0 | 4818.26 | 12729.46
20:00 | 0 | 5 | 0 | 170 | 0 | 120 | 0 | 83 | 352 | 0 | 508 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 16 | 450 | 143 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 7 | 0 | 507 | 0 | 0 | 0 | 180 | 0 | 51 | 0 | 0 | 48 | 0 | 0 | 167 | 0 | 37 | 0 | 0 | 0 | 0 | 8 | 0 | 214 | 0 | 0 | 0 | 878 | 0 | 51 | 0 | 167 | 0 | 337 | 340 | 47 | 193 | 17 | 92 | 50 | 173 | 28 | 19 | 114 | 36 | 52.2 | 0 | 37 | 310 | 320 | 365 | 32 | 30 | 151 | 8 | 0 | 81 | 30 | 0 | 0 | 100 | 0 | 55 | 84 | 150 | 0 | 0 | 0 | 7926.2 | 869 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 429 | 0 | 610.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 189 | 0 | 187 | 0 | 402 | 0 | 0 | 201 | 50 | 90 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 900 | 0 | 4919.55 | 12845.75 | 95.57
21:00 | 0 | 17 | 0 | 240 | 0 | 120 | 0 | 83 | 357 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 450 | 147 | 583 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 7 | 0 | 556 | 0 | 0 | 0 | 180 | 0 | 51 | 0 | 0 | 48 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 215 | 0 | 0 | 0 | 932 | 0 | 51 | 0 | 180 | 0 | 344 | 340 | 48 | 196 | 17 | 105 | 50 | 170 | 29 | 19 | 114 | 36 | 52.2 | 0 | 43 | 315 | 320 | 373 | 32 | 30 | 151 | 8 | 0 | 81 | 30 | 0 | 0 | 100 | 0 | 45 | 85 | 155 | 0 | 0 | 0 | 8138.2 | 917 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 438 | 0 | 615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 193 | 0 | 192 | 0 | 408 | 0 | 0 | 201 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 964 | 0 | 5085 | 13223.2 | 95.57
22:00 | 0 | 17 | 0 | 200 | 0 | 120 | 0 | 83 | 349 | 0 | 509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 450 | 137 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 7 | 0 | 524 | 0 | 0 | 0 | 150 | 0 | 51 | 0 | 0 | 48 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 215 | 0 | 0 | 0 | 951 | 0 | 51 | 0 | 187 | 0 | 349 | 340 | 51 | 214 | 17 | 115 | 50 | 170 | 28 | 19 | 114 | 26 | 52.2 | 0 | 43 | 310 | 320 | 390 | 32 | 30 | 151 | 8 | 0 | 81 | 30 | 0 | 0 | 100 | 0 | 45 | 85 | 155 | 0 | 0 | 0 | 8176.2 | 916 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 423 | 0 | 679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 190 | 0 | 189 | 0 | 414 | 0 | 0 | 201 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 1000 | 0 | 5170 | 13346.2 | 95.58
23:00 | 0 | 17 | 0 | 200 | 0 | 120 | 0 | 85 | 366 | 0 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 143 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 17 | 7 | 0 | 460 | 0 | 0 | 0 | 150 | 0 | 50 | 0 | 0 | 48 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 219 | 0 | 0 | 0 | 995 | 0 | 51 | 0 | 185 | 0 | 345 | 340 | 52 | 214 | 17 | 115 | 50 | 170 | 29 | 19 | 114 | 38 | 52.2 | 0 | 43 | 315 | 320 | 390 | 32 | 30 | 153 | 8 | 0 | 81 | 30 | 0 | 0 | 100 | 0 | 45 | 85 | 156 | 0 | 0 | 0 | 8269.2 | 917 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 443 | 0 | 666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 197 | 0 | 196 | 0 | 414 | 0 | 0 | 201 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 1000 | 0 | 5228 | 13497.2 | 95.58
Total KWH | 0 | 65280 | 0 | 1371400 | 0 | 2882063 | 0 | 1838954.55 | 8236800 | 0 | 14586130 | 5400 | 0 | 33120 | 0 | 0 | 0 | 0 | 0 | 48960 | 9608000 | 3358167 | 11358182 | 0 | 0 | 0 | 1437000 | 0 | 191432 | 337200 | 394800 | 169920 | 0 | 12060909.09 | 0 | 0 | 0 | 4300000 | 31200 | 625248 | 0 | 0 | 242880 | 1920 | 31582 | 3947160 | 0 | 956160 | 0 | 0 | 0 | 0 | 168505.2 | 0 | 5082119 | 0 | 0 | 0 | 17716362 | 130680 | 1027352 | 0 | 3914181.81 | 0 | 8337300 | 7774000 | 1159200 | 4756000 | 426456 | 2592000 | 1193720 | 3211200 | 404040 | 430400 | 2762220 | 788160 | 625786 | 485927 | 914240 | 7457000 | 7665900 | 8639000 | 769000 | 682440 | 3310118 | 125352 | 0 | 1508160 | 715968 | 0 | 0 | 1962620 | 0 | 751200 | 1663200 | 3059520 | 15350 | 372130 | 0 | 180716674.65 | 18042181 | 8472096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 772560 | 9709091 | 8640 | 11572641 | 0 | 0 | 210000 | 0 | 0 | 0 | 0 | 0 | 0 | 599300 | 0 | 388504 | 3924636 | 0 | 4419127 | 0 | 4435636 | 0 | 8683127 | 0 | 32040 | 4922000 | 1164218 | 1094580 | 230766 | 989990 | 0 | 0 | 50031.12 | 978480 | 4969.5 | 0 | 0 | 218672 | 2573000 | 5307430 | 0 | 0 | 16626909.09 | 0 | 105430624.71 | 286147299.36

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 08-06-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10847.71 | MW | 10:00 Hr. | Energy Generated |  |  | 286.1473 |  | MKWHr.
| Day Peak Demand |  |  | 10847.71 | MW | 10:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 13223.2 | MW | 21:00 Hr. | Energy Demand |  |  | 286.1473 |  | MKWHr.
| Evening Peak Demand |  |  | 13223.2 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.7 |  | °C
| Minimum Generation of the Day |  |  | 10612.07 | MW | 12:00 Hr. | Total Gas Supplied |  |  | 1291.98 |  | MMCFD
| Maximum Generation of the Day |  |  | 13497.2 | MW | 23:00 Hr. | Production Cost per KWHr |  |  | 5.1082 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 67.3023 | 0 | 0.48996 | 0 | 0 | 0.19143 | 0 | 0 | 67.9837 | Gas | 180.798 | Gas | 610394995.8255
| Chattogram Zone |  |  | 10.3383 | 17.7164 | 1.0386 | 0 | 3.9472 | 0.16226 | 0 | 0.0312 | 33.2338 | Coal | 50.1386 | Coal | 342597827.3003
| Cumilla Zone |  |  | 29.0186 | 0 | 10.5095 | 0 | 0 | 0.48593 | 0.78816 | 0 | 40.8022 | HFO | 16.5456 | HFO | 303435413.104
| Mymensingh Zone |  |  | 3.0595 | 0 | 2.4144 | 0 | 0 | 0.38748 | 0 | 0 | 5.8614 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 32.8356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.8356 | Hydro | 3.9472 | Hydro | 394716
| Khulna Zone |  |  | 8.4721 | 9.7091 | 0.00864 | 0 | 0 | 0.77256 | 18.0422 | 0 | 37.0046 | Solar | 4.2838 | Solar | 69535974.8382
| Barishal Zone |  |  | 8.0991 | 16.6269 | 0 | 0 | 0 | 0.0049695 | 0 | 0 | 24.731 | Import | 30.403 | Import | 134884315.56
| Rajshahi Zone |  |  | 21.6725 | 0 | 0 | 0 | 0 | 1.0198 | 11.5726 | 0 | 34.265 | Wind | 0.0312 | Wind | 456768
| Rangpur Zone |  |  | 0 | 6.0862 | 2.0846 | 0 | 0 | 1.2593 | 0 | 0 | 9.4301
| Total |  |  | 180.798 | 50.1386 | 16.5456 | 0 | 3.9472 | 4.2838 | 30.403 | 0.0312 | 286.1473
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 610394995.8255 |  | Hydro | 394716
|  |  |  | Coal | 342597827.3003 |  | Solar | 69535974.8382
|  |  |  | HFO | 303435413.104 |  | Import | 134884315.56
|  |  |  | HSD | 0 |  | Wind | 456768
[5 empty] | Total: | 146,17,00,010 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 5644570.93 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 18.0422 | Peak Hr Flow | 917.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 2275436.37 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 11.5726 | Peak Hr Flow | 615.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 216 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.78816 | Peak Hr Flow | 36.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 266 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 30.403 | Peak Hr Flow | 1568.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3313
|  |  |  | Chattogram |  | 0 |  | 1237
|  |  |  | Cumilla |  | 0 |  | 1457
|  |  |  | Mymensingh |  | 0 |  | 1093
|  |  |  | Sylhet |  | 0 |  | 651
|  |  |  | Khulna |  | 0 |  | 1824
|  |  |  | Barishal |  | 0 |  | 504
|  |  |  | Rajshahi |  | 0 |  | 1499
|  |  |  | Rangpur |  | 0 |  | 994
|  |  |  | Total |  | 0 |  | 12572
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Meghnaghat CCPP(Summit) GT-2 |  |  | 110
[7 empty] | 5 | Sylhet 225 MW CCPP GT |  |  | 142
[7 empty] | 6 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 741
|  |  |  | Total Unavailable Capacity |  |  |  | 1041
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 09:34 | Kishoreganj 132/33kV S/S Tr-1 (404T) HT is restored.
|  | 09:35 | Kishoreganj 132/33kV S/S 33 kV T1 Bus is restored.
| 10:00 |  | Day Peak Gen. 10847 MW
| 10:52 | 11:59 | Barishal 230/132kV S/S T-4 LT Scheduled S/D Due to Babugonj 33kv feeder bus DS | [7 empty] | 7.0MW load
|  |  | maintenance by pbs-2 | [7 empty] | interrup.
| 10:52 | 10:58 | Barishal 230/132kV S/S T-4 HT Scheduled S/D Due to Babugonj 33kv feeder bus DS | [7 empty] | 7.0MW load
|  |  | maintenance by pbs-2 | [7 empty] | interrup.
| 11:16 |  | Raozan 25 MW PP Synchronized
| 11:41 |  | Sylhet CCPP 225 MW tripped .
| 11:50 |  | Siddhirganj GT-1 was shutdown.
| 11:58 |  | From NLDC: JERA Meghnaghat Power Limited 718 MW CCPP GT-12 tripped due to control valve
malfunction which resulted in high temperature at fuel gas.
| 12:07 |  | Siddhirganj GT-2 was shutdown .
|  | 12:36 | Siddhirganj 230/132kV S/S 335MW EGCB 1 is restored.
| 13:54 |  | JERA Meghnaghat Power Limited 718 MW CCPP GT -12 was sync.
| 18:32 |  | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-2 Forced S/D Due to Abnormal sound at
VT(Y) phase.
|  | 19:30 | Rangpur 132/33kV S/S Rangpur-Teesta Solar-1 is restored.
|  | 21:17 | Siddhirganj 132/33kV S/S 132kV MTR 2 is restored.
|  | 21:17 | Siddhirganj 230/132kV S/S MTR 2 HT is restored.
| 21:33 | 22:47 | Mongla 132/33kV S/S T-1 LT Tripped showing Over current and lockout 1&2 relays Due to | [7 empty] | 22.0MW load
|  |  | Sort circuit by bird and Auxiliary tx-02 fault | [7 empty] | interrup.
| 21:34 |  | TR-2, 33 kv side Trip at Mongla S/S Showing O/C. | [7 empty] | 22MW load interrup.
| 22:47 |  | TR-2, 33 KV side close at Mongla S/S.
| 00:38 |  | Ghorasal Repowered CCPP Unit-4 Shutdown
| 03:27 | 03:40 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Tripped from Shahjibazar 132/33kV end showing
Distance Relay relays.
| 05:31 |  | Raozan 25 MW PP Shutdown
| 06:00 |  | Minimum Generation is 11484 MW
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 08-06-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 120 | 2882063 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 240 | 1371400 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 83 | 1838954.55 | Allocation limit by Titas, instructed by DS(Gen)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 357 | 8236800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9608000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 147 | 3358167 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 1437000 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 5400 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17 | 394800 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 7 | 169920 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | Fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 33120 | Machine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 65280 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 48960 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 191432 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 556 | 12060909.09 | None
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 583 | 11358182 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 348 | 14586130 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 35 | 337200 | -
Dhaka Area Total |  |  |  |  | 5939.724 | 2976 | 67983717.64
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 180 | 4300000 | Unit #1 Under Maintenance, Unit#2 Running at 150MW
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 168505.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 130680 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 167 | 3947160 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 215 | 5082119 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 625248 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 48 | 242880 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 42 | 956160 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 31582 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 1920 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 932 | 17716362 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 31200 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 0 | 0 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4895.72 | 1643 | 33233816.2
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 196 | 4756000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 344 | 8337300 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 7774000 | machine problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 17 | 426456 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 48 | 1159200 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 180 | 3914181.81 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1027352 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 43 | 914240 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1193720 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 170 | 3211200 | -
| Import (Tripura) |  | Import | 0 | 160 | 36 | 788160 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 625786 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 430400 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2762220 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 29 | 404040 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 105 | 2592000 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 485927 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1794.2 | 40802182.81
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 155 | 3059520 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15350 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 85 | 1663200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 45 | 751200 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 372130 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 285 | 5861400
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 32 | 769000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 682440 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 151 | 3310118 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 715968 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1508160 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 1962620 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 125352 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7457000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 373 | 8639000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7665900 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2325 | 1440 | 32835558
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 917 | 18042181 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 358 | 8472096 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 8640 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 772560 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 438 | 9709091 | U#1 Reserve shut down as per NLDC Communication
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3699.2 | 1713 | 37004568
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 11 | 218672 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2573000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 964 | 16626909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5307430 | -
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4969.5 | -
Barishal Area Total |  |  |  |  | 2236 | 1315 | 24730980.59
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 210000 | machine running
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 171 | 3924636 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 193 | 4419127 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 192 | 4435636 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 408 | 8683127 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 32040 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 615 | 11572641 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 388504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 599300 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 1579 | 34265011
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 49 | 1164218 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 201 | 4922000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 989990 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 50031.12 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1094580 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 230766 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 978480 | -
Rangpur Area Total |  |  |  |  | 950 | 478 | 9430065.12
Eastern Grid Total |  |  |  |  | 16705.895 | 8138.2 | 180716674.65
Western Grid Total |  |  |  |  | 10338.16 | 5085 | 105430624.71
National Grid Total |  |  |  |  | 27044.055 | 13223.2 | 286147299.36
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 08-06-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7750.9 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4821 | MW
i) Dhaka area |  |  | 3313.21 |  | MW | i) Khulna area |  |  |  | 1824 | MW
ii) Chattogram area |  |  | 1237 |  | MW | ii) Barishal area |  |  |  | 504 | MW
iii) Cumilla area |  |  | 1456.69 |  | MW | iii) Rajshahi area |  |  |  | 1499 | MW
iv) Mymensingh area |  |  | 1093 |  | MW | iv) Rangpur area |  |  |  | 994 | MW
v) Sylhet area |  |  | 651 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12571.9 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 70 | 21:00 | 133 | Patuakhali | 95 | 23:00
2 | AKSML | 109 | 13:00 | 68 | Jaldhaka | 96 | 22:00 | 134 | Payra | 40 | 22:00
3 | Aftabnagar | 30 | 00:00 | 69 | Jamalpur | 139 | 20:00 | 135 | Postogola | 43 | 00:00
4 | Agargaon | 110 | 10:00 | 70 | Jashore | 152 | 00:00 | 136 | Purbachal | 16 | 00:00
5 | Agrabad | 76 | 00:00 | 71 | Jhenaidah | 134 | 23:00 | 137 | Purbasadipur | 124 | 23:00
6 | Amnura | 45 | 23:00 | 72 | Joydebpur | 68 | 21:00 | 138 | Rahanpur | 38 | 22:00
7 | Ashuganj | 96 | 23:00 | 73 | Joypurhat | 70 | 23:00 | 139 | Rahim | 1 | 00:00
8 | BSRM | 134 | 23:00 | 74 | Juldah | 14 | 23:00 | 140 | Rajbari | 82 | 22:00
9 | Bagerhat | 92 | 23:00 | 75 | KSRM | 9 | 17:00 | 141 | Rajendrapur | 91 | 00:00
10 | Bajitpur | 60 | 22:00 | 76 | Kabirpur | 108 | 03:00 | 142 | Rajshahi | 110 | 22:00
11 | Bakulia | 81 | 23:00 | 77 | Kachua | 112 | 19:30 | 143 | Rajshahi-230 | 95 | 23:00
12 | Banani | 22.8 | 19:00 | 78 | Kallyanpur | 90 | 23:00 | 144 | Ramganj | 118 | 01:00
13 | Bangabhaban | 3 | 00:00 | 79 | Kalurghat | 26 | 00:00 | 145 | Rampur | 43 | 00:00
14 | Barapukuria | 67 | 23:00 | 80 | Kamrangirchar | 36.6 | 00:00 | 146 | Rangamati | 18 | 19:30
15 | Barguna | 28 | 01:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 142 | 20:00
16 | Barishal | 116 | 23:00 | 82 | Kasba | 41 | 01:00 | 148 | Ruppur | 5.2 | 10:00
17 | Barishal-230 | 112 | 22:00 | 83 | Kazla | 62 | 16:00 | 149 | SSM | 0 | 00:00
18 | Baroaulia | 50 | 02:00 | 84 | Keranigonj | 77 | 23:00 | 150 | Saidpur | 101 | 00:00
19 | Baroirhat | 70 | 22:00 | 85 | Khagrachori | 36 | 19:30 | 151 | Satkhira | 151 | 23:00
20 | Bashundhara | 135 | 19:00 | 86 | Khulna | 64 | 00:00 | 152 | Satmasjid | 74 | 00:00
21 | BashundharaCement | 1 | 00:00 | 87 | Khulshi | 97 | 00:00 | 153 | Savar | 102 | 23:00
22 | Beanibazar | 94 | 23:00 | 88 | Kishoreganj | 152 | 23:00 | 154 | SevenRings | 0.66 | 21:00
23 | Benapole | 72 | 22:00 | 89 | Kodda | 129 | 22:00 | 155 | ShahCement | 13 | 00:00
24 | Bhaluka | 98 | 15:00 | 90 | Kulaura | 58 | 00:00 | 156 | Shahjadpur | 84 | 19:00
25 | Bhandaria | 63 | 00:00 | 91 | Kurigram | 66 | 21:00 | 157 | Shahjibazar | 127 | 22:00
26 | Bhangura | 41 | 20:00 | 92 | Kushtia | 125 | 21:00 | 158 | Shahmirpur | 47 | 00:00
27 | Bheramara(GK) | 69 | 23:00 | 93 | Lalbag | 12 | 00:00 | 159 | Shariatpur | 106 | 23:00
28 | Bhulta | 107 | 22:00 | 94 | Lalmonirhat | 67 | 00:00 | 160 | Sherpur | 150 | 00:00
29 | Bog-Sherpur | 56 | 23:00 | 95 | MI_Cement | 1.2 | 10:00 | 161 | Shikalbaha | 23 | 23:00
30 | Bogura | 161 | 21:00 | 96 | Madanganj | 38 | 13:00 | 162 | Shitalakhya | 55 | 23:00
31 | Borhanuddin | 93 | 23:00 | 97 | Madaripur | 127 | 21:00 | 163 | Sholosohor | 36 | 00:00
32 | Brahmanbaria | 144 | 01:00 | 98 | Madartek | 74.46 | 00:00 | 164 | Shyampur | 44 | 00:00
33 | Cantonment | 102 | 19:00 | 99 | Madunaghat | 58 | 09:00 | 165 | Siddhirganj | 71 | 21:00
34 | Chandina | 21.69 | 00:00 | 100 | Magura | 69 | 00:00 | 166 | Sirajganj | 110 | 23:00
35 | Chandpur | 82 | 00:00 | 101 | Mahasthangarh | 94 | 23:00 | 167 | Sonargaon | 52 | 23:00
36 | Chandraghona | 40 | 20:00 | 102 | Manikganj | 98 | 22:00 | 168 | Sreemongol | 75 | 23:00
37 | Chapai | 71 | 21:00 | 103 | Maniknagar | 58 | 23:00 | 169 | Sreepur | 56 | 20:00
38 | Charsaidpur | 8 | 11:00 | 104 | Matarbari | 51 | 21:00 | 170 | Srinagar | 56.9 | 22:00
39 | Chauddagram | 87 | 21:00 | 105 | Matuail | 36 | 00:00 | 171 | Sunamganj | 63 | 23:00
40 | Chhatak | 43 | 00:00 | 106 | Millgate | 55 | 10:00 | 172 | Sylhet | 50 | 21:00
41 | Chowmuhani | 238 | 22:00 | 107 | Mirpur | 86 | 00:00 | 173 | Sylhet-132 | 121 | 19:00
42 | Chuadanga | 123 | 23:00 | 108 | Mirsorai | 8 | 00:00 | 174 | TK | 40 | 00:00
43 | Coxsbazar | 136 | 22:00 | 109 | Mirzapur | 37 | 00:00 | 175 | Tangail | 168 | 13:00
44 | Cumilla(N) | 169 | 22:00 | 110 | Mithapukur | 68 | 23:00 | 176 | Thakurgaon | 119 | 22:00
45 | Cumilla(S) | 152 | 23:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 77 | 13:00
46 | Daudkandi | 142 | 22:00 | 112 | Mogbazar | 85.6 | 19:00 | 178 | Ullahpara | 40 | 19:30
47 | Dhaka | 22 | 13:00 | 113 | Mongla | 22 | 00:00 | 179 | Ullon | 34 | 00:00
48 | Dhamrai | 76 | 23:00 | 114 | Motijheel | 25 | 19:30 | 180 | Uttara | 50 | 15:00
49 | Dhanmondi | 73 | 19:00 | 115 | Muktagacha | 40 | 23:00 | 181 | UttaraNew | 76 | 09:00
50 | Dohazari | 109 | 23:00 | 116 | Munshiganj | 120 | 23:00 | 182 | Zigatola | 55 | 00:00
51 | Faridpur | 162 | 22:00 | 117 | Muradnagar | 36 | 21:00
52 | Fatullah | 46 | 22:00 | 118 | Mymensingh | 198 | 23:00
53 | Fenchuganj | 40 | 19:30 | 119 | Naogaon | 143 | 23:00
54 | Feni | 130 | 23:00 | 120 | Narail | 61 | 20:00
55 | GPH | 1 | 00:00 | 121 | Narinda | 45 | 19:00
56 | Ghatail | 80 | 23:00 | 122 | Narshingdi | 156 | 23:00
57 | Ghorashal | 13 | 14:00 | 123 | Natore | 156 | 22:00
58 | Ghorashal-230 | 62 | 22:00 | 124 | Nawabganj | 66.2 | 22:00
59 | Goalpara | 40 | 00:00 | 125 | Netrakona | 141 | 23:00
60 | Gollamari | 84 | 00:00 | 126 | New | 35.4 | 00:00
61 | Gopalganj | 119 | 23:00 | 127 | Niamatpur | 86 | 22:00
62 | Gulshan | 66 | 19:00 | 128 | Noapara | 45 | 23:00
63 | Halishahar | 32 | 19:00 | 129 | PHP | 2 | 00:00
64 | HaripurSBU | 56 | 23:00 | 130 | Pabna | 123 | 21:00
65 | Hasnabad | 55 | 23:00 | 131 | Palashbari | 126 | 21:00
66 | Hathazari | 89 | 20:00 | 132 | Panchagarh | 62 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 08-06-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13044.7 | 0 |  | 13044.7
1:00 | 12665.5 | 0 |  | 12665.5
2:00 | 12378.5 | 0 |  | 12378.5
3:00 | 12015 | 0 |  | 12015
4:00 | 11677 | 0 |  | 11677
5:00 | 11400.5 | 0 |  | 11400.5
6:00 | 10830.04 | 0 |  | 10830.04
7:00 | 10833.11 | 0 |  | 10833.11
8:00 | 10722.05 | 0 |  | 10722.05
9:00 | 10839.84 | 0 |  | 10839.84
10:00 | 10847.71 | 0 |  | 10847.71
11:00 | 10842.9 | 0 |  | 10842.9
12:00 | 10612.07 | 0 |  | 10612.07
13:00 | 11566.17 | 0 |  | 11566.17
14:00 | 12130.94 | 0 |  | 12130.94
15:00 | 12102.79 | 0 |  | 12102.79
16:00 | 11862.32 | 0 |  | 11862.32
17:00 | 11273.97 | 0 |  | 11273.97
18:00 | 10541.08 | 0 |  | 10541.08
19:00 | 11850.45 | 0 |  | 11850.45
19:30 | 12729.46 | 0 |  | 12729.46
20:00 | 12845.75 | 0 |  | 12845.75
21:00 | 13223.2 | 0 |  | 13223.2
22:00 | 13346.2 | 0 |  | 13346.2
23:00 | 13497.2 | 0 |  | 13497.2
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 08-06-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8479.7 | 4565 | 13044.7 | DAILY GENERATION CURVE
00:30 | 8386.1 | 4469 | 12855.1
01:00 | 8292.5 | 4373 | 12665.5 | 08-06-2025
01:30 | 8226 | 4296 | 12522
02:00 | 8159.5 | 4219 | 12378.5
02:30 | 8083.25 | 4113.5 | 12196.75
03:00 | 8007 | 4008 | 12015
03:30 | 7838 | 4008 | 11846
04:00 | 7669 | 4008 | 11677
04:30 | 7657.25 | 3881.5 | 11538.75
05:00 | 7645.5 | 3755 | 11400.5
05:30 | 7513.195 | 3602.075 | 11115.27
06:00 | 7380.89 | 3449.15 | 10830.04
06:30 | 7345.905 | 3485.67 | 10831.575
07:00 | 7310.92 | 3522.19 | 10833.11
07:30 | 7185.64 | 3591.94 | 10777.58
08:00 | 7060.36 | 3661.69 | 10722.05
08:30 | 7085.285 | 3695.66 | 10780.945
09:00 | 7110.21 | 3729.63 | 10839.84
09:30 | 7097.16 | 3746.615 | 10843.775
10:00 | 7084.11 | 3763.6 | 10847.71
10:30 | 7071.2 | 3774.105 | 10845.305
11:00 | 7058.29 | 3784.61 | 10842.9
11:30 | 6829.12 | 3898.365 | 10727.485
12:00 | 6599.95 | 4012.12 | 10612.07
12:30 | 6849.615 | 4239.505 | 11089.12
13:00 | 7099.28 | 4466.89 | 11566.17
13:30 | 7194.755 | 4653.8 | 11848.555
14:00 | 7290.23 | 4840.71 | 12130.94
14:30 | 7278.07 | 4838.795 | 12116.865
15:00 | 7265.91 | 4836.88 | 12102.79
15:30 | 7242.27 | 4740.285 | 11982.555
16:00 | 7218.63 | 4643.69 | 11862.32
16:30 | 7091.13 | 4477.015 | 11568.145
17:00 | 6963.63 | 4310.34 | 11273.97
17:30 | 6753.675 | 4153.85 | 10907.525
18:00 | 6543.72 | 3997.36 | 10541.08
18:30 | 7017.36 | 4178.405 | 11195.765
19:00 | 7491 | 4359.45 | 11850.45
19:30 | 7911.2 | 4818.26 | 12729.46
20:00 | 7926.2 | 4919.55 | 12845.75
20:30 | 8032.2 | 5002.275 | 13034.475 |  | Executive Engineer
21:00 | 8138.2 | 5085 | 13223.2 |  | Network Operation Division
21:30 | 8157.2 | 5127.5 | 13284.7
22:00 | 8176.2 | 5170 | 13346.2
22:30 | 8222.7 | 5199 | 13421.7
23:00 | 8269.2 | 5228 | 13497.2

## En-Curve
QF-LDC-12
Date | 08-06-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4694 | 3760.5 | 861 | 0 | 38 | 470 | 167 | 2053 | 0 | 148 | 853.2 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 4581.5 | 3749.5 | 861 | 0 | 37 | 466 | 167 | 2034 | 0 | 139 | 820.1 | 0 | 0 | 0 | 0 | 08-06-2025
01:00 | 4469 | 3738.5 | 861 | 0 | 36 | 462 | 167 | 2015 | 0 | 130 | 787 | 0 | 0 | 0 | 0
01:30 | 4404 | 3719 | 860.5 | 0 | 37 | 439.5 | 167 | 1995.5 | 0 | 121.5 | 778 | 0 | 0 | 0 | 0 | Energy Generated | 286.1473 |  | MKWHr
02:00 | 4339 | 3699.5 | 860 | 0 | 38 | 417 | 167 | 1976 | 0 | 113 | 769 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 4281 | 3694.25 | 860.5 | 0 | 37.5 | 415.5 | 167 | 1923 | 0 | 113 | 705 | 0 | 0 | 0 | 0 | Total Energy Requirement | 286.1473 |  | MKWHr
03:00 | 4223 | 3689 | 861 | 0 | 37 | 414 | 167 | 1870 | 0 | 113 | 641 | 0 | 0 | 0 | 0
03:30 | 4186 | 3629 | 861 | 0 | 35.5 | 414.5 | 167 | 1825 | 0 | 109.5 | 618.5 | 0 | 0 | 0 | 0
04:00 | 4149 | 3569 | 861 | 0 | 34 | 415 | 167 | 1780 | 0 | 106 | 596 | 0 | 0 | 0 | 0
04:30 | 4152 | 3563.25 | 751 | 0 | 34 | 418 | 167 | 1757.5 | 0 | 106 | 590 | 0 | 0 | 0 | 0
05:00 | 4155 | 3557.5 | 641 | 0 | 34 | 421 | 167 | 1735 | 0 | 106 | 584 | 0 | 0 | 0 | 0
05:30 | 4098 | 3516.5 | 514 | 0 | 32 | 420 | 167 | 1732 | 20.27 | 88.5 | 527 | 0 | 0 | 0 | 0
06:00 | 4041 | 3475.5 | 387 | 0 | 30 | 419 | 167 | 1729 | 40.54 | 71 | 470 | 0 | 0 | 0 | 0
06:30 | 4049 | 3460.5 | 386.5 | 0 | 30 | 420.5 | 167 | 1717 | 94.075 | 54.5 | 452.5 | 0 | 0 | 0 | 0
07:00 | 4057 | 3445.5 | 386 | 0 | 30 | 422 | 167 | 1705 | 147.61 | 38 | 435 | 0 | 0 | 0 | 0
07:30 | 4058 | 3319 | 389 | 0 | 30 | 423.51 | 167 | 1708 | 227.57 | 38 | 417.5 | 0 | 0 | 0 | 0
08:00 | 4059 | 3192.5 | 392 | 0 | 30 | 425.02 | 167 | 1711 | 307.53 | 38 | 400 | 0 | 0 | 0 | 0
08:30 | 4053.5 | 3186.5 | 392 | 0 | 30 | 424.525 | 167 | 1710.5 | 367.92 | 38 | 411 | 0 | 0 | 0 | 0
09:00 | 4048 | 3180.5 | 392 | 0 | 30 | 424.03 | 167 | 1710 | 428.31 | 38 | 422 | 0 | 0 | 0 | 0
09:30 | 4024 | 3180 | 397 | 0 | 30 | 422.215 | 167 | 1713 | 451.56 | 37.5 | 421.5 | 0 | 0 | 0 | 0
10:00 | 4000 | 3179.5 | 402 | 0 | 30 | 420.4 | 167 | 1716 | 474.81 | 37 | 421 | 0 | 0 | 0 | 0
10:30 | 4003 | 3162.75 | 402 | 0 | 30 | 421.955 | 167 | 1717.5 | 499.1 | 37 | 405 | 0 | 0 | 0 | 0
11:00 | 4006 | 3146 | 402 | 0 | 30 | 423.51 | 167 | 1719 | 523.39 | 37 | 389 | 0 | 0 | 0 | 0
11:30 | 4021 | 2979 | 480.5 | 0 | 31 | 423.435 | 167 | 1716 | 490.55 | 37 | 382 | 0 | 0 | 0 | 0
12:00 | 4036 | 2812 | 559 | 0 | 32 | 423.36 | 167 | 1713 | 457.71 | 37 | 375 | 0 | 0 | 0 | 0
12:30 | 4119 | 2962.5 | 717.5 | 0 | 33 | 428.61 | 147 | 1801.5 | 455.01 | 38 | 384 | 0 | 0 | 3 | 0
13:00 | 4202 | 3113 | 876 | 0 | 34 | 433.86 | 127 | 1890 | 452.31 | 39 | 393 | 0 | 0 | 6 | 0
13:30 | 4179 | 3134.5 | 876 | 0 | 34 | 473.71 | 147 | 2075.5 | 447.345 | 48.5 | 426 | 0 | 0 | 7 | 0
14:00 | 4156 | 3156 | 876 | 0 | 34 | 513.56 | 167 | 2261 | 442.38 | 58 | 459 | 0 | 0 | 8 | 0
14:30 | 4098.5 | 3156 | 893 | 0 | 34 | 516.615 | 167 | 2258.5 | 436.15 | 54 | 496.1 | 0 | 0 | 7 | 0
15:00 | 4041 | 3156 | 910 | 0 | 34 | 519.67 | 167 | 2256 | 429.92 | 50 | 533.2 | 0 | 0 | 6 | 0
15:30 | 4100.5 | 3093.5 | 913.5 | 0 | 33 | 518.17 | 167 | 2182 | 380.685 | 50 | 537.2 | 0 | 0 | 7 | 0
16:00 | 4160 | 3031 | 917 | 0 | 32 | 516.67 | 167 | 2108 | 331.45 | 50 | 541.2 | 0 | 0 | 8 | 0
16:30 | 4153 | 2924.5 | 917 | 0 | 32 | 466.115 | 167 | 2097 | 240.43 | 50 | 514.6 | 0 | 0 | 6.5 | 0
17:00 | 4146 | 2818 | 917 | 0 | 32 | 415.56 | 167 | 2086 | 149.41 | 50 | 488 | 0 | 0 | 5 | 0
17:30 | 4029 | 2681.5 | 917 | 0 | 31 | 416.465 | 167 | 2045.5 | 94.56 | 50 | 471.5 | 0 | 0 | 4 | 0
18:00 | 3912 | 2545 | 917 | 0 | 30 | 417.37 | 167 | 2005 | 39.71 | 50 | 455 | 0 | 0 | 3 | 0
18:30 | 4131 | 2821 | 893 | 0 | 34 | 455.41 | 167 | 2069 | 19.855 | 77.5 | 526.5 | 0 | 0 | 1.5 | 0
19:00 | 4350 | 3097 | 869 | 0 | 38 | 493.45 | 167 | 2133 | 0 | 105 | 598 | 0 | 0 | 0 | 0
19:30 | 4403 | 3219 | 869 | 0 | 34 | 583.26 | 167 | 2447 | 0 | 130 | 877.2 | 0 | 0 | 0 | 0
20:00 | 4426 | 3267 | 869 | 0 | 36 | 610.55 | 167 | 2458 | 0 | 128 | 884.2 | 0 | 0 | 0 | 0
20:30 | 4483.5 | 3292 | 893 | 0 | 36 | 612.775 | 167 | 2521 | 0 | 137 | 892.2 | 0 | 0 | 0 | 0
21:00 | 4541 | 3317 | 917 | 0 | 36 | 615 | 167 | 2584 | 0 | 146 | 900.2 | 0 | 0 | 0 | 0
21:30 | 4522.5 | 3347.5 | 916.5 | 0 | 31 | 647 | 167 | 2604 | 0 | 146 | 903.2 | 0 | 0 | 0 | 0
22:00 | 4504 | 3378 | 916 | 0 | 26 | 679 | 167 | 2624 | 0 | 146 | 906.2 | 0 | 0 | 0 | 0
22:30 | 4538.5 | 3385.5 | 916.5 | 0 | 32 | 672.5 | 167 | 2655.5 | 0 | 154 | 900.2 | 0 | 0 | 0 | 0
23:00 | 4573 | 3393 | 917 | 0 | 38 | 666 | 167 | 2687 | 0 | 162 | 894.2 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 08-06-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 400 | 10:00 | 390 | 23:00 | Payra | 417 | 18:00 | 410 | 19:30
Ashuganj | 410 | 6:00 | 409 | 0:00 | Rahanpur | 409 | 18:30 | 393 | 22:00
Bhulta | 414 | 05:00 | 404 | 23:00 | Rampal | 405 | 09:00 | 393 | 00:00
Bibiana | 395 | 18:00 | 387 | 22:00
BIPTC | 408 | 08:00 | 385 | 23:00
Bogura | 399 | 18:00 | 382 | 22:00
Gopalganj | 406 | 09:00 | 393 | 23:00
Kaliakoir | 390 | 18:00 | 381 | 23:00
Madunaghat | 401 | 06:00 | 396 | 23:00
Meghnaghat | 404 | 07:00 | 395 | 23:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 236 | 09:00 | 230 | 23:00 | Keranigonj | 234 | 08:00 | 227 | 23:00
AKSML | 232 | 11:00 | 228 | 17:00 | Khulna(S) | 232 | 09:00 | 218 | 21:00
Aminbazar | 236 | 07:00 | 230 | 23:00 | Madunaghat | 233 | 11:00 | 229 | 23:00
Ashuganj | 241 | 08:00 | 235 | 23:00 | Madunaghat-400 | 234 | 06:00 | 231 | 00:00
Ashuganj-400 | 241 | 08:00 | 235 | 23:00 | Maniknagar | 232 | 03:00 | 225 | 23:00
Baghabari | 235 | 08:00 | 224 | 05:00 | Meghnaghat | 240 | 05:00 | 235 | 21:00
Barapukuria | 223 | 18:00 | 215 | 22:00 | Meghnaghat-400 | 234 | 05:00 | 229 | 23:00
Barapukuria-230 | 223 | 18:00 | 215 | 22:00 | Mirsorai | 233 | 08:00 | 225 | 23:00
Barishal | 240 | 09:00 | 231 | 00:00 | Rajshahi | 235 | 05:00 | 221 | 22:00
Bheramara | 235 | 05:00 | 221 | 21:00 | Rampal | 232 | 18:30 | 218 | 23:00
Bhulta | 241 | 05:00 | 228 | 13:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 231 | 11:00 | 221 | 14:00 | Rampura | 241 | 06:00 | 234 | 23:00
BIPTC | 236 | 05:00 | 222 | 21:00 | Shikalbaha | 231 | 11:00 | 227 | 13:00
Bogura | 234 | 18:30 | 223 | 22:00 | Shyampur | 233 | 06:00 | 228 | 23:00
Bogura-400 | 233 | 18:30 | 222 | 22:00 | Siddhirganj | 234 | 05:00 | 228 | 23:00
Borhanuddin | 243 | 18:30 | 237 | 00:00 | Sirajgonj | 241 | 08:00 | 234 | 00:00
BSRM | 233 | 06:00 | 225 | 23:00 | Sreepur | 234 | 18:30 | 227 | 00:00
Cumilla(N) | 229 | 04:00 | 224 | 23:00 | Tongi | 241 | 18:00 | 228 | 15:00
Faridpur | 238 | 18:00 | 227 | 23:00
Fenchuganj | 233 | 18:00 | 226 | 03:00
Ghorashal | 240 | 01:00 | 240 | 01:00
Ghorashal-230 | 240 | 4:00 | 233 | 00:00
Gopalganj | 240 | 18:00 | 230 | 23:00
GPH | 232 | 05:00 | 227 | 23:00
Haripur | 232 | 06:00 | 227 | 23:00
Hasnabad | 235 | 07:00 | 229 | 13:00
Hathazari | 233 | 04:00 | 229 | 23:00
Ishurdi | 236 | 05:00 | 224 | 21:00
Jhenaidah | 230 | 09:00 | 216 | 21:00
Kaliakoir | 243 | 08:00 | 237 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 05:00 | 130 | 00:00 | Madartek | 134 | 08:00 | 130 | 23:00
Agargaon | 136 | 06:00 | 132 | 23:00 | Madunaghat | 132 | 18:00 | 129 | 13:00
Agrabad | 132 | 09:00 | 129 | 13:00 | Magura | 134 | 08:00 | 121 | 23:00
AKS | 131 | 01:00 | 127 | 13:00 | Mahasthangarh | 134 | 18:00 | 125 | 00:00
Aminbazar | 134 | 05:00 | 131 | 00:00 | Manikganj | 134 | 10:00 | 128 | 23:00
Amnura | 135 | 05:00 | 124 | 22:00 | Maniknagar | 132 | 04:00 | 128 | 23:00
Ashuganj | 140 | 04:00 | 136 | 23:00 | Matarbari | 117 | 12:00 | 109 | 13:00
Bagerhat | 132 | 10:00 | 117 | 23:00 | Matuail | 136.5 | 06:00 | 133 | 23:00
Bajitpur | 134 | 06:00 | 127 | 23:00 | Millgate | 136 | 04:00 | 132 | 00:00
Bakulia | 138 | 13:00 | 129 | 23:00 | Mirpur | 134 | 08:00 | 129 | 23:00
Banani | 135 | 06:00 | 130 | 00:00 | Mirzapur | 133 | 17:00 | 127 | 00:00
Bangabhaban | 132 | 03:00 | 128 | 23:00 | Mithapukur | 131 | 18:30 | 122 | 23:00
Barapukuria | 134 | 18:00 | 125 | 23:00 | MI_Cement | 137 | 08:00 | 134 | 00:00
Barguna | 134 | 11:00 | 128 | 23:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 132 | 09:00 | 125 | 00:00 | Mogbazar | 135 | 05:00 | 131 | 12:00
Barishal-230 | 133 | 11:00 | 126 | 00:00 | Mongla | 132 | 09:00 | 119 | 00:00
Baroaulia | 135 | 18:30 | 130 | 23:00 | Motijheel | 132 | 03:00 | 128 | 23:00
Baroirhat | 124 | 08:00 | 119 | 22:00 | Muktagacha | 127 | 16:00 | 121 | 06:00
Bashundhara | 136 | 07:00 | 131 | 00:00 | Munshiganj | 133 | 05:00 | 129 | 23:00
BashundharaCement | 136 | 04:00 | 132 | 23:00 | Muradnagar | 128 | 07:00 | 122 | 23:00
Beanibazar | 128 | 06:00 | 122 | 22:00 | Mymensingh | 128 | 16:00 | 118 | 23:00
Benapole | 131 | 18:00 | 116 | 23:00 | Naogaon | 132 | 18:00 | 120 | 23:00
Bhaluka | 133 | 18:30 | 127 | 22:00 | Narail | 134 | 09:00 | 120 | 01:00
Bhandaria | 128 | 13:00 | 115 | 00:00 | Narinda | 0 | 00:00 | N/A | N/A
Bhangura | 134 | 09:00 | 127 | 22:00 | Narshingdi | 143 | 18:00 | 125 | 23:00
Bheramara | 138 | 08:00 | 132 | 21:00 | Natore | 134 | 08:00 | 126 | 21:00
Bheramara(GK) | 139 | 18:00 | 132 | 00:00 | Nawabganj | 135 | 06:00 | 130 | 23:00
Bhulta | 132 | 10:00 | 126 | 16:00 | Netrakona | 126 | 07:00 | 116 | 22:00
Bog-Sherpur | 135 | 09:00 | 126 | 23:00 | New | 137 | 05:00 | 133 | 00:00
Bogura | 136 | 09:00 | 127 | 23:00 | Niamatpur | 136 | 10:00 | 130 | 00:00
Bogura-230 | 137 | 11:00 | 129 | 22:00 | Noapara | 135 | 18:30 | 122 | 00:00
Brahmanbaria | 134 | 11:00 | 130 | 00:00 | Pabna | 135 | 08:00 | 127 | 21:00
Cantonment | 136 | 06:00 | 132 | 13:00 | Palashbari | 129 | 18:30 | 118 | 23:00
Chandina | 130 | 18:00 | 125 | 23:00 | Panchagarh | 133 | 18:00 | 120 | 13:00
Chandpur | 126 | 00:00 | 119 | 14:00 | Patuakhali | 134 | 10:00 | 129 | 23:00
Chandraghona | 133 | 06:00 | 130 | 23:00 | Payra | 137 | 10:00 | 132 | 22:00
Chapai | 133 | 10:00 | 126 | 21:00 | PHP | 125 | 02:00 | 117 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 136 | 03:00 | 134 | 14:00 | Postogola | 138 | 06:00 | 134 | 23:00
Chauddagram | 124 | 01:00 | 119 | 13:00 | Purbachal | 135 | 07:00 | 130 | 21:00
Chhatak | 126 | 08:00 | 119 | 14:00 | Purbasadipur | 128 | 18:30 | 116 | 13:00
Chowmuhani | 117 | 02:00 | 108 | 15:00 | Rahanpur | 137 | 18:30 | 130 | 22:00
Chuadanga | 132 | 09:00 | 118 | 21:00 | Rahanpur-400 | 136 | 09:00 | 130 | 22:00
Coxsbazar | 118 | 18:00 | 109 | 23:00 | Rahim | 136 | 06:00 | 133 | 21:00
Cumilla(N) | 130 | 18:00 | 125 | 23:00 | Rajbari | 138 | 18:00 | 130 | 00:00
Cumilla(S) | 133 | 04:00 | 123 | 13:00 | Rajendrapur | 140 | 18:00 | 130 | 00:00
Daudkandi | 127 | 09:00 | 120 | 14:00 | Rajshahi | 134 | 05:00 | 127 | 22:00
Dhaka | 135 | 06:00 | 131 | 00:00 | Rajshahi-230 | 135 | 08:00 | 118 | 22:00
Dhamrai | 138 | 08:00 | 132 | 00:00 | Ramganj | 119 | 00:00 | 111 | 14:00
Dhanmondi | 137 | 03:00 | 133.5 | 23:00 | Rampur | 132 | 06:00 | 129 | 23:00
Dohazari | 126 | 05:00 | 122 | 13:00 | Rampura | 134 | 04:00 | 130 | 13:00
Faridpur | 138 | 05:00 | 131 | 23:00 | Rangamati | 132 | 18:00 | 129 | 00:00
Fatullah | 135 | 06:00 | 123 | 20:00 | Rangpur | 128 | 19:00 | 120 | 13:00
Fenchuganj | 137 | 01:00 | 132 | 23:00 | Ruppur | 138 | 09:00 | 131 | 21:00
Feni | 122 | 08:00 | 116 | 13:00 | Saidpur | 129 | 18:00 | 121 | 00:00
Ghatail | 127 | 17:00 | 120 | 00:00 | Satkhira | 132 | 18:00 | 116 | 23:00
Ghorashal | 143 | 18:00 | 139 | 01:00 | Satmasjid | 136 | 08:00 | 132 | 21:00
Goalpara | 137 | 18:00 | 125 | 23:00 | Savar | 132 | 04:00 | 129 | 00:00
Gollamari | 138 | 18:00 | 127 | 23:00 | SevenRings | 143 | 06:00 | 139 | 00:00
Gopalganj | 137 | 09:00 | 127 | 00:00 | ShahCement | 136 | 03:00 | 134 | 14:00
Gopalganj-400 | 139 | 09:00 | 133 | 00:00 | Shahjadpur | 136 | 03:00 | 132 | 22:00
Gulshan | 134 | 05:00 | 130 | 00:00 | Shahjibazar | 133 | 11:00 | 129 | 02:00
Halishahar | 133 | 05:00 | 130 | 13:00 | Shahmirpur | 132 | 04:00 | 129 | 13:00
Haripur | 136 | 02:00 | 133 | 23:00 | Shariatpur | 135 | 10:00 | 127 | 23:00
HaripurSBU | 136 | 11:00 | 130 | 09:00 | Sherpur | 120 | 09:00 | 112 | 06:00
Hasnabad | 138 | 09:00 | 134 | 23:00 | Shikalbaha | 122 | 18:00 | 118 | 06:00
Hathazari | 135 | 03:00 | 131 | 23:00 | Shikalbaha-230 | 134 | 18:30 | 130 | 13:00
Ishurdi | 139 | 09:00 | 132 | 21:00 | Shitalakhya | 137 | 08:00 | 134 | 00:00
Jaldhaka | 127 | 18:30 | 116 | 13:00 | Sholosohor | 133 | 12:00 | 128 | 23:00
Jamalpur | 123 | 09:00 | 115 | 08:00 | Shyampur | 135 | 00:00 | 132 | 22:00
Jashore | 134 | 18:00 | 119 | 21:00 | Shyampur-230 | 135 | 05:00 | 131 | 23:00
Jhenaidah | 136 | 09:00 | 121 | 00:00 | Siddhirganj | 137 | 03:00 | 133 | 21:00
Jhenaidah-230 | 136 | 09:00 | 125 | 23:00 | Sirajganj | 134 | 10:00 | 124 | 23:00
Joydebpur | 144 | 18:30 | 139 | 00:00 | Sonargaon | 135 | 07:00 | 133 | 00:00
Joypurhat | 131 | 18:30 | 117 | 23:00 | Sreemongol | 133 | 09:00 | 129 | 00:00
Juldah | 132 | 02:00 | 129 | 13:00 | Sreepur | 136 | 18:30 | 130 | 23:00
Kabirpur | 137 | 18:00 | 130 | 02:00 | Srinagar | 136 | 09:00 | 131 | 22:00
Kachua | 124 | 02:00 | 119 | 14:00 | SSM | 138 | 08:00 | 132 | 03:00
Kaliakoir | 139 | 08:00 | 134 | 00:00 | Sunamganj | 127 | 18:00 | 117 | 23:00
Kallyanpur | 134 | 04:00 | 130 | 23:00 | Sylhet | 130 | 08:00 | 125 | 14:00
Kalurghat | 131 | 05:00 | 129 | 23:00 | Sylhet-132 | 130 | 09:00 | 125 | 15:00
Kamrangirchar | 136 | 03:00 | 131 | 23:00 | Tangail | 129 | 17:00 | 121 | 00:00
Kaptai | 135 | 2:00 | 133 | 23:00 | Thakurgaon | 130 | 18:00 | 116 | 13:00
Kasba | 128 | 18:30 | 123 | 01:00 | TK | 131 | 05:00 | 128 | 23:00
Kazla | 132 | 06:00 | 128 | 23:00 | Tongi | 138 | 07:00 | 135 | 00:00
Keranigonj | 136 | 06:00 | 131 | 23:00 | Ullahpara | 135 | 09:00 | 127 | 23:00
Khagrachori | 131 | 09:00 | 128 | 13:00 | Ullon | 134 | 05:00 | 130 | 21:00
Khulna | 137 | 18:30 | 125 | 00:00 | Uttara | 134 | 06:00 | 130 | 22:00
Khulna(S) | 138 | 18:00 | 127 | 23:00 | UttaraNew | 133 | 07:00 | 129 | 23:00
Khulshi | 132 | 04:00 | 129 | 13:00 | Zigatola | 137 | 08:00 | 132 | 23:00
Kishoreganj | 132 | 18:00 | 124 | 00:00
Kodda | 139 | 18:30 | 131 | 00:00
KSRM | 134 | 02:00 | 130 | 13:00
Kulaura | 135 | 07:00 | 131 | 22:00
Kurigram | 126 | 18:30 | 115 | 23:00
Kushtia | 134 | 18:00 | 127 | 22:00
Lalbag | 136 | 06:00 | 133 | 00:00
Lalmonirhat | 126 | 17:00 | 118 | 00:00
Madanganj | 136 | 03:00 | 132 | 23:00
Madaripur | 136 | 10:00 | 130 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division