## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 09-06-2025 | [28 empty] | Date: | 09-06-2025 | [28 empty] | Date: | 09-06-2025 | [28 empty] | Date: | 09-06-2025 | [28 empty] | Date: | 09-06-2025 | [12 empty] | Date: | 09-06-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [12 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 200 | 0 | 120 | 0 | 85 | 371 | 0 | 746 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 147 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 7 | 0 | 460 | 0 | 0 | 0 | 80 | 0 | 50 | 0 | 0 | 48 | 18 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 217 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 187 | 0 | 344 | 340 | 52 | 214 | 17 | 115 | 50 | 170 | 21 | 13 | 114 | 40 | 52.2 | 0 | 43 | 320 | 320 | 391 | 32 | 30 | 153 | 0 | 0 | 81 | 30 | 0 | 0 | 0 | 0 | 45 | 85 | 156 | 0 | 0 | 0 | 8118.2 | 916 | 387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 482 | 0 | 676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 199 | 0 | 198 | 0 | 414 | 0 | 0 | 201 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 1040 | 0 | 5316 | 13434.2 | 95.58
01:00 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 85 | 366 | 0 | 750 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 145 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 15.5 | 7 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 64 | 24 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 217 | 0 | 0 | 0 | 970 | 0 | 51 | 0 | 189 | 0 | 350 | 340 | 50 | 216 | 17 | 115 | 50 | 170 | 9 | 13 | 114 | 40 | 52.2 | 0 | 43 | 320 | 320 | 380 | 32 | 30 | 153 | 0 | 0 | 81 | 30 | 0 | 0 | 0 | 0 | 45 | 85 | 157 | 0 | 0 | 0 | 7891.7 | 916 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 477 | 0 | 746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 197 | 0 | 196 | 0 | 414 | 0 | 0 | 190 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 1113 | 0 | 5410 | 13301.7 | 95.58
02:00 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 83 | 345 | 0 | 750 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 142 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 15.5 | 7 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 84 | 24 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 218 | 0 | 0 | 0 | 855 | 0 | 51 | 0 | 185 | 0 | 351 | 340 | 48 | 215 | 17 | 115 | 50 | 170 | 9 | 13 | 114 | 40 | 52.2 | 0 | 43 | 310 | 320 | 352 | 32 | 30 | 149 | 0 | 0 | 81 | 30 | 0 | 0 | 0 | 0 | 45 | 85 | 157 | 0 | 0 | 0 | 7723.7 | 917 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 478 | 0 | 756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 188 | 0 | 187 | 0 | 396 | 0 | 0 | 190 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 1150 | 0 | 5400 | 13123.7 | 95.58
03:00 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 83 | 335 | 0 | 758 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 136 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 15.5 | 7 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 84 | 24 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 218 | 0 | 0 | 0 | 762 | 0 | 51 | 0 | 189 | 0 | 350 | 340 | 50 | 214 | 17 | 115 | 50 | 170 | 9 | 13 | 114 | 40 | 52.2 | 0 | 42 | 310 | 320 | 385 | 32 | 30 | 148 | 0 | 0 | 81 | 30 | 0 | 0 | 0 | 0 | 45 | 85 | 157 | 0 | 0 | 0 | 7657.7 | 917 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 0 | 724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 182 | 0 | 182 | 0 | 401 | 0 | 0 | 190 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 1000 | 0 | 5177 | 12834.7 | 95.58
04:00 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 83 | 357 | 0 | 758 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 137 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 15.5 | 7 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 84 | 24 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 220 | 0 | 0 | 0 | 785 | 0 | 51 | 0 | 189 | 0 | 350 | 340 | 50 | 216 | 17 | 115 | 50 | 170 | 9 | 13 | 114 | 38 | 52.2 | 0 | 42 | 315 | 320 | 382 | 32 | 30 | 120 | 0 | 0 | 20 | 30 | 0 | 0 | 0 | 0 | 45 | 85 | 157 | 0 | 0 | 0 | 7618.7 | 916 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 193 | 0 | 192 | 0 | 355 | 0 | 0 | 190 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 120 | 220 | 0 | 0 | 900 | 0 | 4928 | 12546.7 | 95.58
05:00 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 80 | 362 | 0 | 754 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 135 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 15.5 | 7 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 84 | 12 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 221 | 0 | 0 | 0 | 734 | 0 | 51 | 0 | 189 | 0 | 353 | 340 | 51 | 217 | 17 | 115 | 50 | 170 | 9 | 0 | 114 | 34 | 52.2 | 0 | 42 | 315 | 320 | 360 | 32 | 30 | 120 | 0 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 45 | 45 | 157 | 0 | 0 | 0 | 7520.7 | 916 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 194 | 0 | 194 | 0 | 337 | 0 | 0 | 190 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 110 | 220 | 0 | 0 | 760 | 0 | 4754 | 12274.7 | 95.59
06:00 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 76 | 346 | 0 | 753 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 137 | 400 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 15.5 | 7 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 12 | 12 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 780 | 2 | 51 | 0 | 189 | 0 | 352 | 320 | 48 | 200 | 17 | 115 | 50 | 136 | 9 | 14 | 114 | 34 | 0 | 7 | 42 | 305 | 320 | 390 | 32 | 30 | 120 | 0 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 35 | 45 | 157 | 0 | 4.33 | 0 | 7276.83 | 910 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.87 | 366 | 0 | 494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 2.74 | 164 | 0 | 187 | 0 | 187 | 0 | 353 | 0 | 0.28 | 200 | 50 | 50 | 2 | 113 | 0 | 0 | 0.5 | 11 | 0.03 | 0 | 0 | 11 | 100 | 110 | 0 | 0 | 520 | 0 | 4210.42 | 11487.25 | 95.59
07:00 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 73 | 365 | 0 | 752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 143 | 400 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 15.5 | 7 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 12 | 12 | 1 | 167 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 800 | 5 | 51 | 0 | 187 | 0 | 347 | 300 | 49 | 201 | 17 | 115 | 51 | 136 | 9 | 14 | 114 | 30 | 0 | 19 | 42 | 310 | 320 | 386 | 32 | 30 | 120 | 0 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 24 | 45 | 155 | 1 | 11.55 | 0 | 7285.05 | 916 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.62 | 386 | 0 | 424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 10.67 | 174 | 0 | 197 | 0 | 196 | 0 | 362 | 0 | 0.96 | 200 | 50 | 35 | 5 | 92 | 0 | 0 | 1.5 | 41 | 0.12 | 0 | 0 | 11 | 100 | 110 | 0 | 0 | 500 | 0 | 4227.87 | 11512.92 | 95.59
08:00 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 73 | 355 | 0 | 749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 142 | 400 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 15.5 | 7 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 12 | 12 | 2 | 167 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 752 | 10 | 51 | 0 | 187 | 0 | 300 | 300 | 49 | 189 | 17 | 115 | 50 | 136 | 9 | 14 | 114 | 30 | 0 | 39 | 8 | 310 | 320 | 363 | 32 | 30 | 120 | 0 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 24 | 45 | 155 | 1 | 23.91 | 0 | 7152.41 | 921 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.8 | 363 | 0 | 415.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 22.69 | 170 | 0 | 189 | 0 | 187 | 0 | 336 | 0 | 2.03 | 201 | 50 | 35 | 13 | 92 | 0 | 0 | 3.1 | 92 | 0.33 | 0 | 0 | 9 | 94 | 110 | 0 | 0 | 500 | 0 | 4250.21 | 11402.62 | 95.59
09:00 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 73 | 339 | 0 | 750 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 140 | 400 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 17 | 7 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 3 | 167 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 770 | 14 | 51 | 0 | 187 | 0 | 300 | 300 | 49 | 192 | 17 | 115 | 50 | 136 | 9 | 14 | 114 | 32 | 0 | 29 | 8 | 305 | 320 | 360 | 32 | 30 | 128 | 0 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 24 | 45 | 152 | 2 | 34.68 | 0 | 7002.68 | 931 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.55 | 360 | 0 | 416.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 32.99 | 164 | 0 | 163 | 0 | 161 | 0 | 337 | 0 | 3.21 | 200 | 49 | 35 | 20 | 39 | 0 | 0 | 4.8 | 135 | 0.45 | 0 | 0 | 11 | 96 | 110 | 0 | 0 | 500 | 0 | 4248.28 | 11250.96 | 95.59
10:00 | 0 | 0 | 24 | 20 | 0 | 0 | 0 | 70 | 337 | 0 | 747 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 142 | 400 | 0 | 0 | 0 | 0 | 0 | 26 | 17 | 17 | 7 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 4 | 167 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 780 | 18 | 51 | 0 | 187 | 0 | 300 | 300 | 48 | 192 | 17 | 115 | 50 | 136 | 9 | 14 | 114 | 30 | 0 | 65 | 8 | 310 | 320 | 308 | 32 | 30 | 128 | 0 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 24 | 45 | 152 | 2 | 43.73 | 0 | 6995.73 | 930 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.84 | 360 | 0 | 413.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 46.52 | 162 | 0 | 162 | 0 | 160 | 0 | 340 | 0 | 4.22 | 201 | 49 | 35 | 26 | 0 | 0 | 0 | 6.1 | 161 | 0.55 | 0 | 0 | 11 | 96 | 110 | 0 | 0 | 500 | 0 | 4279.85 | 11275.58 | 95.59
11:00 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 70 | 323 | 0 | 739 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 140 | 400 | 0 | 0 | 0 | 0 | 0 | 30 | 17 | 17 | 7 | 0 | 460 | 0 | 0 | 0 | 0 | 6 | 17 | 0 | 0 | 0 | 0 | 4 | 167 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 750 | 19 | 51 | 0 | 185 | 0 | 300 | 300 | 45 | 189 | 17 | 115 | 50 | 136 | 9 | 14 | 105 | 28 | 0 | 80 | 8 | 305 | 320 | 304 | 32 | 30 | 128 | 0 | 0 | 81 | 30 | 0 | 0 | 0 | 0 | 24 | 45 | 148 | 2 | 48.07 | 0 | 6918.07 | 931 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.73 | 361 | 0 | 413.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 50.91 | 150 | 0 | 161 | 0 | 159 | 0 | 334 | 0 | 4.85 | 201 | 49 | 35 | 30 | 0 | 0 | 0 | 6.1 | 163 | 0.7 | 0 | 0 | 10 | 90 | 110 | 0 | 0 | 500 | 0 | 4297.24 | 11215.31 | 95.59
12:00 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 70 | 325 | 0 | 729 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 143 | 400 | 0 | 0 | 0 | 0 | 0 | 31 | 35 | 18 | 7 | 0 | 460 | 0 | 0 | 0 | 0 | 11 | 17 | 0 | 0 | 0 | 0 | 4 | 167 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 793 | 13 | 51 | 0 | 185 | 0 | 300 | 300 | 48 | 199 | 17 | 115 | 50 | 136 | 9 | 11 | 114 | 32 | 0 | 36 | 8 | 305 | 320 | 335 | 32 | 30 | 132 | 0 | 0 | 80 | 30 | 0 | 0 | 0 | 0 | 24 | 45 | 148 | 1 | 45.42 | 0 | 6989.42 | 932 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.17 | 372 | 0 | 418.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107 | 0 | 57.52 | 156 | 0 | 167 | 0 | 165 | 0 | 355 | 0 | 4.98 | 201 | 50 | 0 | 32 | 0 | 0 | 0 | 6.7 | 191 | 0.71 | 0 | 0 | 8 | 100 | 110 | 0 | 0 | 500 | 0 | 4399.62 | 11389.04 | 95.59
13:00 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 74 | 344 | 0 | 720 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 142 | 300 | 0 | 0 | 0 | 0 | 0 | 30 | 35 | 18 | 7 | 0 | 525 | 0 | 0 | 0 | 0 | 7 | 17 | 0 | 0 | 0 | 0 | 4 | 167 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 890 | 8 | 51 | 0 | 185 | 0 | 330 | 335 | 48 | 209 | 16 | 115 | 50 | 136 | 9 | 13 | 114 | 32 | 0 | 59 | 8 | 315 | 320 | 274 | 32 | 30 | 143 | 0 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 24 | 45 | 148 | 1 | 45.8 | 0 | 7056.8 | 931 | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.76 | 420 | 0 | 450.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 52.64 | 169 | 0 | 189 | 0 | 193 | 0 | 414 | 0 | 4.84 | 203 | 49 | 0 | 20 | 0 | 0 | 0 | 3.5 | 190 | 0.7 | 0 | 0 | 8 | 120 | 110 | 0 | 0 | 529 | 0 | 4607.06 | 11663.86 | 95.59
14:00 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 76 | 340 | 0 | 727 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 144 | 250 | 0 | 0 | 0 | 0 | 0 | 27 | 52 | 19.5 | 7 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 3 | 167 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 1019 | 16 | 51 | 0 | 185 | 0 | 334 | 340 | 47 | 192 | 16 | 95 | 70 | 141 | 15 | 13 | 114 | 34 | 8 | 59 | 8 | 310 | 320 | 325 | 32 | 28 | 110 | 0 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 35 | 70 | 146 | 2 | 43.49 | 0 | 7180.99 | 932 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.36 | 471 | 0 | 559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 45.21 | 168 | 0 | 189 | 0 | 189 | 0 | 339 | 0 | 4.28 | 190 | 50 | 0 | 27 | 0 | 0 | 0 | 6 | 158 | 0.65 | 0 | 0 | 8 | 116 | 110 | 0 | 0 | 769 | 0 | 4842.5 | 12023.49 | 95.59
15:00 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 74 | 325 | 0 | 723 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 142 | 250 | 0 | 0 | 0 | 0 | 0 | 22 | 52 | 17 | 7 | 0 | 485 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 1 | 167 | 0 | 36 | 0 | 0 | 0 | 0 | 4 | 0 | 213 | 0 | 0 | 0 | 1055 | 15 | 51 | 0 | 185 | 0 | 335 | 340 | 45 | 194 | 16 | 95 | 70 | 165 | 18 | 14 | 114 | 40 | 25 | 49 | 17 | 300 | 320 | 335 | 32 | 5 | 110 | 0 | 0 | 78 | 30 | 0 | 0 | 0 | 0 | 35 | 70 | 146 | 2 | 35.12 | 0 | 7233.12 | 932 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.13 | 480 | 0 | 558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 35.38 | 164 | 0 | 162 | 0 | 162 | 0 | 345 | 0 | 3.48 | 200 | 50 | 0 | 21 | 0 | 0 | 0 | 5.1 | 142 | 0.52 | 0 | 0 | 10 | 118 | 140 | 0 | 0 | 850 | 0 | 4854.61 | 12087.73 | 95.59
16:00 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 74 | 333 | 0 | 726 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 144 | 250 | 0 | 0 | 0 | 0 | 0 | 14 | 52 | 18 | 0 | 0 | 465 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 36 | 0 | 0 | 0 | 0 | 8 | 0 | 213 | 0 | 0 | 0 | 1038 | 2 | 51 | 0 | 185 | 0 | 334 | 340 | 44 | 190 | 16 | 95 | 70 | 170 | 34 | 14 | 114 | 34 | 25 | 37 | 35 | 300 | 320 | 329 | 31 | 10 | 120 | 0 | 0 | 76 | 30 | 0 | 0 | 0 | 0 | 35 | 70 | 146 | 1 | 24.93 | 0 | 7194.93 | 932 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.14 | 480 | 0 | 559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 21.1 | 156 | 0 | 159 | 0 | 158 | 0 | 336 | 0 | 1.98 | 200 | 50 | 0 | 14 | 0 | 0 | 0 | 3.7 | 95 | 0.14 | 0 | 0 | 10 | 118 | 215 | 0 | 0 | 852 | 0 | 4797.06 | 11991.99 | 95.59
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 316 | 0 | 726 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 140 | 250 | 0 | 0 | 0 | 0 | 0 | 7 | 35 | 18 | 7 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 18 | 0 | 0 | 0 | 0 | 8 | 0 | 217 | 0 | 0 | 0 | 895 | 4 | 51 | 0 | 185 | 0 | 334 | 340 | 44 | 191 | 16 | 95 | 70 | 170 | 37 | 14 | 114 | 30 | 25 | 21 | 35 | 305 | 320 | 323 | 31 | 30 | 129 | 0 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 35 | 45 | 147 | 1 | 11.97 | 0 | 6862.97 | 932 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.72 | 444 | 0 | 566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 10.33 | 147 | 0 | 157 | 0 | 157 | 0 | 335 | 0 | 1 | 200 | 47 | 0 | 7 | 30 | 0 | 0 | 2 | 46 | 0.98 | 0 | 0 | 10 | 118 | 215 | 0 | 0 | 780 | 0 | 4587.03 | 11450 | 95.59
18:00 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 77 | 339 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 143 | 250 | 0 | 0 | 0 | 0 | 0 | 2 | 35 | 18 | 7 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 12 | 0 | 0 | 167 | 0 | 30 | 0 | 0 | 0 | 0 | 8 | 0 | 217 | 0 | 0 | 0 | 925 | 2 | 51 | 0 | 185 | 0 | 280 | 280 | 45 | 200 | 16 | 102 | 80 | 170 | 48 | 14 | 114 | 30 | 43 | 4 | 35 | 305 | 320 | 323 | 31 | 30 | 132 | 0 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 35 | 45 | 148 | 0 | 2.8 | 0 | 6545.8 | 932 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | 444 | 0 | 482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 3.47 | 148 | 0 | 158 | 0 | 158 | 0 | 404 | 0 | 0.26 | 200 | 49 | 0 | 2 | 35 | 0 | 0 | 0.6 | 12 | 0.39 | 0 | 0 | 10 | 100 | 220 | 0 | 0 | 750 | 0 | 4396.82 | 10942.62 | 95.59
19:00 | 0 | 17 | 0 | 39 | 0 | 0 | 0 | 80 | 386 | 0 | 357 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 145 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 18 | 7 | 0 | 540 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 12 | 0 | 0 | 167 | 0 | 37 | 0 | 0 | 0 | 0 | 8 | 0 | 217 | 0 | 0 | 0 | 1166 | 0 | 51 | 0 | 187 | 0 | 320 | 310 | 46 | 207 | 16 | 115 | 80 | 170 | 56 | 14 | 114 | 36 | 52.2 | 0 | 35 | 310 | 320 | 385 | 31 | 30 | 135 | 0 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 46 | 90 | 148 | 0 | 0 | 2 | 7630.2 | 885 | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 472 | 0 | 559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 165 | 0 | 166 | 0 | 403 | 0 | 0 | 200 | 50 | 70 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 760 | 0 | 4724 | 12354.2 | 95.59
19:30 | 0 | 17 | 8 | 40 | 0 | 0 | 0 | 80 | 375 | 0 | 360 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 450 | 144 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 18 | 7 | 0 | 506 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 24 | 0 | 0 | 167 | 0 | 37 | 0 | 0 | 0 | 0 | 8 | 0 | 218 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 185 | 0 | 330 | 340 | 46 | 206 | 16 | 94 | 80 | 170 | 56 | 12 | 114 | 38 | 52.2 | 0 | 35 | 325 | 320 | 376 | 32 | 30 | 145 | 0 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 81 | 125 | 149 | 0 | 0 | 4 | 7800.2 | 885 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582 | 0 | 616 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 189 | 0 | 200 | 0 | 404 | 0 | 0 | 200 | 50 | 85 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 990 | 0 | 5233 | 13033.2
20:00 | 0 | 17 | 16 | 40 | 0 | 0 | 0 | 77 | 372 | 0 | 360 | 40 | 0 | 4 | 0 | 0 | 0 | 0 | 54 | 0 | 450 | 133 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 18 | 7 | 0 | 494 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 48 | 12 | 0 | 167 | 0 | 40 | 0 | 0 | 0 | 0 | 8 | 0 | 220 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 185 | 0 | 338 | 340 | 46 | 197 | 16 | 102 | 80 | 170 | 56 | 12 | 114 | 36 | 52.2 | 0 | 35 | 315 | 320 | 376 | 32 | 30 | 150 | 0 | 0 | 79 | 30 | 0 | 0 | 0 | 11 | 81 | 128 | 150 | 0 | 0 | 4 | 7886.2 | 885 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617.1 | 0 | 720 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 188 | 0 | 195 | 0 | 402 | 0 | 0 | 200 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 1070 | 0 | 5460.1 | 13346.3 | 95.59
21:00 | 0 | 17 | 16 | 40 | 0 | 0 | 0 | 77 | 378 | 0 | 320 | 54 | 0 | 17 | 0 | 0 | 0 | 0 | 80 | 0 | 450 | 134 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 17.5 | 7 | 0 | 507 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 100 | 45 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 219 | 0 | 0 | 0 | 1109 | 0 | 51 | 0 | 185 | 0 | 338 | 340 | 48 | 201 | 16 | 95 | 80 | 170 | 56 | 9 | 114 | 26 | 52.2 | 0 | 35 | 315 | 320 | 377 | 32 | 30 | 150 | 0 | 0 | 80 | 30 | 0 | 0 | 0 | 54.5 | 94 | 139 | 151 | 0 | 0 | 9 | 8075.2 | 931 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617.1 | 0 | 753.45 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 201 | 0 | 203 | 0 | 406 | 0 | 0 | 190 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 1230 | 0 | 5774.55 | 13849.75 | 95.59
22:00 | 0 | 17 | 16 | 50 | 0 | 0 | 0 | 77 | 366 | 0 | 320 | 54 | 0 | 17 | 0 | 0 | 0 | 0 | 90 | 0 | 450 | 142 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 17 | 7 | 0 | 474 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 100 | 100 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 219 | 0 | 0 | 0 | 1090 | 0 | 51 | 0 | 185 | 0 | 344 | 340 | 48 | 199 | 17 | 95 | 80 | 170 | 57 | 8 | 114 | 38 | 52.2 | 0 | 35 | 315 | 320 | 376 | 32 | 30 | 140 | 0 | 0 | 80 | 30 | 0 | 0 | 0 | 54.5 | 102 | 136 | 152 | 0 | 0 | 7 | 8103.7 | 932 | 366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617.1 | 0 | 754.44 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204 | 0 | 203 | 0 | 207 | 0 | 407 | 0 | 0 | 190 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 1237 | 0 | 5857.54 | 13961.24 | 95.59
23:00 | 0 | 17 | 16 | 50 | 0 | 0 | 0 | 75 | 371 | 0 | 320 | 54 | 0 | 17 | 0 | 0 | 0 | 0 | 90 | 0 | 450 | 143 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 17 | 7 | 0 | 535 | 0 | 0 | 0 | 0 | 1 | 65 | 0 | 0 | 100 | 100 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 218 | 0 | 0 | 0 | 1134 | 0 | 51 | 0 | 175 | 0 | 341 | 340 | 50 | 210 | 17 | 115 | 80 | 170 | 57 | 13 | 114 | 42 | 52.2 | 0 | 35 | 310 | 320 | 386 | 32 | 30 | 143 | 0 | 0 | 81 | 30 | 0 | 0 | 0 | 54.5 | 93 | 146 | 151 | 0 | 0 | 9 | 8252.7 | 932 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 0 | 760.86 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 204 | 0 | 208 | 0 | 414 | 0 | 0 | 190 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 1237 | 0 | 5888.86 | 14141.56 | 95.59
Total KWH | 0 | 120960 | 234240 | 2096600 | 0 | 0 | 0 | 1792954.55 | 8478000 | 0 | 15211240 | 360000 | 0 | 212112 | 0 | 0 | 0 | 0 | 377280 | 0 | 8794500 | 3370880 | 9313182 | 0 | 0 | 0 | 0 | 0 | 234875 | 1143600 | 400200 | 169200 | 0 | 11563636.36 | 0 | 0 | 0 | 50000 | 25920 | 985518 | 0 | 0 | 895680 | 455040 | 26426 | 4029880 | 0 | 862080 | 6290909.09 | 0 | 0 | 0 | 127139.4 | 0 | 5198887 | 0 | 0 | 0 | 22047270 | 121230 | 1192764 | 0 | 4482909.09 | 0 | 8356000 | 7884000 | 1146720 | 4902000 | 406224 | 2637120 | 1463650 | 3855360 | 609840 | 290930 | 2759940 | 820800 | 730963 | 516245 | 675056 | 7520500 | 7679700 | 8882000 | 755000 | 635760 | 3317645 | 0 | 0 | 1837440 | 718944 | 0 | 0 | 0 | 231840 | 1135200 | 1824000 | 3541440 | 15400 | 373750 | 37440 | 186226019.49 | 22326545 | 8657280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 684000 | 11236360 | 0 | 14124029 | 0 | 0 | 0 | 417984 | 0 | 0 | 0 | 0 | 0 | 779870 | 0 | 395248 | 4117000 | 0 | 4570864 | 0 | 4595518 | 0 | 8924000 | 0 | 35940 | 4766000 | 1154182 | 1474716 | 224508 | 1651411 | 0 | 0 | 52079.28 | 1446760 | 5031 | 0 | 0 | 238618 | 2650000 | 3893470 | 0 | 0 | 20704000 | 0 | 119125413.28 | 305351432.77

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 10-06-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 09-06-2025 | during | 10-06-2025 | during | 10-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 120 | 120 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 40 | 260 | 260 | 40 | 40 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 70 | 77 | 97.7 | 97.7 | 75 | 75 | Allocation limit by Titas, instructed by DS(Gen)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 325 | 378 | 400.75 | 400.75 | 371 | 371 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 143 | 134 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 18 | 17.5 | 33 | 33 | 15 | 15 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 7 | 7 | 22 | 22 | 7 | 7 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 16 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 17 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 80 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 34 | 0 | 34 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 460 | 507 | 584 | 584 | 525 | 525 | None
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 400 | 500 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 729 | 320 | 0 | 0 | 0 | 0 | On test
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 108 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2609 | 2722.5 | 4765.9 | 4763.9 | 3864.52 | 3862.52
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 13 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 167 | 167 | 165 | 165 | 165 | 165 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 219 | 221 | 221 | 221 | 221 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 72 | 72 | 72 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 17 | 65 | 68 | 68 | 68 | 68 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 23 | 42 | 38 | 40 | 38 | 40 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4 | 0 | 4.33 | 0 | 4.33 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 45 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 793 | 1109 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 11 | 0 | 2 | 12 | 2 | 12 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 0 | 0 | 575 | 575 | 0 | 0 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1242 | 1755 | 3618.05 | 3605.72 | 3023.05 | 3010.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 199 | 201 | 221.43 | 221.43 | 205.43 | 205.43 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 300 | 338 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 300 | 340 | 340 | 340 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 17 | 16 | 46.7 | 46.7 | 17 | 17 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 48 | 48 | 55 | 55 | 52 | 52 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 185 | 185 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 8 | 35 | 47 | 47 | 35 | 35 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 80 | 163 | 163 | 50 | 50 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 136 | 170 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 32 | 26 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 9 | 17.75 | 24.5 | 13 | 13 | Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 56 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 115 | 95 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 36 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1611 | 1816.2 | 2464.43 | 2401.18 | 2285.98 | 2215.98
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 09-06-2025 | during | 10-06-2025 | during | 10-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 148 | 151 | 157.5 | 157.5 | 150 | 150 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 45 | 139 | 200 | 200 | 130 | 130 | Fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 24 | 94 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 45.42 | 0 | 49.95 | 0 | 49.95 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 9 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 263.42 | 447.5 | 601.05 | 549 | 513.55 | 461.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 32 | 32 | 32 | 32 | 32 | 32 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 132 | 150 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 80 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 25 | 25 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 335 | 377 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1264 | 1334 | 1427 | 1427 | 1322 | 1322
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 932 | 931 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 367 | 370 | 410 | 410 | 350 | 350 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 98.17 | 0 | 95 | 0 | 95 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 372 | 617.1 | 1234.2 | 1234.2 | 618 | 618 | U#1 Reserve shut down as per NLDC Communication
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3699.2 | 1769.17 | 1918.1 | 3607.2 | 3512.2 | 2931 | 2836
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 8 | 11 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 100 | 120 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 500 | 1230 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 110 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.71 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 718.71 | 1581 | 2172 | 2171 | 2120 | 2119
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Cooling System Problem
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 156 | 186 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 167 | 201 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 165 | 203 | 220 | 220 | 198 | 198 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 355 | 406 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 | 30 | 30 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 58 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.98 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 418.54 | 753.45 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 57.52 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 107 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 1431.04 | 1807.45 | 3193.47 | 3026.87 | 3086.69 | 2920.09
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 50 | 50 | 50 | 50 | 50 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 201 | 190 | 200 | 200 | 200 | 200 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.7 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 191 | 0 | 179.3 | 0 | 179.3 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 480.7 | 468 | 727.9 | 512 | 727.9 | 512
System Total |  |  |  |  | 28565.2 | 27044.055 | 11389.04 | 13849.75 | 22577 | 21968.87 | 19874.69 | 19259.81
Forecast Scenario (10-06-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13810 |  | 0 |  | 13810
|  |  |  | 1:00 | 13700 |  | 0 |  | 13700
|  |  |  | 2:00 | 13520 |  | 0 |  | 13520
|  |  |  | 3:00 | 13220 |  | 0 |  | 13220
|  |  |  | 4:00 | 12930 |  | 0 |  | 12930
|  |  |  | 5:00 | 12650 |  | 0 |  | 12650
|  |  |  | 6:00 | 11830 |  | 0 |  | 11830
|  |  |  | 7:00 | 11860 |  | 0 |  | 11860
|  |  |  | 8:00 | 11750 |  | 0 |  | 11750
|  |  |  | 9:00 | 11600 |  | 0 |  | 11600
|  |  |  | 10:00 | 11620 |  | 0 |  | 11620
|  |  |  | 11:00 | 11560 |  | 0 |  | 11560
|  |  |  | 12:00 | 11730 |  | 0 |  | 11730
|  |  |  | 13:00 | 12010 |  | 0 |  | 12010
|  |  |  | 14:00 | 12370 |  | 0 |  | 12370
|  |  |  | 15:00 | 12430 |  | 0 |  | 12430
|  |  |  | 16:00 | 12340 |  | 0 |  | 12340
|  |  |  | 17:00 | 11800 |  | 0 |  | 11800
|  |  |  | 18:00 | 11290 |  | 0 |  | 11290
|  |  |  | 18:30 | 11950 |  | 0 |  | 11950
|  |  |  | 19:00 | 12700 |  | 0 |  | 12700
|  |  |  | 19:30 | 13430 |  | 0 |  | 13430
|  |  |  | 20:00 | 13750 |  | 0 |  | 13750
|  |  |  | 21:00 | 14270 |  | 0 |  | 14270
|  |  |  | 22:00 | 14400 |  | 0 |  | 14400
|  |  |  | 23:00 | 14250 |  | 0 |  | 14250
Probable Maximum Temperature: |  |  | 35.00°C
Probable Maximum Demand at Day Peak: |  |  | 11730.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 14270.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14270.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 303.39 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:23 hrs on 10-06-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 09-06-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11389.04 | MW | 12:00 Hr. | Energy Generated |  |  | 305.3514 |  | MKWHr.
| Day Peak Demand |  |  | 11389.04 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.516 |  | MKWHr.
| Evening Peak Generation |  |  | 13849.75 | MW | 21:00 Hr. | Energy Demand |  |  | 305.8674 |  | MKWHr.
| Evening Peak Demand |  |  | 13921.75 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.2 |  | °C
| Minimum Generation of the Day |  |  | 11215.31 | MW | 11:00 Hr. | Total Gas Supplied |  |  | 1191.41 |  | MMCFD
| Maximum Generation of the Day |  |  | 14141.56 | MW | 23:00 Hr. | Production Cost per KWHr |  |  | 5.4814 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 61.1904 | 0 | 2.4482 | 0 | 0 | 0.23488 | 0 | 0 | 63.8735 | Gas | 169.9617 | Gas | 553792460.259
| Chattogram Zone |  |  | 6.111 | 28.3382 | 2.4634 | 0 | 4.0299 | 0.14766 | 0 | 0.02592 | 41.116 | Coal | 66.1987 | Coal | 453562193.07
| Cumilla Zone |  |  | 30.1252 | 0 | 11.2683 | 0 | 0 | 0.51624 | 0.8208 | 0 | 42.7305 | HFO | 22.9524 | HFO | 421410131.128
| Mymensingh Zone |  |  | 3.5414 | 0 | 3.2285 | 0 | 0 | 0.38915 | 0 | 0 | 7.1591 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 31.347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.347 | Hydro | 4.0299 | Hydro | 402988
| Khulna Zone |  |  | 8.6573 | 11.2364 | 0 | 0 | 0 | 0.684 | 22.3265 | 0 | 42.9042 | Solar | 4.9114 | Solar | 80152310.9708
| Barishal Zone |  |  | 6.7821 | 20.704 | 0 | 0 | 0 | 0.005031 | 0 | 0 | 27.4911 | Import | 37.2714 | Import | 164059680.52
| Rajshahi Zone |  |  | 22.2074 | 0 | 0.41798 | 0 | 0 | 1.2111 | 14.124 | 0 | 37.9605 | Wind | 0.02592 | Wind | 379468.8
| Rangpur Zone |  |  | 0 | 5.9202 | 3.1261 | 0 | 0 | 1.7233 | 0 | 0 | 10.7697
| Total |  |  | 169.9617 | 66.1987 | 22.9524 | 0 | 4.0299 | 4.9114 | 37.2714 | 0.02592 | 305.3514
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 553792460.259 |  | Hydro | 402988
|  |  |  | Coal | 453562193.07 |  | Solar | 80152310.9708
|  |  |  | HFO | 421410131.128 |  | Import | 164059680.52
|  |  |  | HSD | 0 |  | Wind | 379468.8
[5 empty] | Total: | 167,37,59,232 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 1963034.53 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.3265 | Peak Hr Flow | 931.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 6276218.19 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 14.124 | Peak Hr Flow | 753.45 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 364 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.8208 | Peak Hr Flow | 26.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 390 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 37.2714 | Peak Hr Flow | 1710.45 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3513
|  |  |  | Chattogram |  | 0 |  | 1345
|  |  |  | Cumilla |  | 25 |  | 1505
|  |  |  | Mymensingh |  | 0 |  | 1283
|  |  |  | Sylhet |  | 28 |  | 648
|  |  |  | Khulna |  | 0 |  | 1906
|  |  |  | Barishal |  | 0 |  | 528
|  |  |  | Rajshahi |  | 0 |  | 1568
|  |  |  | Rangpur |  | 16 |  | 1043
|  |  |  | Total |  | 69 |  | 13339
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Meghnaghat CCPP(Summit) GT-2 |  |  | 110
[7 empty] | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 599
|  |  |  | Total Unavailable Capacity |  |  |  | 899
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:20 |  | Ullon-Dhanmondi 132kV Ckt-2 was shutdown.
| 09:01 | 19:20 | Monakasha-Rahanpur 400kV Ckt-1 Scheduled S/D from Rahanpur 400/132kV end Due to
Maintenance
| 09:07 | 16:19 | Ghorasal-Joydeb-B 132kV Ckt-2 Scheduled S/D from Joydebpur 132/33kV end Due to Hotspot
Maintenance
| 12:00 |  | Day peak generation: 11385 MW
| 13:51 |  | Bhola Nutan Biddut BD LTD Synchronized with remarks:- GT12
| 13:52 |  | Bhola Natun Biddut BD LTD GT-2 was sync.
| 14:13 |  | Raozan 25 MW PP Synchronized
| 15:37 |  | Fenchuganj-Sreemangal 132kV Ckt-2 Forced S/D from Fenchuganj 230/132/33kV end Due to
According to direction of NLDC SDE for AT-2 overload.
| 15:37 |  | Fenchuganj-Sreemangal 132kV Ckt-1 Forced S/D from Fenchuganj 230/132/33kV end Due to
According to direction of NLDC SDE for AT-2 overload.
| 15:46 | 17:34 | Munshiganj 132/33kV S/S Transformer-2 HT Tripped showing Backup protection relay relays | [7 empty] | 52.0MW load
|  |  | Due to Palli biddut one phase out | [7 empty] | interrup.
| 16:46 | 17:34 | Munshiganj 132/33kV S/S Transformer-1 HT Tripped showing Backup protection relay relays | [7 empty] | 52.0MW load
|  |  | Due to Backup | [7 empty] | interrup.
| 17:38 |  | JERA Meghnaghat Power Limited 718 MW CCPP GT-11 tripped due to the compressor trip of the
respective GT.
| 17:58 |  | Ghorashal Unit-7 365 MW CCPP GT was sync.
| 21:00 |  | Evening Peak 13848 MW.
| 21:38 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is OFF with remarks:-
| 23:02 |  | Barapukuria 230/132/33kV S/S 132/33 KV T-3, 404T LT Forced S/D Due to TR-3. Mk box cable
burning problem..
| 23:02 |  | Barapukuria 230/132/33kV S/S 132/33 KV T-3, 404T HT Forced S/D Due to TR-3. Mk box
cable burning problem.
| 06:38 |  | Chandpur 132/33kV S/S 33 kV T-2 section Scheduled S/D
| 06:38 |  | Chandpur 132/33kV S/S 33 kV T-1 Section Scheduled S/D | [7 empty] | 12.0MW load
interrup.
| 06:58 |  | Niamatpur 132/33kV S/S Transformer-2 (417T) LT Forced S/D Due to PBS 33kV Deluabari | [7 empty] | 25.0MW load
|  |  | Feeder Source DS- R Phase Red hot Maintenance | [7 empty] | interrup.
| 06:58 |  | Niamatpur 132/33kV S/S Transformer-2 (417T) HT Forced S/D Due to PBS 33kV Deluabari
Feeder Source DS- R Phase Red hot Maintenance
| 07:10 |  | Aminbazar-Mirpur 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end.
| 07:30 |  | Kodda 132/33kV S/S Summit 149 MW PS Scheduled S/D Due to Red hot maintenance
| 07:34 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is ON with remarks:-
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 09-06-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 40 | 2096600 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 77 | 1792954.55 | Allocation limit by Titas, instructed by DS(Gen)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 378 | 8478000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8794500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 134 | 3370880 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 360000 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17.5 | 400200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 7 | 169200 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 234240 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 17 | 212112 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 120960 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 80 | 377280 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 234875 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 507 | 11563636.36 | None
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 500 | 9313182 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 320 | 15211240 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 1143600 | -
Dhaka Area Total |  |  |  |  | 5939.724 | 2722.5 | 63873459.91
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 50000 | Unit #1 Under Maintenance, Unit#2 Running at 150MW
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 127139.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 121230 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 167 | 4029880 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 219 | 5198887 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 985518 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 895680 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 42 | 862080 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 26426 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 45 | 455040 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1109 | 22047270 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 25920 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 0 | 6290909.09 | U1 S/D 25/Mar/25 & U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4895.72 | 1755 | 41115979.49
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 201 | 4902000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 338 | 8356000 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 7884000 | machine problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 16 | 406224 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 48 | 1146720 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 185 | 4482909.09 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1192764 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 35 | 675056 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1463650 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 170 | 3855360 | -
| Import (Tripura) |  | Import | 0 | 160 | 26 | 820800 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 730963 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 9 | 290930 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2759940 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 56 | 609840 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 95 | 2637120 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 516245 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1816.2 | 42730521.09
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 151 | 3541440 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15400 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 139 | 1824000 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 94 | 1135200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 373750 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 9 | 37440 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 54.5 | 231840 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 447.5 | 7159070
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 32 | 755000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 635760 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 150 | 3317645 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 718944 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1837440 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7520500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 377 | 8882000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7679700 | -
Sylhet Area Total |  |  |  |  | 2325 | 1334 | 31346989
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 931 | 22326545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 370 | 8657280 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 684000 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 617.1 | 11236360 | U#1 Reserve shut down as per NLDC Communication
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3699.2 | 1918.1 | 42904185
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 11 | 238618 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2650000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1230 | 20704000 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 3893470 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 5031 | -
Barishal Area Total |  |  |  |  | 2236 | 1581 | 27491119
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | machine problem
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 186 | 4117000 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 201 | 4570864 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 203 | 4595518 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 406 | 8924000 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 58 | 417984 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 35940 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 753.45 | 14124029 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 395248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 779870 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 1807.45 | 37960453
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1154182 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 190 | 4766000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1651411 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 52079.28 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1474716 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 224508 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1446760 | -
Rangpur Area Total |  |  |  |  | 950 | 468 | 10769656.28
Eastern Grid Total |  |  |  |  | 16705.895 | 8075.2 | 186226019.49
Western Grid Total |  |  |  |  | 10338.16 | 5774.55 | 119125413.28
National Grid Total |  |  |  |  | 27044.055 | 13849.75 | 305351432.77
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 09-06-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8241.42 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5028.7 | MW
i) Dhaka area |  |  | 3513.35 |  | MW | i) Khulna area |  |  |  | 1905.9 | MW
ii) Chattogram area |  |  | 1345 |  | MW | ii) Barishal area |  |  |  | 528.2 | MW
iii) Cumilla area |  |  | 1480.07 |  | MW | iii) Rajshahi area |  |  |  | 1567.6 | MW
iv) Mymensingh area |  |  | 1283 |  | MW | iv) Rangpur area |  |  |  | 1027 | MW
v) Sylhet area |  |  | 620 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13270.12 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 77 | 21:00 | 133 | Patuakhali | 93 | 01:00
2 | AKSML | 106 | 13:00 | 68 | Jaldhaka | 98 | 21:00 | 134 | Payra | 40 | 00:00
3 | Aftabnagar | 30 | 00:00 | 69 | Jamalpur | 158 | 23:00 | 135 | Postogola | 48 | 12:00
4 | Agargaon | 97 | 21:00 | 70 | Jashore | 148 | 21:00 | 136 | Purbachal | 17 | 22:00
5 | Agrabad | 76 | 00:00 | 71 | Jhenaidah | 142 | 23:00 | 137 | Purbasadipur | 129 | 23:00
6 | Amnura | 45 | 22:00 | 72 | Joydebpur | 73 | 21:00 | 138 | Rahanpur | 39 | 23:00
7 | Ashuganj | 97 | 00:00 | 73 | Joypurhat | 72 | 23:00 | 139 | Rahim | 1 | 00:00
8 | BSRM | 182 | 23:00 | 74 | Juldah | 14 | 00:00 | 140 | Rajbari | 89 | 23:00
9 | Bagerhat | 89 | 00:00 | 75 | KSRM | 10 | 06:00 | 141 | Rajendrapur | 100 | 21:00
10 | Bajitpur | 60 | 21:00 | 76 | Kabirpur | 115 | 21:00 | 142 | Rajshahi | 116 | 22:00
11 | Bakulia | 83 | 00:00 | 77 | Kachua | 115 | 00:00 | 143 | Rajshahi-230 | 98 | 00:00
12 | Banani | 24 | 19:00 | 78 | Kallyanpur | 90 | 00:00 | 144 | Ramganj | 120 | 06:00
13 | Bangabhaban | 4 | 20:00 | 79 | Kalurghat | 26 | 00:00 | 145 | Rampur | 41 | 00:00
14 | Barapukuria | 67 | 00:00 | 80 | Kamrangirchar | 36.7 | 01:00 | 146 | Rangamati | 18 | 20:00
15 | Barguna | 26 | 23:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 150 | 19:30
16 | Barishal | 114 | 23:00 | 82 | Kasba | 44 | 22:00 | 148 | Ruppur | 5.8 | 12:00
17 | Barishal-230 | 118 | 23:00 | 83 | Kazla | 65 | 23:00 | 149 | SSM | 0 | 00:00
18 | Baroaulia | 55 | 21:00 | 84 | Keranigonj | 76 | 00:00 | 150 | Saidpur | 107 | 23:00
19 | Baroirhat | 69 | 00:00 | 85 | Khagrachori | 32 | 00:00 | 151 | Satkhira | 150 | 21:00
20 | Bashundhara | 138 | 21:00 | 86 | Khulna | 64 | 00:00 | 152 | Satmasjid | 80 | 21:00
21 | BashundharaCement | 1 | 11:00 | 87 | Khulshi | 154 | 21:00 | 153 | Savar | 110 | 00:00
22 | Beanibazar | 84 | 20:00 | 88 | Kishoreganj | 160 | 00:00 | 154 | SevenRings | 0.61 | 22:00
23 | Benapole | 71 | 22:00 | 89 | Kodda | 136 | 21:00 | 155 | ShahCement | 0 | 00:00
24 | Bhaluka | 110 | 23:00 | 90 | Kulaura | 55 | 19:00 | 156 | Shahjadpur | 91 | 20:00
25 | Bhandaria | 63 | 23:00 | 91 | Kurigram | 70 | 21:00 | 157 | Shahjibazar | 126 | 22:00
26 | Bhangura | 44 | 22:00 | 92 | Kushtia | 136 | 21:00 | 158 | Shahmirpur | 47 | 01:00
27 | Bheramara(GK) | 74 | 22:00 | 93 | Lalbag | 13 | 00:00 | 159 | Shariatpur | 108 | 22:00
28 | Bhulta | 109 | 00:00 | 94 | Lalmonirhat | 72 | 19:30 | 160 | Sherpur | 176 | 23:00
29 | Bog-Sherpur | 64 | 21:00 | 95 | MI_Cement | 0.9 | 11:00 | 161 | Shikalbaha | 27 | 14:00
30 | Bogura | 169 | 21:00 | 96 | Madanganj | 31 | 23:00 | 162 | Shitalakhya | 53.7 | 19:00
31 | Borhanuddin | 92 | 01:00 | 97 | Madaripur | 130 | 22:00 | 163 | Sholosohor | 36 | 22:00
32 | Brahmanbaria | 146 | 02:00 | 98 | Madartek | 77 | 23:00 | 164 | Shyampur | 50 | 13:00
33 | Cantonment | 104 | 19:00 | 99 | Madunaghat | 63 | 23:00 | 165 | Siddhirganj | 72 | 23:00
34 | Chandina | 26.16 | 03:00 | 100 | Magura | 73 | 22:00 | 166 | Sirajganj | 116 | 23:00
35 | Chandpur | 94 | 22:00 | 101 | Mahasthangarh | 94 | 00:00 | 167 | Sonargaon | 55 | 23:00
36 | Chandraghona | 39 | 00:00 | 102 | Manikganj | 100 | 23:00 | 168 | Sreemongol | 88 | 23:00
37 | Chapai | 72 | 22:00 | 103 | Maniknagar | 58 | 00:00 | 169 | Sreepur | 61 | 22:00
38 | Charsaidpur | 8 | 15:00 | 104 | Matarbari | 51 | 00:00 | 170 | Srinagar | 57.9 | 23:00
39 | Chauddagram | 86 | 22:00 | 105 | Matuail | 36 | 00:00 | 171 | Sunamganj | 53 | 19:00
40 | Chhatak | 36 | 03:00 | 106 | Millgate | 65 | 00:00 | 172 | Sylhet | 50 | 22:00
41 | Chowmuhani | 243 | 20:00 | 107 | Mirpur | 93 | 00:00 | 173 | Sylhet-132 | 121 | 21:00
42 | Chuadanga | 126 | 23:00 | 108 | Mirsorai | 8 | 00:00 | 174 | TK | 39.4 | 00:00
43 | Coxsbazar | 137 | 22:00 | 109 | Mirzapur | 41 | 21:00 | 175 | Tangail | 184 | 22:00
44 | Cumilla(N) | 165 | 23:00 | 110 | Mithapukur | 68 | 00:00 | 176 | Thakurgaon | 119 | 20:00
45 | Cumilla(S) | 153 | 00:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 84 | 23:00
46 | Daudkandi | 142 | 22:00 | 112 | Mogbazar | 89.9 | 19:00 | 178 | Ullahpara | 42 | 20:00
47 | Dhaka | 24 | 19:00 | 113 | Mongla | 24 | 00:00 | 179 | Ullon | 34 | 00:00
48 | Dhamrai | 86 | 21:00 | 114 | Motijheel | 26 | 21:00 | 180 | Uttara | 57 | 21:00
49 | Dhanmondi | 78 | 21:00 | 115 | Muktagacha | 44 | 22:00 | 181 | UttaraNew | 48 | 22:00
50 | Dohazari | 112 | 23:00 | 116 | Munshiganj | 122 | 23:00 | 182 | Zigatola | 56 | 00:00
51 | Faridpur | 175 | 23:00 | 117 | Muradnagar | 37 | 22:00
52 | Fatullah | 49 | 23:00 | 118 | Mymensingh | 222 | 21:00
53 | Fenchuganj | 47 | 19:00 | 119 | Naogaon | 151 | 23:00
54 | Feni | 132 | 00:00 | 120 | Narail | 65.5 | 21:00
55 | GPH | 1 | 00:00 | 121 | Narinda | 45 | 00:00
56 | Ghatail | 90 | 21:00 | 122 | Narshingdi | 159 | 21:00
57 | Ghorashal | 15 | 13:00 | 123 | Natore | 165 | 21:00
58 | Ghorashal-230 | 63 | 20:00 | 124 | Nawabganj | 69 | 23:00
59 | Goalpara | 42 | 00:00 | 125 | Netrakona | 160 | 22:00
60 | Gollamari | 92 | 23:00 | 126 | New | 37.1 | 22:00
61 | Gopalganj | 120.8 | 23:00 | 127 | Niamatpur | 85 | 00:00
62 | Gulshan | 70 | 19:00 | 128 | Noapara | 45 | 00:00
63 | Halishahar | 34 | 19:00 | 129 | PHP | 8 | 23:00
64 | HaripurSBU | 57 | 23:00 | 130 | Pabna | 124 | 22:00
65 | Hasnabad | 57 | 23:00 | 131 | Palashbari | 128 | 01:00
66 | Hathazari | 89 | 00:00 | 132 | Panchagarh | 65 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 09-06-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13434.2 | 30 |  | 13465.55
1:00 | 13301.7 | 47 |  | 13350.7
2:00 | 13123.7 | 45 |  | 13170.7
3:00 | 12834.7 | 39 |  | 12875.7
4:00 | 12546.7 | 32 |  | 12579.7
5:00 | 12274.7 | 25 |  | 12300.7
6:00 | 11487.25 | 0 |  | 11487.25
7:00 | 11512.92 | 0 |  | 11512.92
8:00 | 11402.62 | 0 |  | 11402.62
9:00 | 11250.96 | 0 |  | 11250.96
10:00 | 11275.58 | 0 |  | 11275.58
11:00 | 11215.31 | 0 |  | 11215.31
12:00 | 11389.04 | 0 |  | 11389.04
13:00 | 11663.86 | 0 |  | 11663.86
14:00 | 12023.49 | 0 |  | 12023.49
15:00 | 12087.73 | 0 |  | 12087.73
16:00 | 11991.99 | 0 |  | 11991.99
17:00 | 11450 | 0 |  | 11450
18:00 | 10942.62 | 0 |  | 10942.62
19:00 | 12354.2 | 0 |  | 12354.2
19:30 | 13033.2 | 54 |  | 13089.2
20:00 | 13346.3 | 52 |  | 13400.3
21:00 | 13849.75 | 69 |  | 13921.75
22:00 | 13961.24 | 86 |  | 14051.24
23:00 | 14141.56 | 91 |  | 14236.56
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 09-06-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8118.2 | 5316 | 13434.2 | DAILY GENERATION CURVE
00:30 | 8004.95 | 5363 | 13367.95
01:00 | 7891.7 | 5410 | 13301.7 | 09-06-2025
01:30 | 7807.7 | 5405 | 13212.7
02:00 | 7723.7 | 5400 | 13123.7
02:30 | 7690.7 | 5288.5 | 12979.2
03:00 | 7657.7 | 5177 | 12834.7
03:30 | 7638.2 | 5052.5 | 12690.7
04:00 | 7618.7 | 4928 | 12546.7
04:30 | 7569.7 | 4841 | 12410.7
05:00 | 7520.7 | 4754 | 12274.7
05:30 | 7398.765 | 4482.21 | 11880.975
06:00 | 7276.83 | 4210.42 | 11487.25
06:30 | 7280.94 | 4219.145 | 11500.085
07:00 | 7285.05 | 4227.87 | 11512.92
07:30 | 7218.73 | 4239.04 | 11457.77
08:00 | 7152.41 | 4250.21 | 11402.62
08:30 | 7077.545 | 4249.245 | 11326.79
09:00 | 7002.68 | 4248.28 | 11250.96
09:30 | 6999.205 | 4264.065 | 11263.27
10:00 | 6995.73 | 4279.85 | 11275.58
10:30 | 6956.9 | 4288.545 | 11245.445
11:00 | 6918.07 | 4297.24 | 11215.31
11:30 | 6953.745 | 4348.43 | 11302.175
12:00 | 6989.42 | 4399.62 | 11389.04
12:30 | 7023.11 | 4503.34 | 11526.45
13:00 | 7056.8 | 4607.06 | 11663.86
13:30 | 7118.895 | 4724.78 | 11843.675
14:00 | 7180.99 | 4842.5 | 12023.49
14:30 | 7207.055 | 4848.555 | 12055.61
15:00 | 7233.12 | 4854.61 | 12087.73
15:30 | 7214.025 | 4825.835 | 12039.86
16:00 | 7194.93 | 4797.06 | 11991.99
16:30 | 7028.95 | 4692.045 | 11720.995
17:00 | 6862.97 | 4587.03 | 11450
17:30 | 6704.385 | 4491.925 | 11196.31
18:00 | 6545.8 | 4396.82 | 10942.62
18:30 | 7088 | 4560.41 | 11648.41
19:00 | 7630.2 | 4724 | 12354.2
19:30 | 7800.2 | 5233 | 13033.2
20:00 | 7886.2 | 5460.1 | 13346.3
20:30 | 7980.7 | 5617.325 | 13598.025 |  | Executive Engineer
21:00 | 8075.2 | 5774.55 | 13849.75 |  | Network Operation Division
21:30 | 8089.45 | 5816.045 | 13905.495
22:00 | 8103.7 | 5857.54 | 13961.24
22:30 | 8178.2 | 5873.2 | 14051.4
23:00 | 8252.7 | 5888.86 | 14141.56

## En-Curve
QF-LDC-12
Date | 09-06-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4404 | 3375 | 916 | 0 | 40 | 676 | 167 | 2773 | 0 | 162 | 921.2 | 0 | 0 | 0 | 30 | DAILY ENERGY CURVE
00:30 | 4284 | 3383.75 | 916 | 0 | 40 | 711 | 167 | 2786.5 | 0 | 153.5 | 926.2 | 0 | 0 | 0 | 38.5 | 09-06-2025
01:00 | 4164 | 3392.5 | 916 | 0 | 40 | 746 | 167 | 2800 | 0 | 145 | 931.2 | 0 | 0 | 0 | 47
01:30 | 4110.5 | 3380 | 916.5 | 0 | 40 | 751 | 167 | 2761.5 | 0 | 145 | 941.2 | 0 | 0 | 0 | 46 | Energy Generated | 305.3514 |  | MKWHr
02:00 | 4057 | 3367.5 | 917 | 0 | 40 | 756 | 167 | 2723 | 0 | 145 | 951.2 | 0 | 0 | 0 | 45 | Energy not Served | 0.516 |  | MKWHr
02:30 | 4066 | 3371 | 917 | 0 | 40 | 740 | 167 | 2582.5 | 0 | 144.5 | 951.2 | 0 | 0 | 0 | 42 | Total Energy Requirement | 305.8674 |  | MKWHr
03:00 | 4075 | 3374.5 | 917 | 0 | 40 | 724 | 167 | 2442 | 0 | 144 | 951.2 | 0 | 0 | 0 | 39
03:30 | 4088.5 | 3332.5 | 916.5 | 0 | 39 | 675 | 167 | 2377 | 0 | 144 | 951.2 | 0 | 0 | 0 | 35.5
04:00 | 4102 | 3290.5 | 916 | 0 | 38 | 626 | 167 | 2312 | 0 | 144 | 951.2 | 0 | 0 | 0 | 32
04:30 | 4076.5 | 3310 | 916 | 0 | 36 | 623.5 | 167 | 2221 | 0 | 135.5 | 925.2 | 0 | 0 | 0 | 28.5
05:00 | 4051 | 3329.5 | 916 | 0 | 34 | 621 | 167 | 2130 | 0 | 127 | 899.2 | 0 | 0 | 0 | 25
05:30 | 4036.5 | 3248.5 | 913 | 0 | 34 | 557.5 | 167 | 2023 | 21.875 | 101 | 778.6 | 0 | 0 | 0 | 12.5
06:00 | 4022 | 3167.5 | 910 | 0 | 34 | 494 | 167 | 1916 | 43.75 | 75 | 658 | 0 | 0 | 0 | 0
06:30 | 4036.5 | 3168 | 913 | 0 | 32 | 459 | 167 | 1926 | 97.585 | 75 | 626 | 0 | 0 | 0 | 0
07:00 | 4051 | 3168.5 | 916 | 0 | 30 | 424 | 167 | 1936 | 151.42 | 75 | 594 | 0 | 0 | 0 | 0
07:30 | 3972 | 3165.5 | 918.5 | 0 | 30 | 419.63 | 167 | 1901 | 232.14 | 58 | 594 | 0 | 0 | 0 | 0
08:00 | 3893 | 3162.5 | 921 | 0 | 30 | 415.26 | 167 | 1866 | 312.86 | 41 | 594 | 0 | 0 | 0 | 0
08:30 | 3797.5 | 3156.25 | 926 | 0 | 31 | 415.77 | 167 | 1872.5 | 370.27 | 33 | 557.5 | 0 | 0 | 0 | 0
09:00 | 3702 | 3150 | 931 | 0 | 32 | 416.28 | 167 | 1879 | 427.68 | 25 | 521 | 0 | 0 | 0 | 0
09:30 | 3636 | 3150 | 930.5 | 0 | 31 | 414.95 | 167 | 1884.5 | 495.82 | 45.5 | 508 | 0 | 0 | 0 | 0
10:00 | 3570 | 3150 | 930 | 0 | 30 | 413.62 | 167 | 1890 | 563.96 | 66 | 495 | 0 | 0 | 0 | 0
10:30 | 3534.5 | 3139 | 930.5 | 0 | 29 | 413.785 | 167 | 1875.5 | 596.66 | 66 | 490.5 | 0 | 0 | 3 | 0
11:00 | 3499 | 3128 | 931 | 0 | 28 | 413.95 | 167 | 1861 | 629.36 | 66 | 486 | 0 | 0 | 6 | 0
11:30 | 3554.5 | 3129 | 931.5 | 0 | 30 | 416.245 | 167 | 1888.5 | 628.93 | 75 | 473 | 0 | 0 | 8.5 | 0
12:00 | 3610 | 3130 | 932 | 0 | 32 | 418.54 | 167 | 1916 | 628.5 | 84 | 460 | 0 | 0 | 11 | 0
12:30 | 3706.5 | 3093.5 | 931.5 | 0 | 32 | 434.58 | 167 | 2003.5 | 604.87 | 84 | 460 | 0 | 0 | 9 | 0
13:00 | 3803 | 3057 | 931 | 0 | 32 | 450.62 | 167 | 2091 | 581.24 | 84 | 460 | 0 | 0 | 7 | 0
13:30 | 3770 | 3002.25 | 931.5 | 0 | 33 | 504.81 | 167 | 2295 | 566.615 | 92.5 | 477.5 | 0 | 0 | 3.5 | 0
14:00 | 3737 | 2947.5 | 932 | 0 | 34 | 559 | 167 | 2499 | 551.99 | 101 | 495 | 0 | 0 | 0 | 0
14:30 | 3703.5 | 2957.25 | 932 | 0 | 37 | 558.5 | 167 | 2567 | 500.86 | 113.5 | 519 | 0 | 0 | 0 | 0
15:00 | 3670 | 2967 | 932 | 0 | 40 | 558 | 167 | 2635 | 449.73 | 126 | 543 | 0 | 0 | 0 | 0
15:30 | 3652.5 | 2997.5 | 932 | 0 | 37 | 558.5 | 167 | 2627.5 | 377.36 | 135 | 555.5 | 0 | 0 | 0 | 0
16:00 | 3635 | 3028 | 932 | 0 | 34 | 559 | 167 | 2620 | 304.99 | 144 | 568 | 0 | 0 | 0 | 0
16:30 | 3630 | 2987 | 932 | 0 | 32 | 562.5 | 167 | 2493 | 226.495 | 123.5 | 567.5 | 0 | 0 | 0 | 0
17:00 | 3625 | 2946 | 932 | 0 | 30 | 566 | 167 | 2366 | 148 | 103 | 567 | 0 | 0 | 0 | 0
17:30 | 3593.5 | 2781 | 932 | 0 | 30 | 524 | 167 | 2367 | 92.81 | 119.5 | 589.5 | 0 | 0 | 0 | 0
18:00 | 3562 | 2616 | 932 | 0 | 30 | 482 | 167 | 2368 | 37.62 | 136 | 612 | 0 | 0 | 0 | 0
18:30 | 3739 | 2851.5 | 908.5 | 0 | 33 | 520.5 | 167 | 2508 | 18.81 | 161.5 | 740.6 | 0 | 0 | 0 | 0
19:00 | 3916 | 3087 | 885 | 0 | 36 | 559 | 167 | 2648 | 0 | 187 | 869.2 | 0 | 0 | 0 | 0
19:30 | 4018 | 3176 | 885 | 0 | 38 | 616 | 167 | 2922 | 0 | 195 | 1016.2 | 0 | 0 | 0 | 54
20:00 | 3984 | 3148 | 885 | 0 | 36 | 720 | 167 | 3036.1 | 0 | 241 | 1129.2 | 0 | 0 | 0 | 52
20:30 | 4011 | 3135.75 | 908 | 0 | 31 | 736.725 | 167 | 3116.1 | 0 | 241 | 1251.45 | 0 | 0 | 0 | 60.5
21:00 | 4038 | 3123.5 | 931 | 0 | 26 | 753.45 | 167 | 3196.1 | 0 | 241 | 1373.7 | 0 | 0 | 0 | 69
21:30 | 4050 | 3105.25 | 931.5 | 0 | 32 | 753.945 | 167 | 3189.6 | 0 | 241 | 1435.2 | 0 | 0 | 0 | 77.5
22:00 | 4062 | 3087 | 932 | 0 | 38 | 754.44 | 167 | 3183.1 | 0 | 241 | 1496.7 | 0 | 0 | 0 | 86
22:30 | 4089.5 | 3115 | 932 | 0 | 40 | 757.65 | 167 | 3200.05 | 0 | 241 | 1508.7 | 0 | 0 | 0.5 | 88.5
23:00 | 4117 | 3143 | 932 | 0 | 42 | 760.86 | 167 | 3217 | 0 | 241 | 1520.7 | 0 | 0 | 1 | 91
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 09-06-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 397 | 06:00 | 384 | 23:00 | Payra | 416 | 07:00 | 406 | 23:00
Ashuganj | 421 | 10:00 | 398 | 23:00 | Rahanpur | 408 | 09:00 | 393 | 14:00
Bhulta | 414 | 06:00 | 397 | 23:00 | Rampal | 405 | 08:00 | 386 | 21:00
Bibiana | 393 | 08:00 | 387 | 21:00
BIPTC | 401 | 06:00 | 387 | 00:00
Bogura | 398 | 09:00 | 381 | 00:00
Gopalganj | 404 | 08:00 | 388 | 23:00
Kaliakoir | 388 | 06:00 | 376 | 22:00
Madunaghat | 399 | 06:00 | 393 | 14:00
Meghnaghat | 401 | 05:00 | 390 | 23:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 235 | 06:00 | 227 | 23:00 | Keranigonj | 233 | 06:00 | 226 | 20:00
AKSML | 230 | 00:00 | 225 | 01:00 | Khulna(S) | 231 | 18:30 | 213 | 23:00
Aminbazar | 235 | 06:00 | 228 | 23:00 | Madunaghat | 233 | 18:00 | 227 | 14:00
Ashuganj | 241 | 06:00 | 233 | 19:00 | Madunaghat-400 | 233 | 06:00 | 227 | 14:00
Ashuganj-400 | 241 | 06:00 | 233 | 19:00 | Maniknagar | 229 | 05:00 | 223 | 22:00
Baghabari | 236 | 08:00 | 226 | 00:00 | Meghnaghat | 240 | 08:00 | 230 | 23:00
Barapukuria | 222 | 05:00 | 214 | 00:00 | Meghnaghat-400 | 233 | 05:00 | 226 | 23:00
Barapukuria-230 | 222 | 05:00 | 214 | 00:00 | Mirsorai | 231 | 18:30 | 224 | 00:00
Barishal | 239 | 10:00 | 227 | 23:00 | Rajshahi | 235 | 07:00 | 221 | 00:00
Bheramara | 234 | 06:00 | 222 | 19:30 | Rampal | 231 | 10:00 | 215 | 22:00
Bhulta | 241 | 05:00 | 226 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 232 | 06:00 | 224 | 22:00 | Rampura | 241 | 06:00 | 231 | 19:00
BIPTC | 237 | 08:00 | 222 | 19:30 | Shikalbaha | 230 | 08:00 | 220 | 07:00
Bogura | 233 | 09:00 | 222 | 00:00 | Shyampur | 233 | 06:00 | 225 | 23:00
Bogura-400 | 232 | 09:00 | 221 | 00:00 | Siddhirganj | 231 | 02:00 | 225 | 20:00
Borhanuddin | 241 | 08:00 | 235 | 23:00 | Sirajgonj | 241 | 08:00 | 235 | 00:00
BSRM | 231 | 18:00 | 222 | 23:00 | Sreepur | 234 | 09:00 | 227 | 23:00
Cumilla(N) | 230 | 18:00 | 222 | 23:00 | Tongi | 240 | 10:00 | 231 | 23:00
Faridpur | 236 | 10:00 | 223 | 23:00
Fenchuganj | 231 | 09:00 | 226 | 21:00
Ghorashal | 240 | 00:00 | 240 | 00:00
Ghorashal-230 | 240 | 06:00 | 230 | 19:30
Gopalganj | 238 | 07:00 | 227 | 23:00
GPH | 232 | 18:00 | 225 | 13:00
Haripur | 230 | 05:00 | 224 | 23:00
Hasnabad | 233 | 07:00 | 226 | 21:00
Hathazari | 232 | 18:00 | 227 | 13:00
Ishurdi | 237 | 08:00 | 225 | 19:30
Jhenaidah | 231 | 09:00 | 214 | 21:00
Kaliakoir | 242 | 06:00 | 233 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 05:00 | 128 | 19:00 | Madartek | 134 | 06:00 | 127 | 19:00
Agargaon | 136 | 06:00 | 130 | 23:00 | Madunaghat | 134 | 18:00 | 128 | 13:00
Agrabad | 132 | 03:00 | 127 | 13:00 | Magura | 134 | 18:00 | 120 | 23:00
AKS | 131 | 18:00 | 126 | 13:00 | Mahasthangarh | 132 | 06:00 | 123 | 01:00
Aminbazar | 134 | 05:00 | 130 | 00:00 | Manikganj | 134 | 09:00 | 127 | 21:00
Amnura | 136 | 07:00 | 124 | 00:00 | Maniknagar | 131 | 06:00 | 127 | 21:00
Ashuganj | 140 | 06:00 | 136 | 00:00 | Matarbari | 117 | 11:00 | 108 | 19:00
Bagerhat | 132 | 10:00 | 115 | 23:00 | Matuail | 135 | 05:00 | 131 | 23:00
Bajitpur | 133 | 10:00 | 127 | 21:00 | Millgate | 136 | 05:00 | 129 | 23:00
Bakulia | 133 | 18:00 | 129 | 00:00 | Mirpur | 133 | 04:00 | 129 | 00:00
Banani | 134 | 05:00 | 128 | 19:30 | Mirzapur | 133 | 18:30 | 127 | 19:30
Bangabhaban | 131 | 06:00 | 126 | 23:00 | Mithapukur | 130 | 06:00 | 121 | 00:00
Barapukuria | 134 | 18:30 | 125 | 00:00 | MI_Cement | 136 | 05:00 | 132 | 22:00
Barguna | 134 | 18:00 | 127 | 23:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 133 | 18:30 | 122 | 22:00 | Mogbazar | 135 | 05:00 | 130 | 19:00
Barishal-230 | 132 | 10:00 | 123 | 23:00 | Mongla | 133 | 18:00 | 117 | 00:00
Baroaulia | 133 | 03:00 | 129 | 12:00 | Motijheel | 131 | 06:00 | 126 | 23:00
Baroirhat | 128 | 18:00 | 118 | 01:00 | Muktagacha | 129 | 21:00 | 123 | 02:00
Bashundhara | 136 | 06:00 | 126 | 23:00 | Munshiganj | 135 | 07:00 | 129 | 13:00
BashundharaCement | 136 | 03:00 | 34 | 01:00 | Muradnagar | 130 | 18:30 | 122 | 22:00
Beanibazar | 125 | 10:00 | 121 | 21:00 | Mymensingh | 130 | 21:00 | 116 | 21:00
Benapole | 131 | 18:00 | 114 | 23:00 | Naogaon | 130 | 06:00 | 119 | 00:00
Bhaluka | 134 | 18:30 | 127 | 00:00 | Narail | 134 | 10:00 | 117 | 23:00
Bhandaria | 129 | 18:00 | 112 | 23:00 | Narinda | 131 | 06:00 | 127 | 21:00
Bhangura | 134 | 08:00 | 126 | 20:00 | Narshingdi | 142 | 06:00 | 124 | 23:00
Bheramara | 138 | 08:00 | 132 | 00:00 | Natore | 135 | 09:00 | 126 | 00:00
Bheramara(GK) | 138 | 09:00 | 132 | 00:00 | Nawabganj | 135 | 06:00 | 129 | 23:00
Bhulta | 130 | 06:00 | 125 | 21:00 | Netrakona | 124 | 06:00 | 112 | 23:00
Bog-Sherpur | 134 | 06:00 | 126 | 00:00 | New | 137 | 05:00 | 131 | 19:00
Bogura | 135 | 08:00 | 128 | 01:00 | Niamatpur | 135 | 06:00 | 130 | 00:00
Bogura-230 | 136 | 06:00 | 128 | 00:00 | Noapara | 134 | 18:00 | 119 | 23:00
Brahmanbaria | 134 | 06:00 | 128 | 19:00 | Pabna | 136 | 10:00 | 128 | 00:00
Cantonment | 135 | 05:00 | 131 | 13:00 | Palashbari | 128 | 18:30 | 117 | 00:00
Chandina | 132 | 18:00 | 125 | 00:00 | Panchagarh | 135 | 05:00 | 117 | 14:00
Chandpur | 132 | 18:00 | 121 | 00:00 | Patuakhali | 134 | 09:00 | 129 | 00:00
Chandraghona | 133 | 08:00 | 130 | 00:00 | Payra | 137 | 09:00 | 132 | 00:00
Chapai | 130 | 05:00 | 125 | 00:00 | PHP | 127 | 18:00 | 117 | 01:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 136 | 08:00 | 132 | 20:00 | Postogola | 137 | 04:00 | 133 | 23:00
Chauddagram | 128 | 18:00 | 118 | 00:00 | Purbachal | 134 | 06:00 | 128 | 19:00
Chhatak | 125 | 18:00 | 117 | 22:00 | Purbasadipur | 129 | 19:00 | 115 | 13:00
Chowmuhani | 124 | 18:00 | 112 | 01:00 | Rahanpur | 135 | 04:00 | 130 | 00:00
Chuadanga | 132 | 09:00 | 119 | 23:00 | Rahanpur-400 | 136 | 09:00 | 130 | 14:00
Coxsbazar | 118 | 16:00 | 110 | 00:00 | Rahim | 135 | 07:00 | 132 | 14:00
Cumilla(N) | 132 | 18:00 | 125 | 01:00 | Rajbari | 136 | 06:00 | 126 | 23:00
Cumilla(S) | 132 | 04:00 | 121 | 13:00 | Rajendrapur | 139 | 06:00 | 13 | 01:00
Daudkandi | 128 | 18:30 | 119 | 23:00 | Rajshahi | 135 | 06:00 | 127 | 00:00
Dhaka | 134 | 05:00 | 128 | 19:00 | Rajshahi-230 | 136 | 10:00 | 117 | 00:00
Dhamrai | 136 | 05:00 | 130 | 21:00 | Ramganj | 125 | 18:00 | 110 | 13:00
Dhanmondi | 136 | 06:00 | 131.5 | 23:00 | Rampur | 132 | 18:00 | 128 | 12:00
Dohazari | 130 | 02:00 | 122 | 14:00 | Rampura | 134 | 06:00 | 128 | 19:00
Faridpur | 137 | 18:00 | 128 | 23:00 | Rangamati | 132 | 18:00 | 128 | 12:00
Fatullah | 135 | 06:00 | 131 | 23:00 | Rangpur | 128 | 06:00 | 118 | 23:00
Fenchuganj | 137 | 10:00 | 132 | 15:00 | Ruppur | 138 | 08:00 | 132 | 00:00
Feni | 127 | 18:00 | 117 | 23:00 | Saidpur | 129 | 04:00 | 119 | 14:00
Ghatail | 128 | 18:30 | 121 | 13:00 | Satkhira | 131 | 18:00 | 113 | 23:00
Ghorashal | 142 | 01:00 | 137 | 19:30 | Satmasjid | 135 | 06:00 | 130 | 21:00
Goalpara | 137 | 18:30 | 120 | 23:00 | Savar | 133 | 08:00 | 128 | 00:00
Gollamari | 137 | 09:00 | 124 | 23:00 | SevenRings | 144 | 06:00 | 138 | 21:00
Gopalganj | 136 | 10:00 | 125 | 23:00 | ShahCement | 136 | 08:00 | 132 | 20:00
Gopalganj-400 | 138 | 07:00 | 131 | 23:00 | Shahjadpur | 134 | 00:00 | 132 | 06:00
Gulshan | 134 | 05:00 | 127 | 23:00 | Shahjibazar | 134 | 10:00 | 124 | 23:00
Halishahar | 133 | 03:00 | 128 | 19:00 | Shahmirpur | 133 | 18:30 | 127 | 14:00
Haripur | 135 | 09:00 | 132 | 21:00 | Shariatpur | 135 | 18:30 | 125 | 23:00
HaripurSBU | 135 | 09:00 | 132 | 22:00 | Sherpur | 125 | 21:00 | 112 | 13:00
Hasnabad | 137 | 05:00 | 133 | 23:00 | Shikalbaha | 123 | 19:00 | 118 | 13:00
Hathazari | 135 | 18:00 | 130 | 01:00 | Shikalbaha-230 | 133 | 06:00 | 129 | 14:00
Ishurdi | 139 | 08:00 | 132 | 00:00 | Shitalakhya | 136 | 05:00 | 132 | 22:00
Jaldhaka | 126 | 18:30 | 115 | 23:00 | Sholosohor | 132 | 04:00 | 127 | 13:00
Jamalpur | 129 | 21:00 | 118 | 13:00 | Shyampur | 134 | 01:00 | 131 | 13:00
Jashore | 134 | 09:00 | 115 | 00:00 | Shyampur-230 | 134 | 05:00 | 130 | 23:00
Jhenaidah | 136 | 09:00 | 120 | 23:00 | Siddhirganj | 136 | 03:00 | 131 | 22:00
Jhenaidah-230 | 136 | 08:00 | 124 | 21:00 | Sirajganj | 134 | 10:00 | 125 | 00:00
Joydebpur | 144 | 09:00 | 135 | 22:00 | Sonargaon | 135 | 01:00 | 129 | 23:00
Joypurhat | 128 | 06:00 | 116 | 00:00 | Sreemongol | 132 | 06:00 | 121 | 21:00
Juldah | 133 | 23:00 | 130 | 00:00 | Sreepur | 136 | 10:00 | 132 | 01:00
Kabirpur | 136 | 07:00 | 128 | 23:00 | Srinagar | 135 | 06:00 | 129 | 23:00
Kachua | 130 | 18:00 | 119 | 00:00 | SSM | 138 | 05:00 | 132 | 00:00
Kaliakoir | 138 | 05:00 | 132 | 22:00 | Sunamganj | 121 | 18:00 | 115 | 20:00
Kallyanpur | 133 | 01:00 | 130 | 00:00 | Sylhet | 126 | 08:00 | 122 | 19:00
Kalurghat | 131 | 18:00 | 128 | 13:00 | Sylhet-132 | 127 | 18:00 | 123 | 22:00
Kamrangirchar | 136 | 06:00 | 131 | 19:30 | Tangail | 129 | 10:00 | 123 | 19:30
Kaptai | 135 | 18:00 | 132 | 14:00 | Thakurgaon | 133 | 05:00 | 114 | 14:00
Kasba | 129 | 18:30 | 120 | 22:00 | TK | 132 | 18:30 | 127 | 13:00
Kazla | 131 | 06:00 | 127 | 21:00 | Tongi | 138 | 10:00 | 132 | 21:00
Keranigonj | 135 | 06:00 | 131 | 00:00 | Ullahpara | 135 | 08:00 | 127 | 00:00
Khagrachori | 131 | 18:00 | 127 | 13:00 | Ullon | 133 | 05:00 | 127 | 23:00
Khulna | 136 | 18:00 | 123 | 23:00 | Uttara | 133 | 05:00 | 129 | 00:00
Khulna(S) | 142 | 06:00 | 124 | 23:00 | UttaraNew | 133 | 05:00 | 128 | 19:00
Khulshi | 131 | 04:00 | 127 | 13:00 | Zigatola | 136 | 06:00 | 131 | 21:00
Kishoreganj | 131 | 10:00 | 123 | 21:00
Kodda | 137 | 16:00 | 130 | 15:00
KSRM | 134 | 02:00 | 7 | 01:00
Kulaura | 134 | 18:00 | 130 | 03:00
Kurigram | 127 | 19:00 | 114 | 00:00
Kushtia | 134 | 07:00 | 126 | 22:00
Lalbag | 136 | 06:00 | 132 | 00:00
Lalmonirhat | 127 | 18:30 | 117 | 23:00
Madanganj | 136 | 03:00 | 132 | 00:00
Madaripur | 135 | 07:00 | 127 | 23:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division