## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 11-06-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 10-06-2025 | during | 11-06-2025 | during | 11-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 30 | 230 | 230 | 230 | 230 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 120 | 260 | 260 | 260 | 260 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 363 | 350 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 340 | 300 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 140 | 140 | 335 | 335 | 150 | 150 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 17.5 | 17.5 | 33 | 33 | 20 | 20 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 7 | 7 | 22 | 22 | 7 | 7 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 16 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 34 | 0 | 34 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 540 | 491 | 584 | 584 | 466 | 466 | None
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 583 | 583 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 320 | 320 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 108 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2576.5 | 2499.5 | 4778.2 | 4776.2 | 4064.27 | 4062.27
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 4 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 15 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 167 | 167 | 165 | 165 | 165 | 165 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 218 | 221 | 221 | 221 | 221 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 72 | 72 | 72 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 33 | 33 | 68 | 68 | 68 | 68 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 76 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 42 | 42 | 38 | 40 | 38 | 40 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4 | 0 | 4.36 | 0 | 4.36 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 810 | 1044 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 15 | 0 | 3 | 10 | 3 | 10 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 0 | 0 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25 & U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1301 | 1584 | 3619.08 | 3603.72 | 3619.08 | 3603.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 207 | 209 | 221.43 | 221.43 | 205.43 | 205.43 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 331 | 342 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 340 | 340 | 340 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 15 | 16 | 46.7 | 46.7 | 17 | 17 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 25 | 25 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 170 | 163 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 35 | 36 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 80 | 163 | 163 | 80 | 80 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 85 | 170 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 40 | 16 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 0 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 90 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 47 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 71 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1707 | 1734 | 2471.18 | 2401.18 | 2337.98 | 2267.98
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 10-06-2025 | during | 11-06-2025 | during | 11-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 146 | 149 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 50 | 118 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 24 | 85 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 40.45 | 0 | 45.42 | 0 | 45.42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 8 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 261.45 | 360 | 596.52 | 549 | 596.52 | 549
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 32 | 32 | 32 | 32 | 32 | 32 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 140 | 148 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 80 | 83 | 83 | 83 | 83 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 25 | 25 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 341 | 345 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1277 | 1300 | 1429 | 1429 | 1306 | 1306
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 931 | 884 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 388 | 340 | 410 | 410 | 380 | 380 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 69.22 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 374 | 1058 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3699.2 | 1762.22 | 2299 | 3256.2 | 3176.2 | 3226.2 | 3146.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 602 | 1060 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 307 | 307 | 0 | 0 | Coal shortage
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.74 | 0 | 0 | 0 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 952.74 | 1410 | 2171 | 2171 | 1852 | 1852
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 50 | 50 | 0 | 0 | Machine Standby
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 157 | 168 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 173 | 181 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 175 | 187 | 220 | 220 | 198 | 198 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 383 | 378 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 | 30 | 30 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.96 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 424.58 | 705 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 57.65 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 87 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 1462.19 | 1619 | 3242.47 | 3075.87 | 3085.69 | 2919.09
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 49 | 48 | 50 | 50 | 50 | 50 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 189 | 190 | 200 | 200 | 200 | 200 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 108 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.4 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 2 | 114 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 29 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 192 | 0 | 172.14 | 0 | 172.14 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 465.4 | 460 | 720.74 | 512 | 720.74 | 512
System Total |  |  |  |  | 28565.2 | 27044.055 | 11765.5 | 13265.5 | 22284.39 | 21694.17 | 20808.48 | 20218.26
Forecast Scenario (11-06-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12500 |  | 0 |  | 12500
|  |  |  | 1:00 | 12440 |  | 0 |  | 12440
|  |  |  | 2:00 | 12310 |  | 0 |  | 12310
|  |  |  | 3:00 | 12060 |  | 0 |  | 12060
|  |  |  | 4:00 | 11810 |  | 0 |  | 11810
|  |  |  | 5:00 | 11580 |  | 0 |  | 11580
|  |  |  | 6:00 | 10810 |  | 0 |  | 10810
|  |  |  | 7:00 | 10890 |  | 0 |  | 10890
|  |  |  | 8:00 | 10830 |  | 0 |  | 10830
|  |  |  | 9:00 | 10720 |  | 0 |  | 10720
|  |  |  | 10:00 | 10800 |  | 0 |  | 10800
|  |  |  | 11:00 | 10780 |  | 0 |  | 10780
|  |  |  | 12:00 | 11000 |  | 0 |  | 11000
|  |  |  | 13:00 | 11340 |  | 0 |  | 11340
|  |  |  | 14:00 | 11760 |  | 0 |  | 11760
|  |  |  | 15:00 | 11890 |  | 0 |  | 11890
|  |  |  | 16:00 | 11850 |  | 0 |  | 11850
|  |  |  | 17:00 | 11370 |  | 0 |  | 11370
|  |  |  | 18:00 | 10930 |  | 0 |  | 10930
|  |  |  | 18:30 | 11500 |  | 0 |  | 11500
|  |  |  | 19:00 | 12400 |  | 0 |  | 12400
|  |  |  | 19:30 | 13200 |  | 0 |  | 13200
|  |  |  | 20:00 | 13570 |  | 0 |  | 13570
|  |  |  | 21:00 | 14150 |  | 0 |  | 14150
|  |  |  | 22:00 | 14280 |  | 0 |  | 14280
|  |  |  | 23:00 | 14470 |  | 0 |  | 14470
Probable Maximum Temperature: |  |  | 34.30°C
Probable Maximum Demand at Day Peak: |  |  | 11000.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14150.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14150.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 286.54 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:29 hrs on 11-06-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 10-06-2025 | [28 empty] | Date: | 10-06-2025 | [28 empty] | Date: | 10-06-2025 | [28 empty] | Date: | 10-06-2025 | [28 empty] | Date: | 10-06-2025 | [12 empty] | Date: | 10-06-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [12 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 16 | 50 | 0 | 0 | 0 | 69 | 371 | 0 | 320 | 54 | 0 | 17 | 0 | 0 | 0 | 0 | 90 | 0 | 450 | 141 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 17 | 7 | 0 | 509 | 0 | 0 | 0 | 0 | 1 | 65 | 0 | 0 | 100 | 100 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 9 | 0 | 219 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 175 | 0 | 343 | 340 | 50 | 202 | 16 | 115 | 80 | 170 | 50 | 13 | 114 | 42 | 52.2 | 0 | 35 | 320 | 320 | 376 | 32 | 30 | 151 | 0 | 0 | 81 | 30 | 0 | 0 | 0 | 54.5 | 93 | 146 | 152 | 0 | 0 | 4 | 8320.7 | 932 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 604 | 0 | 760.26 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 204 | 0 | 208 | 0 | 414 | 0 | 0 | 190 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 1235 | 0 | 5876.26 | 14196.96 | 95.59
01:00 | 0 | 17 | 16 | 50 | 0 | 0 | 0 | 69 | 359 | 0 | 320 | 54 | 0 | 17 | 0 | 0 | 0 | 0 | 90 | 0 | 450 | 140 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 17 | 7 | 0 | 483 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 100 | 100 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 16 | 0 | 218 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 175 | 0 | 350 | 340 | 50 | 193 | 17 | 100 | 80 | 170 | 57 | 13 | 114 | 42 | 52.2 | 0 | 35 | 315 | 320 | 350 | 32 | 30 | 152 | 0 | 0 | 81 | 30 | 0 | 0 | 0 | 54.5 | 46 | 101 | 152 | 0 | 0 | 0 | 8151.7 | 932 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605 | 0 | 758.32 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 204 | 0 | 208 | 0 | 340 | 0 | 0 | 190 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 1237 | 0 | 5776.32 | 13928.02 | 95.59
02:00 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 69 | 339 | 0 | 320 | 51 | 0 | 11 | 0 | 0 | 0 | 0 | 54 | 0 | 450 | 131 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 17 | 7 | 0 | 485 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 100 | 100 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 16 | 0 | 218 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 175 | 0 | 351 | 340 | 50 | 191 | 17 | 107 | 80 | 170 | 29 | 13 | 114 | 40 | 52.2 | 0 | 36 | 305 | 320 | 353 | 32 | 30 | 148 | 0 | 0 | 81 | 30 | 0 | 0 | 0 | 0 | 46 | 93 | 153 | 0 | 0 | 0 | 7923.2 | 931 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 604 | 0 | 758.01 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 200 | 0 | 205 | 0 | 338 | 0 | 0 | 190 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 120 | 220 | 0 | 0 | 1244 | 0 | 5749.01 | 13672.21 | 95.59
03:00 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 69 | 356 | 0 | 320 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 129 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 17 | 7 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 100 | 72 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 16 | 0 | 219 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 175 | 0 | 348 | 340 | 50 | 201 | 17 | 115 | 80 | 155 | 17 | 13 | 114 | 40 | 52.2 | 0 | 36 | 310 | 320 | 373 | 32 | 30 | 152 | 0 | 0 | 81 | 30 | 0 | 0 | 0 | 0 | 46 | 93 | 154 | 0 | 0 | 0 | 7756.2 | 932 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 0 | 760.23 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 193 | 0 | 192 | 0 | 360 | 0 | 0 | 190 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 1120 | 0 | 5541.23 | 13297.43 | 95.59
04:00 | 0 | 0 | 0 | 48.8 | 0 | 0 | 0 | 69 | 364 | 0 | 320 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 132 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 17 | 7 | 0 | 503 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 100 | 24 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 221 | 0 | 0 | 0 | 1109 | 0 | 51 | 0 | 175 | 0 | 352 | 340 | 50 | 196 | 17 | 113 | 80 | 155 | 18 | 13 | 114 | 38 | 52.2 | 0 | 36 | 315 | 320 | 373 | 32 | 30 | 154 | 0 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 46 | 93 | 154 | 0 | 0 | 0 | 7668 | 932 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 762.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 197 | 0 | 195 | 0 | 345 | 0 | 0 | 190 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 1100 | 0 | 5438.14 | 13106.14 | 95.59
05:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 66 | 352 | 0 | 320 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 131 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 17 | 7 | 0 | 466 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 60 | 12 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 221 | 0 | 0 | 0 | 1105 | 0 | 51 | 0 | 175 | 0 | 354 | 340 | 51 | 182 | 17 | 103 | 80 | 136 | 18 | 13 | 114 | 38 | 52.2 | 0 | 36 | 305 | 320 | 337 | 32 | 30 | 151 | 0 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 47 | 93 | 155 | 0 | 0 | 0 | 7533.2 | 932 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 542 | 0 | 773.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 191 | 0 | 190 | 0 | 325 | 0 | 0 | 190 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 120 | 220 | 0 | 0 | 1090 | 0 | 5360.42 | 12893.62 | 95.59
06:00 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 66 | 340 | 0 | 320 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 135 | 450 | 0 | 0 | 0 | 0 | 0 | 2 | 52 | 17 | 7 | 0 | 476 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 60 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 221 | 0 | 0 | 0 | 1000 | 2 | 51 | 0 | 127 | 0 | 300 | 300 | 51 | 192 | 17 | 115 | 80 | 120 | 12 | 13 | 114 | 38 | 25 | 2 | 36 | 315 | 320 | 364 | 32 | 30 | 149 | 0 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 45 | 102 | 154 | 0 | 3.14 | 0 | 7161.14 | 931 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.77 | 459 | 0 | 677.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 1.24 | 164 | 0 | 178 | 0 | 178 | 0 | 338 | 0 | 0.28 | 190 | 50 | 70 | 2 | 70 | 0 | 0 | 0.5 | 12 | 0.61 | 0 | 0 | 10 | 120 | 220 | 0 | 0 | 1000 | 0 | 5035.46 | 12196.6 | 95.59
07:00 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 66 | 341 | 0 | 320 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 139 | 450 | 0 | 0 | 0 | 0 | 0 | 7 | 52 | 17 | 7 | 0 | 475 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 36 | 0 | 1 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 221 | 0 | 0 | 0 | 960 | 5 | 51 | 0 | 127 | 0 | 300 | 300 | 51 | 190 | 16 | 115 | 80 | 100 | 9 | 13 | 114 | 38 | 25 | 14 | 36 | 305 | 320 | 364 | 33 | 30 | 138 | 0 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 45 | 102 | 154 | 1 | 9.67 | 0 | 7073.67 | 932 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.59 | 427 | 0 | 572.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 10.21 | 166 | 0 | 164 | 0 | 166 | 0 | 337 | 0 | 1.04 | 190 | 50 | 70 | 6 | 70 | 0 | 0 | 1.7 | 42 | 0.2 | 0 | 0 | 9 | 120 | 220 | 0 | 0 | 970 | 0 | 4925.19 | 11998.86 | 95.59
08:00 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 66 | 333 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 140 | 450 | 0 | 0 | 0 | 0 | 0 | 14 | 52 | 17.5 | 7 | 0 | 465 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 12 | 0 | 1 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 219 | 0 | 0 | 0 | 936 | 10 | 51 | 0 | 127 | 0 | 300 | 300 | 51 | 180 | 16 | 90 | 80 | 85 | 9 | 13 | 114 | 36 | 25 | 39 | 36 | 300 | 320 | 351 | 33 | 30 | 128 | 0 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 45 | 102 | 154 | 1 | 22.77 | 0 | 6820.27 | 932 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.35 | 430 | 0 | 577.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 20.21 | 160 | 0 | 159 | 0 | 161 | 0 | 324 | 0 | 2.12 | 200 | 49 | 70 | 12 | 70 | 0 | 0 | 3.3 | 84 | 0.35 | 0 | 0 | 10 | 110 | 220 | 0 | 0 | 950 | 0 | 4970.09 | 11790.36 | 95.59
09:00 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 66 | 316 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 140 | 450 | 0 | 0 | 0 | 0 | 0 | 22 | 52 | 17.5 | 7 | 0 | 475 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 3 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 218 | 0 | 0 | 0 | 928 | 14 | 51 | 0 | 127 | 0 | 300 | 300 | 51 | 190 | 16 | 100 | 80 | 85 | 9 | 13 | 114 | 36 | 8 | 53 | 36 | 295 | 320 | 336 | 33 | 30 | 129 | 0 | 0 | 81 | 30 | 0 | 0 | 0 | 0 | 45 | 50 | 152 | 2 | 35.12 | 0 | 6745.62 | 932 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.42 | 418 | 0 | 464.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 37.22 | 146 | 0 | 158 | 0 | 160 | 0 | 336 | 0 | 3.37 | 200 | 49 | 35 | 20 | 43 | 0 | 0 | 4.6 | 125 | 0.39 | 0 | 0 | 10 | 116 | 220 | 0 | 0 | 925 | 0 | 4899.02 | 11644.64 | 95.59
10:00 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 67 | 325 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 143 | 500 | 0 | 0 | 0 | 0 | 0 | 28 | 52 | 17.5 | 7 | 0 | 515 | 0 | 0 | 0 | 0 | 3 | 33 | 0 | 0 | 0 | 0 | 4 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 3 | 0 | 217 | 0 | 0 | 0 | 926 | 18 | 51 | 0 | 157 | 0 | 336 | 340 | 47 | 197 | 16 | 115 | 80 | 85 | 8 | 13 | 114 | 30 | 8 | 64 | 36 | 310 | 320 | 323 | 33 | 30 | 139 | 0 | 0 | 81 | 30 | 0 | 0 | 0 | 0 | 45 | 50 | 150 | 2 | 20.42 | 0 | 7077.92 | 932 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.51 | 373 | 0 | 413.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 47.66 | 156 | 0 | 172 | 0 | 174 | 0 | 349 | 0 | 4.28 | 200 | 49 | 35 | 21 | 0 | 0 | 0 | 4.3 | 161 | 0.39 | 0 | 0 | 10 | 120 | 220 | 0 | 0 | 620 | 0 | 4560.34 | 11638.26 | 95.59
11:00 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 337 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 142 | 500 | 0 | 0 | 0 | 0 | 0 | 31 | 35 | 17.5 | 7 | 0 | 515 | 0 | 0 | 0 | 0 | 10 | 33 | 0 | 0 | 0 | 0 | 2 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 832 | 16 | 51 | 0 | 170 | 0 | 339 | 340 | 33 | 194 | 0 | 115 | 80 | 85 | 9 | 13 | 114 | 32 | 0 | 70 | 35 | 310 | 320 | 334 | 33 | 30 | 135 | 0 | 0 | 80 | 30 | 0 | 0 | 0 | 0 | 45 | 50 | 148 | 2 | 45.93 | 0 | 7004.43 | 931 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.62 | 364 | 0 | 413.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 50.8 | 153 | 0 | 169 | 0 | 171 | 0 | 345 | 0 | 4.8 | 200 | 49 | 0 | 14 | 0 | 0 | 0 | 4.1 | 177 | 0.76 | 0 | 0 | 10 | 120 | 220 | 0 | 0 | 600 | 0 | 4540.06 | 11544.49 | 95.59
12:00 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 363 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 140 | 583 | 0 | 0 | 0 | 0 | 0 | 31 | 35 | 17.5 | 7 | 0 | 540 | 0 | 0 | 0 | 0 | 15 | 33 | 0 | 0 | 0 | 0 | 4 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 810 | 15 | 51 | 0 | 170 | 0 | 331 | 340 | 25 | 207 | 15 | 115 | 80 | 85 | 9 | 19 | 114 | 40 | 0 | 71 | 35 | 305 | 320 | 341 | 32 | 30 | 140 | 0 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 24 | 50 | 146 | 1 | 40.45 | 0 | 7122.95 | 931 | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.22 | 374 | 0 | 424.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 57.65 | 157 | 0 | 173 | 0 | 175 | 0 | 383 | 0 | 4.96 | 189 | 49 | 2 | 29 | 0 | 0 | 0 | 4.4 | 192 | 0.74 | 0 | 0 | 10 | 120 | 220 | 0 | 0 | 602 | 0 | 4642.55 | 11765.5 | 95.59
13:00 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 367 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 140 | 583 | 0 | 0 | 0 | 0 | 0 | 31 | 52 | 17.5 | 7 | 0 | 540 | 0 | 0 | 0 | 0 | 26 | 33 | 0 | 0 | 0 | 0 | 4 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 928 | 14 | 51 | 0 | 170 | 0 | 332 | 340 | 25 | 205 | 16 | 102 | 80 | 93 | 14 | 19 | 114 | 34 | 0 | 67 | 21 | 320 | 320 | 381 | 32 | 30 | 150 | 0 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 26 | 53 | 148 | 2 | 45.88 | 0 | 7325.38 | 932 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.04 | 441 | 0 | 518.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 53.42 | 170 | 0 | 189 | 0 | 192 | 0 | 414 | 0 | 4.84 | 200 | 48 | 35 | 11 | 0 | 0 | 0 | 6.7 | 170 | 0.65 | 0 | 0 | 10 | 115 | 220 | 0 | 0 | 680 | 0 | 4973.74 | 12299.12 | 95.59
14:00 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 370 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 142 | 583 | 0 | 0 | 0 | 0 | 0 | 28 | 70 | 17.5 | 0 | 0 | 525 | 0 | 0 | 0 | 0 | 24 | 33 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 957 | 7 | 51 | 0 | 170 | 0 | 333 | 340 | 25 | 201 | 16 | 93 | 80 | 111 | 26 | 19 | 114 | 40 | 0 | 43 | 21 | 315 | 320 | 383 | 32 | 30 | 149 | 0 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 43 | 79 | 148 | 2 | 37.32 | 0 | 7428.82 | 932 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.07 | 487 | 0 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 46.1 | 175 | 0 | 188 | 0 | 192 | 0 | 414 | 0 | 4.34 | 200 | 48 | 35 | 25 | 0 | 0 | 0 | 6 | 162 | 0.67 | 0 | 0 | 10 | 120 | 220 | 0 | 0 | 850 | 0 | 5082.18 | 12511 | 95.59
15:00 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 371 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 138 | 583 | 0 | 0 | 0 | 0 | 0 | 23 | 70 | 17.5 | 7 | 0 | 545 | 0 | 0 | 0 | 0 | 7 | 33 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 957 | 15 | 51 | 0 | 170 | 0 | 326 | 330 | 25 | 207 | 16 | 100 | 80 | 136 | 27 | 19 | 114 | 40 | 0 | 49 | 22 | 310 | 320 | 378 | 32 | 30 | 147 | 0 | 0 | 78 | 30 | 0 | 0 | 0 | 0 | 45 | 85 | 145 | 1 | 37.32 | 0 | 7428.82 | 931 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.83 | 502 | 0 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 38.37 | 176 | 0 | 188 | 0 | 193 | 0 | 414 | 0 | 3.46 | 200 | 48 | 35 | 21 | 0 | 0 | 0 | 5.1 | 135 | 0.56 | 0 | 0 | 11 | 115 | 220 | 0 | 0 | 900 | 0 | 5176.32 | 12605.14 | 95.59
16:00 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 374 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 142 | 583 | 0 | 0 | 0 | 0 | 0 | 14 | 52 | 17.5 | 7 | 0 | 510 | 0 | 0 | 0 | 0 | 9 | 33 | 0 | 0 | 6 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 912 | 12 | 51 | 0 | 170 | 0 | 329 | 335 | 24 | 196 | 15 | 105 | 80 | 120 | 28 | 19 | 114 | 40 | 10 | 34 | 22 | 305 | 320 | 361 | 32 | 30 | 146 | 0 | 0 | 78 | 30 | 0 | 0 | 0 | 0 | 24 | 65 | 145 | 1 | 24.51 | 0 | 7207.01 | 931 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.91 | 688 | 0 | 526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 25.55 | 176 | 0 | 189 | 0 | 193 | 0 | 391 | 0 | 2.43 | 200 | 48 | 35 | 13 | 0 | 0 | 0 | 3.5 | 92 | 0.33 | 0 | 0 | 11 | 115 | 220 | 0 | 0 | 900 | 0 | 5199.72 | 12406.73 | 95.59
17:00 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 345 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 140 | 583 | 0 | 0 | 0 | 0 | 0 | 2 | 52 | 17.5 | 7 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 12 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 880 | 2 | 51 | 0 | 162 | 0 | 315 | 340 | 25 | 187 | 15 | 113 | 80 | 120 | 28 | 19 | 114 | 38 | 16 | 24 | 22 | 305 | 320 | 346 | 32 | 30 | 147 | 0 | 0 | 78 | 30 | 0 | 0 | 0 | 0 | 24 | 65 | 146 | 1 | 11.65 | 0 | 7091.15 | 931 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.19 | 786 | 0 | 467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 12.21 | 164 | 0 | 181 | 0 | 181 | 0 | 376 | 0 | 1 | 200 | 48 | 35 | 6 | 25 | 0 | 0 | 1.9 | 44 | 0.04 | 0 | 0 | 10 | 114 | 220 | 0 | 0 | 800 | 0 | 4983.34 | 12074.49 | 95.59
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 142 | 500 | 0 | 0 | 0 | 0 | 0 | 2 | 52 | 17.5 | 7 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 12 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 907 | 0 | 51 | 0 | 163 | 0 | 300 | 280 | 25 | 199 | 15 | 115 | 80 | 120 | 38 | 20 | 114 | 36 | 16 | 10 | 25 | 300 | 320 | 324 | 32 | 30 | 138 | 0 | 0 | 78 | 30 | 0 | 0 | 0 | 0 | 24 | 65 | 147 | 0 | 3.06 | 0 | 6569.56 | 931 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.98 | 758 | 0 | 472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3.39 | 157 | 0 | 171 | 0 | 163 | 0 | 352 | 0 | 0.31 | 200 | 48 | 35 | 2 | 35 | 0 | 0 | 0.6 | 13 | 0.04 | 0 | 0 | 10 | 100 | 180 | 0 | 0 | 800 | 0 | 4810.32 | 11379.88 | 95.59
19:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 300 | 145 | 583 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 17.5 | 7 | 0 | 536 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 48 | 12 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1130 | 0 | 51 | 0 | 157 | 0 | 329 | 310 | 25 | 207 | 15 | 115 | 80 | 128 | 47 | 17 | 114 | 42 | 20 | 0 | 36 | 310 | 320 | 382 | 32 | 30 | 143 | 0 | 0 | 80 | 30 | 0 | 0 | 0 | 0 | 41 | 99 | 147 | 0 | 0 | 0 | 7388.5 | 884 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 866 | 2 | 538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 177 | 0 | 167 | 0 | 414 | 0 | 0 | 200 | 48 | 100 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 200 | 0 | 0 | 835 | 0 | 5221 | 12609.5 | 95.59
19:30 | 0 | 17 | 8 | 120 | 0 | 0 | 0 | 0 | 337 | 0 | 322 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 14 | 300 | 140 | 583 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 17.5 | 7 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 100 | 12 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 1 | 0 | 218 | 0 | 0 | 0 | 1044 | 0 | 51 | 0 | 163 | 0 | 340 | 340 | 25 | 187 | 15 | 115 | 80 | 170 | 47 | 17 | 114 | 4 | 52.2 | 0 | 35 | 310 | 320 | 345 | 32 | 30 | 143 | 0 | 0 | 80 | 30 | 0 | 0 | 0 | 0 | 85 | 117 | 149 | 0 | 0 | 5 | 7481.7 | 884 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1083 | 17 | 622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 187 | 0 | 182 | 0 | 382 | 0 | 0 | 200 | 48 | 115 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 1020 | 0 | 5717 | 13198.7
20:00 | 0 | 17 | 0 | 120 | 0 | 30 | 0 | 0 | 350 | 0 | 320 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 140 | 583 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 17.5 | 7 | 0 | 491 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 76 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 4 | 0 | 218 | 0 | 0 | 0 | 1044 | 0 | 51 | 0 | 163 | 0 | 342 | 340 | 25 | 209 | 16 | 115 | 80 | 170 | 47 | 0 | 90 | 16 | 34 | 0 | 36 | 315 | 320 | 345 | 32 | 30 | 148 | 0 | 0 | 80 | 30 | 0 | 0 | 0 | 0 | 85 | 118 | 149 | 0 | 0 | 8 | 7477.5 | 884 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1058 | 17 | 705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 181 | 0 | 187 | 0 | 378 | 0 | 0 | 190 | 48 | 114 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 120 | 220 | 0 | 0 | 1060 | 0 | 5788 | 13265.5 | 95.59
21:00 | 0 | 0 | 0 | 120 | 0 | 120 | 0 | 0 | 342 | 0 | 321 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 141 | 583 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 17.5 | 0 | 0 | 465 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 24 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 218 | 0 | 0 | 0 | 930 | 0 | 51 | 0 | 163 | 0 | 348 | 340 | 27 | 219 | 16 | 68 | 80 | 100 | 26 | 0 | 52 | 36 | 8 | 0 | 36 | 300 | 320 | 337 | 32 | 30 | 142 | 0 | 0 | 80 | 30 | 0 | 0 | 0 | 0 | 85 | 120 | 150 | 0 | 0 | 10 | 7202.5 | 932 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1026 | 17 | 668.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 177 | 0 | 184 | 0 | 374 | 0 | 0 | 180 | 48 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 110 | 220 | 0 | 0 | 1000 | 0 | 5660.42 | 12862.92 | 95.59
22:00 | 0 | 0 | 0 | 120 | 0 | 110 | 0 | 0 | 353 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 142 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 7 | 0 | 440 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 12 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 219 | 0 | 0 | 0 | 809 | 0 | 51 | 0 | 168 | 0 | 355 | 340 | 27 | 191 | 16 | 50 | 80 | 51 | 26 | 11 | 52 | 36 | 0 | 0 | 36 | 310 | 320 | 349 | 32 | 28 | 152 | 0 | 0 | 81 | 30 | 0 | 0 | 0 | 0 | 85 | 120 | 150 | 0 | 0 | 6 | 6811 | 856 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 828 | 17 | 671.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 184 | 0 | 191 | 0 | 398 | 0 | 0 | 180 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 120 | 220 | 0 | 0 | 900 | 0 | 5374.37 | 12185.37 | 95.59
23:00 | 0 | 0 | 0 | 120 | 0 | 110 | 0 | 0 | 347 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 138 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 463 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 12 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 163 | 0 | 0 | 0 | 817 | 0 | 51 | 0 | 168 | 0 | 355 | 340 | 26 | 201 | 16 | 62 | 80 | 60 | 45 | 6 | 70 | 34 | 5 | 0 | 36 | 310 | 320 | 378 | 32 | 30 | 152 | 0 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 55 | 105 | 157 | 0 | 0 | 0 | 6794 | 856 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 786 | 17 | 677.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 180 | 0 | 186 | 0 | 414 | 0 | 0 | 180 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 120 | 220 | 0 | 0 | 800 | 0 | 5263.93 | 12057.93 | 95.59
Total KWH | 0 | 64320 | 32640 | 2740936 | 0 | 429781 | 0 | 682681.82 | 8535600 | 0 | 7664300 | 218160 | 0 | 65520 | 0 | 0 | 0 | 0 | 211680 | 11520 | 8641500 | 3314676 | 12524545 | 0 | 0 | 0 | 0 | 0 | 221155 | 1497600 | 381600 | 162360 | 0 | 11714545.45 | 0 | 0 | 0 | 0 | 120960 | 959479 | 0 | 0 | 861120 | 377280 | 17285 | 4010540 | 0 | 1075200 | 0 | 0 | 0 | 0 | 142000.2 | 0 | 5165400 | 0 | 0 | 0 | 23247270 | 119610 | 1169792 | 0 | 3847272 | 0 | 8309100 | 8026000 | 871200 | 4804000 | 366984 | 2469120 | 1910780 | 2840640 | 609840 | 307540 | 2489760 | 869760 | 521117 | 548027 | 768960 | 7506500 | 7684700 | 8875000 | 752000 | 675720 | 3498300 | 2016 | 0 | 1932480 | 713568 | 0 | 0 | 0 | 98640 | 1148400 | 2104800 | 3520320 | 14800 | 331910 | 35280 | 174835590.47 | 22226909 | 8688672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 686160 | 15039998 | 87840 | 14438771 | 0 | 0 | 0 | 351648 | 0 | 0 | 0 | 0 | 0 | 740590 | 0 | 393000 | 4102364 | 0 | 4568409 | 0 | 4633991 | 0 | 8835345.5 | 0 | 36540 | 4675000 | 1073890 | 1799385 | 184406 | 1556889 | 0 | 0 | 47176.56 | 1416960 | 4789 | 0 | 0 | 249883 | 2794000 | 5323680 | 0 | 0 | 22578909.09 | 0 | 126535205.15 | 301370795.62

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 10-06-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11765.5 | MW | 12:00 Hr. | Energy Generated |  |  | 301.3708 |  | MKWHr.
| Day Peak Demand |  |  | 11765.5 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.709 |  | MKWHr.
| Evening Peak Generation |  |  | 13265.5 | MW | 20:00 Hr. | Energy Demand |  |  | 302.0798 |  | MKWHr.
| Evening Peak Demand |  |  | 13340.5 | MW | 20:00 Hr. | Maximum Temperature |  |  | 36.8 |  | °C
| Minimum Generation of the Day |  |  | 11544.49 | MW | 11:00 Hr. | Total Gas Supplied |  |  | 1197.83 |  | MMCFD
| Maximum Generation of the Day |  |  | 14196.96 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.5219 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 56.7925 | 0 | 2.1014 | 0 | 0 | 0.22115 | 0 | 0 | 59.1151 | Gas | 167.0027 | Gas | 568024120.3385
| Chattogram Zone |  |  | 6.2406 | 23.2473 | 2.3399 | 0 | 4.0105 | 0.13689 | 0 | 0.12096 | 36.0961 | Coal | 66.6151 | Coal | 458551817.8103
| Cumilla Zone |  |  | 29.6127 | 0 | 9.6994 | 0 | 0 | 0.54803 | 0.86976 | 0 | 40.7299 | HFO | 21.3236 | HFO | 391693929.484
| Mymensingh Zone |  |  | 3.5203 | 0 | 3.3871 | 0 | 0 | 0.34671 | 0 | 0 | 7.2542 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 31.6403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.6403 | Hydro | 4.0105 | Hydro | 401054
| Khulna Zone |  |  | 8.6887 | 15.04 | 0.08784 | 0 | 0 | 0.68616 | 22.2269 | 0 | 46.7296 | Solar | 4.7624 | Solar | 77233750.0616
| Barishal Zone |  |  | 8.3676 | 22.5789 | 0 | 0 | 0 | 0.004789 | 0 | 0 | 30.9513 | Import | 37.5354 | Import | 166469045.2
| Rajshahi Zone |  |  | 22.1401 | 0 | 0.35165 | 0 | 0 | 1.1701 | 14.4388 | 0 | 38.1007 | Wind | 0.12096 | Wind | 1770854.4
| Rangpur Zone |  |  | 0 | 5.7489 | 3.3563 | 0 | 0 | 1.6485 | 0 | 0 | 10.7537
| Total |  |  | 167.0027 | 66.6151 | 21.3236 | 0 | 4.0105 | 4.7624 | 37.5354 | 0.12096 | 301.3708
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 568024120.3385 |  | Hydro | 401054
|  |  |  | Coal | 458551817.8103 |  | Solar | 77233750.0616
|  |  |  | HFO | 391693929.484 |  | Import | 166469045.2
|  |  |  | HSD | 0 |  | Wind | 1770854.4
[5 empty] | Total: | 166,41,44,571 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 423400 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.2269 | Peak Hr Flow | 884.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 8911345.46 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 14.4388 | Peak Hr Flow | 705.00 MW at 20:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 320 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.86976 | Peak Hr Flow | 16.00 MW at 20:00 hrs.
Maximum Power Flow: |  |  | MW: | 382 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 37.5354 | Peak Hr Flow | 1605.00 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3634
|  |  |  | Chattogram |  | 0 |  | 1190
|  |  |  | Cumilla |  | 15 |  | 896
|  |  |  | Mymensingh |  | 0 |  | 1321
|  |  |  | Sylhet |  | 22 |  | 612
|  |  |  | Khulna |  | 0 |  | 1881
|  |  |  | Barishal |  | 0 |  | 516
|  |  |  | Rajshahi |  | 0 |  | 1594
|  |  |  | Rangpur |  | 35 |  | 1063
|  |  |  | Total |  | 72 |  | 12707
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 489
|  |  |  | Total Unavailable Capacity |  |  |  | 789
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:12 | Niamatpur 132/33kV S/S Transformer-2 (417T) HT is restored.
|  | 08:12 | Niamatpur 132/33kV S/S Transformer-2 (417T) LT is restored.
|  | 08:26 | Chandpur 132/33kV S/S 33 kV T-2 section is restored.
|  | 09:00 | Chandpur 132/33kV S/S 33 kV T-1 Section is restored.
| 09:11 | 12:50 | Maniknagar 132/33kV S/S Transformer GT-1 HT Scheduled S/D Due to Maintenance work at 33KV
side. Shut down taken by Mr. Rokonul Islam, SDE, DPDC.
| 10:09 |  | Raozan 25 MW PP Shutdown
| 11:07 | 12:57 | Chowmuhani 132/33kV S/S TR2-425T LT Scheduled S/D Due to Tr-02 X-former & associate 33 KV | [7 empty] | 30.0MW load
|  |  | BUS Section Emergency shutdown taken for 33KV Incoming DS to BUSBAR R Phase (red hot) | [7 empty] | interrup.
Loop Maintenance.
| 11:07 | 12:57 | Chowmuhani 132/33kV S/S TR2-425T HT Scheduled S/D Due to Tr-02 X-former & associate 33 KV | [7 empty] | 30.0MW load
|  |  | BUS Section Emergency shutdown taken for 33KV Incoming DS to BUSBAR R Phase (red hot) | [7 empty] | interrup.
Loop Maintenance.
| 12:00 |  | Day Peak Gen: 11761 MW.
|  | 12:48 | Kodda 132/33kV S/S Summit 149 MW PS is restored.
| 14:56 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U1
|  | 15:20 | Barapukuria 230/132/33kV S/S 132/33 KV T-3, 404T HT is restored.
|  | 15:25 | Barapukuria 230/132/33kV S/S 132/33 KV T-3, 404T LT is restored.
| 15:57 |  | BIPTC S/S 20DF21 Tripped showing 87.1(Differential relay) relays Due to Tripped by C1
unbalance 60/61 stage-3 instant L2
| 19:19 |  | Raozan 25 MW PP Synchronized
| 19:55 | 20:11 | Kasba 132/33kV S/S TR-1 LT Tripped showing OC/EF relays Due to Kasba-1 PBS OC/EF due to | [7 empty] | 10.0MW load
|  |  | bad weather | [7 empty] | interrup.
| 19:57 |  | Ghorasal Repowered CCPP Unit-4 Synchronized
| 20:00 |  | Evening peak Generation is 13265 MW
|  | 20:24 | Daudkandi-Sonargaon 132 kV Ckt-2 is restored.
| 20:55 | 21:34 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing Ph-Y,Z1, Master realy Trip.
relays.
| 21:37 | 21:48 | Nawabganj 132/33kV S/S TR-2 LT Tripped showing Overcurrent protection relay relays.
| 21:56 | 00:24 | Kasba 132/33kV S/S TR-1 HT Scheduled S/D Due to 33kV kasba-1 feeder PT Jumper Maintenance
by PBS
| 21:56 | 00:24 | Kasba 132/33kV S/S TR-1 LT Scheduled S/D Due to 33kV kasba-1 feeder PT Jumper Maintenance
by PBS
| 22:00 | 07:34 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-1 Forced S/D from Bog-Sherpur 132/33kV end Due to As
per the instructions of ALDC.
| 22:02 | 22:40 | Shahjadpur 132/33kV S/S T-2(415T) HT Forced S/D Due to Emergency maintenance work | [7 empty] | 24.0MW load
interrup.
| 22:14 | 23:38 | Dhamrai 132/33kV S/S Transformer-2 LT Tripped showing O/C,SPS,86 Relay relays Due to PBS | [7 empty] | 20.0MW load
|  |  | feeder fault | [7 empty] | interrup.
| 22:14 | 23:38 | Dhamrai 132/33kV S/S Transformer-1 LT Tripped showing O/C,SPS,86 relay relays Due to PBS | [7 empty] | 20.0MW load
|  |  | feeder fault | [7 empty] | interrup.
| 01:10 |  | Sikalbaha 225 MW ST was shutdown.
| 02:26 |  | Noapara 132/33kV S/S T-2 LT Tripped showing 7SJ81 SIEMENES relays Due to 33kV REB-1 | [7 empty] | 23.0MW load
|  |  | FEEDER FAULT | [7 empty] | interrup.
| 02:26 | 02:57 | Noapara 132/33kV S/S T-1 LT Tripped showing 7SJ81 SIEMENS relays Due to 33kV REB-1 FEEDER | [7 empty] | 23.0MW load
|  |  | FAULT | [7 empty] | interrup.
| 03:25 | 05:23 | Noapara 132/33kV S/S T-2 HT Scheduled S/D Due to None | [7 empty] | 14.5MW load
interrup.
| 06:44 | 07:57 | Barishal-Patuakhali(Barguna T at Bakergonj) 132 kV Ckt Scheduled S/D from Barguna | [7 empty] | 14.0MW load
|  |  | 132/33kV end Due to R phase CT connector flashing and from Patuakhali 132/33kV end Due to | [7 empty] | interrup. Barguna
|  |  | Barguna ss red hot maintenence | [7 empty] | 132/33kV end and
13.0MW load
interrup.
Patuakhali 132/33kV
end
| 07:30 |  | Aminbazar-Mirpur 132kV Ckt-2 Scheduled S/D from Mirpur 132/33kV end Due to Loop
Conductor(CT to CB) Change work on Mirpur S/S.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 10-06-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 30 | 429781 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 120 | 2740936 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 682681.82 | Allocation limit by Titas, instructed by DS(Gen)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 350 | 8535600 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 8641500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 140 | 3314676 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 218160 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17.5 | 381600 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 7 | 162360 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 32640 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 16 | 65520 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 64320 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 11520 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 211680 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 221155 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 491 | 11714545.45 | None
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 583 | 12524545 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 320 | 7664300 | On test
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 1497600 | -
Dhaka Area Total |  |  |  |  | 5939.724 | 2499.5 | 59115120.27
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 4 | 142000.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 119610 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 167 | 4010540 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 5165400 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 33 | 959479 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 76 | 861120 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 42 | 1075200 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 17285 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 377280 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1044 | 23247270 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 120960 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 0 | 0 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4895.72 | 1584 | 36096144.2
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 209 | 4804000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 342 | 8309100 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 8026000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 16 | 366984 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 25 | 871200 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 163 | 3847272 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1169792 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 768960 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1910780 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 170 | 2840640 | -
| Import (Tripura) |  | Import | 0 | 160 | 16 | 869760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 34 | 521117 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 0 | 307540 | Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 90 | 2489760 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 47 | 609840 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 2469120 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 548027 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1734 | 40729892
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 149 | 3520320 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14800 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 118 | 2104800 | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 85 | 1148400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 331910 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 8 | 35280 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 98640 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 360 | 7254150
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 32 | 752000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 675720 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 148 | 3498300 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 713568 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1932480 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 2016 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7506500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 345 | 8875000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7684700 | -
Sylhet Area Total |  |  |  |  | 2325 | 1300 | 31640284
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 884 | 22226909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 340 | 8688672 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 87840 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 686160 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1058 | 15039998 | U#1 Reserve shut down as per NLDC Communication
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3699.2 | 2299 | 46729579
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 10 | 249883 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2794000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1060 | 22578909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5323680 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 0 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4789 | -
Barishal Area Total |  |  |  |  | 2236 | 1410 | 30951261.09
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Cooling System Problem
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 168 | 4102364 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 181 | 4568409 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 187 | 4633991 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 378 | 8835345.5 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 351648 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 36540 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 705 | 14438771 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 393000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 740590 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 1619 | 38100658.5
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 48 | 1073890 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 190 | 4675000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 108 | 1556889 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 47176.56 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 114 | 1799385 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 184406 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1416960 | -
Rangpur Area Total |  |  |  |  | 950 | 460 | 10753706.56
Eastern Grid Total |  |  |  |  | 16705.895 | 7477.5 | 174835590.47
Western Grid Total |  |  |  |  | 10338.16 | 5788 | 126535205.15
National Grid Total |  |  |  |  | 27044.055 | 13265.5 | 301370795.62
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 10-06-2025
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7616.41 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5019.2 | MW
i) Dhaka area |  |  | 3633.91 |  | MW | i) Khulna area |  |  |  | 1881.4 | MW
ii) Chattogram area |  |  | 1190.5 |  | MW | ii) Barishal area |  |  |  | 516 | MW
iii) Cumilla area |  |  | 881 |  | MW | iii) Rajshahi area |  |  |  | 1593.8 | MW
iv) Mymensingh area |  |  | 1321 |  | MW | iv) Rangpur area |  |  |  | 1028 | MW
v) Sylhet area |  |  | 590 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12635.61 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 80 | 21:00 | 133 | Patuakhali | 94 | 22:00
2 | AKSML | 107 | 00:00 | 68 | Jaldhaka | 96 | 21:00 | 134 | Payra | 42 | 23:00
3 | Aftabnagar | 30 | 00:00 | 69 | Jamalpur | 165 | 22:00 | 135 | Postogola | 44 | 00:00
4 | Agargaon | 103 | 21:00 | 70 | Jashore | 149 | 23:00 | 136 | Purbachal | 18 | 21:00
5 | Agrabad | 72 | 01:00 | 71 | Jhenaidah | 144 | 22:00 | 137 | Purbasadipur | 138 | 22:00
6 | Amnura | 45 | 00:00 | 72 | Joydebpur | 76 | 19:30 | 138 | Rahanpur | 39 | 23:00
7 | Ashuganj | 100.5 | 00:00 | 73 | Joypurhat | 73 | 23:00 | 139 | Rahim | 1 | 01:00
8 | BSRM | 197 | 23:00 | 74 | Juldah | 13 | 00:00 | 140 | Rajbari | 92 | 22:00
9 | Bagerhat | 89 | 23:00 | 75 | KSRM | 10 | 00:00 | 141 | Rajendrapur | 104 | 20:00
10 | Bajitpur | 60 | 20:00 | 76 | Kabirpur | 120 | 21:00 | 142 | Rajshahi | 118 | 00:00
11 | Bakulia | 81 | 00:00 | 77 | Kachua | 105 | 00:00 | 143 | Rajshahi-230 | 100 | 21:00
12 | Banani | 26 | 19:00 | 78 | Kallyanpur | 90 | 00:00 | 144 | Ramganj | 126 | 19:30
13 | Bangabhaban | 4 | 11:00 | 79 | Kalurghat | 24 | 00:00 | 145 | Rampur | 40 | 00:00
14 | Barapukuria | 72 | 23:00 | 80 | Kamrangirchar | 32 | 00:00 | 146 | Rangamati | 18 | 20:00
15 | Barguna | 26 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 156 | 20:00
16 | Barishal | 120 | 23:00 | 82 | Kasba | 43 | 00:00 | 148 | Ruppur | 7.6 | 16:00
17 | Barishal-230 | 116 | 00:00 | 83 | Kazla | 64 | 01:00 | 149 | SSM | 0 | 00:00
18 | Baroaulia | 52 | 01:00 | 84 | Keranigonj | 78 | 21:00 | 150 | Saidpur | 113 | 22:00
19 | Baroirhat | 66 | 00:00 | 85 | Khagrachori | 30 | 00:00 | 151 | Satkhira | 157 | 23:00
20 | Bashundhara | 150 | 21:00 | 86 | Khulna | 66 | 20:00 | 152 | Satmasjid | 84 | 19:30
21 | BashundharaCement | 1 | 07:00 | 87 | Khulshi | 150 | 15:00 | 153 | Savar | 114 | 21:00
22 | Beanibazar | 80 | 03:00 | 88 | Kishoreganj | 159 | 20:00 | 154 | SevenRings | 0.73 | 11:00
23 | Benapole | 74 | 22:00 | 89 | Kodda | 141 | 19:00 | 155 | ShahCement | 3 | 21:00
24 | Bhaluka | 131 | 21:00 | 90 | Kulaura | 50 | 20:00 | 156 | Shahjadpur | 89 | 21:00
25 | Bhandaria | 67 | 22:00 | 91 | Kurigram | 70 | 19:00 | 157 | Shahjibazar | 124 | 00:00
26 | Bhangura | 46 | 22:00 | 92 | Kushtia | 142 | 21:00 | 158 | Shahmirpur | 47 | 00:00
27 | Bheramara(GK) | 74 | 22:00 | 93 | Lalbag | 13 | 19:00 | 159 | Shariatpur | 105 | 00:00
28 | Bhulta | 112 | 23:00 | 94 | Lalmonirhat | 72 | 20:00 | 160 | Sherpur | 186 | 23:00
29 | Bog-Sherpur | 62 | 01:00 | 95 | MI_Cement | 1 | 12:00 | 161 | Shikalbaha | 27 | 00:00
30 | Bogura | 178 | 23:00 | 96 | Madanganj | 38 | 09:00 | 162 | Shitalakhya | 57.9 | 16:00
31 | Borhanuddin | 92 | 22:00 | 97 | Madaripur | 135 | 00:00 | 163 | Sholosohor | 36 | 00:00
32 | Brahmanbaria | 138 | 04:00 | 98 | Madartek | 78 | 21:00 | 164 | Shyampur | 52 | 13:00
33 | Cantonment | 114 | 19:00 | 99 | Madunaghat | 57 | 00:00 | 165 | Siddhirganj | 80 | 17:00
34 | Chandina | 22.34 | 05:00 | 100 | Magura | 75 | 23:00 | 166 | Sirajganj | 120 | 22:00
35 | Chandpur | 94 | 00:00 | 101 | Mahasthangarh | 100 | 00:00 | 167 | Sonargaon | 53 | 00:00
36 | Chandraghona | 37 | 00:00 | 102 | Manikganj | 106 | 21:00 | 168 | Sreemongol | 93 | 19:00
37 | Chapai | 71 | 23:00 | 103 | Maniknagar | 60 | 00:00 | 169 | Sreepur | 65 | 21:00
38 | Charsaidpur | 8 | 16:00 | 104 | Matarbari | 49 | 00:00 | 170 | Srinagar | 56.4 | 00:00
39 | Chauddagram | 80 | 01:00 | 105 | Matuail | 34 | 00:00 | 171 | Sunamganj | 60 | 22:00
40 | Chhatak | 42 | 23:00 | 106 | Millgate | 43 | 18:30 | 172 | Sylhet | 52 | 21:00
41 | Chowmuhani | 250 | 19:00 | 107 | Mirpur | 97.5 | 21:00 | 173 | Sylhet-132 | 133 | 19:00
42 | Chuadanga | 123 | 00:00 | 108 | Mirsorai | 8 | 00:00 | 174 | TK | 38 | 00:00
43 | Coxsbazar | 137 | 00:00 | 109 | Mirzapur | 43 | 21:00 | 175 | Tangail | 190 | 22:00
44 | Cumilla(N) | 163 | 00:00 | 110 | Mithapukur | 70 | 19:30 | 176 | Thakurgaon | 122 | 01:00
45 | Cumilla(S) | 161 | 19:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 86 | 19:00
46 | Daudkandi | 141 | 19:30 | 112 | Mogbazar | 91.8 | 19:00 | 178 | Ullahpara | 44 | 22:00
47 | Dhaka | 28 | 21:00 | 113 | Mongla | 25 | 23:00 | 179 | Ullon | 46 | 21:00
48 | Dhamrai | 92 | 21:00 | 114 | Motijheel | 28 | 21:00 | 180 | Uttara | 66 | 23:00
49 | Dhanmondi | 81 | 19:00 | 115 | Muktagacha | 46 | 22:00 | 181 | UttaraNew | 49 | 00:00
50 | Dohazari | 110 | 01:00 | 116 | Munshiganj | 128 | 00:00 | 182 | Zigatola | 58 | 01:00
51 | Faridpur | 176 | 21:00 | 117 | Muradnagar | 35 | 00:00
52 | Fatullah | 48 | 00:00 | 118 | Mymensingh | 223 | 00:00
53 | Fenchuganj | 46 | 23:00 | 119 | Naogaon | 154 | 23:00
54 | Feni | 129 | 00:00 | 120 | Narail | 68 | 21:00
55 | GPH | 1 | 00:00 | 121 | Narinda | 46 | 00:00
56 | Ghatail | 86 | 00:00 | 122 | Narshingdi | 161 | 01:00
57 | Ghorashal | 15 | 00:00 | 123 | Natore | 183 | 23:00
58 | Ghorashal-230 | 74 | 19:30 | 124 | Nawabganj | 66.6 | 21:00
59 | Goalpara | 42 | 00:00 | 125 | Netrakona | 162 | 21:00
60 | Gollamari | 96 | 00:00 | 126 | New | 38 | 14:00
61 | Gopalganj | 123.2 | 22:00 | 127 | Niamatpur | 86 | 01:00
62 | Gulshan | 76 | 19:00 | 128 | Noapara | 47 | 23:00
63 | Halishahar | 31 | 19:00 | 129 | PHP | 9 | 19:30
64 | HaripurSBU | 67 | 19:30 | 130 | Pabna | 124 | 23:00
65 | Hasnabad | 60 | 23:00 | 131 | Palashbari | 130 | 03:00
66 | Hathazari | 80 | 23:00 | 132 | Panchagarh | 62 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 10-06-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14196.96 | 90 |  | 14291.01
1:00 | 13928.02 | 70 |  | 14001.02
2:00 | 13672.21 | 74 |  | 13749.21
3:00 | 13297.43 | 70 |  | 13370.43
4:00 | 13106.14 | 43 |  | 13151.14
5:00 | 12893.62 | 35 |  | 12930.62
6:00 | 12196.6 | 0 |  | 12196.6
7:00 | 11998.86 | 0 |  | 11998.86
8:00 | 11790.36 | 0 |  | 11790.36
9:00 | 11644.64 | 0 |  | 11644.64
10:00 | 11638.26 | 0 |  | 11638.26
11:00 | 11544.49 | 0 |  | 11544.49
12:00 | 11765.5 | 0 |  | 11765.5
13:00 | 12299.12 | 0 |  | 12299.12
14:00 | 12511 | 0 |  | 12511
15:00 | 12605.14 | 0 |  | 12605.14
16:00 | 12406.73 | 0 |  | 12406.73
17:00 | 12074.49 | 0 |  | 12074.49
18:00 | 11379.88 | 0 |  | 11379.88
19:00 | 12609.5 | 49 |  | 12660.5
19:30 | 13198.7 | 78 |  | 13280.7
20:00 | 13265.5 | 72 |  | 13340.5
21:00 | 12862.92 | 84 |  | 12950.92
22:00 | 12185.37 | 62 |  | 12250.37
23:00 | 12057.93 | 60 |  | 12120.93
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 10-06-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8320.7 | 5876.26 | 14196.96 | DAILY GENERATION CURVE
00:30 | 8236.2 | 5826.29 | 14062.49
01:00 | 8151.7 | 5776.32 | 13928.02 | 10-06-2025
01:30 | 8037.45 | 5762.665 | 13800.115
02:00 | 7923.2 | 5749.01 | 13672.21
02:30 | 7839.7 | 5645.12 | 13484.82
03:00 | 7756.2 | 5541.23 | 13297.43
03:30 | 7712.1 | 5489.685 | 13201.785
04:00 | 7668 | 5438.14 | 13106.14
04:30 | 7600.6 | 5399.28 | 12999.88
05:00 | 7533.2 | 5360.42 | 12893.62
05:30 | 7347.17 | 5197.94 | 12545.11
06:00 | 7161.14 | 5035.46 | 12196.6
06:30 | 7117.405 | 4980.325 | 12097.73
07:00 | 7073.67 | 4925.19 | 11998.86
07:30 | 6946.97 | 4947.64 | 11894.61
08:00 | 6820.27 | 4970.09 | 11790.36
08:30 | 6782.945 | 4934.555 | 11717.5
09:00 | 6745.62 | 4899.02 | 11644.64
09:30 | 6911.77 | 4729.68 | 11641.45
10:00 | 7077.92 | 4560.34 | 11638.26
10:30 | 7041.175 | 4550.2 | 11591.375
11:00 | 7004.43 | 4540.06 | 11544.49
11:30 | 7063.69 | 4591.305 | 11654.995
12:00 | 7122.95 | 4642.55 | 11765.5
12:30 | 7224.165 | 4808.145 | 12032.31
13:00 | 7325.38 | 4973.74 | 12299.12
13:30 | 7377.1 | 5027.96 | 12405.06
14:00 | 7428.82 | 5082.18 | 12511
14:30 | 7428.82 | 5129.25 | 12558.07
15:00 | 7428.82 | 5176.32 | 12605.14
15:30 | 7317.915 | 5188.02 | 12505.935
16:00 | 7207.01 | 5199.72 | 12406.73
16:30 | 7149.08 | 5091.53 | 12240.61
17:00 | 7091.15 | 4983.34 | 12074.49
17:30 | 6830.355 | 4896.83 | 11727.185
18:00 | 6569.56 | 4810.32 | 11379.88
18:30 | 6979.03 | 5015.66 | 11994.69
19:00 | 7388.5 | 5221 | 12609.5
19:30 | 7481.7 | 5717 | 13198.7
20:00 | 7477.5 | 5788 | 13265.5
20:30 | 7340 | 5724.21 | 13064.21 |  | Executive Engineer
21:00 | 7202.5 | 5660.42 | 12862.92 |  | Network Operation Division
21:30 | 7006.75 | 5517.395 | 12524.145
22:00 | 6811 | 5374.37 | 12185.37
22:30 | 6802.5 | 5319.15 | 12121.65
23:00 | 6794 | 5263.93 | 12057.93

## En-Curve
QF-LDC-12
Date | 10-06-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4095 | 3147 | 932 | 0 | 42 | 760.26 | 167 | 3302 | 0 | 241 | 1509.7 | 0 | 0 | 1 | 90 | DAILY ENERGY CURVE
00:30 | 4024 | 3131.5 | 932 | 0 | 42 | 759.29 | 167 | 3304 | 0 | 241 | 1461.2 | 0 | 0 | 0.5 | 80 | 10-06-2025
01:00 | 3953 | 3116 | 932 | 0 | 42 | 758.32 | 167 | 3306 | 0 | 241 | 1412.7 | 0 | 0 | 0 | 70
01:30 | 3924 | 3105 | 931.5 | 0 | 41 | 758.165 | 167 | 3309 | 0 | 216 | 1348.45 | 0 | 0 | 0 | 72 | Energy Generated | 301.3708 |  | MKWHr
02:00 | 3895 | 3094 | 931 | 0 | 40 | 758.01 | 167 | 3312 | 0 | 191 | 1284.2 | 0 | 0 | 0 | 74 | Energy not Served | 0.709 |  | MKWHr
02:30 | 3920.5 | 3105.5 | 931.5 | 0 | 40 | 759.12 | 167 | 3173 | 0 | 191 | 1197.2 | 0 | 0 | 0 | 72 | Total Energy Requirement | 302.0798 |  | MKWHr
03:00 | 3946 | 3117 | 932 | 0 | 40 | 760.23 | 167 | 3034 | 0 | 191 | 1110.2 | 0 | 0 | 0 | 70
03:30 | 3949.4 | 3124 | 932 | 0 | 39 | 761.185 | 167 | 3016.5 | 0 | 173.5 | 1039.2 | 0 | 0 | 0 | 56.5
04:00 | 3952.8 | 3131 | 932 | 0 | 38 | 762.14 | 167 | 2999 | 0 | 156 | 968.2 | 0 | 0 | 0 | 43
04:30 | 3918.9 | 3104 | 932 | 0 | 38 | 767.78 | 167 | 2988 | 0 | 156 | 928.2 | 0 | 0 | 0 | 39
05:00 | 3885 | 3077 | 932 | 0 | 38 | 773.42 | 167 | 2977 | 0 | 156 | 888.2 | 0 | 0 | 0 | 35
05:30 | 3861.5 | 2994 | 931.5 | 0 | 38 | 725.24 | 167 | 2838 | 19.77 | 147 | 823.1 | 0 | 0 | 0 | 17.5
06:00 | 3838 | 2911 | 931 | 0 | 38 | 677.06 | 167 | 2699 | 39.54 | 138 | 758 | 0 | 0 | 0 | 0
06:30 | 3820.5 | 2901.5 | 931.5 | 0 | 38 | 624.755 | 167 | 2648 | 93.975 | 138 | 734.5 | 0 | 0 | 0 | 0
07:00 | 3803 | 2892 | 932 | 0 | 38 | 572.45 | 167 | 2597 | 148.41 | 138 | 711 | 0 | 0 | 0 | 0
07:30 | 3706.5 | 2860.75 | 932 | 0 | 37 | 575.105 | 167 | 2581 | 226.755 | 138 | 670.5 | 0 | 0 | 0 | 0
08:00 | 3610 | 2829.5 | 932 | 0 | 36 | 577.76 | 167 | 2565 | 305.1 | 138 | 630 | 0 | 0 | 0 | 0
08:30 | 3609 | 2832 | 932 | 0 | 36 | 520.89 | 167 | 2542.5 | 385.11 | 129.5 | 563.5 | 0 | 0 | 0 | 0
09:00 | 3608 | 2834.5 | 932 | 0 | 36 | 464.02 | 167 | 2520 | 465.12 | 121 | 497 | 0 | 0 | 0 | 0
09:30 | 3728.5 | 2907 | 932 | 0 | 33 | 438.61 | 167 | 2344 | 488.84 | 121 | 480 | 0 | 0 | 1.5 | 0
10:00 | 3849 | 2979.5 | 932 | 0 | 30 | 413.2 | 167 | 2168 | 512.56 | 121 | 463 | 0 | 0 | 3 | 0
10:30 | 3884 | 2942.5 | 931.5 | 0 | 31 | 413.59 | 167 | 2106.5 | 556.285 | 112 | 440.5 | 0 | 0 | 6.5 | 0
11:00 | 3919 | 2905.5 | 931 | 0 | 32 | 413.98 | 167 | 2045 | 600.01 | 103 | 418 | 0 | 0 | 10 | 0
11:30 | 3982.5 | 2957 | 931 | 0 | 36 | 419.28 | 167 | 2034.5 | 603.715 | 103 | 408.5 | 0 | 0 | 12.5 | 0
12:00 | 4046 | 3008.5 | 931 | 0 | 40 | 424.58 | 167 | 2024 | 607.42 | 103 | 399 | 0 | 0 | 15 | 0
12:30 | 4101.5 | 3021 | 931.5 | 0 | 37 | 471.335 | 167 | 2160.5 | 599.475 | 104.5 | 418 | 0 | 0 | 20.5 | 0
13:00 | 4157 | 3033.5 | 932 | 0 | 34 | 518.09 | 167 | 2297 | 591.53 | 106 | 437 | 0 | 0 | 26 | 0
13:30 | 4156 | 3051 | 932 | 0 | 37 | 519.045 | 167 | 2419.5 | 514.515 | 115 | 469 | 0 | 0 | 25 | 0
14:00 | 4155 | 3068.5 | 932 | 0 | 40 | 520 | 167 | 2542 | 437.5 | 124 | 501 | 0 | 0 | 24 | 0
14:30 | 4150.5 | 3061 | 931.5 | 0 | 40 | 520 | 167 | 2574.5 | 452.07 | 124.5 | 521.5 | 0 | 0 | 15.5 | 0
15:00 | 4146 | 3053.5 | 931 | 0 | 40 | 520 | 167 | 2607 | 466.64 | 125 | 542 | 0 | 0 | 7 | 0
15:30 | 4114 | 3019.5 | 931 | 0 | 40 | 523 | 167 | 2677.5 | 385.435 | 116 | 524.5 | 0 | 0 | 8 | 0
16:00 | 4082 | 2985.5 | 931 | 0 | 40 | 526 | 167 | 2748 | 304.23 | 107 | 507 | 0 | 0 | 9 | 0
16:30 | 4041.5 | 2971 | 931 | 0 | 39 | 496.5 | 167 | 2731 | 222.61 | 107 | 529.5 | 0 | 0 | 4.5 | 0
17:00 | 4001 | 2956.5 | 931 | 0 | 38 | 467 | 167 | 2714 | 140.99 | 107 | 552 | 0 | 0 | 0 | 0
17:30 | 3820 | 2825 | 931 | 0 | 37 | 469.5 | 167 | 2713.5 | 92.685 | 108.5 | 563 | 0 | 0 | 0 | 0
18:00 | 3639 | 2693.5 | 931 | 0 | 36 | 472 | 167 | 2713 | 44.38 | 110 | 574 | 0 | 0 | 0 | 0
18:30 | 3780.5 | 2819 | 907.5 | 0 | 39 | 505 | 167 | 2896 | 22.19 | 156 | 702.5 | 0 | 0 | 0 | 24.5
19:00 | 3922 | 2944.5 | 884 | 0 | 42 | 538 | 167 | 3079 | 0 | 202 | 831 | 0 | 0 | 0 | 49
19:30 | 3932 | 2911.5 | 884 | 0 | 4 | 622 | 167 | 3395 | 0 | 201 | 1082.2 | 0 | 0 | 0 | 78
20:00 | 3985 | 2912.5 | 884 | 0 | 16 | 705 | 167 | 3400 | 0 | 194 | 1002 | 0 | 0 | 0 | 72
20:30 | 4011.5 | 2908 | 908 | 0 | 26 | 686.71 | 167 | 3292 | 0 | 185.5 | 879.5 | 0 | 0 | 0 | 78
21:00 | 4038 | 2903.5 | 932 | 0 | 36 | 668.42 | 167 | 3184 | 0 | 177 | 757 | 0 | 0 | 0 | 84
21:30 | 4074.5 | 2861.75 | 894 | 0 | 36 | 669.895 | 167 | 2974.5 | 0 | 140.5 | 706 | 0 | 0 | 0 | 73
22:00 | 4111 | 2820 | 856 | 0 | 36 | 671.37 | 167 | 2765 | 0 | 104 | 655 | 0 | 0 | 0 | 62
22:30 | 4115.5 | 2828 | 856 | 0 | 35 | 674.65 | 167 | 2698 | 0 | 86.5 | 661 | 0 | 0 | 0 | 61
23:00 | 4120 | 2836 | 856 | 0 | 34 | 677.93 | 167 | 2631 | 0 | 69 | 667 | 0 | 0 | 0 | 60
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 10-06-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 397 | 22:00 | 385 | 00:00 | Payra | 415 | 10:00 | 407 | 00:00
Ashuganj | 423 | 22:00 | 393 | 19:00 | Rahanpur | 408 | 10:00 | 395 | 20:00
Bhulta | 413 | 22:00 | 391 | 19:00 | Rampal | 405 | 18:00 | 387 | 00:00
Bibiana | 394 | 22:00 | 385 | 19:00
BIPTC | 403 | 06:00 | 391 | 00:00
Bogura | 398 | 10:00 | 382 | 20:00
Gopalganj | 404 | 18:00 | 389 | 00:00
Kaliakoir | 392 | 22:00 | 376 | 00:00
Madunaghat | 397 | 18:00 | 392 | 01:00
Meghnaghat | 401 | 22:00 | 389 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 234 | 22:00 | 227 | 00:00 | Keranigonj | 234 | 22:00 | 226 | 00:00
AKSML | 232 | 21:00 | 225 | 15:00 | Khulna(S) | 230 | 09:00 | 214 | 00:00
Aminbazar | 235 | 22:00 | 228 | 00:00 | Madunaghat | 233 | 19:30 | 227 | 15:00
Ashuganj | 241 | 22:00 | 232 | 19:30 | Madunaghat-400 | 232 | 19:00 | 228 | 01:00
Ashuganj-400 | 241 | 22:00 | 232 | 19:30 | Maniknagar | 231 | 21:00 | 223 | 00:00
Baghabari | 236 | 07:00 | 225 | 19:30 | Meghnaghat | 240 | 21:00 | 230 | 00:00
Barapukuria | 222 | 10:00 | 214 | 00:00 | Meghnaghat-400 | 234 | 21:00 | 227 | 00:00
Barapukuria-230 | 222 | 10:00 | 214 | 00:00 | Mirsorai | 231 | 19:30 | 224 | 00:00
Barishal | 240 | 18:00 | 228 | 00:00 | Rajshahi | 234 | 10:00 | 219 | 20:00
Bheramara | 234 | 08:00 | 222 | 19:30 | Rampal | 231 | 18:00 | 216 | 00:00
Bhulta | 240 | 22:00 | 225 | 02:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 230 | 22:00 | 225 | 00:00 | Rampura | 240 | 22:00 | 227 | 19:00
BIPTC | 237 | 09:00 | 222 | 19:30 | Shikalbaha | 231 | 19:30 | 226 | 00:00
Bogura | 232 | 10:00 | 222 | 20:00 | Shyampur | 233 | 22:00 | 226 | 00:00
Bogura-400 | 232 | 10:00 | 222 | 20:00 | Siddhirganj | 233 | 21:00 | 225 | 00:00
Borhanuddin | 242 | 18:00 | 235 | 00:00 | Sirajgonj | 240 | 10:00 | 233 | 22:00
BSRM | 231 | 21:00 | 223 | 00:00 | Sreepur | 235 | 22:00 | 227 | 01:00
Cumilla(N) | 232 | 20:00 | 222 | 00:00 | Tongi | 241 | 23:00 | 228 | 19:00
Faridpur | 236 | 18:00 | 224 | 00:00
Fenchuganj | 231 | 06:00 | 225 | 19:00
Ghorashal | 240 | 00:00 | 238 | 15:00
Ghorashal-230 | 240 | 22:00 | 229 | 14:00
Gopalganj | 237 | 10:00 | 227 | 00:00
GPH | 230 | 19:00 | 225 | 00:00
Haripur | 232 | 21:00 | 224 | 00:00
Hasnabad | 233 | 21:00 | 226 | 00:00
Hathazari | 233 | 19:30 | 228 | 00:00
Ishurdi | 237 | 08:00 | 225 | 19:30
Jhenaidah | 230 | 09:00 | 214 | 00:00
Kaliakoir | 246 | 22:00 | 233 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 22:00 | 126 | 18:30 | Madartek | 134 | 22:00 | 125 | 19:00
Agargaon | 135 | 22:00 | 130 | 00:00 | Madunaghat | 132 | 02:00 | 128 | 15:00
Agrabad | 134 | 19:30 | 128 | 15:00 | Magura | 134 | 18:30 | 120 | 00:00
AKS | 132 | 19:30 | 127 | 15:00 | Mahasthangarh | 132 | 10:00 | 124 | 00:00
Aminbazar | 134 | 22:00 | 130 | 00:00 | Manikganj | 135 | 23:00 | 125 | 00:00
Amnura | 135 | 07:00 | 125 | 00:00 | Maniknagar | 132 | 21:00 | 127 | 00:00
Ashuganj | 143 | 21:00 | 135 | 19:00 | Matarbari | 123 | 14:00 | 111 | 00:00
Bagerhat | 131 | 09:00 | 116 | 00:00 | Matuail | 137 | 21:00 | 131 | 00:00
Bajitpur | 133 | 21:00 | 118 | 01:00 | Millgate | 137 | 23:00 | 128 | 18:30
Bakulia | 132 | 09:00 | 129 | 23:00 | Mirpur | 133 | 22:00 | 128 | 13:00
Banani | 134 | 22:00 | 126 | 13:00 | Mirzapur | 140 | 23:00 | 126 | 01:00
Bangabhaban | 131 | 21:00 | 126 | 00:00 | Mithapukur | 128 | 07:00 | 120 | 20:00
Barapukuria | 133 | 10:00 | 125 | 00:00 | MI_Cement | 135 | 22:00 | 132 | 00:00
Barguna | 133 | 10:00 | 127 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 132 | 09:00 | 123 | 00:00 | Mogbazar | 135 | 22:00 | 122 | 16:00
Barishal-230 | 134 | 18:00 | 124 | 00:00 | Mongla | 132 | 18:30 | 118 | 00:00
Baroaulia | 134 | 19:00 | 129 | 00:00 | Motijheel | 131 | 21:00 | 126 | 00:00
Baroirhat | 134 | 19:30 | 118 | 15:00 | Muktagacha | 135 | 23:00 | 123 | 13:00
Bashundhara | 136 | 23:00 | 125 | 18:00 | Munshiganj | 136 | 21:00 | 130 | 00:00
BashundharaCement | 136 | 21:00 | 131 | 19:00 | Muradnagar | 137 | 21:00 | 123 | 20:00
Beanibazar | 128 | 22:00 | 120 | 19:00 | Mymensingh | 135 | 23:00 | 114 | 20:00
Benapole | 130 | 18:00 | 115 | 00:00 | Naogaon | 129 | 08:00 | 120 | 00:00
Bhaluka | 134 | 22:00 | 125 | 20:00 | Narail | 135 | 11:00 | 120 | 00:00
Bhandaria | 126 | 18:00 | 112 | 00:00 | Narinda | 132 | 21:00 | 127 | 00:00
Bhangura | 133 | 10:00 | 126 | 00:00 | Narshingdi | 145 | 22:00 | 125 | 00:00
Bheramara | 138 | 10:00 | 131 | 20:00 | Natore | 134 | 09:00 | 125 | 20:00
Bheramara(GK) | 138 | 10:00 | 131 | 20:00 | Nawabganj | 138 | 22:00 | 129 | 00:00
Bhulta | 131 | 21:00 | 125 | 00:00 | Netrakona | 125 | 22:00 | 110 | 20:00
Bog-Sherpur | 134 | 10:00 | 126 | 20:00 | New | 139 | 22:00 | 130 | 19:30
Bogura | 135 | 16:00 | 128 | 20:00 | Niamatpur | 136 | 08:00 | 129 | 23:00
Bogura-230 | 136 | 10:00 | 129 | 20:00 | Noapara | 133 | 10:00 | 120 | 00:00
Brahmanbaria | 139 | 21:00 | 125 | 19:00 | Pabna | 136 | 09:00 | 127 | 00:00
Cantonment | 135 | 22:00 | 131 | 00:00 | Palashbari | 126 | 10:00 | 118 | 00:00
Chandina | 136 | 21:00 | 125 | 00:00 | Panchagarh | 132 | 05:00 | 116 | 12:00
Chandpur | 140 | 20:00 | 119 | 23:00 | Patuakhali | 134 | 18:00 | 129 | 00:00
Chandraghona | 133 | 19:30 | 130 | 00:00 | Payra | 136 | 09:00 | 131 | 00:00
Chapai | 130 | 18:00 | 126 | 00:00 | PHP | 134 | 20:00 | 117 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 137 | 21:00 | 132 | 00:00 | Postogola | 137 | 22:00 | 133 | 00:00
Chauddagram | 134 | 20:00 | 117 | 15:00 | Purbachal | 135 | 22:00 | 126 | 19:00
Chhatak | 123 | 22:00 | 116 | 19:00 | Purbasadipur | 128 | 18:00 | 114 | 20:00
Chowmuhani | 130 | 20:00 | 108 | 22:00 | Rahanpur | 136 | 10:00 | 131 | 00:00
Chuadanga | 133 | 10:00 | 118 | 20:00 | Rahanpur-400 | 136 | 08:00 | 131 | 00:00
Coxsbazar | 120 | 14:00 | 111 | 00:00 | Rahim | 136 | 21:00 | 132 | 00:00
Cumilla(N) | 137 | 20:00 | 124 | 13:00 | Rajbari | 135 | 09:00 | 126 | 00:00
Cumilla(S) | 139 | 15:00 | 123 | 00:00 | Rajendrapur | 146 | 23:00 | 129 | 19:00
Daudkandi | 137 | 21:00 | 120 | 00:00 | Rajshahi | 135 | 08:00 | 126 | 00:00
Dhaka | 134 | 22:00 | 126 | 19:00 | Rajshahi-230 | 135 | 10:00 | 117 | 23:00
Dhamrai | 142 | 23:00 | 130 | 19:00 | Ramganj | 132 | 20:00 | 110 | 15:00
Dhanmondi | 136 | 21:00 | 123 | 16:00 | Rampur | 133 | 20:00 | 129 | 11:00
Dohazari | 127 | 07:00 | 122 | 00:00 | Rampura | 134 | 23:00 | 126 | 19:00
Faridpur | 136 | 09:00 | 129 | 00:00 | Rangamati | 133 | 19:30 | 129 | 00:00
Fatullah | 136 | 22:00 | 131 | 00:00 | Rangpur | 126 | 18:30 | 117 | 20:00
Fenchuganj | 136 | 22:00 | 132 | 19:00 | Ruppur | 138 | 09:00 | 130 | 20:00
Feni | 132 | 20:00 | 116 | 02:00 | Saidpur | 128 | 05:00 | 118 | 20:00
Ghatail | 136 | 23:00 | 120 | 01:00 | Satkhira | 131 | 18:00 | 114 | 00:00
Ghorashal | 143 | 23:00 | 137 | 14:00 | Satmasjid | 135 | 22:00 | 130 | 00:00
Goalpara | 137 | 18:00 | 123 | 00:00 | Savar | 132 | 22:00 | 128 | 13:00
Gollamari | 136 | 10:00 | 125 | 00:00 | SevenRings | 144 | 22:00 | 135 | 19:30
Gopalganj | 136 | 18:30 | 125 | 00:00 | ShahCement | 137 | 21:00 | 132 | 00:00
Gopalganj-400 | 138 | 09:00 | 131 | 00:00 | Shahjadpur | 137 | 10:00 | 131 | 20:00
Gulshan | 134 | 22:00 | 126 | 19:00 | Shahjibazar | 140 | 21:00 | 124 | 00:00
Halishahar | 134 | 19:30 | 130 | 00:00 | Shahmirpur | 134 | 19:30 | 128 | 13:00
Haripur | 137 | 21:00 | 132 | 00:00 | Shariatpur | 135 | 18:00 | 125 | 00:00
HaripurSBU | 136 | 22:00 | 132 | 00:00 | Sherpur | 127 | 22:00 | 110 | 13:00
Hasnabad | 136 | 05:00 | 133 | 00:00 | Shikalbaha | 123 | 19:30 | 118 | 09:00
Hathazari | 137 | 19:30 | 131 | 01:00 | Shikalbaha-230 | 135 | 19:30 | 130 | 15:00
Ishurdi | 139 | 09:00 | 131 | 20:00 | Shitalakhya | 135 | 22:00 | 132 | 00:00
Jaldhaka | 124 | 10:00 | 112 | 20:00 | Sholosohor | 134 | 19:30 | 128 | 01:00
Jamalpur | 132 | 23:00 | 116 | 04:00 | Shyampur | 135 | 21:00 | 131 | 00:00
Jashore | 133 | 08:00 | 118 | 00:00 | Shyampur-230 | 135 | 21:00 | 131 | 00:00
Jhenaidah | 136 | 09:00 | 120 | 00:00 | Siddhirganj | 136 | 21:00 | 125 | 22:00
Jhenaidah-230 | 136 | 09:00 | 124 | 00:00 | Sirajganj | 134 | 10:00 | 124 | 20:00
Joydebpur | 144 | 22:00 | 131 | 14:00 | Sonargaon | 139 | 21:00 | 130 | 00:00
Joypurhat | 128 | 08:00 | 117 | 00:00 | Sreemongol | 139 | 21:00 | 122 | 00:00
Juldah | 134 | 19:30 | 129 | 15:00 | Sreepur | 137 | 22:00 | 130 | 19:30
Kabirpur | 142 | 23:00 | 126 | 19:00 | Srinagar | 137 | 22:00 | 129 | 00:00
Kachua | 136 | 21:00 | 120 | 02:00 | SSM | 134 | 12:00 | 132 | 00:00
Kaliakoir | 142 | 23:00 | 132 | 00:00 | Sunamganj | 122 | 07:00 | 115 | 19:00
Kallyanpur | 132 | 03:00 | 130 | 00:00 | Sylhet | 128 | 22:00 | 121 | 19:00
Kalurghat | 132 | 19:30 | 128 | 00:00 | Sylhet-132 | 128 | 22:00 | 123 | 19:00
Kamrangirchar | 136 | 22:00 | 131 | 01:00 | Tangail | 139 | 23:00 | 124 | 02:00
Kaptai | 134 | 5:00 | 123 | 12:00 | Thakurgaon | 130 | 05:00 | 113 | 12:00
Kasba | 136 | 21:00 | 120 | 00:00 | TK | 132 | 20:00 | 128 | 02:00
Kazla | 132 | 22:00 | 127 | 00:00 | Tongi | 137 | 23:00 | 130 | 19:00
Keranigonj | 137 | 22:00 | 130 | 00:00 | Ullahpara | 135 | 09:00 | 126 | 19:30
Khagrachori | 133 | 20:00 | 127 | 00:00 | Ullon | 133 | 22:00 | 124 | 19:00
Khulna | 135 | 10:00 | 123 | 00:00 | Uttara | 133 | 22:00 | 129 | 00:00
Khulna(S) | 137 | 18:00 | 124 | 00:00 | UttaraNew | 136 | 23:00 | 129 | 00:00
Khulshi | 132 | 19:30 | 128 | 01:00 | Zigatola | 137 | 22:00 | 130 | 01:00
Kishoreganj | 134 | 22:00 | 122 | 19:00
Kodda | 145 | 22:00 | 129 | 01:00
KSRM | 135 | 19:30 | 130 | 11:00
Kulaura | 135 | 22:00 | 130 | 19:00
Kurigram | 124 | 18:00 | 113 | 19:00
Kushtia | 134 | 09:00 | 126 | 00:00
Lalbag | 137 | 22:00 | 131 | 00:00
Lalmonirhat | 123 | 07:00 | 116 | 21:00
Madanganj | 136 | 21:00 | 131 | 19:00
Madaripur | 135 | 09:00 | 127 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division