## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 12-06-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-06-2025 | during | 12-06-2025 | during | 12-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 120 | 120 | 230 | 230 | 230 | 230 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 120 | 120 | 260 | 260 | 260 | 260 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 363 | 363 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 143 | 141 | 335 | 335 | 150 | 150 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 12 | 12 | 33 | 33 | 20 | 20 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 7 | 19 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 8 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 16 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 32 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 480 | 520 | 584 | 584 | 525.6 | 525.6 | None
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 450 | 540 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 320 | 320 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 90 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2465 | 2738 | 4776.2 | 4776.2 | 4136.87 | 4136.87
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 15 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 167 | 167 | 165 | 165 | 165 | 165 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 142 | 149 | 141 | 145 | 141 | 145 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 40 | 72 | 72 | 72 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 65 | 65 | 65 | 65 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 88 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 34 | 42 | 38 | 40 | 38 | 40 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4 | 0 | 4.08 | 0 | 4.08 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 17 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 805 | 1141 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 6 | 16 | 14 | 12 | 14 | 12 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 0 | 0 | 575 | 575 | 0 | 0 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1173 | 1735 | 3546.8 | 3526.72 | 2941.8 | 2921.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 207 | 202 | 221.43 | 221.43 | 205.43 | 205.43 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 332 | 350 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 340 | 340 | 340 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 15 | 15 | 0 | 0 | 17 | 17 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 26 | 36 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 55 | 182 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 8 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 35 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 65 | 50 | 163 | 163 | 80 | 80 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 73 | 136 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 36 | 32 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 24 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 15 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 85 | 113 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 48 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 76 | 94 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 73 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1454 | 1688 | 2424.48 | 2354.48 | 2337.98 | 2267.98
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-06-2025 | during | 12-06-2025 | during | 12-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 136 | 136 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 34 | 139 | 200 | 200 | 130 | 130 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 2 | 81 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 50.58 | 0 | 49 | 0 | 49 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 10 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 224.58 | 366 | 600.1 | 549 | 530.1 | 479
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 35 | 33 | 32 | 32 | 32 | 32 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 148 | 152 | 0 | 0 | 0 | 0 | Borescope Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 81 | 83 | 83 | 83 | 83 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 16 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 4 | 8 | 25 | 25 | 10 | 10 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 320 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 349 | 390 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 0 | 0 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1308 | 1380 | 926 | 926 | 849 | 849
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 892 | 892 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 390 | 378 | 410 | 410 | 360 | 360 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 97.64 | 0 | 71 | 0 | 71 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 768 | 1225 | 1234.2 | 1234.2 | 1194 | 1194 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3699.2 | 2147.64 | 2512 | 3247.2 | 3176.2 | 3157 | 3086
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 10 | 9 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 500 | 1100 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 0 | 0 | 307 | 307 | 0 | 0 | Coal shortage
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.76 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 850.76 | 1449 | 2172 | 2171 | 1813 | 1812
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 177 | 174 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 184 | 191 | 220 | 220 | 198 | 198 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 184 | 190 | 220 | 220 | 198 | 198 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 406 | 408 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 | 30 | 30 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.1 | 0 | 5.1 | 0 | 5.1 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 433.53 | 732.3 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 58.87 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 110 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 1558.5 | 1695.3 | 3151.97 | 2985.87 | 3045.19 | 2879.09
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 49 | 47 | 50 | 50 | 50 | 50 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 200 | 200 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 106 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.8 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 182 | 0 | 177.33 | 0 | 177.33 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 501.8 | 468 | 725.93 | 512 | 725.93 | 512
System Total |  |  |  |  | 28565.2 | 27044.055 | 11683.28 | 14031.3 | 21570.68 | 20977.47 | 19536.87 | 18943.66
Forecast Scenario (12-06-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13600 |  | 0 |  | 13600
|  |  |  | 1:00 | 13490 |  | 0 |  | 13490
|  |  |  | 2:00 | 13310 |  | 0 |  | 13310
|  |  |  | 3:00 | 13010 |  | 0 |  | 13010
|  |  |  | 4:00 | 12720 |  | 0 |  | 12720
|  |  |  | 5:00 | 12440 |  | 0 |  | 12440
|  |  |  | 6:00 | 11620 |  | 0 |  | 11620
|  |  |  | 7:00 | 11650 |  | 0 |  | 11650
|  |  |  | 8:00 | 11540 |  | 0 |  | 11540
|  |  |  | 9:00 | 11390 |  | 0 |  | 11390
|  |  |  | 10:00 | 11410 |  | 0 |  | 11410
|  |  |  | 11:00 | 11350 |  | 0 |  | 11350
|  |  |  | 12:00 | 11520 |  | 0 |  | 11520
|  |  |  | 13:00 | 11800 |  | 0 |  | 11800
|  |  |  | 14:00 | 12160 |  | 0 |  | 12160
|  |  |  | 15:00 | 12220 |  | 0 |  | 12220
|  |  |  | 16:00 | 12130 |  | 0 |  | 12130
|  |  |  | 17:00 | 11590 |  | 0 |  | 11590
|  |  |  | 18:00 | 11080 |  | 0 |  | 11080
|  |  |  | 18:30 | 11490 |  | 0 |  | 11490
|  |  |  | 19:00 | 12490 |  | 0 |  | 12490
|  |  |  | 19:30 | 13220 |  | 0 |  | 13220
|  |  |  | 20:00 | 13540 |  | 0 |  | 13540
|  |  |  | 21:00 | 14060 |  | 0 |  | 14060
|  |  |  | 22:00 | 14190 |  | 0 |  | 14190
|  |  |  | 23:00 | 14370 |  | 0 |  | 14370
Probable Maximum Temperature: |  |  | 33.60°C
Probable Maximum Demand at Day Peak: |  |  | 11520.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14060.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14060.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 298.68 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:07 hrs on 12-06-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 11-06-2025 | [28 empty] | Date: | 11-06-2025 | [28 empty] | Date: | 11-06-2025 | [28 empty] | Date: | 11-06-2025 | [28 empty] | Date: | 11-06-2025 | [12 empty] | Date: | 11-06-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [12 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 120 | 0 | 110 | 0 | 0 | 366 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 141 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 7 | 0 | 468 | 0 | 0 | 0 | 0 | 6 | 33 | 0 | 0 | 12 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 135 | 0 | 0 | 0 | 833 | 0 | 51 | 0 | 168 | 0 | 354 | 340 | 27 | 201 | 16 | 68 | 80 | 68 | 26 | 11 | 88 | 36 | 16 | 0 | 36 | 320 | 320 | 372 | 32 | 30 | 156 | 7 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 24 | 55 | 158 | 0 | 0 | 0 | 6797 | 856 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 821 | 17 | 673.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 191 | 0 | 196 | 0 | 414 | 0 | 0 | 180 | 48 | 115 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 790 | 0 | 5305.96 | 12102.96 | 95.59
01:00 | 0 | 0 | 0 | 120 | 0 | 110 | 0 | 0 | 354 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 138 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 7 | 0 | 465 | 0 | 0 | 0 | 0 | 10 | 33 | 0 | 0 | 12 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 110 | 0 | 0 | 0 | 805 | 0 | 51 | 0 | 170 | 0 | 355 | 320 | 28 | 202 | 16 | 75 | 70 | 71 | 6 | 13 | 98 | 36 | 27 | 0 | 36 | 315 | 320 | 372 | 32 | 30 | 156 | 7 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 8 | 45 | 157 | 0 | 0 | 0 | 6722 | 932 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 807 | 17 | 673.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 187 | 0 | 192 | 0 | 414 | 0 | 0 | 180 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 800 | 0 | 5348.37 | 12070.37 | 95.6
02:00 | 0 | 0 | 0 | 120 | 0 | 110 | 0 | 0 | 365 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 140 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 7 | 0 | 478 | 0 | 0 | 0 | 0 | 4 | 33 | 0 | 0 | 12 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 101 | 0 | 0 | 0 | 804 | 0 | 51 | 0 | 170 | 0 | 353 | 340 | 28 | 206 | 16 | 88 | 70 | 85 | 8 | 6 | 98 | 36 | 52.2 | 0 | 36 | 310 | 320 | 372 | 32 | 30 | 156 | 8 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 8 | 45 | 157 | 0 | 0 | 0 | 6797.2 | 932 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 821 | 17 | 675.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 192 | 0 | 197 | 0 | 414 | 0 | 0 | 180 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 800 | 0 | 5381.02 | 12178.22 | 95.61
03:00 | 0 | 0 | 0 | 120 | 0 | 110 | 0 | 0 | 355 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 140 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 17 | 7 | 0 | 443 | 0 | 0 | 0 | 0 | 1 | 33 | 0 | 0 | 12 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 126 | 0 | 0 | 0 | 800 | 0 | 51 | 0 | 170 | 0 | 355 | 340 | 28 | 193 | 16 | 84 | 70 | 85 | 10 | 0 | 107 | 34 | 52.2 | 0 | 36 | 315 | 320 | 353 | 32 | 30 | 154 | 8 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 8 | 45 | 157 | 0 | 0 | 0 | 6758.2 | 933 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 805 | 17 | 671.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 185 | 0 | 190 | 0 | 396 | 0 | 0 | 180 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 120 | 220 | 0 | 0 | 800 | 0 | 5321.65 | 12079.85 | 95.62
04:00 | 0 | 0 | 0 | 120 | 0 | 110 | 0 | 0 | 338 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 139 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 7 | 0 | 437 | 0 | 0 | 0 | 0 | 3 | 33 | 0 | 0 | 12 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 150 | 0 | 0 | 0 | 800 | 0 | 51 | 0 | 170 | 0 | 354 | 340 | 28 | 192 | 16 | 86 | 70 | 85 | 18 | 11 | 114 | 34 | 52.2 | 0 | 36 | 315 | 320 | 359 | 32 | 30 | 151 | 8 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 0 | 45 | 157 | 0 | 0 | 0 | 6764.2 | 933 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 788 | 0 | 671.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 180 | 0 | 185 | 0 | 337 | 0 | 0 | 180 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 120 | 220 | 0 | 0 | 760 | 0 | 5174.1 | 11938.3 | 95.63
05:00 | 0 | 0 | 0 | 120 | 0 | 109 | 0 | 0 | 325 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 138 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 14 | 7 | 0 | 425 | 0 | 0 | 0 | 0 | 4 | 33 | 0 | 0 | 12 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 798 | 0 | 51 | 0 | 170 | 0 | 354 | 330 | 28 | 180 | 16 | 88 | 70 | 85 | 19 | 11 | 114 | 34 | 52.2 | 0 | 36 | 300 | 320 | 315 | 32 | 30 | 147 | 8 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 0 | 45 | 157 | 0 | 0 | 0 | 6670.2 | 932 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 774 | 0 | 674.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 176 | 0 | 181 | 0 | 319 | 0 | 0 | 190 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 120 | 220 | 0 | 0 | 730 | 0 | 5111.23 | 11781.43 | 95.64
06:00 | 0 | 0 | 0 | 120 | 0 | 110 | 0 | 0 | 320 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 140 | 400 | 0 | 0 | 0 | 0 | 0 | 2 | 52 | 14 | 7 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 12 | 0 | 0 | 167 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 770 | 1 | 5 | 0 | 26 | 0 | 280 | 280 | 28 | 186 | 15 | 88 | 70 | 85 | 19 | 11 | 114 | 34 | 16 | 5 | 36 | 310 | 320 | 305 | 32 | 30 | 130 | 8 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 0 | 45 | 157 | 0 | 3.66 | 0 | 6140.66 | 932 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.24 | 779 | 0 | 513.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 2.96 | 161 | 0 | 176 | 0 | 181 | 0 | 330 | 0 | 0.24 | 200 | 48 | 115 | 1 | 113 | 0 | 0 | 0.2 | 12 | 0.04 | 0 | 0 | 10 | 120 | 180 | 0 | 0 | 650 | 0 | 4893.13 | 11033.79 | 95.65
07:00 | 0 | 0 | 0 | 120 | 0 | 110 | 0 | 0 | 340 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 143 | 400 | 0 | 0 | 0 | 0 | 0 | 7 | 52 | 14 | 7 | 0 | 378 | 0 | 0 | 0 | 0 | 7 | 33 | 0 | 0 | 0 | 0 | 1 | 167 | 0 | 38 | 0 | 0 | 0 | 0 | 8 | 0 | 150 | 0 | 0 | 0 | 779 | 6 | 5 | 0 | 26 | 0 | 280 | 280 | 28 | 188 | 15 | 84 | 69 | 85 | 19 | 11 | 114 | 32 | 16 | 13 | 36 | 305 | 320 | 307 | 32 | 30 | 129 | 8 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 0 | 45 | 157 | 1 | 14.74 | 0 | 6183.74 | 932 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.08 | 741 | 0 | 421.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 14.1 | 163 | 0 | 163 | 0 | 162 | 0 | 332 | 0 | 1.19 | 200 | 49 | 70 | 4 | 113 | 0 | 0 | 1.5 | 32 | 0.19 | 0 | 0 | 10 | 100 | 180 | 0 | 0 | 600 | 0 | 4680.92 | 10864.66 | 95.66
08:00 | 0 | 0 | 0 | 120 | 0 | 110 | 0 | 0 | 333 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 139 | 350 | 0 | 0 | 0 | 0 | 0 | 13 | 52 | 14 | 7 | 0 | 333 | 0 | 0 | 0 | 0 | 2 | 33 | 0 | 0 | 0 | 0 | 3 | 167 | 0 | 13 | 0 | 0 | 0 | 0 | 8 | 0 | 149 | 0 | 0 | 0 | 749 | 11 | 5 | 0 | 26 | 0 | 280 | 280 | 28 | 193 | 15 | 72 | 70 | 85 | 12 | 14 | 114 | 32 | 16 | 40 | 35 | 310 | 320 | 307 | 32 | 30 | 129 | 8 | 0 | 78 | 30 | 0 | 0 | 0 | 0 | 0 | 45 | 154 | 1 | 27.35 | 0 | 6054.35 | 933 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.64 | 738 | 0 | 418.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 26.95 | 164 | 0 | 162 | 0 | 163 | 0 | 341 | 0 | 2.05 | 200 | 50 | 70 | 7 | 113 | 0 | 0 | 3.1 | 62 | 0.23 | 0 | 0 | 10 | 100 | 180 | 0 | 0 | 600 | 0 | 4776.48 | 10830.83 | 95.67
09:00 | 0 | 0 | 0 | 120 | 0 | 110 | 0 | 0 | 321 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 142 | 350 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 13 | 7 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 800 | 14 | 5 | 0 | 26 | 0 | 280 | 280 | 28 | 203 | 15 | 72 | 70 | 68 | 9 | 14 | 70 | 34 | 0 | 54 | 35 | 310 | 320 | 337 | 32 | 30 | 136 | 8 | 0 | 78 | 30 | 0 | 0 | 0 | 0 | 0 | 16 | 138 | 2 | 38.04 | 0 | 6040.04 | 892 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.99 | 750 | 0 | 429.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 37.75 | 171 | 0 | 170 | 0 | 171 | 0 | 377 | 0 | 3.65 | 200 | 50 | 35 | 7 | 58 | 0 | 0 | 2.1 | 126 | 0.59 | 0 | 0 | 10 | 100 | 180 | 0 | 0 | 560 | 0 | 4826.73 | 10866.77 | 95.68
10:00 | 0 | 0 | 0 | 120 | 0 | 110 | 0 | 0 | 333 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 139 | 350 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 13 | 7 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 167 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 800 | 14 | 5 | 0 | 26 | 0 | 280 | 280 | 28 | 206 | 15 | 72 | 70 | 68 | 9 | 14 | 70 | 32 | 0 | 65 | 35 | 325 | 320 | 336 | 32 | 30 | 145 | 8 | 0 | 76 | 30 | 0 | 0 | 0 | 0 | 0 | 16 | 136 | 2 | 46.49 | 0 | 6082.49 | 892 | 387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.51 | 762 | 0 | 430.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 51.94 | 178 | 0 | 178 | 0 | 179 | 0 | 380 | 0 | 4.54 | 200 | 50 | 0 | 26 | 34 | 0 | 0 | 4.1 | 163 | 0.78 | 0 | 0 | 10 | 100 | 220 | 0 | 0 | 560 | 0 | 4996.48 | 11078.97 | 95.69
11:00 | 0 | 0 | 0 | 120 | 0 | 120 | 0 | 0 | 342 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 142 | 350 | 0 | 0 | 0 | 0 | 0 | 28 | 17 | 12.5 | 7 | 0 | 387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 167 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 800 | 12 | 5 | 0 | 26 | 0 | 280 | 280 | 26 | 208 | 15 | 72 | 50 | 68 | 8 | 14 | 70 | 36 | 0 | 72 | 35 | 320 | 320 | 352 | 32 | 30 | 146 | 8 | 0 | 76 | 30 | 0 | 0 | 0 | 0 | 0 | 16 | 136 | 2 | 49.95 | 0 | 6126.45 | 892 | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.95 | 766 | 0 | 431.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 55.06 | 176 | 0 | 179 | 0 | 180 | 0 | 383 | 0 | 4.92 | 200 | 50 | 0 | 28 | 34 | 0 | 0 | 6.1 | 184 | 0.41 | 0 | 0 | 10 | 100 | 220 | 0 | 0 | 560 | 0 | 5017.42 | 11143.87 | 95.7
12:00 | 0 | 0 | 0 | 120 | 0 | 120 | 0 | 0 | 363 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 143 | 450 | 0 | 0 | 0 | 0 | 0 | 33 | 17 | 12 | 7 | 0 | 480 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 4 | 167 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 805 | 15 | 8 | 0 | 55 | 0 | 332 | 340 | 26 | 207 | 15 | 76 | 65 | 73 | 9 | 19 | 85 | 36 | 0 | 73 | 35 | 315 | 320 | 349 | 35 | 30 | 148 | 4 | 0 | 77 | 30 | 0 | 0 | 0 | 0 | 2 | 34 | 136 | 2 | 50.58 | 0 | 6624.58 | 892 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.64 | 768 | 0 | 433.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 58.87 | 177 | 0 | 184 | 0 | 184 | 0 | 406 | 0 | 5.1 | 200 | 49 | 0 | 30 | 34 | 0 | 0 | 6.8 | 182 | 0.76 | 0 | 0 | 10 | 120 | 220 | 0 | 0 | 500 | 0 | 5058.7 | 11683.28 | 95.71
13:00 | 0 | 0 | 0 | 120 | 0 | 120 | 0 | 0 | 384 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 142 | 500 | 0 | 0 | 0 | 0 | 0 | 32 | 17 | 12 | 7 | 0 | 520 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 73 | 0 | 1 | 167 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 800 | 5 | 23 | 0 | 165 | 0 | 338 | 340 | 26 | 203 | 15 | 96 | 50 | 92 | 9 | 19 | 95 | 36 | 1 | 70 | 42 | 310 | 320 | 380 | 35 | 30 | 150 | 8 | 0 | 75 | 30 | 0 | 0 | 0 | 0 | 35 | 50 | 135 | 2 | 49.84 | 0 | 7037.84 | 892 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.34 | 795 | 0 | 576.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 55.47 | 177 | 0 | 199 | 0 | 199 | 0 | 414 | 0 | 4.93 | 200 | 49 | 35 | 29 | 34 | 0 | 0 | 6.1 | 180 | 0.24 | 0 | 0 | 10 | 120 | 220 | 0 | 0 | 530 | 0 | 5283.65 | 12321.49 | 95.72
14:00 | 0 | 0 | 0 | 120 | 0 | 120 | 0 | 0 | 371 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 140 | 500 | 0 | 0 | 0 | 0 | 0 | 29 | 52 | 12 | 7 | 0 | 492 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 73 | 0 | 1 | 167 | 15 | 34 | 0 | 0 | 0 | 0 | 0 | 14 | 144 | 0 | 0 | 0 | 806 | 3 | 43 | 0 | 165 | 0 | 333 | 340 | 26 | 195 | 15 | 94 | 50 | 135 | 18 | 19 | 95 | 38 | 8 | 49 | 34 | 310 | 320 | 365 | 34 | 30 | 149 | 8 | 0 | 78 | 30 | 0 | 16 | 0 | 0 | 35 | 85 | 135 | 2 | 45.56 | 0 | 7148.56 | 892 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.52 | 872 | 0 | 722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 51.7 | 170 | 0 | 190 | 0 | 190 | 0 | 390 | 0 | 4.58 | 200 | 49 | 70 | 26 | 34 | 0 | 0 | 1.6 | 167 | 0.76 | 0 | 0 | 6 | 120 | 220 | 0 | 0 | 670 | 0 | 5557.16 | 12705.72 | 95.73
15:00 | 0 | 0 | 0 | 120 | 0 | 120 | 0 | 0 | 363 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 400 | 142 | 500 | 0 | 0 | 0 | 0 | 0 | 24 | 52 | 12 | 7 | 0 | 534 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 48 | 0 | 0 | 167 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 17 | 143 | 0 | 0 | 0 | 801 | 2 | 51 | 0 | 172 | 0 | 329 | 335 | 26 | 204 | 15 | 94 | 50 | 155 | 17 | 19 | 94 | 40 | 24 | 49 | 0 | 315 | 320 | 364 | 34 | 30 | 148 | 8 | 0 | 78 | 30 | 0 | 16 | 0 | 0 | 35 | 65 | 133 | 2 | 38.38 | 0 | 7132.38 | 892 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.64 | 906 | 0 | 729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 41.76 | 171 | 0 | 190 | 0 | 190 | 0 | 399 | 0 | 3.69 | 201 | 49 | 35 | 22 | 34 | 0 | 0 | 2.6 | 135 | 0.57 | 0 | 0 | 10 | 120 | 220 | 0 | 0 | 702 | 0 | 5556.26 | 12688.64 | 95.74
16:00 | 0 | 0 | 0 | 120 | 0 | 120 | 0 | 0 | 373 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 400 | 142 | 550 | 0 | 0 | 0 | 0 | 0 | 16 | 52 | 12 | 7 | 0 | 520 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 48 | 0 | 0 | 167 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 17 | 144 | 0 | 0 | 0 | 800 | 1 | 51 | 0 | 174 | 0 | 331 | 335 | 26 | 202 | 14 | 94 | 50 | 155 | 17 | 19 | 94 | 38 | 25 | 29 | 0 | 315 | 320 | 336 | 34 | 30 | 147 | 8 | 0 | 78 | 30 | 0 | 16 | 0 | 0 | 44 | 75 | 134 | 1 | 27.26 | 0 | 7126.26 | 892 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.39 | 908 | 0 | 729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 26.8 | 176 | 0 | 194 | 0 | 195 | 0 | 397 | 0 | 2.58 | 200 | 49 | 35 | 14 | 34 | 0 | 0 | 0.5 | 100 | 0.23 | 0 | 0 | 10 | 120 | 220 | 0 | 0 | 700 | 0 | 5462.5 | 12588.76 | 95.75
17:00 | 0 | 0 | 0 | 120 | 0 | 120 | 0 | 0 | 346 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 400 | 140 | 550 | 0 | 0 | 0 | 0 | 0 | 8 | 52 | 12 | 7 | 0 | 445 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 48 | 0 | 0 | 167 | 17 | 36 | 0 | 0 | 0 | 0 | 0 | 17 | 144 | 0 | 0 | 0 | 758 | 0 | 51 | 0 | 180 | 0 | 335 | 340 | 25 | 188 | 14 | 95 | 50 | 155 | 21 | 19 | 94 | 36 | 25 | 17 | 0 | 310 | 320 | 340 | 34 | 30 | 148 | 8 | 0 | 78 | 30 | 0 | 16 | 0 | 0 | 44 | 75 | 134 | 1 | 12.77 | 2 | 6954.77 | 893 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.87 | 856 | 0 | 729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 11.94 | 163 | 0 | 182 | 0 | 182 | 0 | 376 | 0 | 1.18 | 200 | 47 | 35 | 7 | 34 | 0 | 0 | 0 | 51 | 0.07 | 0 | 0 | 9 | 120 | 220 | 0 | 0 | 700 | 0 | 5209.06 | 12163.83 | 95.76
18:00 | 0 | 0 | 8 | 120 | 0 | 120 | 0 | 0 | 321 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 320 | 138 | 450 | 0 | 0 | 0 | 0 | 0 | 2 | 52 | 12 | 7 | 0 | 450 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 48 | 0 | 0 | 167 | 17 | 42 | 0 | 0 | 0 | 0 | 0 | 17 | 144 | 0 | 0 | 0 | 777 | 0 | 51 | 0 | 142 | 0 | 320 | 340 | 25 | 191 | 14 | 94 | 50 | 155 | 26 | 19 | 94 | 34 | 25 | 6 | 0 | 300 | 320 | 308 | 34 | 30 | 134 | 8 | 0 | 79 | 30 | 0 | 16 | 0 | 0 | 45 | 0 | 134 | 0 | 2.8 | 10 | 6601.8 | 891 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.45 | 815 | 0 | 616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 3.18 | 152 | 0 | 171 | 0 | 167 | 0 | 338 | 0 | 0.29 | 200 | 47 | 35 | 1 | 34 | 0 | 0 | 0.1 | 14 | 0.03 | 0 | 0 | 9 | 120 | 220 | 0 | 0 | 600 | 0 | 4807.05 | 11408.85 | 95.77
19:00 | 0 | 4 | 8 | 120 | 0 | 115 | 0 | 0 | 385 | 0 | 320 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 25 | 420 | 139 | 550 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 12 | 7 | 0 | 542 | 0 | 0 | 0 | 0 | 4 | 50 | 29 | 0 | 50 | 0 | 0 | 167 | 12 | 42 | 0 | 0 | 0 | 0 | 0 | 17 | 147 | 0 | 0 | 0 | 946 | 0 | 51 | 0 | 152 | 0 | 328 | 340 | 25 | 195 | 15 | 94 | 50 | 155 | 42 | 0 | 114 | 0 | 25 | 0 | 0 | 305 | 320 | 388 | 34 | 30 | 134 | 8 | 0 | 79 | 30 | 0 | 16 | 0 | 0 | 82 | 0 | 134 | 0 | 0 | 10 | 7342 | 844 | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 821 | 14 | 646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 171 | 0 | 200 | 0 | 398 | 0 | 0 | 200 | 47 | 70 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 120 | 220 | 0 | 0 | 605 | 0 | 5016 | 12358 | 95.79
19:30 | 0 | 25 | 8 | 120 | 0 | 120 | 0 | 0 | 360 | 0 | 320 | 17 | 0 | 12 | 0 | 0 | 0 | 0 | 17 | 32 | 420 | 140 | 583 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 12 | 7 | 0 | 495 | 0 | 0 | 0 | 0 | 8 | 50 | 31 | 0 | 88 | 0 | 0 | 167 | 17 | 42 | 0 | 0 | 0 | 0 | 1 | 17 | 148 | 0 | 0 | 0 | 1018 | 0 | 51 | 0 | 168 | 0 | 338 | 340 | 25 | 195 | 15 | 94 | 50 | 155 | 49 | 0 | 114 | 8 | 24 | 0 | 0 | 315 | 320 | 368 | 34 | 30 | 145 | 8 | 0 | 79 | 30 | 0 | 16 | 0 | 0 | 83 | 0 | 135 | 0 | 0 | 0 | 7572 | 844 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 996 | 17 | 750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 194 | 0 | 195 | 0 | 399 | 0 | 0 | 200 | 47 | 113 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 120 | 220 | 0 | 0 | 860 | 0 | 5614 | 13186
20:00 | 0 | 17 | 24 | 120 | 0 | 120 | 0 | 0 | 360 | 0 | 320 | 17 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 32 | 420 | 139 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 12 | 7 | 0 | 476 | 0 | 0 | 0 | 0 | 10 | 50 | 32 | 0 | 88 | 0 | 0 | 167 | 17 | 42 | 0 | 0 | 0 | 0 | 3 | 17 | 150 | 0 | 0 | 0 | 1083 | 0 | 51 | 0 | 177 | 0 | 354 | 340 | 25 | 187 | 15 | 94 | 50 | 136 | 48 | 0 | 113 | 36 | 24 | 0 | 0 | 310 | 320 | 356 | 33 | 30 | 149 | 8 | 0 | 79 | 30 | 0 | 16 | 0 | 0 | 82 | 75 | 135 | 0 | 0 | 0 | 7614 | 843 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 17 | 769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 187 | 0 | 187 | 0 | 379 | 0 | 0 | 198 | 47 | 115 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 120 | 220 | 0 | 0 | 970 | 0 | 5792 | 13406 | 95.81
21:00 | 0 | 17 | 8 | 120 | 0 | 120 | 0 | 0 | 363 | 0 | 320 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 32 | 420 | 141 | 540 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 12 | 19 | 0 | 520 | 0 | 0 | 0 | 0 | 16 | 50 | 40 | 0 | 88 | 0 | 0 | 167 | 17 | 42 | 0 | 0 | 0 | 0 | 8 | 17 | 149 | 0 | 0 | 0 | 1141 | 0 | 51 | 0 | 182 | 0 | 350 | 340 | 36 | 202 | 15 | 94 | 50 | 136 | 48 | 15 | 113 | 32 | 24 | 0 | 0 | 320 | 320 | 390 | 33 | 30 | 152 | 8 | 0 | 81 | 30 | 0 | 16 | 0 | 0 | 81 | 139 | 136 | 0 | 0 | 10 | 7907 | 892 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1225 | 17 | 732.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 191 | 0 | 190 | 0 | 408 | 0 | 0 | 200 | 47 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 120 | 220 | 0 | 0 | 1100 | 0 | 6124.3 | 14031.3 | 95.84
22:00 | 0 | 17 | 8 | 120 | 0 | 120 | 0 | 0 | 382 | 0 | 320 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 32 | 420 | 142 | 540 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 12 | 22 | 0 | 555 | 0 | 0 | 0 | 0 | 16 | 50 | 39 | 0 | 88 | 0 | 0 | 167 | 17 | 42 | 0 | 0 | 0 | 0 | 8 | 17 | 149 | 0 | 0 | 0 | 1114 | 0 | 51 | 0 | 187 | 0 | 347 | 340 | 43 | 212 | 15 | 94 | 50 | 136 | 48 | 19 | 113 | 44 | 24 | 0 | 0 | 320 | 320 | 392 | 33 | 30 | 153 | 8 | 0 | 82 | 30 | 0 | 16 | 0 | 0 | 82 | 134 | 136 | 0 | 0 | 12 | 7974 | 820 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1217 | 17 | 729.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 198 | 0 | 197 | 0 | 408 | 0 | 0 | 190 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 220 | 0 | 0 | 1120 | 0 | 6087.47 | 14061.47 | 95.87
23:00 | 0 | 17 | 8 | 120 | 0 | 120 | 0 | 0 | 395 | 0 | 320 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 32 | 420 | 139 | 540 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 12.5 | 22 | 0 | 545 | 0 | 0 | 0 | 0 | 9 | 50 | 38 | 0 | 88 | 0 | 0 | 167 | 17 | 42 | 0 | 0 | 0 | 0 | 8 | 18 | 149 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 187 | 0 | 348 | 340 | 44 | 211 | 15 | 94 | 80 | 136 | 47 | 19 | 112 | 44 | 30 | 0 | 0 | 315 | 320 | 396 | 33 | 30 | 154 | 8 | 0 | 82 | 30 | 0 | 16 | 0 | 0 | 82 | 136 | 137 | 0 | 0 | 3 | 8118.5 | 821 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1226 | 17 | 748.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 197 | 0 | 202 | 0 | 414 | 0 | 0 | 180 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 127 | 220 | 0 | 0 | 1230 | 0 | 6246.71 | 14365.21 | 95.9
Total KWH | 0 | 98880 | 58080 | 2835700 | 0 | 2772812 | 0 | 0 | 8607600 | 0 | 7711640 | 21240 | 0 | 105264 | 0 | 0 | 0 | 0 | 27360 | 216960 | 8664000 | 3368204 | 11484553 | 0 | 0 | 0 | 0 | 0 | 224532 | 1263600 | 265200 | 207360 | 0 | 11179090.91 | 0 | 0 | 0 | 0 | 190560 | 562182 | 206330 | 0 | 871680 | 960 | 22438 | 3995900 | 210762 | 980160 | 0 | 0 | 0 | 0 | 105476.4 | 224145 | 3133716 | 0 | 0 | 0 | 20689089 | 78030 | 874403 | 0 | 3128000 | 0 | 8169200 | 7862000 | 707040 | 4862000 | 372600 | 2096640 | 1452620 | 2711040 | 515760 | 281820 | 2389440 | 807360 | 577224 | 529209 | 524448 | 7600000 | 7666400 | 8892000 | 773000 | 675240 | 3451254.54 | 172512 | 0 | 1913280 | 712032 | 0 | 183000 | 0 | 0 | 733200 | 1435200 | 3365760 | 16800 | 395060 | 56640 | 166285686.85 | 21570181 | 8898624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 683280 | 21207270 | 162240 | 14685777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 803621 | 0 | 422248 | 4106545 | 0 | 4643455 | 0 | 4656918 | 0 | 9181600 | 0 | 38340 | 4749000 | 1083927 | 1782766 | 203616 | 1939584 | 0 | 0 | 29260.92 | 1404000 | 4905 | 0 | 22000 | 227319 | 2750000 | 5248880 | 0 | 0 | 18832000 | 0 | 129337356.92 | 295623043.77

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 11-06-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11683.28 | MW | 12:00 Hr. | Energy Generated |  |  | 295.623 |  | MKWHr.
| Day Peak Demand |  |  | 11683.28 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.428 |  | MKWHr.
| Evening Peak Generation |  |  | 14031.3 | MW | 21:00 Hr. | Energy Demand |  |  | 296.051 |  | MKWHr.
| Evening Peak Demand |  |  | 14055.34 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.6 |  | °C
| Minimum Generation of the Day |  |  | 10830.83 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 1204.59 |  | MMCFD
| Maximum Generation of the Day |  |  | 14365.21 | MW | 23:00 Hr. | Production Cost per KWHr |  |  | 5.4798 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 57.0962 | 0 | 1.7914 | 0 | 0 | 0.22453 | 0 | 0 | 59.1121 | Gas | 164.0375 | Gas | 559102957.6961
| Chattogram Zone |  |  | 4.1139 | 20.6891 | 2.1815 | 0 | 3.9959 | 0.10047 | 0 | 0.19056 | 31.2714 | Coal | 66.5833 | Coal | 465363756.04
| Cumilla Zone |  |  | 27.7097 | 0 | 8.8146 | 0 | 0 | 0.52921 | 0.80736 | 0 | 37.8608 | HFO | 18.8971 | HFO | 347445654.148
| Mymensingh Zone |  |  | 3.3658 | 0 | 2.225 | 0 | 0 | 0.41186 | 0 | 0 | 6.0027 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 32.0387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.0387 | Hydro | 3.9959 | Hydro | 399590
| Khulna Zone |  |  | 8.8986 | 21.2073 | 0.16224 | 0 | 0 | 0.68328 | 21.5702 | 0 | 52.5216 | Solar | 4.8553 | Solar | 78945775.7812
| Barishal Zone |  |  | 8.2262 | 18.854 | 0 | 0 | 0 | 0.004905 | 0 | 0 | 27.0851 | Import | 37.0633 | Import | 165900372.84
| Rajshahi Zone |  |  | 22.5885 | 0 | 0 | 0 | 0 | 1.2642 | 14.6858 | 0 | 38.5385 | Wind | 0.19056 | Wind | 2789798.4
| Rangpur Zone |  |  | 0 | 5.8329 | 3.7224 | 0 | 0 | 1.6369 | 0 | 0 | 11.1922
| Total |  |  | 164.0375 | 66.5833 | 18.8971 | 0 | 3.9959 | 4.8553 | 37.0633 | 0.19056 | 295.623
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 559102957.6961 |  | Hydro | 399590
|  |  |  | Coal | 465363756.04 |  | Solar | 78945775.7812
|  |  |  | HFO | 347445654.148 |  | Import | 165900372.84
|  |  |  | HSD | 0 |  | Wind | 2789798.4
[5 empty] | Total: | 161,99,47,904 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 153890.9 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5702 | Peak Hr Flow | 892.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 14300654.57 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 14.6858 | Peak Hr Flow | 732.30 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 340 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.80736 | Peak Hr Flow | 32.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 536 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 37.0633 | Peak Hr Flow | 1656.30 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3702
|  |  |  | Chattogram |  | 0 |  | 1284
|  |  |  | Cumilla |  | 0 |  | 1376
|  |  |  | Mymensingh |  | 0 |  | 1296
|  |  |  | Sylhet |  | 10 |  | 654
|  |  |  | Khulna |  | 0 |  | 1902
|  |  |  | Barishal |  | 0 |  | 529
|  |  |  | Rajshahi |  | 0 |  | 1629
|  |  |  | Rangpur |  | 13 |  | 1007
|  |  |  | Total |  | 23 |  | 13379
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 489
|  |  |  | Total Unavailable Capacity |  |  |  | 789
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:22 |  | Raozan 25 MW PP Shutdown
| 08:33 |  | Bashundhara-Rampura 132 kV Ckt-1 Project Work S/D from Rampura 230/132kV end Due to
Transmission line conversion of Overhead TX line to XLPE cable by the Dhaka & Western
zone Transmission Grid Expansion project, PGCB. The shutdown will continue until 17 June
2025 at 2000 hours.
| 08:42 | 11:24 | BIPTC S/S 20DF21 Forced S/D Due to maintenance
| 08:49 | 12:26 | Faridpur-Gopalganj(N) 132 kV Ckt-1 Scheduled S/D from Gopalganj 400/132kV end.
| 09:27 | 14:53 | Maniknagar 132/33kV S/S Transformer GT-2 LT Scheduled S/D Due to 33kv control room bus-2
insulation development work (DPDC)
| 09:48 | 12:25 | Faridpur-Gopalganj(N) 132 kV Ckt-1 Scheduled S/D from Faridpur 132/33kV end Due to Red
Hot Maintenance at Gopalgonj SS end.
| 10:18 | 10:52 | Shikalbaha 230/132kV S/S Interconnection-1 Tripped showing REC650 relays Due to O/C | [7 empty] | 18.0MW load
|  |  | Fault. | [7 empty] | interrup.
| 12:00 |  | Day peak Generation is 11679 MW
| 14:20 | 16:54 | Kasba 132/33kV S/S TR-1 HT Scheduled S/D Due to Kasba 1 feeder Y phase PT replace work
| 16:55 | 17:49 | Palashbari 132/33kV S/S TR1-414T LT Forced S/D Due to Red hot | [7 empty] | 5.0MW load
interrup.
| 16:56 | 17:48 | Palashbari 132/33kV S/S TR1-414T HT Forced S/D Due to Red hot | [7 empty] | 5.0MW load
interrup.
| 19:24 |  | Raozan 25 MW PP Synchronized
|  | 19:45 | Aminbazar-Mirpur 132kV Ckt-2 is restored.
| 21:03 | 23:00 | Bhulta 132/33kV S/S GT1 LT Scheduled S/D Due to Red hot maintenance
| 21:05 | 22:57 | Bhulta 132/33kV S/S GT1 HT Scheduled S/D Due to red hot maintenance
| 23:01 |  | Barisal 307 MW Synchronized
| 00:33 |  | Sirajgonj 225MW CCPP Unit-1 Tripped with remarks:- ST
| 03:34 |  | Raozan 25 MW PP Tripped
| 03:38 |  | Raozan 25 MW PP Shutdown
| 06:06 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- ST
| 07:02 |  | Narail 132/33kV S/S TR2 (413-T) LT Scheduled S/D Due to Red Hot Maintenance
| 07:03 |  | Narail 132/33kV S/S TR2 (413-T) HT Scheduled S/D Due to Red Hot Maintenance
| 07:14 |  | Barishal 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to 33 kv muladi feeder red hot | [7 empty] | 30.0MW load
|  |  | maintenance work. | [7 empty] | interrup.
| 07:15 |  | Barishal 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to 33 kv Muladi feeder red hot | [7 empty] | 30.0MW load
|  |  | maintenance work. | [7 empty] | interrup.
| 07:35 |  | Mirpur-Uttara 3PH 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to CT
replacement work of all phases
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 11-06-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 120 | 2772812 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 120 | 2835700 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 363 | 8607600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8664000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 141 | 3368204 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 21240 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 12 | 265200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 19 | 207360 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 8 | 58080 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 16 | 105264 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 98880 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 32 | 216960 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 27360 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 224532 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 520 | 11179090.91 | None
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 540 | 11484553 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 320 | 7711640 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 90 | 1263600 | -
Dhaka Area Total |  |  |  |  | 5939.724 | 2738 | 59112075.91
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 105476.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 78030 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 167 | 3995900 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 149 | 3133716 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 224145 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 40 | 206330 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 562182 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 88 | 871680 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 42 | 980160 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22438 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 210762 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 960 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1141 | 20689089 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 16 | 190560 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 0 | 0 | U1 S/D 25/Mar/25 & U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4895.72 | 1735 | 31271428.4
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 202 | 4862000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 350 | 8169200 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 7862000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 15 | 372600 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 36 | 707040 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 182 | 3128000 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 874403 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 524448 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1452620 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 136 | 2711040 | -
| Import (Tripura) |  | Import | 0 | 160 | 32 | 807360 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 24 | 577224 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 15 | 281820 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 113 | 2389440 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 48 | 515760 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 94 | 2096640 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 529209 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1688 | 37860804
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 136 | 3365760 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 16800 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 139 | 1435200 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 81 | 733200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 395060 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 10 | 56640 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 366 | 6002660
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 33 | 773000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 675240 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3451254.54 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 712032 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1913280 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 183000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 172512 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7600000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 390 | 8892000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7666400 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2325 | 1380 | 32038718.54
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 892 | 21570181 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 378 | 8898624 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 162240 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 683280 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1225 | 21207270 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3699.2 | 2512 | 52521595
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 9 | 227319 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2750000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1100 | 18832000 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5248880 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 22000 | Coal shortage
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4905 | -
Barishal Area Total |  |  |  |  | 2236 | 1449 | 27085104
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Machine Standby
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 174 | 4106545 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 191 | 4643455 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 190 | 4656918 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 408 | 9181600 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 38340 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 732.3 | 14685777 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 422248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 803621 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 1695.3 | 38538504
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 47 | 1083927 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4749000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 106 | 1939584 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 29260.92 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1782766 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 203616 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1404000 | -
Rangpur Area Total |  |  |  |  | 950 | 468 | 11192153.92
Eastern Grid Total |  |  |  |  | 16705.895 | 7907 | 166285686.85
Western Grid Total |  |  |  |  | 10338.16 | 6124.3 | 129337356.92
National Grid Total |  |  |  |  | 27044.055 | 14031.3 | 295623043.77
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 11-06-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8302.32 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5054.4 | MW
i) Dhaka area |  |  | 3702.36 |  | MW | i) Khulna area |  |  |  | 1902 | MW
ii) Chattogram area |  |  | 1284 |  | MW | ii) Barishal area |  |  |  | 529 | MW
iii) Cumilla area |  |  | 1375.96 |  | MW | iii) Rajshahi area |  |  |  | 1629.4 | MW
iv) Mymensingh area |  |  | 1296 |  | MW | iv) Rangpur area |  |  |  | 994 | MW
v) Sylhet area |  |  | 644 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13356.72 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 80 | 21:00 | 133 | Patuakhali | 92 | 23:00
2 | AKSML | 66 | 16:00 | 68 | Jaldhaka | 104 | 00:00 | 134 | Payra | 42 | 00:00
3 | Aftabnagar | 32 | 22:00 | 69 | Jamalpur | 154 | 21:00 | 135 | Postogola | 44 | 23:00
4 | Agargaon | 104 | 23:00 | 70 | Jashore | 156 | 00:00 | 136 | Purbachal | 18 | 21:00
5 | Agrabad | 72 | 19:00 | 71 | Jhenaidah | 150 | 00:00 | 137 | Purbasadipur | 142 | 23:00
6 | Amnura | 45 | 00:00 | 72 | Joydebpur | 83 | 22:00 | 138 | Rahanpur | 39 | 00:00
7 | Ashuganj | 99 | 23:00 | 73 | Joypurhat | 78 | 00:00 | 139 | Rahim | 1 | 00:00
8 | BSRM | 198 | 02:00 | 74 | Juldah | 13 | 15:00 | 140 | Rajbari | 90 | 20:00
9 | Bagerhat | 89 | 00:00 | 75 | KSRM | 11 | 08:00 | 141 | Rajendrapur | 113 | 23:00
10 | Bajitpur | 60 | 19:30 | 76 | Kabirpur | 119 | 21:00 | 142 | Rajshahi | 118 | 00:00
11 | Bakulia | 75 | 15:00 | 77 | Kachua | 96 | 21:00 | 143 | Rajshahi-230 | 103 | 23:00
12 | Banani | 28 | 17:00 | 78 | Kallyanpur | 93 | 22:00 | 144 | Ramganj | 120 | 19:30
13 | Bangabhaban | 5 | 10:00 | 79 | Kalurghat | 28 | 20:00 | 145 | Rampur | 36 | 00:00
14 | Barapukuria | 72 | 22:00 | 80 | Kamrangirchar | 34 | 23:00 | 146 | Rangamati | 16 | 14:00
15 | Barguna | 26 | 22:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 156 | 19:30
16 | Barishal | 120 | 21:00 | 82 | Kasba | 42 | 20:00 | 148 | Ruppur | 7.4 | 15:00
17 | Barishal-230 | 114 | 23:00 | 83 | Kazla | 64 | 21:00 | 149 | SSM | 0 | 00:00
18 | Baroaulia | 55 | 23:00 | 84 | Keranigonj | 78 | 23:00 | 150 | Saidpur | 112 | 00:00
19 | Baroirhat | 63 | 23:00 | 85 | Khagrachori | 26 | 00:00 | 151 | Satkhira | 160 | 00:00
20 | Bashundhara | 128 | 21:00 | 86 | Khulna | 66 | 00:00 | 152 | Satmasjid | 84 | 19:30
21 | BashundharaCement | 1 | 10:00 | 87 | Khulshi | 159 | 16:00 | 153 | Savar | 120 | 23:00
22 | Beanibazar | 84 | 20:00 | 88 | Kishoreganj | 152 | 20:00 | 154 | SevenRings | 6.52 | 23:00
23 | Benapole | 82 | 21:00 | 89 | Kodda | 148 | 20:00 | 155 | ShahCement | 13 | 07:00
24 | Bhaluka | 122 | 22:00 | 90 | Kulaura | 51 | 21:00 | 156 | Shahjadpur | 86 | 23:00
25 | Bhandaria | 66 | 00:00 | 91 | Kurigram | 68 | 06:00 | 157 | Shahjibazar | 127 | 23:00
26 | Bhangura | 46 | 21:00 | 92 | Kushtia | 160 | 19:30 | 158 | Shahmirpur | 57 | 18:30
27 | Bheramara(GK) | 76 | 00:00 | 93 | Lalbag | 12 | 00:00 | 159 | Shariatpur | 104 | 22:00
28 | Bhulta | 120 | 00:00 | 94 | Lalmonirhat | 64 | 20:00 | 160 | Sherpur | 174 | 22:00
29 | Bog-Sherpur | 64 | 22:00 | 95 | MI_Cement | 3.8 | 16:00 | 161 | Shikalbaha | 21 | 00:00
30 | Bogura | 178 | 22:00 | 96 | Madanganj | 35 | 00:00 | 162 | Shitalakhya | 61.1 | 16:00
31 | Borhanuddin | 92 | 01:00 | 97 | Madaripur | 125 | 22:00 | 163 | Sholosohor | 35 | 21:00
32 | Brahmanbaria | 131 | 00:00 | 98 | Madartek | 81.14 | 23:00 | 164 | Shyampur | 48 | 22:00
33 | Cantonment | 122 | 19:00 | 99 | Madunaghat | 53 | 20:00 | 165 | Siddhirganj | 77 | 22:00
34 | Chandina | 23.61 | 16:00 | 100 | Magura | 74 | 23:00 | 166 | Sirajganj | 117 | 22:00
35 | Chandpur | 88 | 19:30 | 101 | Mahasthangarh | 100 | 00:00 | 167 | Sonargaon | 71 | 19:30
36 | Chandraghona | 37 | 19:00 | 102 | Manikganj | 103 | 22:00 | 168 | Sreemongol | 78 | 23:00
37 | Chapai | 79 | 22:00 | 103 | Maniknagar | 50 | 23:00 | 169 | Sreepur | 64 | 20:00
38 | Charsaidpur | 9 | 15:00 | 104 | Matarbari | 50 | 21:00 | 170 | Srinagar | 56.11 | 23:00
39 | Chauddagram | 74 | 01:00 | 105 | Matuail | 36 | 23:00 | 171 | Sunamganj | 63 | 19:30
40 | Chhatak | 41 | 00:00 | 106 | Millgate | 78 | 16:00 | 172 | Sylhet | 50 | 19:30
41 | Chowmuhani | 242 | 19:30 | 107 | Mirpur | 98 | 21:00 | 173 | Sylhet-132 | 134 | 19:00
42 | Chuadanga | 127 | 23:00 | 108 | Mirsorai | 9 | 14:00 | 174 | TK | 34 | 19:30
43 | Coxsbazar | 138 | 12:00 | 109 | Mirzapur | 43 | 21:00 | 175 | Tangail | 191 | 19:30
44 | Cumilla(N) | 141 | 23:00 | 110 | Mithapukur | 80 | 20:00 | 176 | Thakurgaon | 118 | 22:00
45 | Cumilla(S) | 142 | 16:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 85 | 23:00
46 | Daudkandi | 149 | 21:00 | 112 | Mogbazar | 94.9 | 21:00 | 178 | Ullahpara | 44 | 20:00
47 | Dhaka | 26 | 13:00 | 113 | Mongla | 26 | 00:00 | 179 | Ullon | 48 | 23:00
48 | Dhamrai | 94 | 23:00 | 114 | Motijheel | 28 | 23:00 | 180 | Uttara | 82 | 19:30
49 | Dhanmondi | 88 | 19:00 | 115 | Muktagacha | 45 | 22:00 | 181 | UttaraNew | 52 | 23:00
50 | Dohazari | 100 | 23:00 | 116 | Munshiganj | 120 | 23:00 | 182 | Zigatola | 60 | 21:00
51 | Faridpur | 174 | 23:00 | 117 | Muradnagar | 32 | 00:00
52 | Fatullah | 51 | 23:00 | 118 | Mymensingh | 219 | 20:00
53 | Fenchuganj | 45 | 00:00 | 119 | Naogaon | 158 | 00:00
54 | Feni | 115 | 15:00 | 120 | Narail | 66 | 21:00
55 | GPH | 3 | 20:00 | 121 | Narinda | 46 | 19:00
56 | Ghatail | 82 | 20:00 | 122 | Narshingdi | 153 | 23:00
57 | Ghorashal | 14 | 23:00 | 123 | Natore | 175 | 23:00
58 | Ghorashal-230 | 71 | 20:00 | 124 | Nawabganj | 55.6 | 22:00
59 | Goalpara | 44 | 00:00 | 125 | Netrakona | 157 | 20:00
60 | Gollamari | 98 | 23:00 | 126 | New | 38.5 | 23:00
61 | Gopalganj | 118 | 00:00 | 127 | Niamatpur | 89 | 22:00
62 | Gulshan | 88 | 13:00 | 128 | Noapara | 48 | 00:00
63 | Halishahar | 30.5 | 15:00 | 129 | PHP | 9 | 01:00
64 | HaripurSBU | 83 | 21:00 | 130 | Pabna | 121 | 19:00
65 | Hasnabad | 66 | 21:00 | 131 | Palashbari | 116 | 23:00
66 | Hathazari | 82 | 00:00 | 132 | Panchagarh | 62 | 02:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 11-06-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 12102.96 | 74 |  | 12180.29
1:00 | 12070.37 | 67 |  | 12140.37
2:00 | 12178.22 | 59 |  | 12240.22
3:00 | 12079.85 | 49 |  | 12130.85
4:00 | 11938.3 | 40 |  | 11980.3
5:00 | 11781.43 | 28 |  | 11810.43
6:00 | 11033.79 | 0 |  | 11033.79
7:00 | 10864.66 | 0 |  | 10864.66
8:00 | 10830.83 | 0 |  | 10830.83
9:00 | 10866.77 | 0 |  | 10866.77
10:00 | 11078.97 | 0 |  | 11078.97
11:00 | 11143.87 | 0 |  | 11143.87
12:00 | 11683.28 | 0 |  | 11683.28
13:00 | 12321.49 | 0 |  | 12321.49
14:00 | 12705.72 | 0 |  | 12705.72
15:00 | 12688.64 | 0 |  | 12688.64
16:00 | 12588.76 | 0 |  | 12588.76
17:00 | 12163.83 | 0 |  | 12163.83
18:00 | 11408.85 | 0 |  | 11408.85
19:00 | 12358 | 31 |  | 12390
19:30 | 13186 | 28 |  | 13215
20:00 | 13406 | 0 |  | 13406
21:00 | 14031.3 | 23 |  | 14055.34
22:00 | 14061.47 | 23 |  | 14085.47
23:00 | 14365.21 | 34 |  | 14401.21
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 11-06-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6797 | 5305.96 | 12102.96 | DAILY GENERATION CURVE
00:30 | 6759.5 | 5327.165 | 12086.665
01:00 | 6722 | 5348.37 | 12070.37 | 11-06-2025
01:30 | 6759.6 | 5364.695 | 12124.295
02:00 | 6797.2 | 5381.02 | 12178.22
02:30 | 6777.7 | 5351.335 | 12129.035
03:00 | 6758.2 | 5321.65 | 12079.85
03:30 | 6761.2 | 5247.875 | 12009.075
04:00 | 6764.2 | 5174.1 | 11938.3
04:30 | 6717.2 | 5142.665 | 11859.865
05:00 | 6670.2 | 5111.23 | 11781.43
05:30 | 6405.43 | 5002.18 | 11407.61
06:00 | 6140.66 | 4893.13 | 11033.79
06:30 | 6162.2 | 4787.025 | 10949.225
07:00 | 6183.74 | 4680.92 | 10864.66
07:30 | 6119.045 | 4728.7 | 10847.745
08:00 | 6054.35 | 4776.48 | 10830.83
08:30 | 6047.195 | 4801.605 | 10848.8
09:00 | 6040.04 | 4826.73 | 10866.77
09:30 | 6061.265 | 4911.605 | 10972.87
10:00 | 6082.49 | 4996.48 | 11078.97
10:30 | 6104.47 | 5006.95 | 11111.42
11:00 | 6126.45 | 5017.42 | 11143.87
11:30 | 6375.515 | 5038.06 | 11413.575
12:00 | 6624.58 | 5058.7 | 11683.28
12:30 | 6831.21 | 5171.175 | 12002.385
13:00 | 7037.84 | 5283.65 | 12321.49
13:30 | 7093.2 | 5420.405 | 12513.605
14:00 | 7148.56 | 5557.16 | 12705.72
14:30 | 7140.47 | 5556.71 | 12697.18
15:00 | 7132.38 | 5556.26 | 12688.64
15:30 | 7129.32 | 5509.38 | 12638.7
16:00 | 7126.26 | 5462.5 | 12588.76
16:30 | 7040.515 | 5335.78 | 12376.295
17:00 | 6954.77 | 5209.06 | 12163.83
17:30 | 6778.285 | 5008.055 | 11786.34
18:00 | 6601.8 | 4807.05 | 11408.85
18:30 | 6971.9 | 4911.525 | 11883.425
19:00 | 7342 | 5016 | 12358
19:30 | 7572 | 5614 | 13186
20:00 | 7614 | 5792 | 13406
20:30 | 7760.5 | 5958.15 | 13718.65 |  | Executive Engineer
21:00 | 7907 | 6124.3 | 14031.3 |  | Network Operation Division
21:30 | 7940.5 | 6105.885 | 14046.385
22:00 | 7974 | 6087.47 | 14061.47
22:30 | 8046.25 | 6167.09 | 14213.34
23:00 | 8118.5 | 6246.71 | 14365.21

## En-Curve
QF-LDC-12
Date | 11-06-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4128 | 2871 | 856 | 0 | 36 | 673.96 | 167 | 2672 | 0 | 86 | 607 | 0 | 0 | 6 | 74 | DAILY ENERGY CURVE
00:30 | 4079 | 2868.5 | 894 | 0 | 36 | 673.665 | 167 | 2656 | 0 | 103.5 | 601 | 0 | 0 | 8 | 70.5 | 11-06-2025
01:00 | 4030 | 2866 | 932 | 0 | 36 | 673.37 | 167 | 2640 | 0 | 121 | 595 | 0 | 0 | 10 | 67
01:30 | 4050 | 2868 | 932 | 0 | 36 | 674.195 | 167 | 2647 | 0 | 121 | 622.1 | 0 | 0 | 7 | 63 | Energy Generated | 295.623 |  | MKWHr
02:00 | 4070 | 2870 | 932 | 0 | 36 | 675.02 | 167 | 2654 | 0 | 121 | 649.2 | 0 | 0 | 4 | 59 | Energy not Served | 0.428 |  | MKWHr
02:30 | 4043 | 2858.5 | 932.5 | 0 | 35 | 673.335 | 167 | 2643.5 | 0 | 121 | 652.7 | 0 | 0 | 2.5 | 54 | Total Energy Requirement | 296.051 |  | MKWHr
03:00 | 4016 | 2847 | 933 | 0 | 34 | 671.65 | 167 | 2633 | 0 | 121 | 656.2 | 0 | 0 | 1 | 49
03:30 | 3986 | 2839.5 | 933 | 0 | 34 | 671.375 | 167 | 2603 | 0 | 121 | 652.2 | 0 | 0 | 2 | 44.5
04:00 | 3956 | 2832 | 933 | 0 | 34 | 671.1 | 167 | 2573 | 0 | 121 | 648.2 | 0 | 0 | 3 | 40
04:30 | 3901.5 | 2823 | 932.5 | 0 | 34 | 672.665 | 167 | 2555 | 0 | 121 | 649.7 | 0 | 0 | 3.5 | 34
05:00 | 3847 | 2814 | 932 | 0 | 34 | 674.23 | 167 | 2537 | 0 | 121 | 651.2 | 0 | 0 | 4 | 28
05:30 | 3789 | 2624 | 932 | 0 | 34 | 593.84 | 167 | 2492 | 19.67 | 121 | 633.1 | 0 | 0 | 2 | 14
06:00 | 3731 | 2434 | 932 | 0 | 34 | 513.45 | 167 | 2447 | 39.34 | 121 | 615 | 0 | 0 | 0 | 0
06:30 | 3718 | 2430 | 932 | 0 | 33 | 467.655 | 167 | 2408 | 84.57 | 121 | 584.5 | 0 | 0 | 3.5 | 0
07:00 | 3705 | 2426 | 932 | 0 | 32 | 421.86 | 167 | 2369 | 129.8 | 121 | 554 | 0 | 0 | 7 | 0
07:30 | 3707.5 | 2365 | 932.5 | 0 | 32 | 420.185 | 167 | 2353 | 201.06 | 120.5 | 544.5 | 0 | 0 | 4.5 | 0
08:00 | 3710 | 2304 | 933 | 0 | 32 | 418.51 | 167 | 2337 | 272.32 | 120 | 535 | 0 | 0 | 2 | 0
08:30 | 3745 | 2334.5 | 912.5 | 0 | 33 | 424.08 | 167 | 2348.5 | 357.72 | 94 | 431.5 | 0 | 0 | 1 | 0
09:00 | 3780 | 2365 | 892 | 0 | 34 | 429.65 | 167 | 2360 | 443.12 | 68 | 328 | 0 | 0 | 0 | 0
09:30 | 3812.5 | 2397.5 | 892 | 0 | 33 | 430.13 | 167 | 2366 | 516.24 | 60 | 298.5 | 0 | 0 | 0 | 0
10:00 | 3845 | 2430 | 892 | 0 | 32 | 430.61 | 167 | 2372 | 589.36 | 52 | 269 | 0 | 0 | 0 | 0
10:30 | 3854 | 2436.75 | 892 | 0 | 34 | 431.295 | 167 | 2374 | 601.875 | 52 | 268.5 | 0 | 0 | 0 | 0
11:00 | 3863 | 2443.5 | 892 | 0 | 36 | 431.98 | 167 | 2376 | 614.39 | 52 | 268 | 0 | 0 | 0 | 0
11:30 | 3964 | 2585.75 | 892 | 0 | 36 | 432.755 | 167 | 2349 | 641.57 | 52 | 290.5 | 0 | 0 | 3 | 0
12:00 | 4065 | 2728 | 892 | 0 | 36 | 433.53 | 167 | 2322 | 668.75 | 52 | 313 | 0 | 0 | 6 | 0
12:30 | 4095.5 | 2834.5 | 892 | 0 | 36 | 505.05 | 167 | 2348 | 644.335 | 55.5 | 416.5 | 0 | 0 | 8 | 0
13:00 | 4126 | 2941 | 892 | 0 | 36 | 576.57 | 167 | 2374 | 619.92 | 59 | 520 | 0 | 0 | 10 | 0
13:30 | 4079.5 | 2935 | 892 | 0 | 37 | 649.285 | 167 | 2485.5 | 578.32 | 72.5 | 598 | 0 | 0 | 19.5 | 0
14:00 | 4033 | 2929 | 892 | 0 | 38 | 722 | 167 | 2597 | 536.72 | 86 | 676 | 0 | 0 | 29 | 0
14:30 | 4047.5 | 2962.5 | 892 | 0 | 39 | 725.5 | 167 | 2628 | 487.18 | 69 | 660.5 | 0 | 0 | 19 | 0
15:00 | 4062 | 2996 | 892 | 0 | 40 | 729 | 167 | 2659 | 437.64 | 52 | 645 | 0 | 0 | 9 | 0
15:30 | 4051.5 | 3014.5 | 892 | 0 | 39 | 729 | 167 | 2658 | 372.7 | 52 | 658 | 0 | 0 | 5 | 0
16:00 | 4041 | 3033 | 892 | 0 | 38 | 729 | 167 | 2657 | 307.76 | 52 | 671 | 0 | 0 | 1 | 0
16:30 | 3984.5 | 2995.5 | 892.5 | 0 | 37 | 729 | 167 | 2609 | 232.795 | 52 | 674.5 | 0 | 0 | 2.5 | 0
17:00 | 3928 | 2958 | 893 | 0 | 36 | 729 | 167 | 2561 | 157.83 | 52 | 678 | 0 | 0 | 4 | 0
17:30 | 3860.5 | 2842 | 892 | 0 | 35 | 672.5 | 167 | 2500 | 103.84 | 56 | 647 | 0 | 0 | 10.5 | 0
18:00 | 3793 | 2726 | 891 | 0 | 34 | 616 | 167 | 2439 | 49.85 | 60 | 616 | 0 | 0 | 17 | 0
18:30 | 3938 | 2871 | 867.5 | 0 | 17 | 631 | 167 | 2529 | 24.925 | 105.5 | 722 | 0 | 0 | 10.5 | 15.5
19:00 | 4083 | 3016 | 844 | 0 | 0 | 646 | 167 | 2619 | 0 | 151 | 828 | 0 | 0 | 4 | 31
19:30 | 4071 | 3040 | 844 | 0 | 8 | 750 | 167 | 3121 | 0 | 222 | 955 | 0 | 0 | 8 | 28
20:00 | 4001 | 2963 | 843 | 0 | 36 | 769 | 167 | 3408 | 0 | 213 | 996 | 0 | 0 | 10 | 0
20:30 | 4063 | 3025.5 | 867.5 | 0 | 34 | 750.65 | 167 | 3560.5 | 0 | 209 | 1028.5 | 0 | 0 | 13 | 11.5
21:00 | 4125 | 3088 | 892 | 0 | 32 | 732.3 | 167 | 3713 | 0 | 205 | 1061 | 0 | 0 | 16 | 23
21:30 | 4158 | 3112 | 856 | 0 | 38 | 730.885 | 167 | 3700.5 | 0 | 204.5 | 1063.5 | 0 | 0 | 16 | 23
22:00 | 4191 | 3136 | 820 | 0 | 44 | 729.47 | 167 | 3688 | 0 | 204 | 1066 | 0 | 0 | 16 | 23
22:30 | 4225 | 3133.25 | 820.5 | 0 | 44 | 739.09 | 167 | 3797.5 | 0 | 203.5 | 1071 | 0 | 0 | 12.5 | 28.5
23:00 | 4259 | 3130.5 | 821 | 0 | 44 | 748.71 | 167 | 3907 | 0 | 203 | 1076 | 0 | 0 | 9 | 34
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 11-06-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 399 | 06:00 | 382 | 19:30 | Payra | 417 | 05:00 | 406 | 23:00
Ashuganj | 417 | 5:00 | 393 | 22:00 | Rahanpur | 409 | 08:00 | 392 | 23:00
Bhulta | 412 | 05:00 | 391 | 23:00 | Rampal | 406 | 05:00 | 388 | 23:00
Bibiana | 395 | 07:00 | 386 | 22:00
BIPTC | 404 | 08:00 | 393 | 00:00
Bogura | 398 | 06:00 | 379 | 22:00
Gopalganj | 406 | 06:00 | 389 | 23:00
Kaliakoir | 391 | 00:00 | 372 | 23:00
Madunaghat | 400 | 07:00 | 393 | 23:00
Meghnaghat | 402 | 06:00 | 391 | 23:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 236 | 05:00 | 225 | 23:00 | Keranigonj | 234 | 07:00 | 224 | 23:00
AKSML | 232 | 18:30 | 226 | 01:00 | Khulna(S) | 232 | 08:00 | 212 | 23:00
Aminbazar | 237 | 05:00 | 228 | 21:00 | Madunaghat | 234 | 18:00 | 228 | 00:00
Ashuganj | 240 | 05:00 | 228 | 23:00 | Madunaghat-400 | 234 | 19:00 | 228 | 23:00
Ashuganj-400 | 240 | 05:00 | 228 | 23:00 | Maniknagar | 231 | 05:00 | 222 | 23:00
Baghabari | 236 | 01:00 | 224 | 23:00 | Meghnaghat | 240 | 06:00 | 231 | 22:00
Barapukuria | 222 | 02:00 | 212 | 23:00 | Meghnaghat-400 | 234 | 06:00 | 226 | 23:00
Barapukuria-230 | 222 | 02:00 | 212 | 23:00 | Mirsorai | 232 | 18:30 | 223 | 23:00
Barishal | 240 | 07:00 | 228 | 23:00 | Rajshahi | 235 | 08:00 | 218 | 23:00
Bheramara | 234 | 07:00 | 221 | 19:30 | Rampal | 232 | 06:00 | 215 | 23:00
Bhulta | 241 | 05:00 | 223 | 23:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 231 | 18:00 | 224 | 22:00 | Rampura | 241 | 05:00 | 227 | 22:00
BIPTC | 237 | 06:00 | 222 | 19:30 | Shikalbaha | 233 | 18:30 | 227 | 01:00
Bogura | 233 | 06:00 | 220 | 23:00 | Shyampur | 233 | 05:00 | 225 | 23:00
Bogura-400 | 232 | 06:00 | 220 | 22:00 | Siddhirganj | 232 | 06:00 | 224 | 23:00
Borhanuddin | 242 | 18:00 | 236 | 20:00 | Sirajgonj | 241 | 05:00 | 234 | 10:00
BSRM | 231 | 18:30 | 223 | 22:00 | Sreepur | 235 | 03:00 | 222 | 23:00
Cumilla(N) | 237 | 05:00 | 220 | 23:00 | Tongi | 239 | 07:00 | 227 | 23:00
Faridpur | 237 | 06:00 | 224 | 23:00
Fenchuganj | 231 | 06:00 | 225 | 22:00
Ghorashal | 244 | 01:00 | 240 | 00:00
Ghorashal-230 | 240 | 05:00 | 227 | 23:00
Gopalganj | 239 | 06:00 | 223 | 19:00
GPH | 230 | 02:00 | 228 | 00:00
Haripur | 232 | 06:00 | 223 | 23:00
Hasnabad | 234 | 06:00 | 227 | 21:00
Hathazari | 233 | 18:30 | 227 | 23:00
Ishurdi | 237 | 06:00 | 223 | 23:00
Jhenaidah | 231 | 06:00 | 214 | 23:00
Kaliakoir | 244 | 00:00 | 229 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 02:00 | 126 | 22:00 | Madartek | 133 | 04:00 | 126 | 23:00
Agargaon | 136 | 05:00 | 129 | 23:00 | Madunaghat | 133 | 17:00 | 128 | 00:00
Agrabad | 133 | 07:00 | 128 | 01:00 | Magura | 134 | 05:00 | 120 | 22:00
AKS | 132 | 18:30 | 128 | 00:00 | Mahasthangarh | 133 | 06:00 | 122 | 23:00
Aminbazar | 135 | 03:00 | 129 | 22:00 | Manikganj | 134 | 05:00 | 122 | 23:00
Amnura | 137 | 08:00 | 123 | 22:00 | Maniknagar | 132 | 05:00 | 126 | 23:00
Ashuganj | 140 | 06:00 | 135 | 19:00 | Matarbari | 120 | 18:30 | 110 | 23:00
Bagerhat | 133 | 18:00 | 116 | 23:00 | Matuail | 136 | 03:00 | 131 | 23:00
Bajitpur | 133 | 05:00 | 124 | 21:00 | Millgate | 136 | 03:00 | 126 | 23:00
Bakulia | 135 | 18:30 | 129 | 00:00 | Mirpur | 134 | 06:00 | 127 | 23:00
Banani | 134 | 03:00 | 126 | 23:00 | Mirzapur | 139 | 00:00 | 124 | 19:00
Bangabhaban | 131 | 03:00 | 126 | 23:00 | Mithapukur | 129 | 06:00 | 117 | 23:00
Barapukuria | 134 | 06:00 | 124 | 20:00 | MI_Cement | 136 | 05:00 | 131 | 21:00
Barguna | 136 | 08:00 | 127 | 23:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 133 | 18:00 | 124 | 23:00 | Mogbazar | 136 | 05:00 | 127 | 23:00
Barishal-230 | 133 | 07:00 | 124 | 23:00 | Mongla | 134 | 18:30 | 118 | 23:00
Baroaulia | 134 | 00:00 | 129 | 11:00 | Motijheel | 131 | 03:00 | 126 | 23:00
Baroirhat | 129 | 18:30 | 119 | 00:00 | Muktagacha | 137 | 00:00 | 118 | 19:00
Bashundhara | 136 | 06:00 | 126 | 00:00 | Munshiganj | 134 | 03:00 | 129 | 23:00
BashundharaCement | 135 | 07:00 | 130 | 22:00 | Muradnagar | 132 | 19:30 | 122 | 23:00
Beanibazar | 127 | 05:00 | 121 | 19:00 | Mymensingh | 139 | 00:00 | 111 | 23:00
Benapole | 132 | 18:00 | 112 | 23:00 | Naogaon | 131 | 08:00 | 117 | 23:00
Bhaluka | 134 | 06:00 | 123 | 23:00 | Narail | 135 | 04:00 | 118 | 23:00
Bhandaria | 127 | 18:00 | 112 | 23:00 | Narinda | 132 | 05:00 | 126 | 23:00
Bhangura | 135 | 00:00 | 125 | 23:00 | Narshingdi | 143 | 05:00 | 125 | 22:00
Bheramara | 138 | 06:00 | 131 | 19:30 | Natore | 135 | 08:00 | 124 | 23:00
Bheramara(GK) | 138 | 06:00 | 131 | 19:30 | Nawabganj | 136 | 04:00 | 129 | 22:00
Bhulta | 130 | 06:00 | 124 | 16:00 | Netrakona | 124 | 06:00 | 110 | 22:00
Bog-Sherpur | 136 | 08:00 | 125 | 22:00 | New | 138 | 04:00 | 128 | 22:00
Bogura | 136 | 06:00 | 127 | 23:00 | Niamatpur | 135 | 06:00 | 128 | 23:00
Bogura-230 | 137 | 08:00 | 127 | 23:00 | Noapara | 136 | 18:30 | 118 | 23:00
Brahmanbaria | 133 | 06:00 | 123 | 23:00 | Pabna | 137 | 07:00 | 127 | 00:00
Cantonment | 136 | 04:00 | 129 | 23:00 | Palashbari | 127 | 08:00 | 116 | 23:00
Chandina | 133 | 18:30 | 121 | 22:00 | Panchagarh | 130 | 19:00 | 115 | 12:00
Chandpur | 135 | 18:30 | 118 | 00:00 | Patuakhali | 135 | 06:00 | 127 | 23:00
Chandraghona | 133 | 08:00 | 130 | 00:00 | Payra | 137 | 06:00 | 132 | 23:00
Chapai | 132 | 11:00 | 125 | 21:00 | PHP | 133 | 19:00 | 118 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 136 | 05:00 | 130 | 23:00 | Postogola | 138 | 06:00 | 132 | 22:00
Chauddagram | 132 | 18:30 | 118 | 00:00 | Purbachal | 135 | 04:00 | 126 | 23:00
Chhatak | 124 | 08:00 | 115 | 19:00 | Purbasadipur | 126 | 05:00 | 115 | 12:00
Chowmuhani | 126 | 18:30 | 110 | 00:00 | Rahanpur | 137 | 07:00 | 126 | 22:00
Chuadanga | 133 | 18:00 | 118 | 23:00 | Rahanpur-400 | 136 | 06:00 | 130 | 22:00
Coxsbazar | 120 | 09:00 | 111 | 00:00 | Rahim | 135 | 00:00 | 130 | 23:00
Cumilla(N) | 134 | 19:00 | 125 | 22:00 | Rajbari | 137 | 06:00 | 127 | 23:00
Cumilla(S) | 134 | 19:30 | 123 | 22:00 | Rajendrapur | 141 | 01:00 | 126 | 22:00
Daudkandi | 130 | 19:00 | 122 | 22:00 | Rajshahi | 135 | 04:00 | 125 | 23:00
Dhaka | 134 | 03:00 | 126 | 23:00 | Rajshahi-230 | 135 | 06:00 | 115 | 23:00
Dhamrai | 139 | 00:00 | 128 | 23:00 | Ramganj | 127 | 18:30 | 110 | 00:00
Dhanmondi | 137 | 03:00 | 131 | 23:00 | Rampur | 134 | 18:30 | 128 | 00:00
Dohazari | 130 | 18:30 | 122 | 00:00 | Rampura | 134 | 04:00 | 126 | 22:00
Faridpur | 137 | 06:00 | 130 | 23:00 | Rangamati | 132 | 07:00 | 129 | 00:00
Fatullah | 136 | 04:00 | 131 | 22:00 | Rangpur | 127 | 07:00 | 117 | 23:00
Fenchuganj | 136 | 06:00 | 131 | 23:00 | Ruppur | 139 | 08:00 | 130 | 23:00
Feni | 130 | 18:30 | 118 | 00:00 | Saidpur | 128 | 06:00 | 118 | 19:30
Ghatail | 136 | 00:00 | 116 | 19:00 | Satkhira | 133 | 18:00 | 113 | 23:00
Ghorashal | 143 | 00:00 | 136 | 23:00 | Satmasjid | 136 | 06:00 | 124 | 10:00
Goalpara | 138 | 18:30 | 123 | 23:00 | Savar | 133 | 06:00 | 127 | 22:00
Gollamari | 138 | 18:00 | 124 | 23:00 | SevenRings | 143 | 06:00 | 135 | 23:00
Gopalganj | 137 | 18:30 | 125 | 23:00 | ShahCement | 136 | 05:00 | 130 | 23:00
Gopalganj-400 | 139 | 06:00 | 131 | 22:00 | Shahjadpur | 140 | 00:00 | 130 | 20:00
Gulshan | 134 | 00:00 | 126 | 23:00 | Shahjibazar | 133 | 02:00 | 121 | 23:00
Halishahar | 134 | 18:30 | 129 | 01:00 | Shahmirpur | 134 | 16:00 | 129 | 00:00
Haripur | 136 | 05:00 | 131 | 22:00 | Shariatpur | 136 | 07:00 | 126 | 22:00
HaripurSBU | 136 | 05:00 | 131 | 22:00 | Sherpur | 139 | 00:00 | 109 | 18:00
Hasnabad | 137 | 05:00 | 132 | 23:00 | Shikalbaha | 123 | 18:00 | 118 | 00:00
Hathazari | 136 | 18:00 | 130 | 15:00 | Shikalbaha-230 | 134 | 18:30 | 130 | 00:00
Ishurdi | 139 | 06:00 | 131 | 19:30 | Shitalakhya | 136 | 05:00 | 131 | 21:00
Jaldhaka | 124 | 17:00 | 114 | 21:00 | Sholosohor | 134 | 18:30 | 128 | 00:00
Jamalpur | 139 | 00:00 | 114 | 19:00 | Shyampur | 135 | 04:00 | 133 | 00:00
Jashore | 134 | 06:00 | 119 | 23:00 | Shyampur-230 | 136 | 06:00 | 130 | 22:00
Jhenaidah | 137 | 08:00 | 118 | 23:00 | Siddhirganj | 135 | 03:00 | 131 | 23:00
Jhenaidah-230 | 137 | 06:00 | 125 | 23:00 | Sirajganj | 134 | 07:00 | 122 | 22:00
Joydebpur | 140 | 04:00 | 131 | 22:00 | Sonargaon | 135 | 08:00 | 129 | 23:00
Joypurhat | 128 | 06:00 | 115 | 23:00 | Sreemongol | 129 | 06:00 | 118 | 23:00
Juldah | 134 | 18:30 | 129 | 00:00 | Sreepur | 136 | 00:00 | 127 | 23:00
Kabirpur | 138 | 00:00 | 125 | 22:00 | Srinagar | 136 | 06:00 | 129 | 23:00
Kachua | 133 | 18:30 | 119 | 00:00 | SSM | 139 | 19:30 | 132 | 03:00
Kaliakoir | 140 | 00:00 | 130 | 23:00 | Sunamganj | 123 | 18:00 | 113 | 20:00
Kallyanpur | 135 | 01:00 | 128 | 22:00 | Sylhet | 128 | 07:00 | 120 | 21:00
Kalurghat | 132 | 18:30 | 128 | 00:00 | Sylhet-132 | 129 | 08:00 | 122 | 23:00
Kamrangirchar | 136 | 06:00 | 130 | 22:00 | Tangail | 138 | 00:00 | 118 | 19:00
Kaptai | 135 | 8:00 | 133 | 1:00 | Thakurgaon | 129 | 19:00 | 113 | 12:00
Kasba | 132 | 19:30 | 122 | 23:00 | TK | 132 | 18:30 | 128 | 00:00
Kazla | 131 | 00:00 | 126 | 23:00 | Tongi | 138 | 07:00 | 129 | 23:00
Keranigonj | 136 | 06:00 | 130 | 22:00 | Ullahpara | 136 | 07:00 | 124 | 23:00
Khagrachori | 132 | 18:30 | 128 | 00:00 | Ullon | 134 | 05:00 | 127 | 21:00
Khulna | 137 | 18:00 | 123 | 23:00 | Uttara | 134 | 07:00 | 127 | 23:00
Khulna(S) | 138 | 18:00 | 124 | 23:00 | UttaraNew | 136 | 00:00 | 126 | 23:00
Khulshi | 133 | 18:30 | 128 | 00:00 | Zigatola | 137 | 07:00 | 130 | 23:00
Kishoreganj | 130 | 18:00 | 119 | 23:00
Kodda | 139 | 00:00 | 128 | 22:00
KSRM | 134 | 17:00 | 130 | 00:00
Kulaura | 134 | 07:00 | 118 | 23:00
Kurigram | 125 | 18:30 | 113 | 23:00
Kushtia | 135 | 04:00 | 125 | 19:30
Lalbag | 137 | 06:00 | 130 | 23:00
Lalmonirhat | 125 | 18:30 | 115 | 19:30
Madanganj | 135 | 07:00 | 130 | 22:00
Madaripur | 136 | 06:00 | 130 | 21:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division