## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 14-06-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 13-06-2025 | during | 14-06-2025 | during | 14-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 120 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 120 | 120 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 358 | 347 | 400.75 | 400.75 | 400.75 | 400.75 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 142 | 143 | 335 | 335 | 150 | 150 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 16 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 48 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 54 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 12 | 13 | 33 | 33 | 20 | 20 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 7 | 14 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 16 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 16 | 65 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 70 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 50 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 144 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 33 | 0 | 33 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 24 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 450 | 530 | 584 | 584 | 540 | 540 | None
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 450 | 520 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 319 | 320 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 142 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2531 | 3125 | 5120.2 | 5111.2 | 3662.27 | 3661.27
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 8 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 30 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 172 | 172 | 165 | 165 | 165 | 165 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 144 | 146 | 141 | 145 | 141 | 145 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 105 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 46 | 48 | 72 | 48 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 66 | 65 | 65 | 65 | 65 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 42 | 42 | 38 | 40 | 38 | 40 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4 | 0 | 5.2 | 0 | 5.2 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 16 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 100 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 48 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 35 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 53 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1000 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 12 | 9 | 1 | 3 | 1 | 3 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 0 | 0 | 575 | 575 | 0 | 0 | U1 S/D 25/Mar/25 & U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1406 | 2200 | 3509.92 | 3517.72 | 2934.92 | 2942.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 202 | 180 | 221.43 | 221.43 | 205.43 | 205.43 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 225 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 335 | 340 | 340 | 340 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 14 | 13 | 46.7 | 46.7 | 17 | 17 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 45 | 39 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 155 | 182 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 105 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 34 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 50 | 163 | 163 | 80 | 80 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 136 | 200 | 200 | 200 | 185 | 185 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 38 | 46 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 16 | 19 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 105 | 90 | 114 | 114 | 90 | 90 | Machine Problem
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 13 | 47 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 76 | 92 | 115 | 115 | 70 | 70 | Machine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 57 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1339 | 1765.2 | 2471.18 | 2401.18 | 2149.98 | 2079.98
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 13-06-2025 | during | 14-06-2025 | during | 14-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 69 | 60 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 118 | 154 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 63 | 98 | 115 | 115 | 63 | 63 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 39.97 | 0 | 40 | 0 | 40 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 11 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 52 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 320.97 | 375 | 591.1 | 549 | 539.1 | 497
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 33 | 33 | 32 | 32 | 32 | 32 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 28 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Borescope Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 28 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 83 | 85 | 85 | 85 | 85 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 22 | 167 | 160 | 100 | 160 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 10 | 10 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 336 | 347 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1185 | 1334 | 1426 | 1366 | 1349 | 1289
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 734 | 715 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 275 | 164 | 410 | 410 | 360 | 360 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 44 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 99 | 0 | 99 | 0 | 99 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 837 | 1104 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1945 | 2027 | 3611.2 | 3512.2 | 3561 | 3462
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 9 | 10 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 127 | 125 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 870 | 1244 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 257 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.77 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1483.77 | 1960 | 2172 | 2171 | 2160 | 2159
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 163 | 145 | 214 | 214 | 150 | 150 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 180 | 163 | 220 | 220 | 140 | 140 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 180 | 158 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 364 | 370 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 | 30 | 30 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 82 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 111 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 100 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.2 | 0 | 5.1 | 0 | 5.1 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 754.33 | 762 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 41.01 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 97 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 1784.54 | 1921 | 3191.97 | 3025.87 | 2786.59 | 2620.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 50 | 50 | 50 | 50 | 50 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 190 | 190 | 200 | 200 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.7 | 0 | 4.6 | 0 | 4.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 182 | 0 | 82.43 | 0 | 82.43 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 530.7 | 468 | 629.03 | 512 | 629.03 | 512
System Total |  |  |  |  | 28565.2 | 27084.055 | 12525.98 | 15175.2 | 22722.6 | 22166.17 | 19771.89 | 19223.46
Forecast Scenario (14-06-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15080 |  | 0 |  | 15080
|  |  |  | 1:00 | 14850 |  | 0 |  | 14850
|  |  |  | 2:00 | 14550 |  | 0 |  | 14550
|  |  |  | 3:00 | 14270 |  | 0 |  | 14270
|  |  |  | 4:00 | 13850 |  | 0 |  | 13850
|  |  |  | 5:00 | 13680 |  | 0 |  | 13680
|  |  |  | 6:00 | 12970 |  | 0 |  | 12970
|  |  |  | 7:00 | 12640 |  | 0 |  | 12640
|  |  |  | 8:00 | 12440 |  | 0 |  | 12440
|  |  |  | 9:00 | 12150 |  | 0 |  | 12150
|  |  |  | 10:00 | 12200 |  | 0 |  | 12200
|  |  |  | 11:00 | 12220 |  | 0 |  | 12220
|  |  |  | 12:00 | 12520 |  | 0 |  | 12520
|  |  |  | 13:00 | 13320 |  | 0 |  | 13320
|  |  |  | 14:00 | 13050 |  | 0 |  | 13050
|  |  |  | 15:00 | 13270 |  | 0 |  | 13270
|  |  |  | 16:00 | 13190 |  | 0 |  | 13190
|  |  |  | 17:00 | 12800 |  | 0 |  | 12800
|  |  |  | 18:00 | 12160 |  | 0 |  | 12160
|  |  |  | 18:30 | 12650 |  | 0 |  | 12650
|  |  |  | 19:00 | 13330 |  | 0 |  | 13330
|  |  |  | 19:30 | 14600 |  | 0 |  | 14600
|  |  |  | 20:00 | 14750 |  | 0 |  | 14750
|  |  |  | 21:00 | 15290 |  | 0 |  | 15290
|  |  |  | 22:00 | 15350 |  | 0 |  | 15350
|  |  |  | 23:00 | 15400 |  | 0 |  | 15400
Probable Maximum Temperature: |  |  | 32.90°C
Probable Maximum Demand at Day Peak: |  |  | 12520.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15290.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15290.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 325.33 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 17:31 hrs on 15-06-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 13-06-2025 | [28 empty] | Date: | 13-06-2025 | [28 empty] | Date: | 13-06-2025 | [28 empty] | Date: | 13-06-2025 | [28 empty] | Date: | 13-06-2025 | [12 empty] | Date: | 13-06-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [12 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 24 | 120 | 0 | 120 | 0 | 0 | 386 | 0 | 321 | 35 | 0 | 34 | 16 | 0 | 0 | 35 | 90 | 67 | 400 | 139 | 550 | 0 | 35 | 0 | 0 | 0 | 0 | 125 | 13.7 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 1 | 66 | 0 | 0 | 76 | 100 | 0 | 172 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 149 | 0 | 0 | 0 | 1117 | 0 | 51 | 0 | 185 | 0 | 341 | 340 | 43 | 207 | 14 | 92 | 80 | 180 | 17 | 19 | 107 | 46 | 52.2 | 0 | 44 | 305 | 320 | 391 | 33 | 30 | 0 | 8 | 0 | 81 | 30 | 0 | 18 | 100 | 54 | 73 | 172 | 98 | 0 | 0 | 0 | 8391.9 | 780 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 759.12 | 0 | 0 | 0 | 113 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 180 | 0 | 180 | 0 | 414 | 0 | 0 | 190 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 283 | 10 | 128 | 220 | 0 | 0 | 1244 | 0 | 6563.32 | 14955.22 | 96.11
01:00 | 0 | 105 | 24 | 120 | 0 | 120 | 0 | 0 | 371 | 0 | 320 | 35 | 0 | 34 | 16 | 0 | 0 | 35 | 144 | 60 | 400 | 139 | 550 | 0 | 35 | 0 | 0 | 0 | 0 | 125 | 13 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 76 | 100 | 0 | 172 | 4 | 42 | 0 | 0 | 0 | 0 | 8 | 10 | 150 | 0 | 0 | 0 | 1068 | 0 | 51 | 0 | 185 | 0 | 349 | 340 | 47 | 190 | 15 | 93 | 80 | 180 | 8 | 19 | 107 | 42 | 52.2 | 0 | 44 | 310 | 320 | 359 | 33 | 30 | 0 | 8 | 0 | 82 | 30 | 0 | 18 | 100 | 54.3 | 45 | 94 | 98 | 0 | 0 | 0 | 8239.5 | 733 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 24 | 756.78 | 0 | 0 | 0 | 113 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 172 | 0 | 171 | 0 | 397 | 0 | 0 | 190 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 11 | 128 | 220 | 0 | 0 | 1170 | 0 | 6416.98 | 14656.48 | 96.12
02:00 | 0 | 105 | 24 | 120 | 0 | 120 | 0 | 0 | 353 | 0 | 320 | 35 | 0 | 43 | 16 | 0 | 0 | 35 | 144 | 50 | 400 | 138 | 550 | 0 | 35 | 0 | 0 | 0 | 0 | 125 | 13 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 76 | 100 | 0 | 172 | 31 | 42 | 0 | 0 | 0 | 0 | 8 | 34 | 150 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 185 | 0 | 104 | 340 | 48 | 196 | 15 | 92 | 80 | 180 | 9 | 19 | 107 | 42 | 52.2 | 0 | 44 | 310 | 320 | 382 | 33 | 30 | 0 | 8 | 0 | 82 | 30 | 0 | 18 | 100 | 54.5 | 45 | 94 | 98 | 0 | 0 | 2 | 8089.7 | 733 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 51 | 753.95 | 0 | 0 | 0 | 113 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 164 | 0 | 163 | 0 | 407 | 0 | 0 | 190 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 11 | 128 | 220 | 0 | 0 | 1050 | 0 | 6306.15 | 14395.85 | 96.12
03:00 | 0 | 105 | 24 | 120 | 0 | 120 | 0 | 0 | 359 | 0 | 320 | 35 | 0 | 58 | 16 | 0 | 0 | 35 | 144 | 41 | 400 | 143 | 550 | 0 | 35 | 0 | 0 | 0 | 0 | 108 | 13 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 76 | 100 | 0 | 172 | 34 | 42 | 0 | 0 | 0 | 0 | 8 | 34 | 149 | 0 | 0 | 0 | 1080 | 0 | 51 | 0 | 185 | 0 | 0 | 340 | 48 | 193 | 15 | 92 | 80 | 180 | 9 | 19 | 107 | 42 | 52.2 | 0 | 44 | 320 | 320 | 362 | 33 | 30 | 0 | 8 | 0 | 82 | 30 | 0 | 18 | 100 | 54.5 | 45 | 94 | 98 | 0 | 0 | 11 | 7963.7 | 779 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 53 | 758.66 | 0 | 0 | 0 | 113 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 166 | 0 | 166 | 0 | 343 | 0 | 0 | 190 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 10 | 128 | 220 | 0 | 0 | 980 | 0 | 6189.86 | 14153.56 | 96.13
04:00 | 0 | 51 | 8 | 120 | 0 | 120 | 0 | 0 | 341 | 0 | 320 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 20 | 400 | 141 | 550 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 13 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 76 | 72 | 0 | 172 | 17 | 42 | 0 | 0 | 0 | 0 | 8 | 17 | 150 | 0 | 0 | 0 | 1081 | 0 | 51 | 0 | 185 | 0 | 0 | 340 | 48 | 191 | 15 | 93 | 80 | 155 | 9 | 19 | 107 | 42 | 52.2 | 0 | 44 | 305 | 320 | 362 | 33 | 30 | 0 | 8 | 0 | 82 | 25 | 0 | 18 | 100 | 40 | 45 | 94 | 101 | 0 | 0 | 12 | 7447.2 | 875 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1219 | 17 | 754.33 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 160 | 0 | 159 | 0 | 339 | 0 | 0 | 190 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 9 | 128 | 220 | 0 | 0 | 1110 | 0 | 6294.33 | 13741.53 | 96.13
05:00 | 0 | 51 | 8 | 120 | 0 | 120 | 0 | 0 | 358 | 0 | 322 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 16 | 400 | 139 | 550 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 13 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 76 | 72 | 0 | 172 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 150 | 0 | 0 | 0 | 974 | 0 | 51 | 0 | 185 | 0 | 0 | 340 | 48 | 192 | 15 | 92 | 80 | 155 | 9 | 19 | 107 | 42 | 52.2 | 0 | 44 | 315 | 320 | 365 | 33 | 30 | 0 | 8 | 0 | 82 | 25 | 0 | 18 | 100 | 35 | 46 | 94 | 103 | 0 | 0 | 12 | 7330.2 | 875 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1086 | 0 | 758.13 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 167 | 0 | 167 | 0 | 341 | 0 | 0 | 190 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 11 | 128 | 220 | 0 | 0 | 1200 | 0 | 6264.13 | 13594.33 | 96.14
06:00 | 0 | 17 | 8 | 120 | 0 | 120 | 0 | 0 | 333 | 0 | 321 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 16 | 400 | 140 | 550 | 0 | 0 | 0 | 0 | 0 | 1 | 108 | 13 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 76 | 36 | 0 | 172 | 0 | 42 | 0 | 0 | 0 | 0 | 8 | 0 | 150 | 0 | 0 | 0 | 852 | 1 | 51 | 0 | 185 | 0 | 0 | 340 | 48 | 188 | 15 | 92 | 80 | 155 | 8 | 19 | 107 | 40 | 52.2 | 2 | 44 | 300 | 320 | 350 | 33 | 30 | 0 | 8 | 0 | 82 | 30 | 0 | 18 | 100 | 27 | 46 | 94 | 103 | 0 | 1.61 | 12 | 7033.81 | 875 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 994 | 0 | 733.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 2.97 | 139 | 0 | 153 | 0 | 153 | 0 | 331 | 0 | 0.29 | 190 | 48 | 115 | 2 | 113 | 0 | 0 | 0.5 | 12 | 0.03 | 0 | 274 | 10 | 128 | 220 | 0 | 0 | 1140 | 0 | 5945.55 | 12979.36 | 96.14
07:00 | 0 | 0 | 8 | 120 | 0 | 120 | 0 | 0 | 340 | 0 | 320 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 400 | 139 | 550 | 0 | 0 | 0 | 0 | 0 | 6 | 108 | 13 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 1 | 172 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 856 | 2 | 51 | 0 | 185 | 0 | 0 | 335 | 47 | 193 | 15 | 92 | 80 | 155 | 9 | 19 | 105 | 36 | 52.2 | 7 | 15 | 305 | 320 | 364 | 33 | 30 | 0 | 8 | 0 | 81 | 30 | 0 | 18 | 100 | 17 | 65 | 119 | 102 | 1 | 13.38 | 12 | 6955.58 | 874 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 917 | 0 | 666.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11.48 | 146 | 0 | 159 | 0 | 159 | 0 | 342 | 0 | 1 | 190 | 48 | 115 | 6 | 113 | 0 | 0 | 2 | 51 | 0.19 | 0 | 220 | 10 | 128 | 220 | 0 | 0 | 960 | 0 | 5685.55 | 12641.13 | 96.15
08:00 | 0 | 0 | 0 | 120 | 0 | 120 | 0 | 0 | 339 | 0 | 320 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 400 | 139 | 550 | 0 | 0 | 0 | 0 | 0 | 17 | 70 | 13 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 2 | 172 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 806 | 7 | 51 | 0 | 175 | 0 | 0 | 335 | 47 | 187 | 15 | 92 | 80 | 136 | 9 | 19 | 105 | 38 | 52.2 | 18 | 0 | 305 | 320 | 357 | 33 | 30 | 0 | 8 | 0 | 81 | 30 | 0 | 18 | 100 | 17 | 65 | 120 | 99 | 1 | 18.09 | 6 | 6803.29 | 735 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 915 | 0 | 675.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22.79 | 150 | 0 | 162 | 0 | 166 | 0 | 332 | 0 | 2.14 | 190 | 48 | 115 | 14 | 113 | 0 | 0 | 3.4 | 100 | 0.21 | 0 | 215 | 10 | 127 | 220 | 0 | 0 | 938 | 0 | 5643.7 | 12446.99 | 96.15
09:00 | 0 | 2 | 0 | 120 | 0 | 120 | 0 | 0 | 338 | 0 | 320 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 139 | 500 | 0 | 0 | 0 | 0 | 0 | 23 | 70 | 13 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 172 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 790 | 10 | 51 | 0 | 175 | 0 | 0 | 335 | 47 | 190 | 14 | 93 | 80 | 136 | 9 | 19 | 105 | 38 | 16 | 36 | 0 | 300 | 320 | 311 | 33 | 30 | 0 | 8 | 0 | 81 | 30 | 0 | 18 | 100 | 17 | 64 | 120 | 64 | 2 | 34.34 | 11 | 6610.34 | 735 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 915 | 0 | 671.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 18.7 | 151 | 0 | 181 | 0 | 181 | 0 | 337 | 0 | 3.33 | 190 | 48 | 50 | 21 | 60 | 0 | 0 | 5.1 | 121 | 0.31 | 0 | 217 | 9 | 128 | 220 | 0 | 0 | 850 | 0 | 5547.9 | 12158.24 | 96.16
10:00 | 0 | 17 | 0 | 120 | 0 | 120 | 0 | 0 | 352 | 0 | 322 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 138 | 450 | 0 | 0 | 0 | 0 | 0 | 29 | 70 | 13 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 172 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 760 | 12 | 51 | 0 | 165 | 0 | 0 | 335 | 46 | 189 | 14 | 93 | 80 | 136 | 9 | 19 | 105 | 38 | 16 | 67 | 0 | 315 | 320 | 307 | 33 | 30 | 0 | 8 | 0 | 81 | 30 | 0 | 18 | 23 | 17 | 63 | 119 | 68 | 2 | 47.06 | 12 | 6502.06 | 735 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 856 | 0 | 667.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 35.29 | 162 | 0 | 182 | 0 | 184 | 0 | 335 | 0 | 4.48 | 190 | 48 | 50 | 30 | 49 | 0 | 0 | 6.4 | 140 | 0.7 | 0 | 214 | 9 | 128 | 220 | 0 | 0 | 824 | 0 | 5567.95 | 12070.01 | 96.16
11:00 | 0 | 17 | 0 | 120 | 0 | 120 | 0 | 0 | 352 | 0 | 320 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 141 | 450 | 0 | 0 | 0 | 0 | 0 | 32 | 70 | 12 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 24 | 0 | 4 | 172 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 896 | 8 | 51 | 0 | 155 | 0 | 0 | 335 | 45 | 195 | 14 | 78 | 80 | 136 | 9 | 16 | 105 | 38 | 16 | 61 | 0 | 310 | 320 | 329 | 33 | 30 | 0 | 8 | 0 | 80 | 30 | 0 | 18 | 22 | 17 | 63 | 118 | 69 | 2 | 49.22 | 12 | 6650.22 | 735 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 833 | 0 | 677.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 49.6 | 163 | 0 | 189 | 0 | 187 | 0 | 346 | 0 | 5.01 | 190 | 48 | 35 | 32 | 34 | 0 | 0 | 4.9 | 140 | 0.5 | 0 | 219 | 9 | 128 | 220 | 0 | 0 | 840 | 0 | 5578.16 | 12228.38 | 96.17
12:00 | 0 | 17 | 0 | 120 | 0 | 120 | 0 | 0 | 358 | 0 | 319 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 142 | 450 | 0 | 0 | 0 | 0 | 0 | 33 | 70 | 12 | 7 | 0 | 450 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 24 | 0 | 4 | 172 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 1000 | 8 | 51 | 0 | 155 | 0 | 0 | 335 | 45 | 202 | 14 | 76 | 80 | 136 | 13 | 16 | 105 | 38 | 16 | 57 | 0 | 310 | 320 | 336 | 33 | 30 | 0 | 8 | 0 | 80 | 28 | 0 | 18 | 22 | 17 | 63 | 118 | 69 | 2 | 39.97 | 12 | 6781.97 | 734 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 837 | 0 | 754.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 41.01 | 163 | 0 | 180 | 0 | 180 | 0 | 364 | 0 | 5.2 | 190 | 48 | 35 | 34 | 34 | 0 | 0 | 7.7 | 182 | 0.77 | 0 | 257 | 9 | 127 | 220 | 0 | 0 | 870 | 0 | 5744.01 | 12525.98 | 96.17
13:00 | 0 | 17 | 0 | 120 | 0 | 120 | 0 | 0 | 368 | 0 | 320 | 17 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 140 | 500 | 0 | 0 | 0 | 0 | 0 | 32 | 90 | 12 | 7 | 0 | 500 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 24 | 0 | 1 | 172 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 1040 | 0 | 51 | 0 | 164 | 0 | 0 | 340 | 45 | 194 | 14 | 73 | 80 | 148 | 29 | 19 | 105 | 40 | 16 | 66 | 31 | 315 | 320 | 350 | 34 | 30 | 0 | 8 | 0 | 78 | 25 | 0 | 18 | 55 | 17 | 66 | 117 | 65 | 2 | 51.06 | 11 | 7067.06 | 735 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 1072 | 0 | 754.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 53.91 | 162 | 0 | 178 | 0 | 179 | 0 | 395 | 0 | 5.02 | 188 | 48 | 35 | 31 | 34 | 0 | 0 | 7.5 | 195 | 0.29 | 0 | 307 | 10 | 125 | 220 | 0 | 0 | 1050 | 0 | 6256.76 | 13323.82 | 96.18
14:00 | 0 | 17 | 0 | 120 | 0 | 120 | 0 | 0 | 342 | 0 | 319 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 132 | 500 | 0 | 0 | 0 | 0 | 0 | 28 | 90 | 12 | 7 | 0 | 500 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 5 | 172 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 1060 | 17 | 51 | 0 | 155 | 0 | 0 | 335 | 45 | 207 | 14 | 72 | 70 | 170 | 28 | 19 | 104 | 40 | 16 | 61 | 43 | 310 | 320 | 350 | 34 | 30 | 0 | 8 | 0 | 78 | 28 | 0 | 18 | 58 | 0 | 65 | 117 | 64 | 1 | 44.83 | 11 | 7006.83 | 734 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 1000 | 0 | 768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 29.41 | 160 | 0 | 176 | 0 | 179 | 0 | 399 | 0 | 4.56 | 164 | 48 | 35 | 29 | 34 | 0 | 0 | 5.8 | 175 | 0.59 | 0 | 208 | 10 | 125 | 220 | 0 | 0 | 1100 | 0 | 6044.36 | 13051.19 | 96.18
15:00 | 0 | 17 | 4 | 120 | 0 | 120 | 0 | 0 | 380 | 0 | 319 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 137 | 550 | 0 | 0 | 0 | 0 | 0 | 23 | 90 | 13 | 7 | 0 | 500 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 24 | 0 | 4 | 172 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 1154 | 17 | 51 | 0 | 172 | 0 | 0 | 335 | 43 | 205 | 14 | 84 | 50 | 170 | 26 | 19 | 104 | 42 | 17 | 50 | 43 | 315 | 320 | 380 | 34 | 30 | 0 | 8 | 0 | 78 | 28 | 0 | 16 | 57 | 0 | 65 | 108 | 64 | 1 | 22.42 | 11 | 7234.42 | 734 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 1045 | 0 | 766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 29.59 | 160 | 0 | 176 | 0 | 177 | 0 | 398 | 0 | 3.62 | 162 | 48 | 50 | 24 | 45 | 0 | 0 | 5.3 | 141 | 0.18 | 0 | 247 | 10 | 125 | 220 | 0 | 0 | 1100 | 0 | 6042.69 | 13277.11 | 98.19
16:00 | 0 | 17 | 8 | 120 | 0 | 120 | 0 | 0 | 376 | 0 | 320 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 17 | 6 | 400 | 141 | 550 | 0 | 0 | 0 | 0 | 0 | 16 | 90 | 13 | 7 | 0 | 500 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 24 | 0 | 3 | 172 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 1088 | 4 | 51 | 0 | 172 | 0 | 0 | 335 | 44 | 196 | 14 | 93 | 50 | 170 | 27 | 19 | 104 | 40 | 25 | 33 | 29 | 320 | 320 | 345 | 34 | 30 | 0 | 8 | 0 | 79 | 28 | 0 | 16 | 74 | 16 | 69 | 117 | 60 | 1 | 24.25 | 11 | 7150.25 | 734 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 1100 | 0 | 763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 26.61 | 157 | 0 | 177 | 0 | 173 | 0 | 414 | 0 | 2.53 | 200 | 48 | 50 | 16 | 48 | 0 | 0 | 3.8 | 98 | 0.43 | 0 | 251 | 10 | 124 | 220 | 0 | 0 | 1100 | 0 | 6046.37 | 13196.62 | 96.19
17:00 | 0 | 17 | 8 | 120 | 0 | 0 | 0 | 0 | 350 | 0 | 320 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 17 | 16 | 400 | 141 | 550 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 13 | 7 | 0 | 500 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 24 | 0 | 2 | 172 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 1100 | 4 | 51 | 0 | 172 | 0 | 0 | 335 | 43 | 202 | 13 | 93 | 50 | 170 | 29 | 19 | 88 | 38 | 25 | 15 | 29 | 305 | 320 | 360 | 34 | 30 | 0 | 8 | 0 | 79 | 28 | 0 | 16 | 91 | 17 | 65 | 126 | 60 | 1 | 11.58 | 11 | 6995.58 | 734 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 1064 | 0 | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 13.86 | 150 | 0 | 176 | 0 | 179 | 0 | 414 | 0 | 2.53 | 200 | 48 | 50 | 8 | 48 | 0 | 0 | 1.3 | 53 | 0.21 | 0 | 252 | 8 | 124 | 220 | 0 | 0 | 1050 | 0 | 5807.9 | 12803.48 | 96.2
18:00 | 0 | 17 | 8 | 120 | 0 | 0 | 0 | 0 | 347 | 0 | 320 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 17 | 16 | 320 | 140 | 500 | 0 | 0 | 0 | 0 | 0 | 2 | 70 | 13 | 7 | 0 | 500 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 24 | 0 | 1 | 172 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 1013 | 1 | 51 | 1 | 127 | 0 | 100 | 300 | 43 | 193 | 12 | 92 | 50 | 136 | 42 | 19 | 88 | 34 | 25 | 3 | 29 | 305 | 320 | 340 | 34 | 30 | 0 | 8 | 0 | 80 | 28 | 0 | 16 | 91 | 17 | 74 | 117 | 60 | 0 | 2.82 | 11 | 6705.82 | 716 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 980 | 0 | 762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 3.04 | 143 | 0 | 140 | 0 | 140 | 0 | 350 | 0 | 0.27 | 200 | 48 | 50 | 2 | 48 | 0 | 0 | 0.1 | 16 | 0.05 | 0 | 249 | 7 | 125 | 220 | 0 | 0 | 1050 | 0 | 5457.46 | 12163.28 | 96.2
19:00 | 0 | 34 | 8 | 120 | 0 | 0 | 0 | 0 | 387 | 0 | 320 | 12 | 8 | 34 | 16 | 15 | 0 | 4 | 30 | 24 | 420 | 139 | 520 | 0 | 17 | 0 | 0 | 0 | 0 | 90 | 13 | 7 | 0 | 540 | 6 | 16 | 0 | 0 | 12 | 66 | 30 | 0 | 48 | 12 | 0 | 172 | 10 | 33 | 0 | 0 | 0 | 1 | 0 | 11 | 143 | 0 | 0 | 0 | 1135 | 0 | 51 | 20 | 162 | 0 | 35 | 335 | 42 | 202 | 13 | 93 | 50 | 143 | 46 | 19 | 97 | 44 | 25 | 0 | 33 | 300 | 320 | 378 | 33 | 30 | 0 | 8 | 0 | 81 | 30 | 0 | 16 | 125 | 17 | 82 | 154 | 60 | 0 | 0 | 11 | 7508 | 668 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1054 | 17 | 758 | 0 | 0 | 0 | 3 | 0 | 41 | 0 | 0 | 0 | 0 | 30 | 0 | 142 | 0 | 171 | 0 | 168 | 0 | 414 | 0 | 0 | 200 | 48 | 110 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 10 | 125 | 220 | 0 | 0 | 1060 | 12 | 5830 | 13338 | 96.21
19:30 | 0 | 70 | 8 | 120 | 0 | 0 | 0 | 0 | 368 | 0 | 320 | 35 | 40 | 34 | 22 | 15 | 0 | 17 | 120 | 49 | 420 | 141 | 550 | 0 | 35 | 0 | 0 | 0 | 0 | 125 | 13 | 7 | 0 | 540 | 17 | 16 | 0 | 0 | 18 | 66 | 40 | 0 | 100 | 32 | 0 | 172 | 51 | 33 | 0 | 5 | 0 | 10 | 0 | 60 | 143 | 0 | 0 | 0 | 1190 | 0 | 51 | 61 | 162 | 0 | 40 | 340 | 42 | 202 | 13 | 93 | 50 | 200 | 47 | 19 | 104 | 42 | 52.2 | 0 | 33 | 310 | 320 | 377 | 33 | 30 | 0 | 8 | 0 | 81 | 30 | 0 | 16 | 163 | 35 | 86 | 154 | 60 | 0 | 0 | 6 | 8262.2 | 669 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 20 | 758 | 0 | 0 | 0 | 104 | 0 | 41 | 35 | 0 | 0 | 0 | 30 | 0 | 137 | 0 | 171 | 0 | 167 | 0 | 414 | 0 | 0 | 200 | 48 | 115 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 125 | 220 | 0 | 0 | 1180 | 54 | 6261 | 14523.2
20:00 | 0 | 70 | 16 | 120 | 0 | 0 | 0 | 0 | 361 | 0 | 320 | 35 | 38 | 34 | 48 | 15 | 0 | 30 | 144 | 50 | 420 | 140 | 550 | 0 | 35 | 0 | 0 | 0 | 0 | 142 | 13 | 14 | 0 | 540 | 18 | 16 | 0 | 0 | 5 | 66 | 46 | 0 | 100 | 48 | 0 | 172 | 53 | 42 | 0 | 17 | 0 | 17 | 1 | 62 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 56 | 172 | 0 | 120 | 340 | 37 | 184 | 13 | 93 | 50 | 189 | 47 | 19 | 90 | 44 | 52.2 | 0 | 33 | 305 | 320 | 337 | 33 | 30 | 0 | 8 | 0 | 82 | 30 | 0 | 16 | 163 | 36 | 98 | 153 | 60 | 0 | 0 | 6 | 8436.2 | 668 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1115 | 22 | 751 | 0 | 0 | 0 | 86 | 0 | 41 | 50 | 0 | 0 | 0 | 30 | 0 | 141 | 0 | 169 | 0 | 166 | 0 | 414 | 0 | 0 | 200 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 125 | 220 | 0 | 0 | 1205 | 54 | 6229 | 14665.2 | 96.21
21:00 | 0 | 70 | 16 | 120 | 0 | 0 | 0 | 0 | 347 | 0 | 320 | 35 | 24 | 65 | 48 | 15 | 0 | 54 | 144 | 50 | 420 | 143 | 520 | 0 | 35 | 0 | 0 | 0 | 0 | 142 | 13 | 14 | 0 | 530 | 35 | 16 | 0 | 0 | 9 | 66 | 46 | 0 | 100 | 48 | 0 | 172 | 100 | 42 | 0 | 53 | 0 | 30 | 8 | 105 | 146 | 0 | 0 | 0 | 1224 | 0 | 51 | 105 | 182 | 0 | 225 | 340 | 39 | 180 | 13 | 92 | 50 | 200 | 47 | 19 | 90 | 46 | 52.2 | 0 | 34 | 300 | 320 | 347 | 33 | 28 | 0 | 8 | 0 | 83 | 30 | 0 | 18 | 167 | 52 | 98 | 154 | 60 | 0 | 0 | 11 | 8799.2 | 715 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1104 | 44 | 762 | 0 | 0 | 0 | 111 | 0 | 82 | 100 | 0 | 0 | 0 | 30 | 0 | 145 | 0 | 163 | 0 | 158 | 0 | 370 | 0 | 0 | 190 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 125 | 220 | 0 | 0 | 1244 | 54 | 6376 | 15175.2 | 96.22
22:00 | 0 | 70 | 16 | 120 | 0 | 0 | 0 | 0 | 352 | 0 | 320 | 35 | 28 | 68 | 48 | 15 | 0 | 55 | 144 | 50 | 450 | 138 | 520 | 0 | 35 | 0 | 0 | 0 | 0 | 142 | 13 | 14 | 0 | 500 | 35 | 16 | 0 | 0 | 4 | 66 | 46 | 0 | 100 | 48 | 0 | 172 | 106 | 42 | 0 | 53 | 0 | 30 | 8 | 105 | 146 | 0 | 0 | 0 | 1224 | 0 | 51 | 122 | 184 | 0 | 217 | 340 | 40 | 201 | 13 | 92 | 40 | 200 | 47 | 19 | 90 | 44 | 52.2 | 0 | 35 | 310 | 320 | 386 | 33 | 30 | 0 | 8 | 0 | 82 | 30 | 0 | 18 | 167 | 51 | 98 | 154 | 57 | 0 | 0 | 12 | 8877.2 | 716 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1088 | 80 | 760 | 0 | 0 | 0 | 113 | 0 | 87 | 113 | 0 | 0 | 0 | 30 | 0 | 145 | 0 | 159 | 0 | 147 | 0 | 370 | 0 | 0 | 190 | 48 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 11 | 100 | 220 | 0 | 70 | 1244 | 54 | 6407 | 15284.2 | 96.22
23:00 | 0 | 97 | 24 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 320 | 35 | 28 | 70 | 54 | 22 | 0 | 35 | 144 | 50 | 450 | 141 | 520 | 0 | 35 | 0 | 0 | 0 | 0 | 160 | 13 | 14 | 0 | 500 | 35 | 16 | 0 | 0 | 1 | 65 | 46 | 0 | 88 | 48 | 0 | 172 | 106 | 42 | 0 | 80 | 0 | 32 | 8 | 105 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 122 | 185 | 0 | 216 | 340 | 42 | 209 | 13 | 93 | 35 | 200 | 47 | 19 | 104 | 44 | 52.2 | 0 | 35 | 310 | 320 | 384 | 33 | 30 | 0 | 8 | 0 | 83 | 30 | 0 | 18 | 167 | 53 | 90 | 164 | 28 | 0 | 0 | 11 | 8844.2 | 656 | 131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1142 | 87 | 768 | 0 | 0 | 0 | 113 | 0 | 87 | 113 | 0 | 0 | 0 | 30 | 0 | 140 | 0 | 158 | 0 | 141 | 0 | 414 | 0 | 0 | 190 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 283 | 11 | 127 | 220 | 0 | 71 | 1244 | 81 | 6483 | 15327.2 | 96.23
Total KWH | 1638 | 1058880 | 232320 | 2708000 | 0 | 1971875 | 0 | 0 | 8668800 | 0 | 7911370 | 342360 | 159840 | 861840 | 291840 | 118178 | 12435 | 344893 | 1278720 | 562560 | 9621500 | 3354153 | 12583086 | 0 | 312581 | 0 | 0 | 0 | 247432 | 2462400 | 318600 | 281520 | 0 | 12234545.45 | 169364 | 100364 | 0 | 0 | 116640 | 716959 | 231072 | 0 | 1233600 | 751680 | 32906 | 4120620 | 608033 | 965760 | 0 | 232509 | 0 | 144960 | 89096.4 | 625599 | 3471665 | 0 | 0 | 0 | 24861816 | 99900 | 1142616 | 552000 | 4131636 | 0 | 1784000 | 8156000 | 1068480 | 4774000 | 342288 | 2145600 | 1572800 | 4028160 | 572040 | 435930 | 2452140 | 965760 | 894485 | 473382 | 683936 | 7508500 | 7685600 | 8939000 | 789000 | 659880 | 0 | 173952 | 0 | 1924800 | 688992 | 0 | 348000 | 2784610 | 714240 | 1594800 | 2916000 | 1709760 | 13050 | 342750 | 239520 | 181721616.85 | 18251636 | 6070464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 788400 | 25120000 | 500160 | 17371636 | 0 | 0 | 0 | 1180608 | 0 | 351136 | 663936 | 0 | 53 | 836490 | 149927 | 345000 | 3652818 | 0 | 4232118 | 0 | 4220300 | 0 | 8885527 | 0 | 37920 | 4631000 | 1134109 | 2061047 | 231165 | 2021961 | 0 | 0 | 50718 | 1448640 | 4461 | 0 | 6262000 | 239775 | 2986000 | 5359480 | 0 | 152727 | 26420363.64 | 322800 | 145984375.64 | 327705992.49

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 13-06-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12525.98 | MW | 12:00 Hr. | Energy Generated |  |  | 327.706 |  | MKWHr.
| Day Peak Demand |  |  | 12525.98 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.221 |  | MKWHr.
| Evening Peak Generation |  |  | 15175.2 | MW | 21:00 Hr. | Energy Demand |  |  | 328.927 |  | MKWHr.
| Evening Peak Demand |  |  | 15290.2 | MW | 21:00 Hr. | Maximum Temperature |  |  | 36 |  | °C
| Minimum Generation of the Day |  |  | 12070.01 | MW | 10:00 Hr. | Total Gas Supplied |  |  | 1126.22 |  | MMCFD
| Maximum Generation of the Day |  |  | 15327.2 | MW | 23:00 Hr. | Production Cost per KWHr |  |  | 6.3731 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 59.6534 | 0 | 8.0405 | 0 | 0 | 0.24743 | 0 | 0 | 67.9414 | Gas | 156.3572 | Gas | 531857147.0865
| Chattogram Zone |  |  | 4.4374 | 24.8618 | 4.9032 | 0 | 4.1206 | 0.13281 | 0 | 0.11664 | 38.5725 | Coal | 88.582 | Coal | 612550669.7088
| Cumilla Zone |  |  | 23.4078 | 0 | 11.3284 | 0 | 0 | 0.47338 | 0.96576 | 0 | 36.1753 | HFO | 36.9883 | HFO | 683284858.388
| Mymensingh Zone |  |  | 1.7098 | 0 | 5.4646 | 0 | 0 | 0.3558 | 0 | 0 | 7.5301 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 31.5023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.5023 | Hydro | 4.1206 | Hydro | 412062
| Khulna Zone |  |  | 6.0705 | 25.12 | 0.50016 | 0 | 0 | 0.7884 | 18.2516 | 0 | 50.7307 | Solar | 4.9522 | Solar | 81086126.59
| Barishal Zone |  |  | 8.5853 | 32.8351 | 0.3228 | 0 | 0 | 0.004461 | 0 | 0 | 41.7476 | Import | 36.589 | Import | 177604878.56
| Rajshahi Zone |  |  | 20.9908 | 0 | 2.3457 | 0 | 0 | 1.2194 | 17.3716 | 0 | 41.9275 | Wind | 0.11664 | Wind | 1707609.6
| Rangpur Zone |  |  | 0 | 5.7651 | 4.083 | 0 | 0 | 1.7305 | 0 | 0 | 11.5786
| Total |  |  | 156.3572 | 88.582 | 36.9883 | 0 | 4.1206 | 4.9522 | 36.589 | 0.11664 | 327.706
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 531857147.0865 |  | Hydro | 412062
|  |  |  | Coal | 612550669.7088 |  | Solar | 81086126.59
|  |  |  | HFO | 683284858.388 |  | Import | 177604878.56
|  |  |  | HSD | 0 |  | Wind | 1707609.6
[5 empty] | Total: | 208,85,03,351 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 909909.1 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 18.2516 | Peak Hr Flow | 715.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 24948800.02 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 17.3716 | Peak Hr Flow | 762.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 320 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.96576 | Peak Hr Flow | 46.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 456 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 36.589 | Peak Hr Flow | 1523.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4338
|  |  |  | Chattogram |  | 0 |  | 1320
|  |  |  | Cumilla |  | 15 |  | 1554
|  |  |  | Mymensingh |  | 10 |  | 1356
|  |  |  | Sylhet |  | 15 |  | 689
|  |  |  | Khulna |  | 15 |  | 1943
|  |  |  | Barishal |  | 0 |  | 505
|  |  |  | Rajshahi |  | 0 |  | 1709
|  |  |  | Rangpur |  | 55 |  | 1110
|  |  |  | Total |  | 110 |  | 14524
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[5 empty] | Total | 300 |  |  |  | Total | 400
|  |  |  | Total Unavailable Capacity |  |  |  | 700
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:20 | 09:50 | Aminbazar-Mirpur 132kV Ckt-2 Scheduled S/D from Mirpur 132/33kV end.
| 08:37 | 12:04 | Noapara 132/33kV S/S T-2 HT Scheduled S/D Due to Repair of B-phase conductor of REB-1
feeder.
| 08:37 | 12:04 | Noapara 132/33kV S/S T-2 LT Scheduled S/D Due to Repair of B-phase conductor of REB-1
feeder.
| 09:00 | 11:45 | Chowmuhani 132/33kV S/S TR2-425T HT Forced S/D Due to 33kv Incoming DS to BUSBAR R Phase | [7 empty] | 30.0MW load
|  |  | (red hot) Loop Maintenance. | [7 empty] | interrup.
| 09:01 | 11:45 | Chowmuhani 132/33kV S/S TR2-425T LT Forced S/D Due to 33kv Incoming DS to BUSBAR R Phase | [7 empty] | 30.0MW load
|  |  | (red hot) Loop Maintenance. | [7 empty] | interrup.
| 09:53 | 10:30 | Sholosohor 132/33kV S/S Sholoshahar-Madunaghat Ckt-1 Scheduled S/D Due to Energy Meter
Replacement.
| 10:31 | 10:56 | Sholosohor 132/33kV S/S Sholoshahar-Madunaghat Ckt-1 Scheduled S/D Due to Energy Meter
Replacement.Sholoshahar-Madunaghat Ckt-02.
| 11:00 | 11:30 | Sholosohor 132/33kV S/S Sholoshahar-Khulshi Ckt-1 Scheduled S/D Due to Energy Meter
Replacement.
| 11:41 | 12:23 | Sholosohor 132/33kV S/S Sholoshahar-Khulshi Ckt-2 Scheduled S/D Due to Energy Meter
Replacement.
| 12:00 |  | Day Peak Gen. 12525 MW
| 12:54 | 13:58 | Sholosohor 132/33kV S/S TRAFO-02 HT Scheduled S/D Due to Energy Meter replacement.
| 13:08 | 14:22 | Khulshi 132/33kV S/S 405T (T1) HT Tripped showing Trip Relay MVAJM25 (K33) relays Due to
Tripped due to PRD 1&2.
| 13:08 |  | Khulshi 132/33 kV T-1 transformer tripped, showing PRD relay. Currently, no interruption
is occurring due to this tripping.
| 14:04 | 15:57 | Sholosohor 132/33kV S/S TRAFO-01 HT Scheduled S/D Due to Energy Meter replacement.
| 14:33 | 14:41 | Bashundhara-Rampura 132 kV Ckt-2 Tripped from Rampura 230/132kV end showing 21/1 relays | [7 empty] | 89.0MW load
|  |  | Due to Distance Z1 | [7 empty] | interrup. Rampura
230/132kV end
| 15:28 | 17:27 | BIPTC S/S 10CF21 Forced S/D Due to 10CF21 is tripped by impedance 21R
| 16:29 |  | Ghorasal Repowered CCPP Unit-4 Shutdown
|  | 17:14 | KSRM 132/33kV S/S Transformer-01 HT is restored.
| 19:05 |  | BIPTC S/S 10CF15 Tripped showing 87.1 (Differential relay) relays Due to C1 Unbalance
60/61 CPR04
| 19:27 | 20:04 | Aminbazar-Kaliakoir 230kV Ckt-2 Tripped from Aminbazar 400/230/132kV end showing Main-2
General trip Dist R,S,T trip relays Due to Main 2 Distance R,T trip A/R block
| 19:35 |  | Raozan 25 MW PP Synchronized
| 20:20 | 20:41 | Aminbazar-Kaliakoir 230kV Ckt-2 Tripped from Aminbazar 400/230/132kV end showing Main-2
General trip Dist R,S,T trip relays Due to Main -2 Distance R,T trip
| 00:37 | 02:04 | Ashuganj-Kishoreganj 132kV Ckt-1 Scheduled S/D from Bajitpur 132/33kV end.
|  | 00:55 | Fenchuganj-Sreemangal 132kV Ckt-1 is restored.
|  | 00:55 | Fenchuganj-Sreemangal 132kV Ckt-2 is restored.
| 05:22 |  | Raozan 25 MW PP Shutdown
| 06:30 |  | Borhanuddin 230/33kV S/S Tr-Load HT Scheduled S/D Due to Redhot Maintenance Work. | [7 empty] | 90.0MW load
interrup.
| 06:31 |  | Borhanuddin 230/33kV S/S Tr-Load LT Scheduled S/D Due to Redhot Maintenance Work. | [7 empty] | 90.0MW load
interrup.
| 07:00 |  | Minimum Generation is 12927 MW
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 13-06-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 1971875 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 120 | 2708000 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 347 | 8668800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9621500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 143 | 3354153 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 12435 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 1638 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 342360 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 48 | 291840 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 54 | 344893 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 312581 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 13 | 318600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 281520 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 232320 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 15 | 118178 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 65 | 861840 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1058880 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 50 | 562560 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1278720 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 247432 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 24 | 159840 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 530 | 12234545.45 | None
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 520 | 12583086 | Allocation limit by Titas, instructed by DS(Gen)
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 320 | 7911370 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 142 | 2462400 | -
Dhaka Area Total |  |  |  |  | 5939.724 | 3125 | 67941366.45
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 89096.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 99900 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 30 | 144960 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 172 | 4120620 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 146 | 3471665 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 625599 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 46 | 231072 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 716959 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1233600 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 42 | 965760 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 32906 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 100364 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 100 | 608033 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 48 | 751680 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 169364 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 53 | 232509 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 24861816 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 9 | 116640 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 0 | 0 | U1 S/D 25/Mar/25 & U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4895.72 | 2200 | 38572543.4
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 180 | 4774000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 225 | 1784000 | ST Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 8156000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 13 | 342288 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 39 | 1068480 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 182 | 4131636 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1142616 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 105 | 552000 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 34 | 683936 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1572800 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 4028160 | -
| Import (Tripura) |  | Import | 0 | 160 | 46 | 965760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 894485 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 435930 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 90 | 2452140 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 47 | 572040 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 92 | 2145600 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 473382 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1765.2 | 36175253
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 60 | 1709760 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13050 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 154 | 2916000 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 98 | 1594800 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 342750 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 11 | 239520 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 52 | 714240 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 375 | 7530120
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 33 | 789000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 28 | 659880 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Borescope Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 688992 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1924800 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 167 | 2784610 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 348000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 173952 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7508500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 347 | 8939000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7685600 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1334 | 31502334
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 715 | 18251636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 164 | 6070464 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 44 | 500160 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 788400 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1104 | 25120000 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3699.2 | 2027 | 50730660
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 0 | 152727 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 10 | 239775 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 125 | 2986000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 26420363.64 | -
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5359480 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 322800 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6262000 | Coal shortage
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4461 | -
Barishal Area Total |  |  |  |  | 2236 | 1960 | 41747606.64
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Machine Standby
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 145 | 3652818 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 163 | 4232118 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 158 | 4220300 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 370 | 8885527 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 149927 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 53 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 82 | 351136 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 111 | 1180608 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 100 | 663936 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 37920 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 762 | 17371636 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 345000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 836490 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 1921 | 41927469
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1134109 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 190 | 4631000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 2021961 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 50718 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2061047 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 231165 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1448640 | -
Rangpur Area Total |  |  |  |  | 950 | 468 | 11578640
Eastern Grid Total |  |  |  |  | 16705.895 | 8799.2 | 181721616.85
Western Grid Total |  |  |  |  | 10338.16 | 6376 | 145984375.64
National Grid Total |  |  |  |  | 27044.055 | 15175.2 | 327705992.49
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 13-06-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9216.92 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5197.2 | MW
i) Dhaka area |  |  | 4338.02 |  | MW | i) Khulna area |  |  |  | 1928 | MW
ii) Chattogram area |  |  | 1319.9 |  | MW | ii) Barishal area |  |  |  | 505 | MW
iii) Cumilla area |  |  | 1539 |  | MW | iii) Rajshahi area |  |  |  | 1709.2 | MW
iv) Mymensingh area |  |  | 1346 |  | MW | iv) Rangpur area |  |  |  | 1055 | MW
v) Sylhet area |  |  | 674 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14414.12 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 84 | 21:00 | 133 | Patuakhali | 95.9 | 23:00
2 | AKSML | 69.4 | 02:00 | 68 | Jaldhaka | 102 | 23:00 | 134 | Payra | 40 | 00:00
3 | Aftabnagar | 34 | 00:00 | 69 | Jamalpur | 164 | 20:00 | 135 | Postogola | 47 | 00:00
4 | Agargaon | 121 | 23:00 | 70 | Jashore | 154 | 21:00 | 136 | Purbachal | 21 | 23:00
5 | Agrabad | 84 | 23:00 | 71 | Jhenaidah | 147 | 20:00 | 137 | Purbasadipur | 141 | 00:00
6 | Amnura | 47 | 23:00 | 72 | Joydebpur | 106 | 23:00 | 138 | Rahanpur | 38 | 23:00
7 | Ashuganj | 112.5 | 02:00 | 73 | Joypurhat | 78 | 01:00 | 139 | Rahim | 1 | 00:00
8 | BSRM | 200 | 03:00 | 74 | Juldah | 12.5 | 00:00 | 140 | Rajbari | 92 | 23:00
9 | Bagerhat | 86 | 00:00 | 75 | KSRM | 12 | 18:00 | 141 | Rajendrapur | 116 | 23:00
10 | Bajitpur | 60 | 21:00 | 76 | Kabirpur | 148 | 22:00 | 142 | Rajshahi | 125 | 23:00
11 | Bakulia | 86 | 23:00 | 77 | Kachua | 105 | 21:00 | 143 | Rajshahi-230 | 108 | 23:00
12 | Banani | 26 | 16:00 | 78 | Kallyanpur | 108 | 23:00 | 144 | Ramganj | 120 | 23:00
13 | Bangabhaban | 4 | 11:00 | 79 | Kalurghat | 30 | 23:00 | 145 | Rampur | 42 | 23:00
14 | Barapukuria | 79 | 23:00 | 80 | Kamrangirchar | 38 | 20:00 | 146 | Rangamati | 18 | 19:30
15 | Barguna | 26 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 151 | 19:30
16 | Barishal | 118 | 00:00 | 82 | Kasba | 42 | 21:00 | 148 | Ruppur | 7 | 09:00
17 | Barishal-230 | 118 | 00:00 | 83 | Kazla | 75 | 23:00 | 149 | SSM | 0 | 00:00
18 | Baroaulia | 59 | 23:00 | 84 | Keranigonj | 83 | 23:00 | 150 | Saidpur | 115 | 21:00
19 | Baroirhat | 70 | 23:00 | 85 | Khagrachori | 34 | 19:00 | 151 | Satkhira | 152 | 22:00
20 | Bashundhara | 150 | 23:00 | 86 | Khulna | 67 | 00:00 | 152 | Satmasjid | 96 | 21:00
21 | BashundharaCement | 1 | 00:00 | 87 | Khulshi | 154 | 01:00 | 153 | Savar | 145 | 21:00
22 | Beanibazar | 91 | 23:00 | 88 | Kishoreganj | 161 | 22:00 | 154 | SevenRings | 4.18 | 01:00
23 | Benapole | 72 | 22:00 | 89 | Kodda | 193 | 22:00 | 155 | ShahCement | 22 | 08:00
24 | Bhaluka | 145 | 21:00 | 90 | Kulaura | 59 | 19:30 | 156 | Shahjadpur | 90 | 22:00
25 | Bhandaria | 64 | 01:00 | 91 | Kurigram | 73 | 20:00 | 157 | Shahjibazar | 118 | 23:00
26 | Bhangura | 46 | 21:00 | 92 | Kushtia | 170 | 21:00 | 158 | Shahmirpur | 49 | 22:00
27 | Bheramara(GK) | 76 | 21:00 | 93 | Lalbag | 16 | 23:00 | 159 | Shariatpur | 105 | 00:00
28 | Bhulta | 162 | 23:00 | 94 | Lalmonirhat | 69 | 01:00 | 160 | Sherpur | 178 | 00:00
29 | Bog-Sherpur | 70 | 20:00 | 95 | MI_Cement | 10.7 | 15:00 | 161 | Shikalbaha | 16 | 00:00
30 | Bogura | 187 | 01:00 | 96 | Madanganj | 36 | 23:00 | 162 | Shitalakhya | 59.7 | 21:00
31 | Borhanuddin | 92 | 20:00 | 97 | Madaripur | 132 | 00:00 | 163 | Sholosohor | 37 | 22:00
32 | Brahmanbaria | 136 | 01:00 | 98 | Madartek | 94 | 23:00 | 164 | Shyampur | 92 | 00:00
33 | Cantonment | 130 | 19:00 | 99 | Madunaghat | 56 | 23:00 | 165 | Siddhirganj | 87 | 22:00
34 | Chandina | 20.58 | 22:00 | 100 | Magura | 74 | 00:00 | 166 | Sirajganj | 122 | 00:00
35 | Chandpur | 90 | 00:00 | 101 | Mahasthangarh | 106 | 00:00 | 167 | Sonargaon | 80 | 00:00
36 | Chandraghona | 40 | 20:00 | 102 | Manikganj | 135 | 22:00 | 168 | Sreemongol | 87 | 19:00
37 | Chapai | 81 | 22:00 | 103 | Maniknagar | 58 | 23:00 | 169 | Sreepur | 79 | 21:00
38 | Charsaidpur | 22 | 17:00 | 104 | Matarbari | 56 | 20:00 | 170 | Srinagar | 56.68 | 23:00
39 | Chauddagram | 83 | 20:00 | 105 | Matuail | 40 | 23:00 | 171 | Sunamganj | 65 | 20:00
40 | Chhatak | 44 | 22:00 | 106 | Millgate | 54 | 23:00 | 172 | Sylhet | 53 | 00:00
41 | Chowmuhani | 240 | 21:00 | 107 | Mirpur | 115 | 23:00 | 173 | Sylhet-132 | 136 | 21:00
42 | Chuadanga | 127 | 20:00 | 108 | Mirsorai | 9 | 15:00 | 174 | TK | 36 | 23:00
43 | Coxsbazar | 127 | 14:00 | 109 | Mirzapur | 46 | 13:00 | 175 | Tangail | 194 | 21:00
44 | Cumilla(N) | 164 | 22:00 | 110 | Mithapukur | 72 | 07:00 | 176 | Thakurgaon | 127 | 20:00
45 | Cumilla(S) | 171 | 23:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 114 | 23:00
46 | Daudkandi | 159 | 00:00 | 112 | Mogbazar | 110.7 | 21:00 | 178 | Ullahpara | 44 | 19:30
47 | Dhaka | 28 | 20:00 | 113 | Mongla | 28 | 00:00 | 179 | Ullon | 55 | 23:00
48 | Dhamrai | 116 | 20:00 | 114 | Motijheel | 33 | 23:00 | 180 | Uttara | 97 | 19:30
49 | Dhanmondi | 108 | 19:00 | 115 | Muktagacha | 44 | 00:00 | 181 | UttaraNew | 61 | 23:00
50 | Dohazari | 120 | 21:00 | 116 | Munshiganj | 125 | 23:00 | 182 | Zigatola | 66 | 22:00
51 | Faridpur | 178 | 23:00 | 117 | Muradnagar | 34 | 21:00
52 | Fatullah | 56 | 23:00 | 118 | Mymensingh | 226 | 22:00
53 | Fenchuganj | 47 | 19:00 | 119 | Naogaon | 165 | 21:00
54 | Feni | 133 | 00:00 | 120 | Narail | 67 | 23:00
55 | GPH | 3 | 18:30 | 121 | Narinda | 54 | 23:00
56 | Ghatail | 84 | 19:30 | 122 | Narshingdi | 165 | 23:00
57 | Ghorashal | 15 | 00:00 | 123 | Natore | 180 | 23:00
58 | Ghorashal-230 | 74 | 23:00 | 124 | Nawabganj | 69.2 | 23:00
59 | Goalpara | 44 | 21:00 | 125 | Netrakona | 159 | 19:30
60 | Gollamari | 100 | 00:00 | 126 | New | 50 | 23:00
61 | Gopalganj | 123 | 00:00 | 127 | Niamatpur | 92 | 00:00
62 | Gulshan | 98 | 19:00 | 128 | Noapara | 47 | 20:00
63 | Halishahar | 35.5 | 12:00 | 129 | PHP | 8 | 14:00
64 | HaripurSBU | 113 | 22:00 | 130 | Pabna | 125 | 01:00
65 | Hasnabad | 63 | 23:00 | 131 | Palashbari | 131 | 07:00
66 | Hathazari | 86 | 23:00 | 132 | Panchagarh | 69 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 13-06-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14955.22 | 120 |  | 15080.22
1:00 | 14656.48 | 186 |  | 14850.48
2:00 | 14395.85 | 149 |  | 14551.85
3:00 | 14153.56 | 113 |  | 14271.56
4:00 | 13741.53 | 104 |  | 13850.53
5:00 | 13594.33 | 82 |  | 13680.33
6:00 | 12979.36 | 0 |  | 12979.36
7:00 | 12641.13 | 0 |  | 12641.13
8:00 | 12446.99 | 0 |  | 12446.99
9:00 | 12158.24 | 0 |  | 12158.24
10:00 | 12070.01 | 0 |  | 12070.01
11:00 | 12228.38 | 0 |  | 12228.38
12:00 | 12525.98 | 0 |  | 12525.98
13:00 | 13323.82 | 0 |  | 13323.82
14:00 | 13051.19 | 0 |  | 13051.19
15:00 | 13277.11 | 0 |  | 13277.11
16:00 | 13196.62 | 0 |  | 13196.62
17:00 | 12803.48 | 0 |  | 12803.48
18:00 | 12163.28 | 0 |  | 12163.28
19:00 | 13338 | 0 |  | 13338
19:30 | 14523.2 | 74 |  | 14600.2
20:00 | 14665.2 | 81 |  | 14750.2
21:00 | 15175.2 | 110 |  | 15290.2
22:00 | 15284.2 | 120 |  | 15409.2
23:00 | 15327.2 | 156 |  | 15490.2
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 13-06-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8391.9 | 6563.32 | 14955.22 | DAILY GENERATION CURVE
00:30 | 8315.7 | 6490.15 | 14805.85
01:00 | 8239.5 | 6416.98 | 14656.48 | 13-06-2025
01:30 | 8164.6 | 6361.565 | 14526.165
02:00 | 8089.7 | 6306.15 | 14395.85
02:30 | 8026.7 | 6248.005 | 14274.705
03:00 | 7963.7 | 6189.86 | 14153.56
03:30 | 7705.45 | 6242.095 | 13947.545
04:00 | 7447.2 | 6294.33 | 13741.53
04:30 | 7388.7 | 6279.23 | 13667.93
05:00 | 7330.2 | 6264.13 | 13594.33
05:30 | 7182.005 | 6104.84 | 13286.845
06:00 | 7033.81 | 5945.55 | 12979.36
06:30 | 6994.695 | 5815.55 | 12810.245
07:00 | 6955.58 | 5685.55 | 12641.13
07:30 | 6879.435 | 5664.625 | 12544.06
08:00 | 6803.29 | 5643.7 | 12446.99
08:30 | 6706.815 | 5595.8 | 12302.615
09:00 | 6610.34 | 5547.9 | 12158.24
09:30 | 6556.2 | 5557.925 | 12114.125
10:00 | 6502.06 | 5567.95 | 12070.01
10:30 | 6576.14 | 5573.055 | 12149.195
11:00 | 6650.22 | 5578.16 | 12228.38
11:30 | 6716.095 | 5661.085 | 12377.18
12:00 | 6781.97 | 5744.01 | 12525.98
12:30 | 6924.515 | 6000.385 | 12924.9
13:00 | 7067.06 | 6256.76 | 13323.82
13:30 | 7036.945 | 6150.56 | 13187.505
14:00 | 7006.83 | 6044.36 | 13051.19
14:30 | 7120.625 | 6043.525 | 13164.15
15:00 | 7234.42 | 6042.69 | 13277.11
15:30 | 7192.335 | 6044.53 | 13236.865
16:00 | 7150.25 | 6046.37 | 13196.62
16:30 | 7072.915 | 5927.135 | 13000.05
17:00 | 6995.58 | 5807.9 | 12803.48
17:30 | 6850.7 | 5632.68 | 12483.38
18:00 | 6705.82 | 5457.46 | 12163.28
18:30 | 7106.91 | 5643.73 | 12750.64
19:00 | 7508 | 5830 | 13338
19:30 | 8262.2 | 6261 | 14523.2
20:00 | 8436.2 | 6229 | 14665.2
20:30 | 8617.7 | 6302.5 | 14920.2 |  | Executive Engineer
21:00 | 8799.2 | 6376 | 15175.2 |  | Network Operation Division
21:30 | 8838.2 | 6391.5 | 15229.7
22:00 | 8877.2 | 6407 | 15284.2
22:30 | 8860.7 | 6445 | 15305.7
23:00 | 8844.2 | 6483 | 15327.2

## En-Curve
QF-LDC-12
Date | 13-06-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4177 | 2901.7 | 780 | 0 | 46 | 759.12 | 172 | 4118.2 | 0 | 380 | 1620.2 | 0 | 0 | 1 | 120 | DAILY ENERGY CURVE
00:30 | 4121 | 2906.35 | 756.5 | 0 | 44 | 757.95 | 172 | 4052.7 | 0 | 380 | 1614.85 | 0 | 0 | 0.5 | 153 | 13-06-2025
01:00 | 4065 | 2911 | 733 | 0 | 42 | 756.78 | 172 | 3987.2 | 0 | 380 | 1609.5 | 0 | 0 | 0 | 186
01:30 | 3939.5 | 2911 | 733 | 0 | 42 | 755.365 | 172 | 3944.2 | 0 | 380 | 1649.1 | 0 | 0 | 0 | 167.5 | Energy Generated | 327.706 |  | MKWHr
02:00 | 3814 | 2911 | 733 | 0 | 42 | 753.95 | 172 | 3901.2 | 0 | 380 | 1688.7 | 0 | 0 | 0 | 149 | Energy not Served | 1.221 |  | MKWHr
02:30 | 3721 | 2918 | 756 | 0 | 42 | 756.305 | 172 | 3856.7 | 0 | 371.5 | 1681.2 | 0 | 0 | 0 | 131 | Total Energy Requirement | 328.927 |  | MKWHr
03:00 | 3628 | 2925 | 779 | 0 | 42 | 758.66 | 172 | 3812.2 | 0 | 363 | 1673.7 | 0 | 0 | 0 | 113
03:30 | 3605.5 | 2916 | 827 | 0 | 42 | 756.495 | 172 | 3867.1 | 0 | 320 | 1441.45 | 0 | 0 | 0 | 108.5
04:00 | 3583 | 2907 | 875 | 0 | 42 | 754.33 | 172 | 3922 | 0 | 277 | 1209.2 | 0 | 0 | 0 | 104
04:30 | 3604.5 | 2913 | 875 | 0 | 42 | 756.23 | 172 | 3849 | 0 | 277 | 1179.2 | 0 | 0 | 0 | 93
05:00 | 3626 | 2919 | 875 | 0 | 42 | 758.13 | 172 | 3776 | 0 | 277 | 1149.2 | 0 | 0 | 0 | 82
05:30 | 3581 | 2911 | 875 | 0 | 41 | 745.945 | 172 | 3637 | 16.2 | 243.5 | 1064.2 | 0 | 0 | 0 | 41
06:00 | 3536 | 2903 | 875 | 0 | 40 | 733.76 | 172 | 3498 | 32.4 | 210 | 979.2 | 0 | 0 | 0 | 0
06:30 | 3561.5 | 2903.5 | 874.5 | 0 | 38 | 700.32 | 172 | 3344.5 | 88.725 | 170.5 | 956.7 | 0 | 0 | 0 | 0
07:00 | 3587 | 2904 | 874 | 0 | 36 | 666.88 | 172 | 3191 | 145.05 | 131 | 934.2 | 0 | 0 | 0 | 0
07:30 | 3579 | 2899 | 804.5 | 0 | 37 | 671.02 | 172 | 3151.5 | 219.34 | 100.5 | 910.2 | 0 | 0 | 0 | 0
08:00 | 3571 | 2894 | 735 | 0 | 38 | 675.16 | 172 | 3112 | 293.63 | 70 | 886.2 | 0 | 0 | 0 | 0
08:30 | 3551 | 2859 | 735 | 0 | 38 | 673.31 | 172 | 3061 | 350.705 | 71 | 791.6 | 0 | 0 | 0 | 0
09:00 | 3531 | 2824 | 735 | 0 | 38 | 671.46 | 172 | 3010 | 407.78 | 72 | 697 | 0 | 0 | 0 | 0
09:30 | 3503 | 2783.5 | 735 | 0 | 38 | 669.27 | 172 | 2951 | 491.855 | 79.5 | 691 | 0 | 0 | 0 | 0
10:00 | 3475 | 2743 | 735 | 0 | 38 | 667.08 | 172 | 2892 | 575.93 | 87 | 685 | 0 | 0 | 0 | 0
10:30 | 3494 | 2733 | 735 | 0 | 38 | 672.115 | 172 | 2959 | 584.58 | 87 | 674 | 0 | 0 | 0.5 | 0
11:00 | 3513 | 2723 | 735 | 0 | 38 | 677.15 | 172 | 3026 | 593.23 | 87 | 663 | 0 | 0 | 1 | 0
11:30 | 3515.5 | 2719.5 | 734.5 | 0 | 38 | 715.74 | 172 | 3114 | 601.94 | 87 | 672.5 | 0 | 0 | 6.5 | 0
12:00 | 3518 | 2716 | 734 | 0 | 38 | 754.33 | 172 | 3202 | 610.65 | 87 | 682 | 0 | 0 | 12 | 0
12:30 | 3548 | 2769 | 734.5 | 0 | 39 | 754.185 | 172 | 3453.5 | 632.215 | 112.5 | 703.5 | 0 | 0 | 6.5 | 0
13:00 | 3578 | 2822 | 735 | 0 | 40 | 754.04 | 172 | 3705 | 653.78 | 138 | 725 | 0 | 0 | 1 | 0
13:30 | 3559.5 | 2810.5 | 734.5 | 0 | 40 | 761.02 | 172 | 3642.5 | 622.485 | 144 | 696.5 | 0 | 0 | 4.5 | 0
14:00 | 3541 | 2799 | 734 | 0 | 40 | 768 | 172 | 3580 | 591.19 | 150 | 668 | 0 | 0 | 8 | 0
14:30 | 3551 | 2837 | 734 | 0 | 41 | 767 | 172 | 3668 | 529.15 | 152 | 702.5 | 0 | 0 | 10.5 | 0
15:00 | 3561 | 2875 | 734 | 0 | 42 | 766 | 172 | 3756 | 467.11 | 154 | 737 | 0 | 0 | 13 | 0
15:30 | 3541.5 | 2876.5 | 734 | 0 | 41 | 764.5 | 172 | 3771.5 | 404.365 | 149 | 770.5 | 0 | 0 | 12 | 0
16:00 | 3522 | 2878 | 734 | 0 | 40 | 763 | 172 | 3787 | 341.62 | 144 | 804 | 0 | 0 | 11 | 0
16:30 | 3460.5 | 2873.5 | 734 | 0 | 39 | 762 | 172 | 3750.5 | 254.05 | 134 | 808.5 | 0 | 0 | 12 | 0
17:00 | 3399 | 2869 | 734 | 0 | 38 | 761 | 172 | 3714 | 166.48 | 124 | 813 | 0 | 0 | 13 | 0
17:30 | 3335 | 2781 | 725 | 0 | 36 | 761.5 | 172 | 3627 | 107.88 | 124 | 802.5 | 0 | 0 | 11.5 | 0
18:00 | 3271 | 2693 | 716 | 0 | 34 | 762 | 172 | 3540 | 49.28 | 124 | 792 | 0 | 0 | 10 | 0
18:30 | 3377 | 2789 | 692 | 0 | 39 | 760 | 172 | 3661 | 24.64 | 236 | 989 | 0 | 0 | 11 | 0
19:00 | 3483 | 2885 | 668 | 0 | 44 | 758 | 172 | 3782 | 0 | 348 | 1186 | 0 | 0 | 12 | 0
19:30 | 3503 | 2927 | 669 | 0 | 42 | 758 | 172 | 4085 | 0 | 435 | 1914.2 | 0 | 0 | 18 | 74
20:00 | 3518 | 2943 | 668 | 0 | 44 | 751 | 172 | 4099 | 0 | 492 | 1973.2 | 0 | 0 | 5 | 81
20:30 | 3533.5 | 2928.5 | 691.5 | 0 | 45 | 756.5 | 172 | 4109 | 0 | 513 | 2164.2 | 0 | 0 | 7 | 95.5
21:00 | 3549 | 2914 | 715 | 0 | 46 | 762 | 172 | 4119 | 0 | 534 | 2355.2 | 0 | 0 | 9 | 110
21:30 | 3548 | 2918 | 715.5 | 0 | 45 | 761 | 172 | 4131 | 0 | 537 | 2395.7 | 0 | 0 | 6.5 | 115
22:00 | 3547 | 2922 | 716 | 0 | 44 | 760 | 172 | 4143 | 0 | 540 | 2436.2 | 0 | 0 | 4 | 120
22:30 | 3504.5 | 2925.5 | 686 | 0 | 44 | 764 | 172 | 4172.5 | 0 | 569 | 2465.7 | 0 | 0 | 2.5 | 138
23:00 | 3462 | 2929 | 656 | 0 | 44 | 768 | 172 | 4202 | 0 | 598 | 2495.2 | 0 | 0 | 1 | 156
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 13-06-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 394 | 09:00 | 384 | 00:00 | Payra | 416 | 10:00 | 408 | 00:00
Ashuganj | 396 | 10:00 | 382 | 00:00 | Rahanpur | 407 | 18:00 | 393 | 00:00
Bhulta | 396 | 18:00 | 382 | 13:00 | Rampal | 406 | 10:00 | 388 | 00:00
Bibiana | 390 | 10:00 | 384 | 04:00
BIPTC | 406 | 08:00 | 391 | 22:00
Bogura | 396 | 10:00 | 382 | 00:00
Gopalganj | 406 | 09:00 | 388 | 00:00
Kaliakoir | 383 | 09:00 | 373 | 19:00
Madunaghat | 399 | 22:00 | 392 | 00:00
Meghnaghat | 399 | 10:00 | 391 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 232 | 07:00 | 225 | 13:00 | Keranigonj | 230 | 10:00 | 224 | 00:00
AKSML | 234 | 21:00 | 223 | 13:00 | Khulna(S) | 232 | 10:00 | 213 | 00:00
Aminbazar | 232 | 07:00 | 227 | 00:00 | Madunaghat | 235 | 21:00 | 226 | 12:00
Ashuganj | 233 | 07:00 | 130 | 22:00 | Madunaghat-400 | 235 | 22:00 | 227 | 13:00
Ashuganj-400 | 233 | 07:00 | 130 | 22:00 | Maniknagar | 227 | 18:30 | 221 | 00:00
Baghabari | 234 | 08:00 | 225 | 00:00 | Meghnaghat | 235 | 07:00 | 231 | 00:00
Barapukuria | 221 | 18:00 | 213 | 00:00 | Meghnaghat-400 | 230 | 06:00 | 226 | 00:00
Barapukuria-230 | 221 | 18:00 | 213 | 00:00 | Mirsorai | 231 | 23:00 | 224 | 00:00
Barishal | 239 | 09:00 | 228 | 00:00 | Rajshahi | 234 | 09:00 | 220 | 19:30
Bheramara | 234 | 08:00 | 222 | 19:30 | Rampal | 231 | 09:00 | 215 | 00:00
Bhulta | 232 | 07:00 | 223 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 228 | 05:00 | 223 | 00:00 | Rampura | 231 | 06:00 | 222 | 19:00
BIPTC | 237 | 08:00 | 221 | 19:30 | Shikalbaha | 234 | 21:00 | 224 | 15:00
Bogura | 231 | 10:00 | 223 | 00:00 | Shyampur | 230 | 08:00 | 224 | 13:00
Bogura-400 | 230 | 10:00 | 223 | 00:00 | Siddhirganj | 228 | 07:00 | 224 | 00:00
Borhanuddin | 243 | 10:00 | 234 | 00:00 | Sirajgonj | 239 | 08:00 | 234 | 00:00
BSRM | 229 | 21:00 | 221 | 13:00 | Sreepur | 229 | 07:00 | 221 | 19:30
Cumilla(N) | 226 | 10:00 | 219 | 13:00 | Tongi | 233 | 05:00 | 223 | 00:00
Faridpur | 235 | 09:00 | 34 | 18:00
Fenchuganj | 226 | 09:00 | 221 | 00:00
Ghorashal | 238 | 00:00 | 230 | 17:00
Ghorashal-230 | 232 | 07:00 | 223 | 19:30
Gopalganj | 238 | 10:00 | 227 | 00:00
GPH | 232 | 21:00 | 223 | 13:00
Haripur | 228 | 10:00 | 223 | 00:00
Hasnabad | 230 | 09:00 | 224 | 13:00
Hathazari | 235 | 21:00 | 226 | 13:00
Ishurdi | 236 | 08:00 | 224 | 19:30
Jhenaidah | 231 | 09:00 | 212 | 00:00
Kaliakoir | 236 | 07:00 | 229 | 19:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 132 | 21:00 | 124 | 12:00 | Madartek | 131 | 21:00 | 123 | 19:00
Agargaon | 133 | 06:00 | 12 | 22:00 | Madunaghat | 133 | 05:00 | 127 | 12:00
Agrabad | 135 | 21:00 | 127 | 13:00 | Magura | 134 | 07:00 | 119 | 23:00
AKS | 132 | 21:00 | 127 | 13:00 | Mahasthangarh | 131 | 10:00 | 125 | 00:00
Aminbazar | 132 | 07:00 | 127 | 13:00 | Manikganj | 128 | 08:00 | 118 | 19:30
Amnura | 135 | 08:00 | 123 | 00:00 | Maniknagar | 129 | 05:00 | 126 | 00:00
Ashuganj | 137 | 07:00 | 134 | 19:00 | Matarbari | 124 | 21:00 | 107 | 13:00
Bagerhat | 133 | 10:00 | 116 | 00:00 | Matuail | 133.3 | 08:00 | 130.5 | 13:00
Bajitpur | 129 | 10:00 | 122 | 19:30 | Millgate | 131 | 07:00 | 123 | 19:00
Bakulia | 136 | 21:00 | 128 | 15:00 | Mirpur | 131 | 08:00 | 126 | 13:00
Banani | 133 | 21:00 | 124 | 13:00 | Mirzapur | 132 | 10:00 | 126 | 00:00
Bangabhaban | 129 | 06:00 | 125 | 13:00 | Mithapukur | 130 | 19:00 | 122 | 00:00
Barapukuria | 133 | 18:00 | 124 | 00:00 | MI_Cement | 133 | 06:00 | 130 | 13:00
Barguna | 135 | 18:00 | 129 | 00:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal | 132 | 10:00 | 123 | 00:00 | Mogbazar | 134 | 06:00 | 125 | 00:00
Barishal-230 | 133 | 09:00 | 124 | 00:00 | Mongla | 134 | 10:00 | 118 | 00:00
Baroaulia | 134 | 21:00 | 128 | 13:00 | Motijheel | 129 | 06:00 | 125 | 13:00
Baroirhat | 126 | 10:00 | 119 | 02:00 | Muktagacha | 132 | 18:30 | 121 | 19:30
Bashundhara | 132 | 21:00 | 123 | 19:00 | Munshiganj | 132 | 03:00 | 129 | 13:00
BashundharaCement | 133 | 18:30 | 129 | 13:00 | Muradnagar | 128 | 18:00 | 122 | 13:00
Beanibazar | 127 | 12:00 | 119 | 00:00 | Mymensingh | 132 | 17:00 | 110 | 19:30
Benapole | 131 | 10:00 | 115 | 00:00 | Naogaon | 131 | 18:30 | 120 | 00:00
Bhaluka | 129 | 07:00 | 122 | 19:30 | Narail | 150 | 21:00 | 119 | 23:00
Bhandaria | 130 | 08:00 | 115 | 22:00 | Narinda | 129 | 05:00 | 126 | 00:00
Bhangura | 133 | 10:00 | 126 | 00:00 | Narshingdi | 137 | 05:00 | 123 | 00:00
Bheramara | 137 | 08:00 | 129 | 23:00 | Natore | 134 | 08:00 | 126 | 00:00
Bheramara(GK) | 137 | 08:00 | 128 | 23:00 | Nawabganj | 133 | 07:00 | 128 | 00:00
Bhulta | 130 | 10:00 | 125 | 00:00 | Netrakona | 119 | 06:00 | 107 | 00:00
Bog-Sherpur | 133 | 10:00 | 127 | 00:00 | New | 132 | 09:00 | 124 | 19:00
Bogura | 135 | 11:00 | 129 | 00:00 | Niamatpur | 136 | 06:00 | 129 | 00:00
Bogura-230 | 136 | 18:00 | 130 | 00:00 | Noapara | 134 | 09:00 | 119 | 00:00
Brahmanbaria | 128 | 07:00 | 123 | 19:00 | Pabna | 135 | 10:00 | 127 | 00:00
Cantonment | 133 | 06:00 | 129 | 00:00 | Palashbari | 127 | 10:00 | 120 | 19:30
Chandina | 129 | 09:00 | 124 | 13:00 | Panchagarh | 129 | 17:00 | 114 | 00:00
Chandpur | 128 | 10:00 | 121 | 13:00 | Patuakhali | 135 | 18:30 | 131 | 06:00
Chandraghona | 134 | 20:00 | 128 | 13:00 | Payra | 136 | 08:00 | 132 | 00:00
Chapai | 131 | 18:00 | 124 | 23:00 | PHP | 125 | 10:00 | 118 | 02:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 133 | 07:00 | 130 | 00:00 | Postogola | 135 | 05:00 | 132 | 00:00
Chauddagram | 125 | 18:30 | 118 | 13:00 | Purbachal | 132 | 22:00 | 123 | 19:00
Chhatak | 126 | 18:00 | 119 | 01:00 | Purbasadipur | 126 | 06:00 | 113 | 00:00
Chowmuhani | 120 | 10:00 | 112 | 13:00 | Rahanpur | 136 | 10:00 | 130 | 00:00
Chuadanga | 131 | 08:00 | 117 | 00:00 | Rahanpur-400 | 136 | 18:00 | 130 | 00:00
Coxsbazar | 124 | 20:00 | 111 | 13:00 | Rahim | 134 | 08:00 | 130 | 00:00
Cumilla(N) | 129 | 10:00 | 124 | 13:00 | Rajbari | 136 | 09:00 | 126 | 23:00
Cumilla(S) | 132 | 05:00 | 123 | 00:00 | Rajendrapur | 134 | 03:00 | 125 | 00:00
Daudkandi | 128 | 18:30 | 122 | 00:00 | Rajshahi | 135 | 08:00 | 125 | 23:00
Dhaka | 132 | 21:00 | 124 | 12:00 | Rajshahi-230 | 135 | 09:00 | 116 | 00:00
Dhamrai | 131 | 06:00 | 126 | 00:00 | Ramganj | 121 | 10:00 | 114 | 06:00
Dhanmondi | 134 | 07:00 | 131 | 00:00 | Rampur | 135 | 21:00 | 128 | 13:00
Dohazari | 132 | 21:00 | 119 | 13:00 | Rampura | 132 | 21:00 | 124 | 19:00
Faridpur | 136 | 09:00 | 130 | 00:00 | Rangamati | 132 | 20:00 | 127 | 13:00
Fatullah | 133 | 06:00 | 130 | 00:00 | Rangpur | 127 | 16:00 | 118 | 00:00
Fenchuganj | 134 | 12:00 | 130 | 02:00 | Ruppur | 138 | 09:00 | 129 | 23:00
Feni | 124 | 09:00 | 117 | 15:00 | Saidpur | 129 | 18:00 | 115 | 01:00
Ghatail | 129 | 10:00 | 120 | 19:30 | Satkhira | 131 | 09:00 | 114 | 00:00
Ghorashal | 138 | 06:00 | 134 | 12:00 | Satmasjid | 138 | 21:00 | 128 | 13:00
Goalpara | 136 | 08:00 | 123 | 00:00 | Savar | 132 | 20:00 | 125 | 13:00
Gollamari | 137 | 09:00 | 124 | 00:00 | SevenRings | 138 | 07:00 | 132 | 19:30
Gopalganj | 135 | 09:00 | 124 | 00:00 | ShahCement | 133 | 07:00 | 130 | 00:00
Gopalganj-400 | 138 | 09:00 | 131 | 00:00 | Shahjadpur | 136 | 08:00 | 130 | 00:00
Gulshan | 132 | 21:00 | 124 | 19:00 | Shahjibazar | 128 | 08:00 | 120 | 03:00
Halishahar | 137 | 21:00 | 127 | 13:00 | Shahmirpur | 136 | 21:00 | 127 | 12:00
Haripur | 134 | 10:00 | 130 | 13:00 | Shariatpur | 135 | 10:00 | 125 | 00:00
HaripurSBU | 134 | 04:00 | 130 | 13:00 | Sherpur | 130 | 18:30 | 116 | 06:00
Hasnabad | 135 | 08:00 | 132 | 04:00 | Shikalbaha | 124 | 22:00 | 116 | 13:00
Hathazari | 136 | 21:00 | 129 | 15:00 | Shikalbaha-230 | 136 | 20:00 | 129 | 13:00
Ishurdi | 138 | 08:00 | 130 | 23:00 | Shitalakhya | 133 | 06:00 | 130 | 13:00
Jaldhaka | 125 | 18:00 | 111 | 00:00 | Sholosohor | 134 | 20:00 | 126 | 13:00
Jamalpur | 133 | 18:30 | 122 | 06:00 | Shyampur | 133 | 18:00 | 130 | 00:00
Jashore | 134 | 18:30 | 118 | 00:00 | Shyampur-230 | 133 | 07:00 | 129 | 13:00
Jhenaidah | 136 | 07:00 | 115 | 23:00 | Siddhirganj | 134 | 06:00 | 131 | 00:00
Jhenaidah-230 | 136 | 08:00 | 123 | 00:00 | Sirajganj | 137 | 12:00 | 125 | 00:00
Joydebpur | 134 | 02:00 | 127 | 13:00 | Sonargaon | 133 | 18:00 | 128 | 13:00
Joypurhat | 128 | 18:30 | 116 | 00:00 | Sreemongol | 126 | 09:00 | 117 | 19:00
Juldah | 136 | 21:00 | 128 | 13:00 | Sreepur | 133 | 06:00 | 127 | 19:30
Kabirpur | 135 | 01:00 | 121 | 21:00 | Srinagar | 133 | 08:00 | 129 | 00:00
Kachua | 127 | 18:30 | 120 | 13:00 | SSM | 139 | 21:00 | 132 | 13:00
Kaliakoir | 136 | 09:00 | 130 | 13:00 | Sunamganj | 124 | 12:00 | 115 | 01:00
Kallyanpur | 132 | 07:00 | 127 | 13:00 | Sylhet | 127 | 08:00 | 123 | 00:00
Kalurghat | 133 | 21:00 | 127 | 13:00 | Sylhet-132 | 128 | 18:00 | 124 | 00:00
Kamrangirchar | 134 | 04:00 | 129 | 13:00 | Tangail | 130 | 18:00 | 121 | 19:30
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 129 | 19:00 | 113 | 00:00
Kasba | 128 | 18:30 | 121 | 13:00 | TK | 132 | 20:00 | 128 | 00:00
Kazla | 129 | 07:00 | 126 | 00:00 | Tongi | 133 | 05:00 | 127 | 21:00
Keranigonj | 133 | 06:00 | 129 | 00:00 | Ullahpara | 134 | 08:00 | 127 | 00:00
Khagrachori | 133 | 21:00 | 126 | 13:00 | Ullon | 132 | 22:00 | 125 | 00:00
Khulna | 136 | 09:00 | 123 | 00:00 | Uttara | 132 | 03:00 | 125 | 15:00
Khulna(S) | 137 | 09:00 | 123 | 00:00 | UttaraNew | 130 | 07:00 | 122 | 19:00
Khulshi | 134 | 21:00 | 126 | 13:00 | Zigatola | 134 | 10:00 | 130 | 00:00
Kishoreganj | 126 | 07:00 | 115 | 19:30
Kodda | 134 | 02:00 | 126 | 19:30
KSRM | 135 | 21:00 | 128 | 13:00
Kulaura | 133 | 08:00 | 129 | 00:00
Kurigram | 126 | 19:00 | 115 | 00:00
Kushtia | 132 | 09:00 | 122 | 22:00
Lalbag | 134 | 07:00 | 130 | 00:00
Lalmonirhat | 127 | 18:00 | 116 | 00:00
Madanganj | 133 | 18:30 | 129 | 13:00
Madaripur | 135 | 08:00 | 128 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division