## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 15-06-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-06-2025 | during | 15-06-2025 | during | 15-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 368 | 356 | 400.75 | 400.75 | 400.75 | 400.75 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 143 | 146 | 335 | 335 | 150 | 150 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 328 | 335 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 21 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 48 | 127 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 4 | 35 | 55 | 55 | 35 | 35 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 0 | 16 | 33 | 33 | 20 | 20 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 33 | 33 | 52.19 | 52.19 | 35 | 35 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 30 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 34 | 68 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 88 | 105 | 105 | 81 | 81 | Fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 45 | 67 | 104 | 104 | 50 | 50 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 80 | 144 | 162 | 162 | 140 | 140 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 20 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 54 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 520 | 388 | 584 | 584 | 540 | 540
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 540 | 200 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 160 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2512 | 2728 | 5109.2 | 5111.2 | 3522.08 | 3524.08
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 12 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 9 | 0 | 5 | 0 | 5 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 172 | 172 | 165 | 165 | 165 | 165 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 145 | 147 | 141 | 145 | 141 | 145 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 68 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 38 | 70 | 48 | 72 | 48 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 67 | 65 | 65 | 65 | 65 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 60 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 5 | 22 | 2 | 28 | 38 | 40 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 5 | 0 | 4.31 | 0 | 4.31 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 68 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1100 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 8 | 24 | 32 | 24 | 32 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 0 | 155 | 730 | 730 | 0 | 0 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1568 | 2249 | 3637.03 | 3689.72 | 2943.03 | 2971.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 199 | 202 | 221 | 221 | 205.43 | 205.43 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 330 | 344 | 353.35 | 353.35 | 340 | 340 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 340 | 335 | 335 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 15 | 24 | 46.7 | 46.7 | 17 | 17 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 44 | 46 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 185 | 185 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 21 | 130 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 11 | 43 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 26 | 70 | 163 | 163 | 80 | 80 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 179 | 181 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 38 | 46 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 1 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 88 | 103 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 17 | 47 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 63 | 99 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 78 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1697 | 1982.2 | 2465.75 | 2395.75 | 2220.63 | 2150.63
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-06-2025 | during | 15-06-2025 | during | 15-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 5 | 0 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.7 | 0 | 1.7 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 122 | 167 | 200 | 200 | 150 | 150 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 65 | 83 | 115 | 115 | 70 | 70 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 0.77 | 0 | 37 | 0 | 37 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 205.77 | 279 | 587.7 | 549 | 492.7 | 454
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 35 | 33 | 34 | 34 | 32 | 32 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 0 | 0 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Borescope Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 84 | 84 | 84 | 85 | 85 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 166 | 166 | 160 | 160 | 160 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 20 | 20 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 6 | 25 | 25 | 10 | 10 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 345 | 387 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1341 | 1382 | 1399 | 1399 | 1349 | 1289
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 874 | 789 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 52 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 52 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 46 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1190 | 1234.2 | 1234.2 | 1234.2 | 1194 | 1194 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2162 | 2075.2 | 3637.2 | 3552.2 | 3187 | 3102
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 222 | 395 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 9 | 11 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 100 | 120 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1051 | 1244 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 0 | 220 | 220 | 0 | 0 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 278 | 278 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.81 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1880.81 | 2048 | 2172 | 2171 | 1940 | 1939
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 17 | 32 | 32 | 32 | 32 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 138 | 158 | 214 | 214 | 150 | 150 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 127 | 153 | 220 | 220 | 140 | 140 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 350 | 300 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 | 30 | 30 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 94 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 2 | 35 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.63 | 0 | 5.2 | 0 | 5.2 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 739.69 | 1443.43 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 17.71 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 71 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 1447.03 | 2267.43 | 3185.07 | 3018.87 | 2779.69 | 2613.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 47 | 49 | 0 | 0 | 50 | 50 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 194 | 200 | 200 | 200 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 110 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.2 | 0 | 4.6 | 0 | 4.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 90 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 15 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 33 | 0 | 169.27 | 0 | 169.27 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 491.2 | 477 | 665.87 | 462 | 715.87 | 512
System Total |  |  |  |  | 28565.2 | 27084.055 | 13304.81 | 15487.83 | 22858.82 | 22348.74 | 19150 | 18555.92
Forecast Scenario (15-06-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15600 |  | 0 |  | 15600
|  |  |  | 1:00 | 15370 |  | 0 |  | 15370
|  |  |  | 2:00 | 14830 |  | 0 |  | 14830
|  |  |  | 3:00 | 14680 |  | 0 |  | 14680
|  |  |  | 4:00 | 14410 |  | 0 |  | 14410
|  |  |  | 5:00 | 14050 |  | 0 |  | 14050
|  |  |  | 6:00 | 13180 |  | 0 |  | 13180
|  |  |  | 7:00 | 12930 |  | 0 |  | 12930
|  |  |  | 8:00 | 12780 |  | 0 |  | 12780
|  |  |  | 9:00 | 12660 |  | 0 |  | 12660
|  |  |  | 10:00 | 12930 |  | 0 |  | 12930
|  |  |  | 11:00 | 12800 |  | 0 |  | 12800
|  |  |  | 12:00 | 13250 |  | 0 |  | 13250
|  |  |  | 13:00 | 13730 |  | 0 |  | 13730
|  |  |  | 14:00 | 13850 |  | 0 |  | 13850
|  |  |  | 15:00 | 14070 |  | 0 |  | 14070
|  |  |  | 16:00 | 13900 |  | 0 |  | 13900
|  |  |  | 17:00 | 13520 |  | 0 |  | 13520
|  |  |  | 18:00 | 12640 |  | 0 |  | 12640
|  |  |  | 18:30 | 13200 |  | 0 |  | 13200
|  |  |  | 19:00 | 14030 |  | 0 |  | 14030
|  |  |  | 19:30 | 14950 |  | 0 |  | 14950
|  |  |  | 20:00 | 15130 |  | 0 |  | 15130
|  |  |  | 21:00 | 15430 |  | 0 |  | 15430
|  |  |  | 22:00 | 15450 |  | 0 |  | 15450
|  |  |  | 23:00 | 15550 |  | 0 |  | 15550
Probable Maximum Temperature: |  |  | 34.00°C
Probable Maximum Demand at Day Peak: |  |  | 13250.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15430.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15430.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 336.77 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:17 hrs on 15-06-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 14-06-2025 | [28 empty] | Date: | 14-06-2025 | [28 empty] | Date: | 14-06-2025 | [28 empty] | Date: | 14-06-2025 | [28 empty] | Date: | 14-06-2025 | [12 empty] | Date: | 14-06-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [12 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 8 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 320 | 35 | 28 | 99 | 95 | 48 | 8 | 35 | 144 | 57 | 450 | 139 | 520 | 0 | 35 | 0 | 0 | 0 | 0 | 160 | 13 | 14 | 0 | 500 | 35 | 30 | 0 | 0 | 0 | 65 | 46 | 0 | 88 | 48 | 0 | 172 | 106 | 42 | 0 | 108 | 0 | 33 | 8 | 105 | 148 | 0 | 0 | 0 | 1224 | 0 | 51 | 123 | 185 | 0 | 225 | 340 | 42 | 195 | 13 | 92 | 35 | 200 | 39 | 19 | 104 | 44 | 52.2 | 0 | 44 | 310 | 320 | 343 | 33 | 30 | 0 | 8 | 0 | 83 | 30 | 0 | 18 | 167 | 52.5 | 90 | 163 | 28 | 0 | 0 | 2 | 8950.7 | 759 | 124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1069 | 87 | 761 | 0 | 0 | 0 | 113 | 0 | 87 | 113 | 0 | 8 | 0 | 30 | 0 | 136 | 0 | 136 | 0 | 138 | 0 | 414 | 0 | 0 | 190 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 11 | 127 | 220 | 0 | 105 | 1244 | 108 | 6533 | 15483.7 | 96.23
01:00 | 8 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 320 | 35 | 28 | 113 | 95 | 60 | 15 | 35 | 144 | 68 | 450 | 139 | 470 | 0 | 35 | 92 | 0 | 0 | 0 | 160 | 13 | 14 | 0 | 440 | 0 | 30 | 0 | 0 | 9 | 65 | 46 | 0 | 88 | 12 | 0 | 172 | 80 | 42 | 0 | 108 | 0 | 24 | 8 | 68 | 149 | 0 | 0 | 0 | 1224 | 0 | 51 | 125 | 185 | 0 | 226 | 340 | 43 | 182 | 13 | 93 | 30 | 200 | 10 | 19 | 104 | 42 | 52.2 | 0 | 44 | 300 | 320 | 341 | 33 | 30 | 0 | 8 | 0 | 80 | 30 | 0 | 18 | 167 | 53 | 64 | 120 | 28 | 0 | 0 | 0 | 8695.2 | 733 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1014 | 87 | 767 | 0 | 43 | 0 | 113 | 0 | 87 | 113 | 11 | 9 | 0 | 30 | 19.91 | 132 | 0 | 133 | 0 | 136 | 0 | 300 | 0 | 0 | 190 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 265 | 9 | 100 | 220 | 0 | 120 | 1244 | 108 | 6428.91 | 15124.11 | 96.24
02:00 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 320 | 35 | 28 | 113 | 62 | 30 | 0 | 35 | 144 | 68 | 450 | 140 | 400 | 0 | 35 | 0 | 0 | 0 | 0 | 160 | 13 | 14 | 0 | 400 | 0 | 15 | 0 | 0 | 0 | 33 | 46 | 0 | 88 | 12 | 0 | 172 | 51 | 42 | 0 | 35 | 0 | 19.2 | 8 | 51 | 148 | 0 | 0 | 0 | 1225 | 0 | 51 | 127 | 185 | 0 | 223 | 340 | 42 | 199 | 13 | 77 | 30 | 200 | 9 | 19 | 104 | 42 | 52.2 | 0 | 43 | 305 | 320 | 315 | 33 | 30 | 0 | 8 | 0 | 80 | 30 | 0 | 18 | 167 | 54 | 64 | 121 | 31 | 0 | 0 | 0 | 8208.4 | 733 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 984 | 87 | 762 | 0 | 43 | 0 | 113 | 0 | 87 | 113 | 18 | 34 | 0 | 30 | 0 | 132 | 0 | 132 | 0 | 136 | 0 | 300 | 0 | 0 | 190 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 10 | 100 | 220 | 0 | 117 | 1244 | 108 | 6417 | 14625.4 | 96.24
03:00 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 320 | 35 | 28 | 90 | 32 | 0 | 0 | 35 | 144 | 67 | 450 | 138 | 480 | 0 | 35 | 0 | 0 | 0 | 0 | 160 | 13 | 14 | 0 | 480 | 0 | 15 | 0 | 0 | 4 | 33 | 46 | 0 | 88 | 12 | 0 | 172 | 30 | 42 | 0 | 0 | 0 | 19 | 8 | 51 | 149 | 0 | 0 | 0 | 1224 | 0 | 51 | 127 | 185 | 0 | 227 | 340 | 44 | 201 | 13 | 73 | 30 | 200 | 8 | 19 | 104 | 42 | 52.2 | 0 | 44 | 315 | 320 | 315 | 33 | 30 | 0 | 8 | 0 | 84 | 30 | 0 | 18 | 167 | 54.5 | 64 | 121 | 32 | 0 | 0 | 0 | 8266.7 | 733 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1011 | 87 | 763 | 0 | 43 | 0 | 113 | 0 | 0 | 35 | 20 | 52 | 0 | 30 | 0 | 132 | 0 | 133 | 0 | 136 | 0 | 300 | 0 | 0 | 190 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 10 | 100 | 220 | 0 | 117 | 1244 | 108 | 6301 | 14567.7 | 96.25
04:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 35 | 20 | 34 | 32 | 0 | 0 | 35 | 144 | 55 | 450 | 139 | 583 | 0 | 35 | 0 | 0 | 0 | 0 | 160 | 13 | 14 | 0 | 560 | 0 | 15 | 0 | 0 | 2 | 33 | 46 | 0 | 88 | 12 | 0 | 172 | 17 | 42 | 0 | 0 | 0 | 19 | 8 | 51 | 149 | 0 | 0 | 0 | 1224 | 0 | 51 | 128 | 185 | 0 | 231 | 340 | 45 | 180 | 12 | 74 | 30 | 200 | 10 | 19 | 89 | 40 | 52.2 | 0 | 44 | 310 | 320 | 302 | 33 | 30 | 0 | 8 | 0 | 83 | 30 | 0 | 18 | 167 | 54.5 | 65 | 122 | 30 | 0 | 0 | 2 | 7912.7 | 876 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1015 | 87 | 765 | 0 | 43 | 0 | 113 | 0 | 0 | 0 | 20 | 25 | 0 | 30 | 0 | 132 | 0 | 133 | 0 | 136 | 0 | 330 | 0 | 0 | 190 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 264 | 10 | 100 | 220 | 0 | 117 | 1244 | 108 | 6402 | 14314.7 | 96.25
05:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 35 | 28 | 20 | 32 | 0 | 0 | 35 | 144 | 36 | 450 | 139 | 583 | 0 | 35 | 0 | 0 | 0 | 0 | 108 | 13 | 14 | 0 | 584 | 0 | 15 | 0 | 0 | 12 | 33 | 46 | 0 | 88 | 12 | 0 | 132 | 17 | 42 | 0 | 0 | 0 | 19 | 8 | 51 | 150 | 0 | 0 | 0 | 1055 | 0 | 51 | 130 | 185 | 0 | 14 | 340 | 46 | 197 | 12 | 73 | 30 | 200 | 9 | 19 | 89 | 40 | 52.2 | 0 | 44 | 310 | 320 | 361 | 33 | 30 | 0 | 8 | 0 | 83 | 30 | 0 | 18 | 167 | 54 | 65 | 122 | 30 | 0 | 0 | 12 | 7537.2 | 876 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1094 | 87 | 767 | 0 | 43 | 0 | 113 | 0 | 0 | 0 | 20 | 0 | 0 | 30 | 0 | 132 | 0 | 132 | 0 | 135 | 0 | 370 | 0 | 0 | 190 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 11 | 128 | 220 | 0 | 151 | 1244 | 17 | 6446 | 13983.2 | 96.26
06:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 35 | 0 | 16 | 16 | 0 | 0 | 0 | 90 | 16 | 450 | 142 | 583 | 0 | 0 | 0 | 0 | 0 | 1 | 90 | 13 | 14 | 0 | 584 | 0 | 15 | 0 | 0 | 15 | 0 | 38 | 0 | 88 | 12 | 0 | 132 | 17 | 42 | 0 | 0 | 0 | 19 | 0 | 51 | 149 | 0 | 0 | 0 | 1105 | 0 | 51 | 35 | 185 | 0 | 17 | 340 | 46 | 199 | 12 | 68 | 30 | 200 | 9 | 19 | 89 | 38 | 0 | 2 | 44 | 305 | 320 | 386 | 33 | 30 | 0 | 8 | 0 | 83 | 30 | 0 | 18 | 167 | 24 | 65 | 122 | 30 | 0 | 0.45 | 12 | 7145.45 | 876 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1075 | 0 | 754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2.89 | 131 | 0 | 132 | 0 | 135 | 0 | 370 | 0 | 0 | 190 | 48 | 115 | 2 | 110 | 0 | 0 | 0.5 | 11 | 0.04 | 0 | 279 | 10 | 128 | 220 | 0 | 206 | 1080 | 0 | 5992.43 | 13137.88 | 96.26
07:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 17 | 0 | 16 | 16 | 0 | 0 | 0 | 17 | 16 | 450 | 140 | 583 | 0 | 0 | 0 | 0 | 0 | 4 | 52 | 13 | 14 | 0 | 584 | 0 | 0 | 0 | 0 | 1 | 0 | 38 | 0 | 88 | 0 | 1 | 132 | 17 | 32 | 0 | 0 | 0 | 10 | 0 | 51 | 147 | 0 | 0 | 0 | 1070 | 0 | 51 | 8 | 185 | 0 | 23 | 340 | 45 | 197 | 12 | 73 | 30 | 200 | 9 | 19 | 89 | 40 | 0 | 14 | 44 | 315 | 320 | 386 | 33 | 30 | 0 | 8 | 0 | 83 | 30 | 0 | 18 | 163 | 0 | 65 | 122 | 30 | 0 | 0.84 | 12 | 6918.84 | 876 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1127 | 0 | 757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 6 | 130 | 0 | 132 | 0 | 139 | 0 | 370 | 0 | 0 | 190 | 48 | 115 | 6 | 113 | 0 | 0 | 1.8 | 34 | 0.22 | 0 | 279 | 10 | 128 | 220 | 0 | 217 | 990 | 0 | 6011.02 | 12929.86 | 96.27
08:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 16 | 450 | 140 | 583 | 0 | 0 | 0 | 0 | 0 | 11 | 52 | 13 | 14 | 0 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 88 | 0 | 1 | 132 | 17 | 3 | 0 | 0 | 0 | 0 | 0 | 51 | 147 | 0 | 0 | 0 | 901 | 0 | 51 | 0 | 185 | 0 | 29 | 340 | 45 | 199 | 11 | 74 | 30 | 170 | 9 | 19 | 88 | 38 | 0 | 48 | 0 | 320 | 320 | 372 | 33 | 30 | 0 | 8 | 0 | 83 | 30 | 0 | 18 | 163 | 0 | 65 | 122 | 30 | 0 | 0.67 | 12 | 6629.67 | 874 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 1181 | 0 | 739.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 11.86 | 123 | 0 | 125 | 0 | 140 | 0 | 370 | 0 | 0 | 190 | 48 | 115 | 13 | 113 | 0 | 0 | 3.6 | 92 | 0.25 | 0 | 279 | 9 | 128 | 220 | 0 | 222 | 985 | 0 | 6160.02 | 12789.69 | 96.27
09:00 | 0 | 50 | 4 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 16 | 450 | 144 | 583 | 0 | 0 | 0 | 0 | 0 | 13 | 70 | 13 | 14 | 0 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 60 | 0 | 2 | 172 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 145 | 0 | 0 | 0 | 907 | 2 | 43 | 0 | 185 | 0 | 112 | 340 | 46 | 200 | 11 | 74 | 30 | 170 | 9 | 19 | 88 | 36 | 0 | 57 | 0 | 315 | 320 | 385 | 36 | 30 | 0 | 0 | 0 | 80 | 30 | 0 | 18 | 164 | 0 | 65 | 122 | 27 | 1 | 0 | 12 | 6721 | 875 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 1172 | 0 | 742.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 13.47 | 134 | 0 | 124 | 0 | 86 | 0 | 300 | 0 | 0 | 190 | 48 | 70 | 21 | 113 | 0 | 0 | 4.7 | 102 | 0.53 | 0 | 279 | 11 | 120 | 220 | 0 | 223 | 1000 | 0 | 5993.07 | 12714.07 | 96.28
10:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 16 | 450 | 146 | 583 | 0 | 0 | 0 | 0 | 0 | 16 | 70 | 13 | 14 | 0 | 584 | 0 | 0 | 0 | 0 | 2 | 0 | 38 | 0 | 60 | 0 | 3 | 172 | 17 | 3 | 0 | 0 | 0 | 0 | 0 | 17 | 145 | 0 | 0 | 0 | 1092 | 7 | 43 | 0 | 185 | 0 | 138 | 340 | 47 | 194 | 11 | 74 | 27 | 170 | 9 | 19 | 88 | 36 | 0 | 60 | 0 | 315 | 320 | 371 | 36 | 30 | 0 | 0 | 0 | 81 | 30 | 0 | 18 | 164 | 0 | 65 | 121 | 11 | 0 | 0 | 12 | 6979 | 873 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 1172 | 0 | 739.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 13.8 | 138 | 0 | 126 | 0 | 0 | 0 | 300 | 0 | 1.26 | 190 | 48 | 50 | 19 | 108 | 0 | 0 | 5.6 | 174 | 0.68 | 0 | 277 | 9 | 120 | 220 | 0 | 222 | 990 | 0 | 6009.9 | 12988.9 | 96.28
11:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 9 | 0 | 34 | 16 | 0 | 0 | 0 | 17 | 16 | 450 | 146 | 540 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 13 | 14 | 0 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 60 | 0 | 5 | 172 | 17 | 5 | 0 | 0 | 0 | 0 | 0 | 17 | 145 | 0 | 0 | 0 | 1070 | 8 | 43 | 8 | 185 | 0 | 177 | 340 | 46 | 194 | 13 | 73 | 26 | 170 | 10 | 19 | 88 | 34 | 0 | 29 | 0 | 310 | 320 | 335 | 36 | 30 | 0 | 0 | 0 | 81 | 30 | 0 | 18 | 166 | 0 | 65 | 121 | 5 | 0 | 0.02 | 12 | 6824.02 | 874 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 1170 | 0 | 736.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 15.81 | 138 | 0 | 129 | 0 | 0 | 0 | 300 | 0 | 1.27 | 190 | 48 | 50 | 33 | 100 | 0 | 0 | 6.6 | 180 | 0.6 | 0 | 279 | 9 | 100 | 220 | 0 | 222 | 990 | 0 | 6029.04 | 12853.06 | 96.28
12:00 | 0 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 21 | 0 | 34 | 48 | 0 | 0 | 4 | 80 | 45 | 450 | 143 | 540 | 0 | 17 | 0 | 0 | 0 | 20 | 70 | 0 | 14 | 0 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 60 | 0 | 5 | 172 | 17 | 5 | 0 | 0 | 0 | 0 | 0 | 17 | 145 | 0 | 0 | 0 | 1100 | 9 | 43 | 21 | 185 | 0 | 330 | 340 | 44 | 199 | 15 | 63 | 26 | 179 | 17 | 19 | 88 | 38 | 1 | 78 | 11 | 310 | 320 | 345 | 35 | 30 | 0 | 8 | 0 | 81 | 30 | 0 | 16 | 166 | 0 | 65 | 122 | 5 | 1 | 0.77 | 12 | 7323.77 | 874 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 1190 | 0 | 739.69 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 17.71 | 138 | 0 | 127 | 0 | 0 | 0 | 350 | 0 | 1.63 | 194 | 47 | 90 | 15 | 110 | 0 | 0 | 2.2 | 33 | 0.81 | 0 | 278 | 9 | 100 | 220 | 0 | 222 | 1051 | 0 | 5981.04 | 13304.81 | 96.28
13:00 | 0 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 35 | 22 | 62 | 48 | 0 | 0 | 31 | 122 | 50 | 450 | 143 | 500 | 0 | 35 | 0 | 0 | 0 | 20 | 70 | 0 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 100 | 12 | 1 | 172 | 17 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 145 | 0 | 0 | 0 | 1080 | 13 | 43 | 61 | 175 | 0 | 346 | 340 | 45 | 195 | 20 | 72 | 27 | 180 | 9 | 19 | 68 | 42 | 16 | 62 | 38 | 310 | 320 | 366 | 35 | 30 | 0 | 8 | 0 | 84 | 30 | 0 | 16 | 166 | 17 | 62 | 122 | 0 | 1 | 2.99 | 5 | 7523.99 | 878 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 1201 | 0 | 733.45 | 0 | 0 | 0 | 48 | 5 | 24 | 0 | 0 | 0 | 85 | 0 | 19.91 | 136 | 0 | 125 | 0 | 0 | 0 | 250 | 0 | 1.95 | 194 | 48 | 108 | 33 | 110 | 0 | 0 | 8 | 146 | 0.76 | 0 | 278 | 8 | 120 | 220 | 0 | 222 | 1158 | 0 | 6261.07 | 13785.06 | 96.28
14:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 35 | 35 | 65 | 16 | 0 | 0 | 35 | 144 | 51 | 450 | 143 | 540 | 0 | 0 | 5 | 0 | 0 | 18 | 52 | 13 | 14 | 0 | 488 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 48 | 12 | 4 | 172 | 17 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 145 | 0 | 0 | 0 | 1090 | 18 | 43 | 100 | 185 | 0 | 340 | 340 | 45 | 201 | 17 | 74 | 27 | 181 | 23 | 19 | 101 | 44 | 16 | 63 | 44 | 315 | 320 | 336 | 35 | 30 | 0 | 8 | 0 | 82 | 30 | 0 | 16 | 166 | 17 | 66 | 124 | 0 | 1 | 11.95 | 2 | 7541.95 | 877 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 1222 | 0 | 726 | 0 | 0 | 0 | 112 | 5 | 49 | 0 | 12 | 0 | 78 | 0 | 20.64 | 133 | 0 | 125 | 0 | 0 | 0 | 250 | 0 | 1.97 | 194 | 48 | 106 | 19 | 110 | 0 | 0 | 4.6 | 139 | 0.75 | 0 | 278 | 10 | 120 | 180 | 0 | 222 | 1190 | 0 | 6359.96 | 13901.91 | 96.28
15:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 35 | 35 | 34 | 16 | 0 | 0 | 35 | 144 | 51 | 450 | 142 | 540 | 0 | 0 | 1 | 0 | 0 | 12 | 52 | 13 | 14 | 0 | 518 | 0 | 0 | 0 | 0 | 10 | 0 | 38 | 0 | 48 | 12 | 3 | 172 | 17 | 4 | 0 | 0 | 0 | 0 | 0 | 17 | 145 | 0 | 0 | 0 | 1135 | 10 | 43 | 100 | 175 | 0 | 336 | 340 | 44 | 210 | 23 | 73 | 30 | 175 | 26 | 19 | 101 | 42 | 43 | 50 | 43 | 320 | 320 | 385 | 33 | 30 | 0 | 8 | 0 | 83 | 30 | 0 | 16 | 166 | 17 | 56 | 122 | 0 | 1 | 9.3 | 1 | 7645.3 | 877 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 1234.2 | 0 | 767 | 0 | 0 | 0 | 113 | 15 | 49 | 0 | 28 | 0 | 62 | 0 | 19.44 | 133 | 0 | 125 | 0 | 0 | 0 | 250 | 0 | 1.72 | 200 | 48 | 105 | 22 | 110 | 0 | 0 | 3.6 | 148 | 0.55 | 0 | 284 | 10 | 120 | 220 | 0 | 230 | 1200 | 0 | 6480.51 | 14125.81 | 96.28
16:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 35 | 35 | 34 | 95 | 0 | 0 | 17 | 108 | 51 | 450 | 141 | 540 | 0 | 0 | 21 | 0 | 0 | 7 | 52 | 13 | 14 | 0 | 478 | 0 | 0 | 0 | 0 | 13 | 0 | 38 | 0 | 70 | 36 | 1 | 172 | 17 | 4 | 16 | 0 | 0 | 0 | 0 | 17 | 146 | 0 | 0 | 0 | 1110 | 3 | 43 | 70 | 175 | 0 | 342 | 340 | 44 | 194 | 24 | 73 | 35 | 177 | 27 | 19 | 85 | 42 | 52.2 | 34 | 43 | 315 | 320 | 367 | 33 | 30 | 0 | 8 | 0 | 80 | 30 | 0 | 16 | 166 | 17 | 84 | 0 | 0 | 1 | 12.54 | 0 | 7473.74 | 877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 1206 | 0 | 921 | 0 | 0 | 0 | 50 | 17 | 49 | 0 | 28 | 0 | 43 | 12 | 20.59 | 133 | 0 | 125 | 0 | 0 | 0 | 250 | 0 | 1.99 | 200 | 48 | 50 | 11 | 70 | 0 | 0 | 0 | 85 | 0.44 | 0 | 277 | 10 | 120 | 220 | 0 | 302 | 1200 | 0 | 6375.02 | 13848.76 | 96.28
17:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 17 | 35 | 34 | 95 | 0 | 0 | 17 | 35 | 51 | 450 | 143 | 400 | 0 | 0 | 184 | 0 | 0 | 3 | 52 | 15 | 14 | 0 | 400 | 0 | 0 | 0 | 0 | 24 | 0 | 38 | 0 | 100 | 62 | 1 | 172 | 17 | 10 | 80 | 0 | 0 | 0 | 0 | 17 | 146 | 0 | 0 | 0 | 1060 | 5 | 51 | 0 | 180 | 0 | 342 | 340 | 45 | 195 | 27 | 87 | 50 | 174 | 28 | 19 | 86 | 38 | 52.2 | 17 | 43 | 310 | 320 | 291 | 33 | 30 | 0 | 8 | 0 | 83 | 30 | 0 | 16 | 166 | 17 | 73 | 110 | 0 | 0 | 8.32 | 0 | 7368.52 | 877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1226 | 0 | 1112 | 0 | 0 | 0 | 0 | 17 | 49 | 0 | 28 | 0 | 24 | 30 | 9.15 | 134 | 0 | 128 | 0 | 0 | 0 | 300 | 0 | 0.89 | 200 | 48 | 50 | 0 | 50 | 0 | 0 | 0.2 | 21 | 0.1 | 0 | 277 | 9 | 100 | 0 | 0 | 301 | 1200 | 0 | 6206.34 | 13574.86 | 96.29
18:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 17 | 35 | 34 | 93 | 0 | 0 | 17 | 35 | 51 | 300 | 133 | 250 | 0 | 0 | 310 | 0 | 0 | 2 | 52 | 16 | 14 | 0 | 406 | 15 | 0 | 0 | 0 | 15 | 33 | 38 | 0 | 100 | 72 | 0 | 172 | 34 | 12 | 85 | 0 | 0 | 0 | 2 | 33 | 146 | 0 | 0 | 0 | 867 | 1 | 51 | 0 | 127 | 0 | 300 | 280 | 45 | 187 | 27 | 90 | 50 | 164 | 44 | 19 | 104 | 32 | 52.2 | 4 | 44 | 310 | 320 | 291 | 33 | 30 | 0 | 8 | 0 | 83 | 30 | 0 | 16 | 165 | 17 | 74 | 108 | 0 | 0 | 2.89 | 6 | 6898.09 | 877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.51 | 990 | 8 | 1210 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 28 | 0 | 12 | 30 | 3.84 | 137 | 0 | 132 | 0 | 0 | 0 | 300 | 0 | 0.36 | 200 | 48 | 50 | 0 | 50 | 0 | 0 | 0.2 | 4 | 0.02 | 0 | 214 | 9 | 110 | 0 | 0 | 302 | 1000 | 0 | 5793.93 | 12692.02 | 96.29
19:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 24 | 38 | 34 | 93 | 21 | 0 | 35 | 100 | 55 | 400 | 135 | 200 | 0 | 0 | 326 | 0 | 0 | 0 | 125 | 16 | 14 | 0 | 350 | 17 | 0 | 0 | 0 | 6 | 63 | 60 | 0 | 100 | 100 | 0 | 172 | 39 | 20 | 150 | 0 | 0 | 1 | 8 | 38 | 146 | 0 | 0 | 0 | 1095 | 0 | 51 | 8 | 177 | 0 | 319 | 295 | 45 | 203 | 27 | 90 | 70 | 170 | 47 | 19 | 104 | 46 | 52.2 | 0 | 42 | 315 | 320 | 344 | 33 | 30 | 0 | 8 | 0 | 84 | 30 | 0 | 16 | 166 | 17 | 87 | 162 | 0 | 0 | 0 | 12 | 7837.2 | 845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 15 | 1270 | 0 | 0 | 0 | 11 | 17 | 88 | 0 | 35 | 0 | 0 | 30 | 0 | 143 | 0 | 138 | 0 | 0 | 0 | 350 | 0 | 0 | 200 | 49 | 90 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 10 | 120 | 0 | 0 | 354 | 990 | 0 | 6248 | 14085.2 | 96.3
19:30 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 35 | 54 | 68 | 123 | 30 | 0 | 35 | 144 | 68 | 400 | 136 | 200 | 0 | 0 | 330 | 0 | 0 | 0 | 160 | 16 | 14 | 0 | 323 | 17 | 0 | 0 | 0 | 12 | 67 | 70 | 0 | 100 | 100 | 0 | 172 | 51 | 23 | 153 | 0 | 0 | 18 | 8 | 68 | 147 | 0 | 0 | 0 | 1150 | 0 | 51 | 100 | 178 | 0 | 347 | 340 | 45 | 181 | 27 | 93 | 70 | 180 | 47 | 19 | 104 | 44 | 52.2 | 0 | 42 | 305 | 320 | 348 | 33 | 30 | 0 | 8 | 0 | 83 | 30 | 0 | 16 | 166 | 17 | 93 | 162 | 0 | 0 | 0 | 12 | 8287.2 | 830 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1190 | 25 | 1346 | 0 | 0 | 0 | 35 | 17 | 93 | 0 | 36 | 0 | 0 | 30 | 0 | 156 | 0 | 143 | 0 | 0 | 0 | 350 | 0 | 0 | 200 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 264 | 10 | 110 | 0 | 0 | 398 | 1210 | 0 | 6720 | 15007.2
20:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 35 | 54 | 62 | 126 | 30 | 0 | 46 | 144 | 68 | 400 | 132 | 200 | 0 | 0 | 330 | 0 | 0 | 0 | 160 | 18 | 14 | 0 | 323 | 17 | 0 | 0 | 0 | 10 | 67 | 69 | 0 | 100 | 100 | 0 | 172 | 68 | 26 | 155 | 0 | 0 | 18 | 12 | 68 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 93 | 185 | 0 | 347 | 340 | 46 | 192 | 27 | 95 | 70 | 181 | 47 | 19 | 104 | 40 | 52.2 | 0 | 43 | 310 | 320 | 343 | 33 | 30 | 0 | 8 | 0 | 84 | 30 | 0 | 16 | 166 | 17 | 83 | 166 | 0 | 0 | 0 | 12 | 8409.2 | 830 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 30 | 1411 | 0 | 0 | 0 | 35 | 17 | 94 | 0 | 37 | 0 | 0 | 30 | 0 | 156 | 0 | 144 | 0 | 0 | 0 | 300 | 0 | 0 | 200 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 11 | 120 | 0 | 0 | 395 | 1210 | 0 | 6773 | 15182.2 | 96.3
21:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 54 | 54 | 68 | 127 | 30 | 0 | 35 | 144 | 67 | 420 | 146 | 200 | 0 | 0 | 328 | 0 | 0 | 0 | 160 | 16 | 14 | 0 | 388 | 17 | 0 | 0 | 0 | 8 | 67 | 70 | 0 | 100 | 100 | 0 | 172 | 68 | 22 | 155 | 0 | 0 | 19 | 12 | 68 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 130 | 185 | 0 | 344 | 340 | 46 | 202 | 24 | 99 | 70 | 181 | 47 | 19 | 103 | 46 | 52.2 | 0 | 43 | 310 | 320 | 387 | 33 | 30 | 0 | 6 | 0 | 84 | 30 | 0 | 16 | 166 | 17 | 83 | 167 | 0 | 0 | 0 | 12 | 8620.2 | 789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 52 | 1443.43 | 0 | 0 | 0 | 35 | 17 | 94 | 0 | 37 | 0 | 0 | 30 | 0 | 158 | 0 | 153 | 0 | 0 | 0 | 300 | 0 | 0 | 200 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 11 | 120 | 0 | 0 | 395 | 1244 | 0 | 6867.63 | 15487.83 | 96.31
22:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 54 | 54 | 68 | 127 | 30 | 0 | 35 | 144 | 67 | 420 | 185 | 200 | 0 | 0 | 318 | 0 | 0 | 0 | 160 | 16 | 14 | 0 | 390 | 17 | 0 | 0 | 0 | 5 | 67 | 70 | 0 | 100 | 100 | 0 | 172 | 68 | 23 | 156 | 0 | 0 | 19 | 14 | 68 | 148 | 0 | 0 | 0 | 1224 | 0 | 51 | 133 | 185 | 0 | 349 | 340 | 46 | 196 | 24 | 96 | 70 | 181 | 47 | 19 | 103 | 42 | 52.2 | 0 | 45 | 315 | 320 | 390 | 33 | 30 | 0 | 8 | 0 | 84 | 30 | 0 | 16 | 166 | 17 | 83 | 159 | 0 | 0 | 0 | 12 | 8659.2 | 782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1222 | 54 | 1448.17 | 0 | 0 | 0 | 35 | 17 | 94 | 0 | 37 | 0 | 0 | 30 | 0 | 160 | 0 | 158 | 0 | 0 | 0 | 300 | 0 | 0 | 200 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 11 | 120 | 0 | 0 | 396 | 1244 | 0 | 6862.17 | 15521.37 | 96.31
23:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 54 | 54 | 68 | 127 | 30 | 0 | 55 | 144 | 67 | 420 | 294 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 160 | 16 | 14 | 0 | 470 | 17 | 0 | 0 | 0 | 9 | 65 | 71 | 0 | 100 | 100 | 0 | 172 | 68 | 23 | 155 | 0 | 0 | 19 | 14 | 68 | 148 | 0 | 0 | 0 | 1224 | 0 | 51 | 133 | 185 | 0 | 348 | 340 | 46 | 197 | 27 | 96 | 70 | 181 | 47 | 19 | 103 | 30 | 52.2 | 0 | 45 | 320 | 320 | 386 | 33 | 30 | 0 | 8 | 0 | 84 | 30 | 0 | 16 | 167 | 17 | 83 | 159 | 0 | 0 | 0 | 12 | 8669.2 | 782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1227 | 54 | 1462.69 | 0 | 0 | 0 | 35 | 17 | 95 | 0 | 35 | 0 | 0 | 30 | 0 | 162 | 0 | 172 | 0 | 0 | 0 | 350 | 0 | 0 | 200 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 11 | 120 | 0 | 0 | 396 | 1244 | 0 | 6948.69 | 15617.89 | 96.32
Total KWH | 11376 | 1820160 | 595680 | 0 | 0 | 0 | 0 | 0 | 8694000 | 0 | 1106950 | 718920 | 666000 | 1216656 | 1494240 | 304353 | 23724 | 653474 | 2351520 | 1106880 | 9888000 | 3632495 | 10224160 | 0 | 230974 | 2392.84 | 0 | 0 | 142923 | 2512800 | 314400 | 338040 | 0 | 11546818.18 | 140509 | 140509 | 0 | 0 | 151680 | 625451 | 1121040 | 0 | 2024640 | 870720 | 22285 | 3977580 | 934214 | 550080 | 930909.09 | 205745 | 0 | 236160 | 118920.6 | 1109018 | 3538655 | 0 | 0 | 0 | 26650906 | 69255 | 1115960 | 1838327 | 4282182 | 0 | 6088700 | 8142000 | 1079040 | 4812000 | 438192 | 1960320 | 949500 | 4413600 | 556920 | 434990 | 2270880 | 957120 | 830832 | 512691 | 813728 | 7605000 | 7656900 | 8944000 | 797000 | 686400 | 0 | 156528 | 0 | 1907520 | 707616 | 0 | 416000 | 3438960 | 519840 | 1701600 | 2935200 | 268800 | 6000 | 54220 | 188400 | 182502178.71 | 20313454 | 1296000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224064 | 619200 | 27490900 | 731520 | 23012000 | 0 | 222230 | 0 | 1256064 | 153895 | 962016 | 346560 | 361390 | 114912 | 660370 | 354710 | 180000 | 3372636 | 0 | 3475782 | 0 | 1258727 | 0 | 7672800 | 0 | 15660 | 4742000 | 1093963 | 2378707 | 201569 | 2502316 | 0 | 0 | 39093.72 | 1218240 | 4710 | 0 | 6589000 | 231477 | 2742000 | 3701860 | 0 | 5941224 | 27226181.82 | 492000 | 153199231.54 | 335701410.25

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 14-06-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13304.81 | MW | 12:00 Hr. | Energy Generated |  |  | 335.7014 |  | MKWHr.
| Day Peak Demand |  |  | 13304.81 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.388 |  | MKWHr.
| Evening Peak Generation |  |  | 15487.83 | MW | 21:00 Hr. | Energy Demand |  |  | 337.0894 |  | MKWHr.
| Evening Peak Demand |  |  | 15487.83 | MW | 21:00 Hr. | Maximum Temperature |  |  | 32.7 |  | °C
| Minimum Generation of the Day |  |  | 12714.07 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 972.96 |  | MMCFD
| Maximum Generation of the Day |  |  | 15617.89 | MW | 23:00 Hr. | Production Cost per KWHr |  |  | 6.9226 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 45.7473 | 0 | 13.7068 | 0 | 0 | 0.14292 | 0 | 0 | 59.5969 | Gas | 133.5146 | Gas | 470397430.1838
| Chattogram Zone |  |  | 4.0887 | 27.5818 | 7.5269 | 0 | 3.9776 | 0.09154 | 0 | 0.15168 | 43.4183 | Coal | 100.6651 | Coal | 657212499.0794
| Cumilla Zone |  |  | 27.3426 | 0 | 12.6846 | 0 | 0 | 0.51269 | 0.95712 | 0 | 41.497 | HFO | 49.3637 | HFO | 911401821.122
| Mymensingh Zone |  |  | 0.2688 | 0 | 5.345 | 0 | 0 | 0.06022 | 0 | 0 | 5.6741 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 32.3159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.3159 | Hydro | 3.9776 | Hydro | 397758
| Khulna Zone |  |  | 1.296 | 27.4909 | 0.95558 | 0 | 0 | 0.6192 | 20.3135 | 0 | 50.6751 | Solar | 3.7462 | Solar | 60081968.9492
| Barishal Zone |  |  | 6.6753 | 39.7564 | 0.492 | 0 | 0 | 0.00471 | 0 | 0 | 46.9285 | Import | 44.2826 | Import | 222211252.12
| Rajshahi Zone |  |  | 15.7799 | 0 | 3.7718 | 0 | 0 | 0.85603 | 23.012 | 0 | 43.4198 | Wind | 0.15168 | Wind | 2220595.2
| Rangpur Zone |  |  | 0 | 5.836 | 4.881 | 0 | 0 | 1.4589 | 0 | 0 | 12.1759
| Total |  |  | 133.5146 | 100.6651 | 49.3637 | 0 | 3.9776 | 3.7462 | 44.2826 | 0.15168 | 335.7014
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 470397430.1838 |  | Hydro | 397758
|  |  |  | Coal | 657212499.0794 |  | Solar | 60081968.9492
|  |  |  | HFO | 911401821.122 |  | Import | 222211252.12
|  |  |  | HSD | 0 |  | Wind | 2220595.2
[5 empty] | Total: | 232,39,23,324 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 297054.54 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.3135 | Peak Hr Flow | 789.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 31579127.28 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 23.012 | Peak Hr Flow | 1443.43 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 524 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.95712 | Peak Hr Flow | 46.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 588 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 44.2826 | Peak Hr Flow | 2278.43 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4702
|  |  |  | Chattogram |  | 0 |  | 1430
|  |  |  | Cumilla |  | 0 |  | 1563
|  |  |  | Mymensingh |  | 0 |  | 1260
|  |  |  | Sylhet |  | 0 |  | 680
|  |  |  | Khulna |  | 0 |  | 1945
|  |  |  | Barishal |  | 0 |  | 525
|  |  |  | Rajshahi |  | 0 |  | 1718
|  |  |  | Rangpur |  | 0 |  | 1060
|  |  |  | Total |  | 0 |  | 14883
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Nababganj 55 MW PP (Southern power ) |  |  | 55
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
[7 empty] | 4 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 5 | Bheramara 410 MW CCPP GT |  |  | 278
[7 empty] | 6 | Bheramara 410 MW CCPP ST |  |  | 132
[7 empty] | 7 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[5 empty] | Total | 300 |  |  |  | Total | 941
|  |  |  | Total Unavailable Capacity |  |  |  | 1241
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:03 | 08:35 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing OC/EF relays Due to PBS BCIC Feeder Trip
| 08:08 |  | Ashugonj North 360 MW ST was sync.
| 08:50 | 20:55 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Scheduled S/D Due to Replacement of Jack BUS (PTR-02) | [7 empty] | 38.0MW load interrup.
| 08:51 | 20:53 | Sreepur 230/132/33kV S/S 132/33 kV T-2 HT Scheduled S/D Due to Replacement of Jack BUS (PTR-02)
|  | 08:57 | Borhanuddin 230/33kV S/S Tr-Load HT is restored.
|  | 08:58 | Borhanuddin 230/33kV S/S Tr-Load LT is restored.
| 09:14 |  | Sirajgonj 225MW CCPP Unit-3 Shutdown with remarks:- ST
| 09:21 |  | Sirajgonj Unit-3 was forced shutdown due to gas shortage.
| 09:21 |  | Sirajgonj 225MW CCPP Unit-3 Shutdown with remarks:- GT
| 10:09 | 10:20 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing Over current Earth Fault Relay relays
Due to Bad Weather
| 10:40 | 11:14 | Saidpur 132/33kV S/S TR-3 (424T) LT Forced S/D Due to Red hot of 33kv Capacitor Bus DS | [7 empty] | 20.0MW load interrup.
| 10:41 | 11:13 | Saidpur 132/33kV S/S TR-3 (424T) HT Forced S/D
| 11:02 | 17:17 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT Scheduled S/D Due to | [7 empty] | 6.0MW load interrup.
Redhot Maintenance.
| 11:03 | 17:14 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) HT Scheduled S/D Due to
Redhot Maintenance.
| 11:05 | 13:33 | Aminbazar-Mirpur 132kV Ckt-2 Scheduled S/D from Mirpur 132/33kV end.
| 11:36 | 12:01 | Halishahar-Khulshi 132kV Ckt-1 Scheduled S/D from Halishahar 132/33kV end.
| 11:37 | 12:00 | Rampur 230/132/33 S/S Halishahar-1 Scheduled S/D Due to Energy meter change
| 12:00 |  | Day Peak Generation: 13301 MW.
| 13:14 | 13:51 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing Lockout Relay relays.
| 13:14 | 13:44 | Shahjibazar 132/33kV S/S TR-02 HT Tripped showing Lockout Relay relays.
| 13:28 |  | Siddhirganj CCPP 335 MW GT was sync.
| 14:13 | 23:30 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) LT Scheduled S/D Due to Red | [7 empty] | 50.0MW load
|  |  | hot mainteance in pbs section. | [7 empty] | interrup.
| 14:16 | 14:24 | Mirpur-Uttara 132kV Ckt-1 Tripped from Mirpur 132/33kV end showing ABB REF 615 relays | [7 empty] | 80.0MW load
|  |  | Due to Tripped due to fault. Relay shows overcurrent signal. | [7 empty] | interrup. Mirpur
132/33kV end
| 14:42 |  | Adani Power Jharkhand Ltd. Unit-1 synchronized.
| 15:56 |  | Matarbari 2*600 MW (CPGCBL) Synchronized
| 16:43 |  | Bhola Nutan Biddut BD LTD Tripped with remarks:- GT 12
| 16:44 |  | Bhola Nutan Biddut BD LTD GT-2 Tripped with remarks:- None
| 17:11 |  | Raozan 25 MW PP Synchronized
| 17:57 | 18:30 | Bhangura 132/33kV S/S Tr-1(403T) LT Tripped showing O/C and E/F Relay P14D relays. | [7 empty] | 15.0MW load
interrup.
| 17:57 | 18:32 | Bhangura 132/33kV S/S Tr-2(413T) LT Tripped showing O/C and E/F Relay P14D relays. | [7 empty] | 15.0MW load
interrup.
| 20:35 | 23:05 | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) LT Forced S/D Due to For red-hot maintenance | [7 empty] | 50.0MW load
interrup.
| 20:36 | 23:04 | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) HT Forced S/D Due to For red-hot maintenance | [7 empty] | 50.0MW load
| 20:42 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- GT2
| 20:42 |  | Meghnaghat CCPP(Summit) GT-2 Synchronized with remarks:- GT-2 synched as per demand of NLDC
| 21:00 |  | Evening peak generation = 15487 MW
| 21:40 | 23:29 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT Scheduled S/D Due to Red | [7 empty] | 50.0MW load
|  |  | hot mainteance in pbs section. | [7 empty] | interrup.
| 22:04 |  | Meghnaghat CCPP(Summit)-2 Shutdown with remarks:- ST
| 22:08 |  | Summit Meghnaghat-2 589 MW CCPP was shut down.
| 22:08 |  | Meghnaghat CCPP(Summit)-2 Shutdown with remarks:- GT
| 00:19 |  | Bhola Nutan Biddut BD LTD Synchronized
| 02:49 |  | Bhola Notun Bidyut CCPP ST was sync.
| 06:05 |  | Raozan 25 MW PP Tripped
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 14-06-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 356 | 8694000 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9888000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 146 | 3632495 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 23724 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 328 | 2392.84 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 11376 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 718920 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 127 | 1494240 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 653474 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 230974 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 16 | 314400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 338040 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 33 | 595680 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 30 | 304353 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 68 | 1216656 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1820160 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 67 | 1106880 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 2351520 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 142923 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 666000 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 388 | 11546818.18 | None
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 200 | 10224160 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 1106950 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 160 | 2512800 | -
Dhaka Area Total |  |  |  |  | 5939.724 | 2728 | 59596936.02
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 12 | 118920.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 69255 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 236160 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 172 | 3977580 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 147 | 3538655 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 68 | 1109018 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 70 | 1121040 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 67 | 625451 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 2024640 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 22 | 550080 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22285 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 140509 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 68 | 934214 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 870720 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 140509 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 205745 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 26650906 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 8 | 151680 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 155 | 930909.09 | U1 S/D 25/Mar/25 & U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4895.72 | 2249 | 43418276.69
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 202 | 4812000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 344 | 6088700 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 8142000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 24 | 438192 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 46 | 1079040 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 185 | 4282182 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1115960 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 130 | 1838327 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 43 | 813728 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 949500 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 181 | 4413600 | -
| Import (Tripura) |  | Import | 0 | 160 | 46 | 957120 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 830832 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 434990 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 103 | 2270880 | Machine Problem
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 47 | 556920 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 99 | 1960320 | Machine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 512691 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1982.2 | 41496982
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 268800 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 6000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 167 | 2935200 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 83 | 1701600 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 54220 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 188400 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 519840 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 279 | 5674060
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 33 | 797000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 686400 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Borescope Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 707616 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1907520 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 166 | 3438960 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 416000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 6 | 156528 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7605000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 387 | 8944000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7656900 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1382 | 32315924
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 789 | 20313454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 1296000 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 52 | 731520 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 224064 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 619200 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1234.2 | 27490900 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2075.2 | 50675138
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 395 | 5941224 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 11 | 231477 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2742000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 27226181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 0 | 3701860 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 492000 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 278 | 6589000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4710 | -
Barishal Area Total |  |  |  |  | 2236 | 2048 | 46928452.82
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 222230 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 17 | 153895 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 361390 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 158 | 3372636 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 153 | 3475782 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 1258727 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 300 | 7672800 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 354710 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 114912 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 962016 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 1256064 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 346560 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 15660 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1443.43 | 23012000 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 180000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 660370 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2267.43 | 43419752
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 49 | 1093963 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4742000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 2502316 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 39093.72 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2378707 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 201569 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1218240 | -
Rangpur Area Total |  |  |  |  | 950 | 477 | 12175888.72
Eastern Grid Total |  |  |  |  | 16705.895 | 8620.2 | 182502178.71
Western Grid Total |  |  |  |  | 10378.16 | 6867.63 | 153199231.54
National Grid Total |  |  |  |  | 27084.055 | 15487.83 | 335701410.25
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 14-06-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9634.64 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5248 | MW
i) Dhaka area |  |  | 4702.06 |  | MW | i) Khulna area |  |  |  | 1945 | MW
ii) Chattogram area |  |  | 1429.5 |  | MW | ii) Barishal area |  |  |  | 525 | MW
iii) Cumilla area |  |  | 1563.08 |  | MW | iii) Rajshahi area |  |  |  | 1718 | MW
iv) Mymensingh area |  |  | 1260 |  | MW | iv) Rangpur area |  |  |  | 1060 | MW
v) Sylhet area |  |  | 680 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14882.64 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 90 | 21:00 | 133 | Patuakhali | 97 | 00:00
2 | AKSML | 69 | 17:00 | 68 | Jaldhaka | 100 | 00:00 | 134 | Payra | 40 | 00:00
3 | Aftabnagar | 38 | 00:00 | 69 | Jamalpur | 143 | 23:00 | 135 | Postogola | 49 | 00:00
4 | Agargaon | 123 | 00:00 | 70 | Jashore | 163 | 21:00 | 136 | Purbachal | 21 | 00:00
5 | Agrabad | 88 | 19:30 | 71 | Jhenaidah | 144 | 00:00 | 137 | Purbasadipur | 149 | 00:00
6 | Amnura | 47 | 00:00 | 72 | Joydebpur | 119 | 21:00 | 138 | Rahanpur | 39 | 00:00
7 | Ashuganj | 110 | 01:00 | 73 | Joypurhat | 80 | 01:00 | 139 | Rahim | 21 | 14:00
8 | BSRM | 200 | 14:00 | 74 | Juldah | 13 | 00:00 | 140 | Rajbari | 92 | 00:00
9 | Bagerhat | 92 | 01:00 | 75 | KSRM | 20 | 14:00 | 141 | Rajendrapur | 135 | 21:00
10 | Bajitpur | 60 | 00:00 | 76 | Kabirpur | 202 | 20:00 | 142 | Rajshahi | 128 | 01:00
11 | Bakulia | 92 | 21:00 | 77 | Kachua | 106 | 23:00 | 143 | Rajshahi-230 | 114 | 21:00
12 | Banani | 32 | 12:00 | 78 | Kallyanpur | 108 | 00:00 | 144 | Ramganj | 118 | 06:00
13 | Bangabhaban | 6 | 10:00 | 79 | Kalurghat | 34 | 11:00 | 145 | Rampur | 42 | 01:00
14 | Barapukuria | 76 | 00:00 | 80 | Kamrangirchar | 48 | 13:00 | 146 | Rangamati | 20 | 19:00
15 | Barguna | 26 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 165 | 20:00
16 | Barishal | 122 | 21:00 | 82 | Kasba | 41 | 00:00 | 148 | Ruppur | 6 | 12:00
17 | Barishal-230 | 122 | 23:00 | 83 | Kazla | 78 | 23:00 | 149 | SSM | 0 | 00:00
18 | Baroaulia | 60 | 21:00 | 84 | Keranigonj | 95 | 22:00 | 150 | Saidpur | 117 | 01:00
19 | Baroirhat | 70 | 23:00 | 85 | Khagrachori | 32 | 00:00 | 151 | Satkhira | 154 | 01:00
20 | Bashundhara | 153 | 13:00 | 86 | Khulna | 73 | 23:00 | 152 | Satmasjid | 100 | 19:30
21 | BashundharaCement | 1 | 07:00 | 87 | Khulshi | 176 | 19:00 | 153 | Savar | 178 | 15:00
22 | Beanibazar | 88 | 01:00 | 88 | Kishoreganj | 146 | 21:00 | 154 | SevenRings | 4 | 10:00
23 | Benapole | 75 | 22:00 | 89 | Kodda | 242 | 12:00 | 155 | ShahCement | 23 | 12:00
24 | Bhaluka | 163 | 19:30 | 90 | Kulaura | 56 | 21:00 | 156 | Shahjadpur | 90 | 00:00
25 | Bhandaria | 63 | 23:00 | 91 | Kurigram | 72 | 19:30 | 157 | Shahjibazar | 136 | 01:00
26 | Bhangura | 44 | 00:00 | 92 | Kushtia | 170 | 20:00 | 158 | Shahmirpur | 62 | 01:00
27 | Bheramara(GK) | 75 | 00:00 | 93 | Lalbag | 28 | 19:30 | 159 | Shariatpur | 104 | 00:00
28 | Bhulta | 188 | 21:00 | 94 | Lalmonirhat | 69 | 21:00 | 160 | Sherpur | 156 | 20:00
29 | Bog-Sherpur | 72 | 00:00 | 95 | MI_Cement | 13 | 01:00 | 161 | Shikalbaha | 14 | 22:00
30 | Bogura | 183 | 01:00 | 96 | Madanganj | 36 | 00:00 | 162 | Shitalakhya | 75 | 15:00
31 | Borhanuddin | 93 | 02:00 | 97 | Madaripur | 127 | 00:00 | 163 | Sholosohor | 44 | 15:00
32 | Brahmanbaria | 142 | 22:00 | 98 | Madartek | 97 | 01:00 | 164 | Shyampur | 110 | 17:00
33 | Cantonment | 140 | 13:00 | 99 | Madunaghat | 57 | 00:00 | 165 | Siddhirganj | 99 | 13:00
34 | Chandina | 20 | 00:00 | 100 | Magura | 74 | 00:00 | 166 | Sirajganj | 120 | 00:00
35 | Chandpur | 92 | 00:00 | 101 | Mahasthangarh | 104 | 00:00 | 167 | Sonargaon | 84 | 22:00
36 | Chandraghona | 38 | 19:00 | 102 | Manikganj | 154 | 14:00 | 168 | Sreemongol | 88 | 23:00
37 | Chapai | 84 | 23:00 | 103 | Maniknagar | 59 | 00:00 | 169 | Sreepur | 83 | 23:00
38 | Charsaidpur | 36 | 16:00 | 104 | Matarbari | 56 | 20:00 | 170 | Srinagar | 53 | 22:00
39 | Chauddagram | 83 | 23:00 | 105 | Matuail | 48 | 23:00 | 171 | Sunamganj | 66 | 19:30
40 | Chhatak | 44 | 00:00 | 106 | Millgate | 65 | 15:00 | 172 | Sylhet | 52 | 23:00
41 | Chowmuhani | 244 | 20:00 | 107 | Mirpur | 116 | 19:00 | 173 | Sylhet-132 | 136 | 23:00
42 | Chuadanga | 127 | 01:00 | 108 | Mirsorai | 9 | 00:00 | 174 | TK | 35 | 00:00
43 | Coxsbazar | 139 | 19:30 | 109 | Mirzapur | 43 | 21:00 | 175 | Tangail | 186 | 23:00
44 | Cumilla(N) | 169 | 23:00 | 110 | Mithapukur | 68 | 05:00 | 176 | Thakurgaon | 127 | 01:00
45 | Cumilla(S) | 179 | 19:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 115 | 15:00
46 | Daudkandi | 161 | 22:00 | 112 | Mogbazar | 129 | 13:00 | 178 | Ullahpara | 43 | 21:00
47 | Dhaka | 46 | 13:00 | 113 | Mongla | 31 | 14:00 | 179 | Ullon | 57 | 00:00
48 | Dhamrai | 120 | 19:00 | 114 | Motijheel | 36 | 19:00 | 180 | Uttara | 99 | 12:00
49 | Dhanmondi | 133 | 12:00 | 115 | Muktagacha | 41 | 05:00 | 181 | UttaraNew | 62 | 23:00
50 | Dohazari | 118 | 19:30 | 116 | Munshiganj | 125 | 00:00 | 182 | Zigatola | 71 | 00:00
51 | Faridpur | 180 | 21:00 | 117 | Muradnagar | 33 | 22:00
52 | Fatullah | 62 | 15:00 | 118 | Mymensingh | 225 | 00:00
53 | Fenchuganj | 46 | 19:30 | 119 | Naogaon | 169 | 00:00
54 | Feni | 130 | 23:00 | 120 | Narail | 66 | 19:30
55 | GPH | 21 | 06:00 | 121 | Narinda | 64 | 13:00
56 | Ghatail | 84 | 19:00 | 122 | Narshingdi | 171 | 23:00
57 | Ghorashal | 16 | 15:00 | 123 | Natore | 180 | 01:00
58 | Ghorashal-230 | 78 | 22:00 | 124 | Nawabganj | 67 | 00:00
59 | Goalpara | 46 | 00:00 | 125 | Netrakona | 156 | 03:00
60 | Gollamari | 98 | 00:00 | 126 | New | 64 | 15:00
61 | Gopalganj | 123 | 00:00 | 127 | Niamatpur | 92 | 23:00
62 | Gulshan | 120 | 12:00 | 128 | Noapara | 52 | 20:00
63 | Halishahar | 63 | 15:00 | 129 | PHP | 10 | 13:00
64 | HaripurSBU | 135 | 23:00 | 130 | Pabna | 120 | 01:00
65 | Hasnabad | 66 | 13:00 | 131 | Palashbari | 130 | 21:00
66 | Hathazari | 88 | 19:00 | 132 | Panchagarh | 67 | 02:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 14-06-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15483.7 | 159 |  | 15649.7
1:00 | 15124.11 | 292 |  | 15429.25
2:00 | 14625.4 | 244 |  | 14880.4
3:00 | 14567.7 | 156 |  | 14730.7
4:00 | 14314.7 | 139 |  | 14459.7
5:00 | 13983.2 | 112 |  | 14100.2
6:00 | 13137.88 | 90 |  | 13231.93
7:00 | 12929.86 | 51 |  | 12983.16
8:00 | 12789.69 | 46 |  | 12837.69
9:00 | 12714.07 | 0 |  | 12714.07
10:00 | 12988.9 | 0 |  | 12988.9
11:00 | 12853.06 | 0 |  | 12853.06
12:00 | 13304.81 | 0 |  | 13304.81
13:00 | 13785.06 | 0 |  | 13785.06
14:00 | 13901.91 | 0 |  | 13901.91
15:00 | 14125.81 | 0 |  | 14125.81
16:00 | 13848.76 | 99 |  | 13951.76
17:00 | 13574.86 | 0 |  | 13574.86
18:00 | 12692.02 | 0 |  | 12692.02
19:00 | 14085.2 | 0 |  | 14085.2
19:30 | 15007.2 | 0 |  | 15007.2
20:00 | 15182.2 | 0 |  | 15182.2
21:00 | 15487.83 | 0 |  | 15487.83
22:00 | 15521.37 | 0 |  | 15521.37
23:00 | 15617.89 | 0 |  | 15617.89
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 14-06-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8950.7 | 6533 | 15483.7 | DAILY GENERATION CURVE
00:30 | 8822.95 | 6480.955 | 15303.905
01:00 | 8695.2 | 6428.91 | 15124.11 | 14-06-2025
01:30 | 8451.8 | 6422.955 | 14874.755
02:00 | 8208.4 | 6417 | 14625.4
02:30 | 8237.55 | 6359 | 14596.55
03:00 | 8266.7 | 6301 | 14567.7
03:30 | 8089.7 | 6351.5 | 14441.2
04:00 | 7912.7 | 6402 | 14314.7
04:30 | 7724.95 | 6424 | 14148.95
05:00 | 7537.2 | 6446 | 13983.2
05:30 | 7341.325 | 6219.215 | 13560.54
06:00 | 7145.45 | 5992.43 | 13137.88
06:30 | 7032.145 | 6001.725 | 13033.87
07:00 | 6918.84 | 6011.02 | 12929.86
07:30 | 6774.255 | 6085.52 | 12859.775
08:00 | 6629.67 | 6160.02 | 12789.69
08:30 | 6675.335 | 6076.545 | 12751.88
09:00 | 6721 | 5993.07 | 12714.07
09:30 | 6850 | 6001.485 | 12851.485
10:00 | 6979 | 6009.9 | 12988.9
10:30 | 6901.51 | 6019.47 | 12920.98
11:00 | 6824.02 | 6029.04 | 12853.06
11:30 | 7073.895 | 6005.04 | 13078.935
12:00 | 7323.77 | 5981.04 | 13304.81
12:30 | 7423.88 | 6121.055 | 13544.935
13:00 | 7523.99 | 6261.07 | 13785.06
13:30 | 7532.97 | 6310.515 | 13843.485
14:00 | 7541.95 | 6359.96 | 13901.91
14:30 | 7593.625 | 6420.235 | 14013.86
15:00 | 7645.3 | 6480.51 | 14125.81
15:30 | 7559.52 | 6427.765 | 13987.285
16:00 | 7473.74 | 6375.02 | 13848.76
16:30 | 7421.13 | 6290.68 | 13711.81
17:00 | 7368.52 | 6206.34 | 13574.86
17:30 | 7133.305 | 6000.135 | 13133.44
18:00 | 6898.09 | 5793.93 | 12692.02
18:30 | 7367.645 | 6020.965 | 13388.61
19:00 | 7837.2 | 6248 | 14085.2
19:30 | 8287.2 | 6720 | 15007.2
20:00 | 8409.2 | 6773 | 15182.2
20:30 | 8514.7 | 6820.315 | 15335.015 |  | Executive Engineer
21:00 | 8620.2 | 6867.63 | 15487.83 |  | Network Operation Division
21:30 | 8639.7 | 6864.9 | 15504.6
22:00 | 8659.2 | 6862.17 | 15521.37
22:30 | 8664.2 | 6905.43 | 15569.63
23:00 | 8669.2 | 6948.69 | 15617.89

## En-Curve
QF-LDC-12
Date | 14-06-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3365 | 2927 | 759 | 0 | 44 | 761 | 172 | 4157 | 0 | 666 | 2632.7 | 0 | 0 | 0 | 159 | DAILY ENERGY CURVE
00:30 | 3315 | 2865 | 746 | 0 | 43 | 764 | 172 | 4131 | 9.955 | 718 | 2535.45 | 0 | 0 | 4.5 | 225.5 | 14-06-2025
01:00 | 3265 | 2803 | 733 | 0 | 42 | 767 | 172 | 4105 | 19.91 | 770 | 2438.2 | 0 | 0 | 9 | 292
01:30 | 3213 | 2751 | 733 | 0 | 42 | 764.5 | 172 | 4096 | 9.955 | 740.5 | 2348.3 | 0 | 0 | 4.5 | 268 | Energy Generated | 335.7014 |  | MKWHr
02:00 | 3161 | 2699 | 733 | 0 | 42 | 762 | 172 | 4087 | 0 | 711 | 2258.4 | 0 | 0 | 0 | 244 | Energy not Served | 1.388 |  | MKWHr
02:30 | 3174 | 2786 | 733 | 0 | 42 | 762.5 | 172 | 4100 | 0 | 654 | 2171.05 | 0 | 0 | 2 | 200 | Total Energy Requirement | 337.0894 |  | MKWHr
03:00 | 3187 | 2873 | 733 | 0 | 42 | 763 | 172 | 4113 | 0 | 597 | 2083.7 | 0 | 0 | 4 | 156
03:30 | 3181.5 | 2802.5 | 804.5 | 0 | 41 | 764 | 172 | 4107.5 | 0 | 560.5 | 2004.7 | 0 | 0 | 3 | 147.5
04:00 | 3176 | 2732 | 876 | 0 | 40 | 765 | 172 | 4102 | 0 | 524 | 1925.7 | 0 | 0 | 2 | 139
04:30 | 3142 | 2745 | 876 | 0 | 40 | 766 | 152 | 4080.5 | 0 | 480.5 | 1859.95 | 0 | 0 | 7 | 125.5
05:00 | 3108 | 2758 | 876 | 0 | 40 | 767 | 132 | 4059 | 0 | 437 | 1794.2 | 0 | 0 | 12 | 112
05:30 | 3111 | 2756.5 | 876 | 0 | 39 | 760.5 | 132 | 4021 | 12.44 | 337.5 | 1501.1 | 0 | 0 | 13.5 | 101
06:00 | 3114 | 2755 | 876 | 0 | 38 | 754 | 132 | 3983 | 24.88 | 238 | 1208 | 0 | 0 | 15 | 90
06:30 | 3116 | 2753.5 | 876 | 0 | 39 | 755.5 | 132 | 3952 | 59.87 | 219 | 1123 | 0 | 0 | 8 | 70.5
07:00 | 3118 | 2752 | 876 | 0 | 40 | 757 | 132 | 3921 | 94.86 | 200 | 1038 | 0 | 0 | 1 | 51
07:30 | 3096 | 2739.5 | 875 | 0 | 39 | 748.155 | 132 | 3863.5 | 191.12 | 178 | 997 | 0 | 0 | 0.5 | 48.5
08:00 | 3074 | 2727 | 874 | 0 | 38 | 739.31 | 132 | 3806 | 287.38 | 156 | 956 | 0 | 0 | 0 | 46
08:30 | 3054 | 2717 | 874.5 | 0 | 37 | 740.84 | 152 | 3812.5 | 294.54 | 167 | 902.5 | 0 | 0 | 0 | 23
09:00 | 3034 | 2707 | 875 | 0 | 36 | 742.37 | 172 | 3819 | 301.7 | 178 | 849 | 0 | 0 | 0 | 0
09:30 | 2984.5 | 2709.5 | 874 | 0 | 36 | 740.965 | 172 | 3905 | 381.02 | 202.5 | 845 | 0 | 0 | 1 | 0
10:00 | 2935 | 2712 | 873 | 0 | 36 | 739.56 | 172 | 3991 | 460.34 | 227 | 841 | 0 | 0 | 2 | 0
10:30 | 2924 | 2656.5 | 873.5 | 0 | 35 | 738.16 | 172 | 3980 | 459.82 | 227 | 854 | 0 | 0 | 1 | 0
11:00 | 2913 | 2601 | 874 | 0 | 34 | 736.76 | 172 | 3969 | 459.3 | 227 | 867 | 0 | 0 | 0 | 0
11:30 | 3025 | 2596 | 874 | 0 | 36 | 738.225 | 172 | 4025.5 | 380.21 | 266 | 966 | 0 | 0 | 0 | 0
12:00 | 3137 | 2591 | 874 | 0 | 38 | 739.69 | 172 | 4082 | 301.12 | 305 | 1065 | 0 | 0 | 0 | 0
12:30 | 3098.5 | 2558.5 | 876 | 0 | 40 | 736.57 | 172 | 4131.5 | 375.865 | 333 | 1223 | 0 | 0 | 0 | 0
13:00 | 3060 | 2526 | 878 | 0 | 42 | 733.45 | 172 | 4181 | 450.61 | 361 | 1381 | 0 | 0 | 0 | 0
13:30 | 3038 | 2534 | 877.5 | 0 | 43 | 729.725 | 172 | 4212.5 | 460.76 | 340 | 1436 | 0 | 0 | 0 | 0
14:00 | 3016 | 2542 | 877 | 0 | 44 | 726 | 172 | 4244 | 470.91 | 319 | 1491 | 0 | 0 | 0 | 0
14:30 | 3058.5 | 2572.5 | 877 | 0 | 43 | 746.5 | 172 | 4287.6 | 444.26 | 327 | 1480.5 | 0 | 0 | 5 | 0
15:00 | 3101 | 2603 | 877 | 0 | 42 | 767 | 172 | 4331.2 | 417.61 | 335 | 1470 | 0 | 0 | 10 | 0
15:30 | 3079 | 2578.5 | 877 | 0 | 42 | 844 | 172 | 4345.1 | 343.085 | 372.5 | 1322.6 | 0 | 0 | 11.5 | 49.5
16:00 | 3057 | 2554 | 877 | 0 | 42 | 921 | 172 | 4359 | 268.56 | 410 | 1175.2 | 0 | 0 | 13 | 99
16:30 | 3117.5 | 2345.5 | 877 | 0 | 40 | 1016.5 | 172 | 4375.5 | 186.61 | 419 | 1143.7 | 0 | 0 | 18.5 | 49.5
17:00 | 3178 | 2137 | 877 | 0 | 38 | 1112 | 172 | 4392 | 104.66 | 428 | 1112.2 | 0 | 0 | 24 | 0
17:30 | 3180 | 1960 | 877 | 0 | 35 | 1161 | 172 | 4049 | 70.74 | 447 | 1162.2 | 0 | 0 | 19.5 | 0
18:00 | 3182 | 1783 | 877 | 0 | 32 | 1210 | 172 | 3706 | 36.82 | 466 | 1212.2 | 0 | 0 | 15 | 0
18:30 | 3302 | 1813.5 | 861 | 0 | 39 | 1240 | 172 | 3968.5 | 18.41 | 570 | 1393.7 | 0 | 0 | 10.5 | 0
19:00 | 3422 | 1844 | 845 | 0 | 46 | 1270 | 172 | 4231 | 0 | 674 | 1575.2 | 0 | 0 | 6 | 0
19:30 | 3475 | 1811 | 830 | 0 | 44 | 1346 | 172 | 4614 | 0 | 759 | 1944.2 | 0 | 0 | 12 | 0
20:00 | 3454 | 1827 | 830 | 0 | 40 | 1411 | 172 | 4709 | 0 | 764 | 1965.2 | 0 | 0 | 10 | 0
20:30 | 3489 | 1872.5 | 809.5 | 0 | 43 | 1427.215 | 172 | 4744.1 | 0 | 765 | 2003.7 | 0 | 0 | 9 | 0
21:00 | 3524 | 1918 | 789 | 0 | 46 | 1443.43 | 172 | 4779.2 | 0 | 766 | 2042.2 | 0 | 0 | 8 | 0
21:30 | 3527.5 | 1942.5 | 785.5 | 0 | 44 | 1445.8 | 172 | 4773.6 | 0 | 767 | 2040.2 | 0 | 0 | 6.5 | 0
22:00 | 3531 | 1967 | 782 | 0 | 42 | 1448.17 | 172 | 4768 | 0 | 768 | 2038.2 | 0 | 0 | 5 | 0
22:30 | 3567 | 1964 | 782 | 0 | 36 | 1455.43 | 172 | 4771 | 0 | 767 | 2048.2 | 0 | 0 | 7 | 0
23:00 | 3603 | 1961 | 782 | 0 | 30 | 1462.69 | 172 | 4774 | 0 | 766 | 2058.2 | 0 | 0 | 9 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 14-06-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 389 | 03:00 | 376 | 23:00 | Payra | 414 | 02:00 | 408 | 21:00
Ashuganj | 405 | 5:00 | 390 | 23:00 | Rahanpur | 406 | 15:00 | 389 | 23:00
Bhulta | 401 | 01:00 | 385 | 16:00 | Rampal | 402 | 18:00 | 388 | 23:00
Bibiana | 389 | 18:00 | 384 | 15:00
BIPTC | 399 | 06:00 | 387 | 16:00
Bogura | 395 | 13:00 | 375 | 23:00
Gopalganj | 398 | 18:00 | 384 | 23:00
Kaliakoir | 380 | 01:00 | 369 | 15:00
Madunaghat | 398 | 00:00 | 393 | 12:00
Meghnaghat | 396 | 02:00 | 385 | 21:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 230 | 01:00 | 224 | 11:00 | Keranigonj | 227 | 01:00 | 222 | 13:00
AKSML | 234 | 00:00 | 222 | 15:00 | Khulna(S) | 229 | 18:30 | 214 | 00:00
Aminbazar | 231 | 03:00 | 224 | 23:00 | Madunaghat | 235 | 18:00 | 226 | 15:00
Ashuganj | 232 | 03:00 | 228 | 07:00 | Madunaghat-400 | 234 | 00:00 | 228 | 14:00
Ashuganj-400 | 232 | 5:00 | 220 | 23:00 | Maniknagar | 225 | 03:00 | 219 | 15:00
Baghabari | 232 | 02:00 | 224 | 23:00 | Meghnaghat | 235 | 04:00 | 229 | 15:00
Barapukuria | 223 | 13:00 | 213 | 22:00 | Meghnaghat-400 | 229 | 02:00 | 224 | 14:00
Barapukuria-230 | 220 | 13:00 | 214 | 21:00 | Mirsorai | 233 | 01:00 | 221 | 15:00
Barishal | 236 | 07:00 | 217 | 23:00 | Rajshahi | 233 | 01:00 | 219 | 00:00
Bheramara | 233 | 18:30 | 222 | 16:00 | Rampal | 230 | 18:00 | 215 | 23:00
Bhulta | 234 | 01:00 | 220 | 15:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 226 | 03:00 | 222 | 19:00 | Rampura | 234 | 01:00 | 221 | 16:00
BIPTC | 233 | 10:00 | 222 | 00:00 | Shikalbaha | 233 | 01:00 | 224 | 14:00
Bogura | 231 | 15:00 | 219 | 23:00 | Shyampur | 228 | 01:00 | 223 | 11:00
Bogura-400 | 230 | 13:00 | 220 | 22:00 | Siddhirganj | 228 | 18:00 | 222 | 11:00
Borhanuddin | 242 | 08:00 | 220 | 22:00 | Sirajgonj | 238 | 01:00 | 233 | 21:00
BSRM | 232 | 01:00 | 221 | 15:00 | Sreepur | 231 | 01:00 | 224 | 07:00
Cumilla(N) | 226 | 18:00 | 220 | 13:00 | Tongi | 227 | 18:00 | 221 | 15:00
Faridpur | 233 | 18:00 | 219 | 23:00
Fenchuganj | 225 | 00:00 | 221 | 19:00
Ghorashal | 230 | 00:00 | 230 | 00:00
Ghorashal-230 | 232 | 01:00 | 221 | 16:00
Gopalganj | 234 | 18:00 | 221 | 23:00
GPH | 233 | 01:00 | 223 | 15:00
Haripur | 226 | 01:00 | 221 | 11:00
Hasnabad | 228 | 05:00 | 222 | 12:00
Hathazari | 234 | 00:00 | 225 | 15:00
Ishurdi | 234 | 18:30 | 224 | 16:00
Jhenaidah | 227 | 18:00 | 214 | 00:00
Kaliakoir | 234 | 01:00 | 227 | 16:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 01:00 | 128 | 07:00 | Madartek | 135 | 01:00 | 126 | 16:00
Agargaon | 132 | 02:00 | 127 | 15:00 | Madunaghat | 132 | 00:00 | 127 | 14:00
Agrabad | 134 | 18:00 | 126 | 15:00 | Magura | 132 | 18:30 | 119 | 00:00
AKS | 131 | 18:00 | 127 | 12:00 | Mahasthangarh | 133 | 18:00 | 123 | 21:00
Aminbazar | 133 | 02:00 | 127 | 10:00 | Manikganj | 129 | 18:00 | 122 | 00:00
Amnura | 138 | 18:30 | 123 | 00:00 | Maniknagar | 127 | 04:00 | 124 | 12:00
Ashuganj | 140 | 01:00 | 135 | 00:00 | Matarbari | 120 | 10:00 | 112 | 19:00
Bagerhat | 131 | 18:00 | 117 | 23:00 | Matuail | 133 | 18:00 | 129 | 13:00
Bajitpur | 131 | 02:00 | 124 | 00:00 | Millgate | 133 | 01:00 | 127 | 15:00
Bakulia | 135 | 00:00 | 128 | 15:00 | Mirpur | 132 | 05:00 | 126 | 10:00
Banani | 136 | 01:00 | 127 | 16:00 | Mirzapur | 131 | 11:00 | 123 | 15:00
Bangabhaban | 127 | 01:00 | 123 | 13:00 | Mithapukur | 130 | 15:00 | 119 | 23:00
Barapukuria | 136 | 18:00 | 123 | 22:00 | MI_Cement | 133 | 04:00 | 129 | 09:00
Barguna | 136 | 01:00 | 128 | 23:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 130 | 07:00 | 121 | 21:00 | Mogbazar | 133 | 05:00 | 126 | 16:00
Barishal-230 | 130 | 07:00 | 121 | 21:00 | Mongla | 129 | 18:00 | 117 | 19:30
Baroaulia | 135 | 18:00 | 128 | 15:00 | Motijheel | 127 | 01:00 | 123 | 13:00
Baroirhat | 125 | 18:30 | 118 | 13:00 | Muktagacha | 132 | 11:00 | 117 | 23:00
Bashundhara | 136 | 01:00 | 126 | 12:00 | Munshiganj | 132 | 01:00 | 128 | 09:00
BashundharaCement | 132 | 18:30 | 128 | 09:00 | Muradnagar | 127 | 18:00 | 122 | 14:00
Beanibazar | 127 | 02:00 | 122 | 19:00 | Mymensingh | 132 | 11:00 | 112 | 19:00
Benapole | 128 | 18:00 | 116 | 23:00 | Naogaon | 131 | 18:00 | 118 | 23:00
Bhaluka | 135 | 01:00 | 123 | 19:00 | Narail | 132 | 18:30 | 119 | 00:00
Bhandaria | 125 | 08:00 | 110 | 21:00 | Narinda | 127 | 4:00 | 124 | 12:00
Bhangura | 134 | 18:00 | 126 | 00:00 | Narshingdi | 138 | 02:00 | 123 | 21:00
Bheramara | 134 | 09:00 | 127 | 16:00 | Natore | 133 | 18:30 | 128 | 01:00
Bheramara(GK) | 134 | 18:30 | 126 | 23:00 | Nawabganj | 131 | 01:00 | 127 | 15:00
Bhulta | 127 | 01:00 | 125 | 00:00 | Netrakona | 127 | 01:00 | 110 | 23:00
Bog-Sherpur | 134 | 18:00 | 125 | 22:00 | New | 133 | 18:00 | 128 | 12:00
Bogura | 136 | 18:00 | 128 | 23:00 | Niamatpur | 133 | 06:00 | 130 | 00:00
Bogura-230 | 136 | 18:00 | 128 | 21:00 | Noapara | 132 | 17:00 | 121 | 23:00
Brahmanbaria | 131 | 10:00 | 126 | 22:00 | Pabna | 133 | 01:00 | 125 | 19:30
Cantonment | 132 | 03:00 | 127 | 13:00 | Palashbari | 128 | 18:00 | 117 | 21:00
Chandina | 129 | 18:00 | 123 | 15:00 | Panchagarh | 138 | 19:00 | 119 | 00:00
Chandpur | 127 | 18:00 | 119 | 14:00 | Patuakhali | 136 | 00:00 | 130 | 19:30
Chandraghona | 133 | 00:00 | 128 | 15:00 | Payra | 137 | 01:00 | 133 | 21:00
Chapai | 129 | 09:00 | 124 | 00:00 | PHP | 124 | 18:30 | 116 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 133 | 01:00 | 129 | 10:00 | Postogola | 134 | 02:00 | 131 | 10:00
Chauddagram | 125 | 18:30 | 118 | 13:00 | Purbachal | 135 | 01:00 | 127 | 16:00
Chhatak | 126 | 04:00 | 118 | 23:00 | Purbasadipur | 132 | 19:00 | 116 | 00:00
Chowmuhani | 119 | 18:00 | 110 | 06:00 | Rahanpur | 134 | 08:00 | 130 | 00:00
Chuadanga | 131 | 18:30 | 116 | 00:00 | Rahanpur-400 | 135 | 15:00 | 130 | 20:00
Coxsbazar | 120 | 01:00 | 112 | 22:00 | Rahim | 132 | 02:00 | 129 | 12:00
Cumilla(N) | 130 | 18:00 | 124 | 13:00 | Rajbari | 134 | 18:00 | 124 | 23:00
Cumilla(S) | 132 | 04:00 | 121 | 15:00 | Rajendrapur | 138 | 01:00 | 126 | 00:00
Daudkandi | 126 | 05:00 | 121 | 10:00 | Rajshahi | 134 | 18:30 | 125 | 23:00
Dhaka | 133 | 05:00 | 126 | 16:00 | Rajshahi-230 | 135 | 18:30 | 114 | 20:00
Dhamrai | 128 | 00:00 | 124 | 14:00 | Ramganj | 117 | 01:00 | 110 | 15:00
Dhanmondi | 136 | 03:00 | 130 | 15:00 | Rampur | 133 | 00:00 | 126 | 15:00
Dohazari | 130 | 18:00 | 122 | 15:00 | Rampura | 136 | 01:00 | 126 | 16:00
Faridpur | 135 | 11:00 | 127 | 23:00 | Rangamati | 132 | 00:00 | 127 | 15:00
Fatullah | 133 | 01:00 | 129 | 11:00 | Rangpur | 130 | 15:00 | 117 | 23:00
Fenchuganj | 134 | 10:00 | 130 | 20:00 | Ruppur | 135 | 09:00 | 126 | 00:00
Feni | 122 | 18:00 | 116 | 15:00 | Saidpur | 132 | 18:00 | 118 | 00:00
Ghatail | 129 | 12:00 | 115 | 15:00 | Satkhira | 129 | 18:00 | 113 | 23:00
Ghorashal | 136 | 11:00 | 133 | 09:00 | Satmasjid | 132 | 04:00 | 127 | 21:00
Goalpara | 135 | 18:00 | 124 | 23:00 | Savar | 132 | 19:30 | 125 | 09:00
Gollamari | 135 | 18:00 | 125 | 22:00 | SevenRings | 139 | 01:00 | 133 | 07:00
Gopalganj | 134 | 18:00 | 124 | 23:00 | ShahCement | 133 | 02:00 | 129 | 10:00
Gopalganj-400 | 136 | 18:00 | 130 | 21:00 | Shahjadpur | 134 | 07:00 | 130 | 00:00
Gulshan | 135 | 01:00 | 127 | 16:00 | Shahjibazar | 132 | 09:00 | 125 | 00:00
Halishahar | 135 | 00:00 | 126 | 15:00 | Shahmirpur | 135 | 00:00 | 128 | 15:00
Haripur | 133 | 01:00 | 129 | 11:00 | Shariatpur | 133 | 18:00 | 123 | 21:00
HaripurSBU | 133 | 01:00 | 129 | 11:00 | Sherpur | 132 | 11:00 | 114 | 23:00
Hasnabad | 134 | 04:00 | 130 | 11:00 | Shikalbaha | 124 | 00:00 | 117 | 15:00
Hathazari | 136 | 18:00 | 130 | 15:00 | Shikalbaha-230 | 135 | 00:00 | 129 | 14:00
Ishurdi | 135 | 09:00 | 129 | 23:00 | Shitalakhya | 133 | 04:00 | 129 | 09:00
Jaldhaka | 129 | 18:00 | 114 | 00:00 | Sholosohor | 134 | 01:00 | 127 | 12:00
Jamalpur | 135 | 11:00 | 117 | 15:00 | Shyampur | 131 | 03:00 | 128 | 09:00
Jashore | 130 | 18:00 | 117 | 19:30 | Shyampur-230 | 132 | 01:00 | 128 | 15:00
Jhenaidah | 135 | 18:30 | 113 | 23:00 | Siddhirganj | 133 | 03:00 | 129 | 11:00
Jhenaidah-230 | 135 | 18:30 | 123 | 00:00 | Sirajganj | 132 | 18:00 | 124 | 23:00
Joydebpur | 141 | 02:00 | 127 | 08:00 | Sonargaon | 133 | 18:00 | 127 | 10:00
Joypurhat | 128 | 18:00 | 115 | 23:00 | Sreemongol | 131 | 09:00 | 121 | 00:00
Juldah | 135 | 00:00 | 129 | 15:00 | Sreepur | 135 | 01:00 | 128 | 19:00
Kabirpur | 137 | 01:00 | 127 | 00:00 | Srinagar | 132 | 05:00 | 127 | 15:00
Kachua | 126 | 18:00 | 118 | 14:00 | SSM | 139 | 18:00 | 131 | 14:00
Kaliakoir | 136 | 02:00 | 127 | 14:00 | Sunamganj | 124 | 10:00 | 116 | 23:00
Kallyanpur | 131 | 18:00 | 127 | 10:00 | Sylhet | 128 | 08:00 | 124 | 19:30
Kalurghat | 132 | 00:00 | 128 | 12:00 | Sylhet-132 | 128 | 09:00 | 125 | 22:00
Kamrangirchar | 132 | 03:00 | 128 | 13:00 | Tangail | 129 | 11:00 | 118 | 15:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 138 | 19:00 | 117 | 00:00
Kasba | 127 | 18:00 | 121 | 15:00 | TK | 132 | 04:00 | 127 | 15:00
Kazla | 128 | 04:00 | 124 | 12:00 | Tongi | 134 | 18:00 | 130 | 01:00
Keranigonj | 132 | 02:00 | 128 | 13:00 | Ullahpara | 133 | 18:00 | 126 | 23:00
Khagrachori | 132 | 18:30 | 126 | 13:00 | Ullon | 133 | 08:00 | 127 | 15:00
Khulna | 134 | 18:00 | 124 | 19:30 | Uttara | 131 | 02:00 | 125 | 11:00
Khulna(S) | 135 | 18:00 | 125 | 23:00 | UttaraNew | 131 | 01:00 | 127 | 00:00
Khulshi | 132 | 00:00 | 126 | 15:00 | Zigatola | 133 | 03:00 | 128 | 13:00
Kishoreganj | 130 | 11:00 | 119 | 00:00
Kodda | 138 | 01:00 | 124 | 15:00
KSRM | 133 | 00:00 | 128 | 13:00
Kulaura | 132 | 00:00 | 128 | 22:00
Kurigram | 127 | 15:00 | 113 | 22:00
Kushtia | 129 | 07:00 | 119 | 19:30
Lalbag | 132 | 01:00 | 128 | 15:00
Lalmonirhat | 127 | 15:00 | 115 | 21:00
Madanganj | 132 | 18:30 | 128 | 09:00
Madaripur | 135 | 18:30 | 127 | 21:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division