## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 16-06-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 15-06-2025 | during | 16-06-2025 | during | 16-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0.01 | 0.01 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 345 | 349 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 400 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 301 | 288 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 250 | 250 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 333 | 335 | 335 | 333 | 333 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 45 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 64 | 112 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 17 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 25.5 | 26 | 33 | 33 | 25.5 | 25.5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 18 | 18 | 22 | 22 | 14 | 14 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 33 | 33 | 52.19 | 52.19 | 33 | 33 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 56 | 68 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 70 | 105 | 105 | 80 | 80 | Fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 50 | 16 | 104 | 104 | 85 | 85 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 45 | 108 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 20 | 0 | 20 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 54 | 17 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 500 | 463 | 584 | 584 | 470 | 470 | None
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 108 | 160 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2535.5 | 2555 | 5114.4 | 5126.4 | 4281.63 | 4293.63
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 1 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 7 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 172 | 172 | 172 | 172 | 172 | 172 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 37 | 218 | 221 | 221 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 45 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 16 | 73 | 48 | 72 | 48 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 65 | 65 | 65 | 65 | 65 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 88 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 20 | 2 | 28 | 2 | 28 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1 | 0 | 4.63 | 0 | 4.63 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 48 | 12 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1052 | 1090 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 19 | 13 | 56 | 52 | 56 | 52 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 156 | 209 | 1150 | 1150 | 575 | 575 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1615 | 2068 | 4181.35 | 4212.72 | 3535.35 | 3566.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 215 | 190 | 221 | 221 | 205.43 | 205.43 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 350 | 351 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 340 | 340 | 340 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 31 | 25 | 46.7 | 46.7 | 27 | 27 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 41 | 47 | 55 | 55 | 47 | 47 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 185 | 185 | 195 | 195 | 185 | 185 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 100 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 34 | 43 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 80 | 163 | 163 | 80 | 80 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 136 | 153 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 36 | 44 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 93 | 111 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 38 | 113 | 113 | 48 | 48 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 93 | 115 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 39 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1787 | 1936.2 | 2450.75 | 2400.75 | 2243.98 | 2193.98
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 15-06-2025 | during | 16-06-2025 | during | 16-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 34 | 80 | 157.5 | 157.5 | 34 | 34 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 139 | 174 | 200 | 200 | 120 | 120 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 55 | 82 | 115 | 115 | 100 | 100 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 49.9 | 0 | 39 | 0 | 39 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 21 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 291.9 | 369 | 590.1 | 549 | 371.6 | 330.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 36 | 34 | 34 | 34 | 34 | 34 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Borescope Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 81 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 166 | 167 | 165 | 165 | 165 | 165 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 376 | 388 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1379 | 1379 | 1432 | 1432 | 1353 | 1353
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 891 | 893 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 110 | 410 | 410 | 124 | 124 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 70 | 105 | 105 | 70 | 70 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 55 | 0 | 78 | 0 | 78 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1007 | 1085 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1991 | 2196 | 3632.2 | 3554.2 | 3311.2 | 3233.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 396 | 458 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 8 | 11 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1050 | 1110 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 110 | 110 | 110 | 110 | 110 | 110 | machine problem
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 14.5 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 274 | 273 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.86 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1958.86 | 2096.5 | 2062 | 2061 | 2062 | 2061
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 44 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 6 | 32 | 32 | 32 | 32 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 172 | 171 | 214 | 214 | 171 | 171 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 187 | 189 | 220 | 220 | 203 | 203 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 392 | 397 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 22 | 30 | 30 | 30 | 30 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 96 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 112 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.63 | 0 | 5.2 | 0 | 5.2 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1215.37 | 1449.87 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 34.12 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 116 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 2121.12 | 2523.87 | 3192.07 | 3025.87 | 2870.69 | 2704.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 46 | 48 | 47 | 47 | 47 | 47 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 182 | 200 | 200 | 200 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 70 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 8 | 0 | 4.6 | 0 | 4.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 63 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 13 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 85 | 0 | 170.16 | 0 | 170.16 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 467 | 476 | 713.76 | 509 | 713.76 | 509
System Total |  |  |  |  | 28565.2 | 27084.055 | 14146.38 | 15599.57 | 23368.63 | 22870.94 | 20743.21 | 20245.52
Forecast Scenario (16-06-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15720 |  | 0 |  | 15720
|  |  |  | 1:00 | 15350 |  | 0 |  | 15350
|  |  |  | 2:00 | 15120 |  | 0 |  | 15120
|  |  |  | 3:00 | 14660 |  | 0 |  | 14660
|  |  |  | 4:00 | 14340 |  | 0 |  | 14340
|  |  |  | 5:00 | 13920 |  | 0 |  | 13920
|  |  |  | 6:00 | 13370 |  | 0 |  | 13370
|  |  |  | 7:00 | 13010 |  | 0 |  | 13010
|  |  |  | 8:00 | 13080 |  | 0 |  | 13080
|  |  |  | 9:00 | 13320 |  | 0 |  | 13320
|  |  |  | 10:00 | 13630 |  | 0 |  | 13630
|  |  |  | 11:00 | 13780 |  | 0 |  | 13780
|  |  |  | 12:00 | 14140 |  | 0 |  | 14140
|  |  |  | 13:00 | 14070 |  | 0 |  | 14070
|  |  |  | 14:00 | 14090 |  | 0 |  | 14090
|  |  |  | 15:00 | 14060 |  | 0 |  | 14060
|  |  |  | 16:00 | 14210 |  | 0 |  | 14210
|  |  |  | 17:00 | 13720 |  | 0 |  | 13720
|  |  |  | 18:00 | 13100 |  | 0 |  | 13100
|  |  |  | 18:30 | 13600 |  | 0 |  | 13600
|  |  |  | 19:00 | 14370 |  | 0 |  | 14370
|  |  |  | 19:30 | 15100 |  | 0 |  | 15100
|  |  |  | 20:00 | 15300 |  | 0 |  | 15300
|  |  |  | 21:00 | 15640 |  | 0 |  | 15640
|  |  |  | 22:00 | 15700 |  | 0 |  | 15700
|  |  |  | 23:00 | 15800 |  | 0 |  | 15800
Probable Maximum Temperature:
Probable Maximum Demand at Day Peak: |  |  | 14140.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15640.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15640.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 343.50 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:19 hrs on 16-06-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 15-06-2025 | [28 empty] | Date: | 15-06-2025 | [28 empty] | Date: | 15-06-2025 | [28 empty] | Date: | 15-06-2025 | [28 empty] | Date: | 15-06-2025 | [12 empty] | Date: | 15-06-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [12 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 54 | 54 | 68 | 127 | 30 | 0 | 55 | 108 | 68 | 420 | 293 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 160 | 16 | 14 | 0 | 484 | 17 | 0 | 0 | 0 | 6 | 65 | 79 | 0 | 100 | 100 | 0 | 172 | 68 | 27 | 155 | 0 | 0 | 19 | 8 | 68 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 128 | 185 | 0 | 351 | 340 | 46 | 196 | 27 | 111 | 71 | 180 | 38 | 19 | 103 | 46 | 52.2 | 0 | 46 | 315 | 320 | 386 | 33 | 30 | 0 | 8 | 0 | 83 | 28 | 0 | 16 | 167 | 0 | 83 | 159 | 0 | 0 | 0 | 12 | 8652.2 | 782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 54 | 1437.02 | 0 | 0 | 0 | 35 | 17 | 94 | 0 | 35 | 0 | 0 | 30 | 0 | 160 | 0 | 175 | 0 | 0 | 0 | 414 | 0 | 0 | 195 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 11 | 120 | 0 | 0 | 397 | 1244 | 0 | 6986.22 | 15638.42 | 96.32
01:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 54 | 54 | 68 | 127 | 15 | 0 | 52 | 144 | 54 | 400 | 291 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 160 | 16 | 14 | 0 | 410 | 0 | 0 | 0 | 0 | 16 | 65 | 79 | 0 | 100 | 100 | 0 | 172 | 51 | 27 | 155 | 0 | 0 | 19 | 8 | 68 | 150 | 0 | 0 | 0 | 1185 | 0 | 51 | 132 | 185 | 0 | 351 | 340 | 46 | 187 | 26 | 114 | 70 | 181 | 9 | 19 | 103 | 42 | 52.2 | 0 | 46 | 305 | 320 | 358 | 36 | 30 | 0 | 8 | 0 | 84 | 28 | 0 | 16 | 165 | 9 | 83 | 159 | 0 | 0 | 0 | 12 | 8415.2 | 754 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1169 | 54 | 1454.22 | 0 | 0 | 0 | 35 | 15 | 94 | 0 | 35 | 0 | 0 | 30 | 0 | 161 | 0 | 184 | 0 | 0 | 0 | 350 | 0 | 0 | 195 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 11 | 120 | 15 | 0 | 395 | 1244 | 0 | 6880.22 | 15295.42 | 96.34
02:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 54 | 54 | 68 | 127 | 0 | 0 | 52 | 144 | 50 | 400 | 295 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 160 | 16 | 14 | 0 | 419 | 0 | 0 | 0 | 0 | 20 | 65 | 77 | 0 | 100 | 100 | 0 | 172 | 34 | 27 | 155 | 0 | 0 | 19 | 8 | 68 | 148 | 0 | 0 | 0 | 1070 | 0 | 51 | 133 | 185 | 0 | 350 | 340 | 46 | 189 | 26 | 114 | 70 | 180 | 9 | 19 | 103 | 44 | 52.2 | 0 | 45 | 305 | 320 | 358 | 36 | 30 | 0 | 8 | 0 | 84 | 28 | 0 | 16 | 167 | 17 | 83 | 158 | 0 | 0 | 0 | 12 | 8272.2 | 754 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1183 | 54 | 1359.23 | 0 | 0 | 0 | 35 | 15 | 80 | 0 | 35 | 0 | 0 | 30 | 0 | 161 | 0 | 187 | 0 | 0 | 0 | 350 | 0 | 0 | 195 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 245 | 11 | 120 | 30 | 0 | 396 | 1244 | 0 | 6799.23 | 15071.43 | 96.36
03:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 54 | 0 | 60 | 127 | 0 | 0 | 52 | 144 | 50 | 400 | 293 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 160 | 16 | 14 | 0 | 433 | 0 | 0 | 0 | 0 | 9 | 50 | 78 | 0 | 100 | 72 | 0 | 172 | 0 | 27 | 155 | 0 | 0 | 0 | 8 | 34 | 149 | 0 | 0 | 0 | 1105 | 0 | 51 | 133 | 185 | 0 | 350 | 340 | 47 | 196 | 23 | 97 | 70 | 180 | 9 | 19 | 91 | 42 | 52.2 | 0 | 45 | 310 | 320 | 368 | 36 | 30 | 0 | 8 | 0 | 84 | 28 | 0 | 16 | 167 | 17 | 83 | 158 | 0 | 0 | 0 | 12 | 8097.2 | 754 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1189 | 54 | 1313.57 | 0 | 0 | 0 | 35 | 15 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 161 | 0 | 192 | 0 | 0 | 0 | 350 | 0 | 0 | 195 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 11 | 120 | 40 | 0 | 396 | 1100 | 0 | 6519.57 | 14616.77 | 96.38
04:00 | 0 | 17 | 33 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 33 | 0 | 40 | 127 | 0 | 0 | 0 | 144 | 40 | 400 | 297 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 160 | 16 | 14 | 0 | 407 | 0 | 0 | 0 | 0 | 17 | 17 | 48 | 0 | 100 | 48 | 0 | 172 | 0 | 27 | 155 | 0 | 0 | 0 | 8 | 17 | 149 | 0 | 0 | 0 | 1105 | 0 | 51 | 100 | 185 | 0 | 350 | 340 | 47 | 200 | 23 | 96 | 80 | 181 | 9 | 19 | 91 | 42 | 52.2 | 0 | 0 | 310 | 320 | 388 | 36 | 30 | 0 | 8 | 0 | 84 | 28 | 0 | 16 | 167 | 17 | 83 | 158 | 0 | 0 | 0 | 12 | 7798.2 | 877 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1191 | 0 | 1216.15 | 0 | 0 | 0 | 35 | 13 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 162 | 0 | 187 | 0 | 0 | 0 | 350 | 0 | 0 | 195 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 11 | 120 | 109 | 0 | 396 | 1091 | 0 | 6548.15 | 14346.35 | 96.4
05:00 | 0 | 19 | 33 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 37 | 112 | 0 | 0 | 0 | 90 | 25 | 400 | 299 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 160 | 16 | 14 | 0 | 402 | 0 | 0 | 0 | 0 | 13 | 0 | 48 | 0 | 72 | 24 | 0 | 172 | 0 | 27 | 155 | 0 | 0 | 0 | 8 | 17 | 148 | 0 | 0 | 0 | 1065 | 0 | 51 | 50 | 185 | 0 | 350 | 340 | 47 | 198 | 23 | 96 | 80 | 181 | 9 | 19 | 92 | 42 | 52.2 | 0 | 0 | 315 | 320 | 385 | 36 | 30 | 0 | 8 | 0 | 84 | 28 | 0 | 16 | 167 | 17 | 83 | 158 | 0 | 0 | 0 | 10 | 7482.2 | 877 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1207 | 0 | 1220.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 191 | 0 | 0 | 0 | 350 | 0 | 0 | 195 | 49 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 11 | 120 | 110 | 0 | 396 | 1050 | 0 | 6447.27 | 13929.47 | 96.42
06:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 0 | 68 | 82 | 0 | 0 | 0 | 54 | 16 | 400 | 292 | 0 | 0 | 0 | 280 | 0 | 0 | 2 | 160 | 16 | 14 | 0 | 377 | 0 | 0 | 0 | 0 | 8 | 0 | 16 | 0 | 72 | 24 | 0 | 172 | 0 | 27 | 155 | 0 | 0 | 0 | 8 | 17 | 82 | 0 | 0 | 0 | 975 | 0 | 43 | 12 | 185 | 0 | 355 | 340 | 47 | 215 | 23 | 114 | 80 | 155 | 9 | 19 | 92 | 40 | 25 | 1 | 0 | 305 | 320 | 353 | 36 | 30 | 0 | 8 | 0 | 83 | 30 | 0 | 16 | 167 | 0 | 65 | 158 | 0 | 0 | 1.05 | 10 | 7060.05 | 877 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 1076 | 0 | 1203.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0.58 | 161 | 0 | 191 | 0 | 0 | 0 | 350 | 0 | 0.06 | 200 | 48 | 115 | 2 | 113 | 0 | 0 | 0.4 | 16 | 0.01 | 0 | 242 | 11 | 120 | 110 | 0 | 395 | 1043 | 0 | 6317.28 | 13377.33 | 96.44
07:00 | 0 | 50 | 24 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 0 | 91 | 48 | 0 | 0 | 0 | 35 | 16 | 350 | 291 | 0 | 0 | 0 | 280 | 0 | 0 | 5 | 108 | 18 | 14 | 0 | 380 | 0 | 0 | 0 | 0 | 1 | 0 | 16 | 0 | 72 | 0 | 1 | 172 | 0 | 19 | 156 | 0 | 0 | 0 | 0 | 17 | 26 | 0 | 0 | 0 | 975 | 0 | 43 | 8 | 185 | 0 | 354 | 340 | 47 | 188 | 23 | 90 | 80 | 120 | 9 | 19 | 93 | 38 | 8 | 3 | 0 | 305 | 320 | 355 | 36 | 30 | 0 | 8 | 0 | 81 | 30 | 0 | 16 | 167 | 0 | 65 | 158 | 34 | 1 | 3.01 | 12 | 6752.01 | 877 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9 | 1042 | 0 | 1206.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 5.56 | 162 | 0 | 191 | 0 | 0 | 0 | 350 | 0 | 0.86 | 200 | 49 | 70 | 6 | 70 | 0 | 0 | 0 | 45 | 0.05 | 0 | 244 | 11 | 120 | 110 | 0 | 396 | 1039 | 0 | 6262.91 | 13014.92 | 96.46
08:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 0 | 93 | 48 | 0 | 0 | 0 | 35 | 16 | 350 | 289 | 0 | 0 | 0 | 280 | 0 | 0 | 8 | 108 | 19.2 | 14 | 0 | 377 | 0 | 0 | 0 | 0 | 9 | 0 | 16 | 0 | 72 | 0 | 1 | 172 | 0 | 2 | 155 | 0 | 0 | 0 | 0 | 17 | 27 | 0 | 0 | 0 | 995 | 1 | 43 | 0 | 185 | 0 | 353 | 340 | 45 | 181 | 23 | 90 | 80 | 100 | 9 | 19 | 93 | 38 | 8 | 13 | 0 | 310 | 320 | 362 | 36 | 30 | 0 | 8 | 0 | 81 | 30 | 0 | 16 | 167 | 0 | 64 | 158 | 34 | 1 | 12.3 | 12 | 6749.5 | 877 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 1035 | 0 | 1205.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 24.95 | 164 | 0 | 198 | 0 | 0 | 0 | 350 | 0 | 1.99 | 200 | 48 | 65 | 13 | 70 | 0 | 0 | 0.5 | 87 | 0.05 | 0 | 242 | 10 | 120 | 110 | 0 | 396 | 1040 | 0 | 6331.7 | 13081.2 | 96.48
09:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 63 | 48 | 0 | 0 | 3 | 35 | 16 | 350 | 300 | 0 | 0 | 0 | 333 | 0 | 0 | 14 | 108 | 19 | 14 | 0 | 401 | 0 | 0 | 0 | 0 | 11 | 0 | 16 | 0 | 88 | 12 | 2 | 172 | 0 | 2 | 156 | 0 | 0 | 0 | 0 | 17 | 26 | 0 | 0 | 0 | 994 | 1 | 43 | 0 | 185 | 0 | 347 | 340 | 47 | 197 | 23 | 70 | 80 | 100 | 9 | 19 | 93 | 36 | 8 | 20 | 0 | 310 | 320 | 381 | 36 | 30 | 0 | 8 | 0 | 81 | 30 | 0 | 16 | 167 | 0 | 64 | 158 | 34 | 1 | 13.83 | 12 | 6925.83 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 27 | 1008 | 0 | 1219.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 41.48 | 171 | 0 | 203 | 0 | 0 | 0 | 347 | 0 | 3.02 | 200 | 46 | 35 | 25 | 65 | 0 | 0 | 1.8 | 89 | 0.06 | 0 | 248 | 4 | 120 | 110 | 0 | 396 | 1050 | 0 | 6396.32 | 13322.15 | 96.5
10:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 44 | 52 | 48 | 0 | 0 | 35 | 35 | 16 | 350 | 299 | 0 | 0 | 0 | 332 | 0 | 0 | 10 | 160 | 25.5 | 14 | 0 | 400 | 0 | 0 | 0 | 0 | 18 | 0 | 16 | 0 | 88 | 15 | 5 | 172 | 0 | 2 | 156 | 0 | 0 | 0 | 0 | 17 | 26 | 0 | 0 | 0 | 984 | 4 | 43 | 0 | 185 | 0 | 346 | 340 | 45 | 199 | 26 | 70 | 80 | 100 | 9 | 19 | 93 | 32 | 8 | 32 | 0 | 315 | 320 | 385 | 34 | 30 | 0 | 0 | 0 | 80 | 30 | 0 | 16 | 166 | 0 | 64 | 148 | 34 | 1 | 6.7 | 12 | 7039.2 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 71 | 1005 | 0 | 1232.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 32.41 | 171 | 0 | 185 | 0 | 0 | 0 | 352 | 0 | 2.3 | 200 | 46 | 35 | 30 | 70 | 0 | 0 | 5.2 | 144 | 0.09 | 0 | 245 | 8 | 120 | 110 | 0 | 493 | 1050 | 0 | 6594.82 | 13634.02 | 96.52
11:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 54 | 52 | 48 | 0 | 0 | 35 | 35 | 49 | 350 | 298 | 0 | 0 | 0 | 332 | 0 | 0 | 23 | 160 | 25.5 | 14 | 0 | 382 | 0 | 0 | 0 | 0 | 20 | 0 | 16 | 0 | 88 | 48 | 2 | 172 | 0 | 2 | 154 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 0 | 1000 | 5 | 43 | 0 | 185 | 0 | 343 | 340 | 45 | 193 | 26 | 80 | 80 | 107 | 9 | 19 | 93 | 36 | 8 | 49 | 0 | 310 | 340 | 365 | 36 | 30 | 0 | 8 | 0 | 79 | 30 | 0 | 16 | 166 | 0 | 55 | 148 | 34 | 1 | 48.02 | 12 | 7188.52 | 890 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 56 | 1000 | 0 | 1222.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119 | 0 | 57.4 | 171 | 0 | 183 | 0 | 0 | 0 | 342 | 0 | 5.01 | 190 | 46 | 35 | 35 | 65 | 0 | 0 | 3.3 | 203 | 0.79 | 0 | 247 | 8 | 120 | 110 | 0 | 396 | 1050 | 0 | 6592.67 | 13781.19 | 96.53
12:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 54 | 56 | 64 | 0 | 0 | 35 | 45 | 50 | 450 | 301 | 0 | 0 | 0 | 330 | 0 | 0 | 33 | 108 | 25.5 | 18 | 0 | 500 | 0 | 0 | 0 | 0 | 19 | 0 | 16 | 0 | 88 | 48 | 1 | 172 | 0 | 2 | 156 | 0 | 0 | 0 | 0 | 17 | 37 | 0 | 0 | 0 | 1052 | 7 | 43 | 0 | 185 | 0 | 350 | 340 | 41 | 215 | 31 | 93 | 80 | 136 | 9 | 19 | 93 | 36 | 43 | 39 | 34 | 315 | 320 | 376 | 36 | 30 | 0 | 8 | 0 | 82 | 30 | 0 | 16 | 166 | 0 | 55 | 139 | 34 | 2 | 49.9 | 12 | 7608.4 | 891 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 55 | 1007 | 0 | 1215.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116 | 0 | 34.12 | 172 | 0 | 187 | 0 | 0 | 0 | 392 | 0 | 4.63 | 182 | 46 | 63 | 13 | 70 | 0 | 0 | 8 | 85 | 0.86 | 0 | 274 | 8 | 120 | 110 | 0 | 396 | 1050 | 0 | 6537.98 | 14146.38 | 96.53
13:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 13 | 54 | 86 | 64 | 0 | 0 | 35 | 54 | 50 | 450 | 280 | 0 | 0 | 0 | 328 | 0 | 0 | 25 | 108 | 25.5 | 18 | 0 | 502 | 0 | 0 | 0 | 0 | 14 | 0 | 16 | 0 | 88 | 48 | 3 | 172 | 0 | 6 | 155 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 1005 | 7 | 43 | 0 | 175 | 0 | 348 | 340 | 2 | 198 | 31 | 93 | 80 | 148 | 9 | 19 | 93 | 36 | 52.2 | 37 | 37 | 310 | 320 | 320 | 36 | 30 | 0 | 8 | 0 | 82 | 30 | 0 | 16 | 166 | 26 | 64 | 139 | 33 | 2 | 18.03 | 12 | 7441.73 | 891 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 68 | 1000 | 0 | 1321.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116 | 0 | 51.4 | 172 | 0 | 184 | 0 | 0 | 0 | 363 | 0 | 3.72 | 181 | 48 | 70 | 32 | 34 | 0 | 0 | 8 | 85 | 0.14 | 0 | 280 | 7 | 120 | 110 | 0 | 396 | 1050 | 0 | 6629.32 | 14071.05 | 96.55
14:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 17 | 21 | 86 | 32 | 0 | 0 | 17 | 54 | 50 | 450 | 280 | 0 | 0 | 0 | 328 | 0 | 0 | 13 | 108 | 25.5 | 14 | 0 | 490 | 0 | 0 | 0 | 0 | 27 | 0 | 16 | 0 | 88 | 48 | 1 | 172 | 0 | 2 | 155 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 992 | 11 | 43 | 0 | 175 | 0 | 345 | 340 | 16 | 190 | 31 | 93 | 80 | 170 | 26 | 19 | 104 | 40 | 25 | 44 | 36 | 310 | 320 | 364 | 36 | 30 | 0 | 8 | 0 | 81 | 30 | 0 | 16 | 167 | 13 | 64 | 145 | 33 | 2 | 25.56 | 12 | 7425.06 | 890 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 42 | 1013 | 0 | 1394.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112 | 0 | 6.79 | 172 | 0 | 187 | 0 | 0 | 0 | 395 | 0 | 0.59 | 163 | 48 | 70 | 31 | 34 | 0 | 0 | 6.8 | 109 | 0 | 0 | 274 | 7 | 120 | 110 | 0 | 396 | 1050 | 0 | 6669.87 | 14094.93 | 96.56
15:00 | 0 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 17 | 54 | 70 | 0 | 0 | 0 | 17 | 54 | 50 | 450 | 275 | 0 | 0 | 0 | 328 | 0 | 0 | 16 | 108 | 25.5 | 18 | 0 | 490 | 0 | 0 | 0 | 0 | 19 | 0 | 16 | 0 | 88 | 48 | 1 | 172 | 0 | 2 | 210 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 995 | 6 | 43 | 0 | 185 | 0 | 349 | 340 | 36 | 191 | 25 | 112 | 80 | 170 | 26 | 19 | 110 | 42 | 25 | 27 | 36 | 310 | 320 | 364 | 35 | 30 | 0 | 8 | 0 | 84 | 30 | 0 | 16 | 167 | 35 | 0 | 0 | 0 | 1 | 15.37 | 8 | 7302.87 | 893 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 47 | 1000 | 0 | 1423.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 17.41 | 171 | 0 | 167 | 0 | 0 | 0 | 405 | 0 | 1.74 | 197 | 47 | 70 | 26 | 34 | 0 | 0 | 6.1 | 97 | 0 | 0 | 279 | 8 | 120 | 110 | 0 | 429 | 1050 | 0 | 6678.15 | 13981.02 | 96.57
16:00 | 0 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 17 | 45 | 70 | 93 | 0 | 0 | 17 | 54 | 38 | 450 | 273 | 0 | 0 | 0 | 328 | 0 | 0 | 9 | 108 | 25.5 | 18 | 0 | 494 | 0 | 0 | 0 | 0 | 10 | 0 | 16 | 0 | 100 | 60 | 2 | 172 | 0 | 2 | 211 | 0 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 989 | 3 | 43 | 0 | 175 | 0 | 349 | 340 | 44 | 192 | 26 | 115 | 80 | 170 | 27 | 19 | 93 | 38 | 25 | 29 | 36 | 305 | 320 | 367 | 35 | 28 | 0 | 8 | 0 | 84 | 30 | 0 | 16 | 167 | 35 | 52 | 123 | 10 | 0 | 10.65 | 4 | 7639.15 | 892 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 27 | 992 | 0 | 1419.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 19.39 | 172 | 0 | 168 | 0 | 0 | 0 | 394 | 0 | 2.03 | 198 | 47 | 70 | 11 | 34 | 0 | 0 | 4.7 | 41 | 0.25 | 0 | 275 | 8 | 120 | 110 | 0 | 469 | 1050 | 0 | 6573.98 | 14213.13 | 96.58
17:00 | 0 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 17 | 17 | 50 | 109 | 0 | 0 | 17 | 54 | 16 | 380 | 280 | 0 | 0 | 0 | 328 | 0 | 0 | 6 | 108 | 25.5 | 18 | 0 | 435 | 0 | 0 | 0 | 0 | 12 | 0 | 16 | 0 | 70 | 60 | 1 | 172 | 0 | 2 | 210 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 914 | 3 | 43 | 0 | 185 | 0 | 347 | 340 | 46 | 189 | 26 | 114 | 80 | 170 | 36 | 19 | 111 | 38 | 25 | 17 | 42 | 310 | 320 | 293 | 35 | 28 | 0 | 8 | 0 | 81 | 30 | 0 | 16 | 166 | 17 | 64 | 155 | 17 | 0 | 7.56 | 12 | 7340.06 | 891 | 8 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 992 | 0 | 1410.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 12.72 | 171 | 0 | 170 | 0 | 0 | 0 | 328 | 0 | 1.14 | 200 | 47 | 70 | 1 | 34 | 0 | 0 | 2.4 | 56 | 0.13 | 0 | 244 | 7 | 100 | 110 | 0 | 458 | 1010 | 0 | 6385.1 | 13725.16 | 96.59
18:00 | 0 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 17 | 17 | 50 | 126 | 0 | 0 | 17 | 54 | 16 | 330 | 277 | 0 | 0 | 0 | 280 | 0 | 0 | 2 | 108 | 25.5 | 18 | 0 | 366 | 0 | 0 | 0 | 0 | 14 | 0 | 16 | 0 | 70 | 60 | 0 | 172 | 0 | 5 | 209 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 852 | 1 | 43 | 0 | 185 | 0 | 300 | 340 | 46 | 189 | 29 | 115 | 80 | 170 | 37 | 19 | 111 | 26 | 25 | 3 | 43 | 310 | 320 | 293 | 35 | 28 | 0 | 8 | 0 | 81 | 30 | 0 | 16 | 164 | 17 | 67 | 174 | 17 | 0 | 3.81 | 12 | 7067.31 | 893 | 28 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7 | 991 | 0 | 1307.46 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 4 | 0 | 2.75 | 170 | 0 | 161 | 0 | 0 | 0 | 327 | 0 | 0.25 | 200 | 48 | 70 | 1 | 34 | 0 | 0 | 0.8 | 11 | 0.03 | 0 | 196 | 7 | 100 | 110 | 0 | 457 | 860 | 0 | 6033.29 | 13100.6 | 96.6
19:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 18 | 17 | 50 | 127 | 15 | 0 | 19 | 120 | 16 | 400 | 300 | 0 | 0 | 17 | 328 | 0 | 0 | 0 | 134 | 25.5 | 18 | 0 | 483 | 0 | 15 | 0 | 0 | 17 | 39 | 19 | 0 | 100 | 60 | 0 | 172 | 3 | 7 | 209 | 0 | 0 | 6 | 0 | 9 | 218 | 0 | 0 | 0 | 942 | 0 | 43 | 63 | 185 | 0 | 310 | 300 | 46 | 210 | 29 | 115 | 80 | 175 | 38 | 19 | 111 | 28 | 25 | 0 | 43 | 315 | 320 | 368 | 35 | 28 | 0 | 8 | 0 | 81 | 30 | 0 | 16 | 167 | 18 | 92 | 176 | 65 | 0 | 0 | 12 | 7942.5 | 843 | 26 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1015 | 20 | 1401.43 | 0 | 0 | 0 | 12 | 5 | 96 | 0 | 15 | 0 | 0 | 15 | 0 | 171 | 0 | 169 | 0 | 0 | 0 | 414 | 0 | 0 | 200 | 47 | 90 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 16 | 244 | 10 | 110 | 110 | 0 | 459 | 790 | 6 | 6402.43 | 14344.93 | 96.61
19:30 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 50 | 54 | 50 | 127 | 15 | 0 | 35 | 126 | 49 | 400 | 277 | 0 | 0 | 35 | 334 | 0 | 0 | 0 | 160 | 26 | 18 | 0 | 444 | 0 | 15 | 0 | 0 | 23 | 65 | 43 | 0 | 100 | 36 | 0 | 172 | 20 | 10 | 211 | 0 | 0 | 18 | 0 | 45 | 220 | 0 | 0 | 0 | 1010 | 0 | 43 | 135 | 185 | 0 | 349 | 335 | 46 | 189 | 29 | 115 | 80 | 180 | 38 | 19 | 112 | 42 | 43 | 0 | 43 | 310 | 320 | 346 | 35 | 28 | 0 | 8 | 0 | 81 | 30 | 0 | 16 | 167 | 54.5 | 92 | 155 | 66 | 0 | 0 | 12 | 8348.5 | 842 | 26 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1083 | 35 | 1420.47 | 0 | 0 | 0 | 76 | 5 | 96 | 0 | 17 | 0 | 0 | 20 | 0 | 171 | 0 | 185 | 0 | 0 | 0 | 346 | 0 | 0 | 200 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 16 | 272 | 11 | 120 | 110 | 0 | 458 | 870 | 17 | 6708.47 | 15056.97
20:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 48 | 49 | 61 | 127 | 15 | 0 | 35 | 129 | 32 | 400 | 275 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 160 | 26 | 18 | 0 | 421 | 0 | 15 | 0 | 0 | 23 | 65 | 73 | 0 | 100 | 36 | 0 | 172 | 30 | 14 | 209 | 0 | 0 | 18 | 0 | 38 | 218 | 0 | 0 | 0 | 1000 | 0 | 43 | 137 | 185 | 0 | 351 | 340 | 47 | 187 | 29 | 115 | 80 | 166 | 37 | 19 | 111 | 40 | 52.2 | 0 | 43 | 310 | 320 | 338 | 35 | 30 | 0 | 8 | 0 | 81 | 30 | 0 | 16 | 167 | 42 | 92 | 164 | 80 | 0 | 0 | 12 | 8353.2 | 842 | 34 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1077 | 50 | 1419.62 | 0 | 33 | 0 | 90 | 6 | 96 | 0 | 37 | 0 | 0 | 22 | 0 | 172 | 0 | 186 | 0 | 0 | 0 | 325 | 0 | 0 | 200 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 11 | 114 | 110 | 0 | 458 | 1020 | 14 | 6900.62 | 15253.82 | 96.62
21:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 45 | 17 | 68 | 112 | 15 | 0 | 17 | 108 | 16 | 400 | 288 | 0 | 0 | 17 | 333 | 0 | 0 | 0 | 160 | 26 | 18 | 0 | 463 | 0 | 15 | 0 | 0 | 13 | 65 | 73 | 0 | 100 | 12 | 0 | 172 | 16 | 20 | 209 | 0 | 0 | 19 | 1 | 45 | 218 | 0 | 0 | 0 | 1090 | 0 | 43 | 100 | 185 | 0 | 351 | 340 | 47 | 190 | 25 | 115 | 80 | 153 | 38 | 19 | 111 | 44 | 52.2 | 0 | 43 | 305 | 320 | 388 | 34 | 30 | 0 | 8 | 0 | 81 | 30 | 0 | 16 | 167 | 21 | 82 | 174 | 80 | 0 | 0 | 12 | 8307.2 | 893 | 110 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1085 | 70 | 1449.87 | 0 | 44 | 0 | 112 | 6 | 96 | 0 | 37 | 0 | 0 | 22 | 0 | 171 | 0 | 189 | 0 | 0 | 0 | 397 | 0 | 0 | 200 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 11 | 120 | 110 | 0 | 458 | 1110 | 14.5 | 7292.37 | 15599.57 | 96.63
22:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 39 | 17 | 68 | 112 | 0 | 0 | 17 | 108 | 16 | 400 | 285 | 0 | 0 | 17 | 333 | 0 | 0 | 0 | 160 | 26 | 18 | 0 | 453 | 0 | 15 | 0 | 0 | 16 | 65 | 73 | 0 | 88 | 12 | 0 | 172 | 15 | 20 | 211 | 0 | 0 | 19 | 8 | 17 | 218 | 0 | 0 | 0 | 1080 | 0 | 43 | 60 | 185 | 0 | 351 | 340 | 47 | 193 | 28 | 115 | 80 | 151 | 37 | 19 | 111 | 44 | 52.2 | 0 | 43 | 305 | 320 | 386 | 35 | 30 | 0 | 8 | 0 | 81 | 30 | 0 | 16 | 166 | 17 | 82 | 175 | 95 | 0 | 0 | 12 | 8193.2 | 893 | 305 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1085 | 53 | 1451.09 | 0 | 46 | 0 | 70 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 0 | 172 | 0 | 189 | 0 | 0 | 0 | 403 | 0 | 0 | 195 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 11 | 0 | 110 | 0 | 458 | 1110 | 15 | 7225.09 | 15418.29 | 96.64
23:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 29 | 17 | 70 | 112 | 0 | 0 | 17 | 108 | 16 | 400 | 292 | 0 | 0 | 17 | 333 | 0 | 0 | 0 | 160 | 26 | 18 | 0 | 461 | 0 | 15 | 0 | 0 | 23 | 65 | 73 | 0 | 100 | 12 | 0 | 172 | 15 | 20 | 211 | 0 | 0 | 19 | 8 | 15 | 219 | 0 | 0 | 0 | 1100 | 0 | 43 | 50 | 185 | 0 | 350 | 340 | 47 | 197 | 28 | 115 | 80 | 153 | 37 | 19 | 111 | 44 | 52.2 | 0 | 43 | 310 | 320 | 389 | 34 | 30 | 0 | 8 | 0 | 81 | 30 | 0 | 16 | 166 | 17 | 82 | 176 | 96 | 0 | 0 | 12 | 8244.2 | 891 | 330 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1088 | 53 | 1447.99 | 0 | 46 | 0 | 70 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 0 | 171 | 0 | 189 | 0 | 0 | 0 | 414 | 0 | 0 | 190 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 11 | 0 | 110 | 0 | 458 | 1120 | 15 | 7268.99 | 15513.19 | 96.65
Total KWH | 0 | 1543680 | 713280 | 0 | 0 | 0 | 0 | 0 | 8362800 | 0 | 0 | 513720 | 682560 | 1609632 | 2144640 | 83302 | 0 | 588918 | 1967040 | 769920 | 9358000 | 6981295 | 0 | 0 | 127252 | 7698940 | 0 | 0 | 161907 | 3312000 | 524400 | 400320 | 0 | 10184545.45 | 12545 | 82800 | 0 | 0 | 360480 | 548706 | 899152 | 0 | 2113920 | 997440 | 20008 | 4131740 | 245100 | 337440 | 4269090.91 | 0 | 0 | 150720 | 77801.4 | 571236 | 2960600 | 0 | 0 | 0 | 24572725 | 45900 | 1006872 | 1199345 | 4432727 | 0 | 8655200 | 8166000 | 1017120 | 4785000 | 638784 | 2492160 | 1874640 | 3768960 | 505680 | 439060 | 2407680 | 949440 | 841507 | 337891 | 675232 | 7527500 | 7714000 | 9063000 | 839000 | 681240 | 0 | 177144 | 0 | 1916160 | 710112 | 0 | 392000 | 4448000 | 380520 | 1664400 | 3628800 | 709440 | 10350 | 178410 | 277680 | 184636609.76 | 20952727 | 1012032 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 441360 | 25483640 | 487680 | 31750909 | 0 | 188987 | 0 | 627744 | 79576 | 613888 | 0 | 136741 | 0 | 679310 | 220582 | 312752 | 4071000 | 0 | 4671036 | 0 | 0 | 0 | 8867127 | 0 | 29520 | 4759000 | 1114036 | 2116835 | 199607 | 1949001 | 0 | 0 | 46957.56 | 1116720 | 1696 | 26304 | 6218000 | 223593 | 2465000 | 2381790 | 0 | 10209888 | 26074181.82 | 80400 | 160521620.38 | 345158230.14

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 15-06-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14146.38 | MW | 12:00 Hr. | Energy Generated |  |  | 345.1582 |  | MKWHr.
| Day Peak Demand |  |  | 14146.38 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.499 |  | MKWHr.
| Evening Peak Generation |  |  | 15599.57 | MW | 21:00 Hr. | Energy Demand |  |  | 345.6572 |  | MKWHr.
| Evening Peak Demand |  |  | 15641.57 | MW | 21:00 Hr. | Maximum Temperature |  |  | 34 |  | °C
| Minimum Generation of the Day |  |  | 13014.92 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 1016.85 |  | MMCFD
| Maximum Generation of the Day |  |  | 15638.42 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.6406 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 43.5103 | 0 | 14.0559 | 0 | 0 | 0.16191 | 0 | 0 | 57.7282 | Gas | 135.6929 | Gas | 484384969.6565
| Chattogram Zone |  |  | 3.298 | 28.8418 | 5.6994 | 0 | 4.1317 | 0.065908 | 0 | 0.36048 | 42.3974 | Coal | 102.7006 | Coal | 641364312.0794
| Cumilla Zone |  |  | 31.0154 | 0 | 11.8906 | 0 | 0 | 0.33789 | 0.94944 | 0 | 44.1933 | HFO | 44.1251 | HFO | 817693388.818
| Mymensingh Zone |  |  | 0.70944 | 0 | 5.9514 | 0 | 0 | 0.18876 | 0 | 0 | 6.8496 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 33.4682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.4682 | Hydro | 4.1317 | Hydro | 413174
| Khulna Zone |  |  | 1.012 | 25.4836 | 0.48768 | 0 | 0 | 0.44136 | 21.8647 | 0 | 49.2894 | Solar | 3.5824 | Solar | 58154736.0016
| Barishal Zone |  |  | 5.0704 | 42.5021 | 0.1067 | 0 | 0 | 0.001696 | 0 | 0 | 47.6809 | Import | 54.5651 | Import | 284784510.08
| Rajshahi Zone |  |  | 17.6092 | 0 | 1.8675 | 0 | 0 | 1.0216 | 31.7509 | 0 | 52.2492 | Wind | 0.36048 | Wind | 5277427.2
| Rangpur Zone |  |  | 0 | 5.873 | 4.0658 | 0 | 0 | 1.3633 | 0 | 0 | 11.3022
| Total |  |  | 135.6929 | 102.7006 | 44.1251 | 0 | 4.1317 | 3.5824 | 54.5651 | 0.36048 | 345.1582
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 484384969.6565 |  | Hydro | 413174
|  |  |  | Coal | 641364312.0794 |  | Solar | 58154736.0016
|  |  |  | HFO | 817693388.818 |  | Import | 284784510.08
|  |  |  | HSD | 0 |  | Wind | 5277427.2
[5 empty] | Total: | 229,20,72,517 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 925018.19 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.9527 | Peak Hr Flow | 893.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 7476545.5 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 31.7509 | Peak Hr Flow | 1449.87 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 660 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.94944 | Peak Hr Flow | 44.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 794 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 53.6531 | Peak Hr Flow | 2386.87 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4826
|  |  |  | Chattogram |  | 0 |  | 1497
|  |  |  | Cumilla |  | 0 |  | 1502
|  |  |  | Mymensingh |  | 0 |  | 1289
|  |  |  | Sylhet |  | 0 |  | 673
|  |  |  | Khulna |  | 0 |  | 1905
|  |  |  | Barishal |  | 0 |  | 498
|  |  |  | Rajshahi |  | 15 |  | 1670
|  |  |  | Rangpur |  | 25 |  | 1090
|  |  |  | Total |  | 40 |  | 14950
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Bheramara 410 MW CCPP GT |  |  | 278
[7 empty] | 5 | Bheramara 410 MW CCPP ST |  |  | 132
[7 empty] | 6 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[5 empty] | Total | 300 |  |  |  | Total | 886
|  |  |  | Total Unavailable Capacity |  |  |  | 1186
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:35 | 09:32 | Cumilla(S) 132/33kV S/S TR-2 LT Scheduled S/D Due to Red hot maintenance by PDB | [7 empty] | 34.0MW load
interrup.
| 08:36 | 09:32 | Cumilla(S) 132/33kV S/S TR-2 HT Scheduled S/D Due to Do | [7 empty] | 34.0MW load
interrup.
| 08:50 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is ON with remarks:- FGMO Max @ 08:47 hrs
| 09:29 | 11:10 | Ashuganj-Kishoreganj 132kV Ckt-1 Scheduled S/D from Bajitpur 132/33kV end.
|  | 10:00 | Madunaghat 400/230kV S/S ATR-2 7106T HT is restored.
|  | 10:01 | Madunaghat 400/230kV S/S ATR-2 7106T LT is restored.
| 10:10 | 12:41 | BIPTC S/S 10CF15 Scheduled S/D Due to Tripped by C1 unbalance 60/61 CPR04
| 10:31 | 13:17 | Daudkandi-Sonargaon 132 kV Ckt-2 Forced S/D from Sonargaon 132/33kV end Due to By the
instructions of NLDC
| 10:32 | 11:20 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) LT Scheduled S/D Due to Red
hot mainteance
| 10:32 | 11:19 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT Scheduled S/D Due to Red
hot mainteance
| 10:38 | 14:34 | Sonargaon 132/33kV S/S OPML(IEL-1) Forced S/D Due to For working at bus A
| 10:47 | 14:29 | Haripur-Sonargaon 132kV Ckt-2 Scheduled S/D from Haripur 230/132kV end Due to
Maintenance on the other end and from Sonargaon 132/33kV end Due to Due to CB maintenance
| 12:00 | 12:05 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Tripped from Shahjibazar 132/33kV end showing
Distance relay relays Due to N/A
| 12:00 |  | Day peak generation: 14143 MW
| 12:01 |  | HVDC(Nepal) Synchronized with remarks:- inport by Bheramara HVDC Line.
| 12:13 |  | Madunaghat 400/230kV S/S ATR-1 7006T HT Project Work S/D Due to Fire system
install,testing & commissioning purpose.
| 12:13 |  | Madunaghat 400/230kV S/S ATR-1 7006T LT Scheduled S/D
| 12:13 |  | Madunaghat 400/230kV S/S ATR-1 7006T HT Scheduled S/D
| 12:43 | 13:03 | Gopalganj 132/33kV S/S T2 LT Tripped showing Over current instt. relays Due to Over | [7 empty] | 47.0MW load
|  |  | current instt. by REB-8 Gopalganj pbs | [7 empty] | interrup.
|  | 13:03 | Gopalganj 132/33kV S/S T2 LT is restored.
| 15:26 | 15:50 | AKSML-Baroaulia 132kV Ckt-1 Scheduled S/D from AKS 132/33kV end Due to Demand to Baraulia
ss Maintenance
| 16:23 | 20:18 | Dhamrai 132/33kV S/S Transformer-2 LT Tripped showing O/C,86,SPS relay relays Due to PBS
feeder trip
| 16:23 | 16:42 | Dhamrai 132/33kV S/S Transformer-1 LT Tripped showing O/C, 86 & SPS relay relays Due to
PBS feeder tripped
|  | 16:35 | Bogura 400/230kV S/S Bogura - Rooppur 400 KV Line-1 is restored.
| 17:25 | 20:17 | Dhamrai 132/33kV S/S Transformer-2 HT Scheduled S/D Due to 33 kV MAH feeder bus jumper
maintenance
| 17:25 | 20:18 | Dhamrai 132/33kV S/S Transformer-2 LT Scheduled S/D Due to 33 kV MAH feeder bus jumper
maintenance
| 18:22 | 19:10 | Madanganj 132/33kV S/S GT-1 HT Tripped showing Backup protection trip relays Due to PBS | [7 empty] | 8.0MW load
|  |  | 33/11 kv feeder fault | [7 empty] | interrup.
| 18:22 |  | Madanganj 132/33kV S/S GT-1 LT Tripped showing Over current relay relays Due to PBS 33/11 | [7 empty] | 8.0MW load
|  |  | kv feeder fault | [7 empty] | interrup.
| 20:50 |  | Raozan 25 MW PP Synchronized
| 23:13 |  | Bhola 225 MW CCPP GT-1 Sync.
| 23:58 |  | Raozan 25 MW PP Shutdown
| 00:47 |  | Siddhirganj GT-1 was sync.
| 07:00 |  | Min. Gen. 12972 MW
| 07:08 |  | Shahjibazar 132/33kV S/S TR-06 LT Scheduled S/D Due to Shutdown taken by pbs for red hot | [7 empty] | 72.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 07:08 |  | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to Shutdown taken by pbs for red hot | [7 empty] | 72.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 07:08 |  | Shahjibazar 132/33kV S/S TR-02 LT Scheduled S/D Due to Shutdown taken by pbs for red hot | [7 empty] | 72.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 07:09 |  | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to Shutdown taken by pbs for red hot | [7 empty] | 72.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 07:17 |  | Shahjibazar 132/33kV S/S TR-02 HT Scheduled S/D Due to Shutdown taken by pbs for red hot | [7 empty] | 72.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 08:00 |  | Chauddagram 132/33kV S/S 132 kv T-1 LT Scheduled S/D Due to 33kv Bus Shutdown for | [7 empty] | 28.0MW load
|  |  | maintenance (PBS) | [7 empty] | interrup.
| 08:00 |  | Chauddagram 132/33kV S/S 132 kv T-1 HT Scheduled S/D Due to 33kv Bus Shutdown for | [7 empty] | 28.0MW load
|  |  | maintenance (PBS) | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 15-06-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 349 | 8362800 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9358000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 288 | 6981295 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 333 | 7698940 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 45 | 513720 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 112 | 2144640 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 588918 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 127252 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 26 | 524400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 18 | 400320 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 33 | 713280 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 15 | 83302 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 68 | 1609632 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1543680 | Fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 769920 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 1967040 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 161907 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 682560 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 463 | 10184545.45 | None
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 160 | 3312000 | -
Dhaka Area Total |  |  |  |  | 5939.724 | 2555 | 57728151.45
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 1 | 77801.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 45900 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 150720 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 172 | 4131740 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 2960600 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 45 | 571236 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 73 | 899152 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 548706 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 2113920 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 20 | 337440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20008 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 82800 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 16 | 245100 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 997440 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 12545 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1090 | 24572725 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 13 | 360480 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 209 | 4269090.91 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4895.72 | 2068 | 42397404.31
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 190 | 4785000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 351 | 8655200 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 8166000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 25 | 638784 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 47 | 1017120 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 185 | 4432727 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 43 | 1006872 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 100 | 1199345 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 43 | 675232 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1874640 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 153 | 3768960 | -
| Import (Tripura) |  | Import | 0 | 160 | 44 | 949440 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 841507 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 439060 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 111 | 2407680 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 505680 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 2492160 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 337891 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1936.2 | 44193298
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 80 | 709440 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10350 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 174 | 3628800 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 82 | 1664400 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 178410 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 277680 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 21 | 380520 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 369 | 6849600
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 34 | 839000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 681240 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Borescope Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 710112 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1916160 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 167 | 4448000 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 392000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 177144 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7527500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 388 | 9063000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7714000 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1379 | 33468156
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 893 | 20952727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 110 | 1012032 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 70 | 487680 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 441360 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1085 | 25483640 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2196 | 49289439
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 458 | 10209888 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 26304 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 11 | 223593 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2465000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1110 | 26074181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 110 | 2381790 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 14.5 | 80400 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 273 | 6218000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1696 | -
Barishal Area Total |  |  |  |  | 2236 | 2096.5 | 47680852.82
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 44 | 188987 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 6 | 79576 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 136741 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 171 | 4071000 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 189 | 4671036 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 397 | 8867127 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 220582 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 613888 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 112 | 627744 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 29520 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1449.87 | 31750909 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 312752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 679310 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2523.87 | 52249172
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 48 | 1114036 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4759000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1949001 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 46957.56 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2116835 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 199607 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1116720 | -
Rangpur Area Total |  |  |  |  | 950 | 476 | 11302156.56
Eastern Grid Total |  |  |  |  | 16705.895 | 8307.2 | 184636609.76
Western Grid Total |  |  |  |  | 10378.16 | 7292.37 | 160521620.38
National Grid Total |  |  |  |  | 27084.055 | 15599.57 | 345158230.14
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 15-06-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9787.63 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5122.6 | MW
i) Dhaka area |  |  | 4826.37 |  | MW | i) Khulna area |  |  |  | 1904.6 | MW
ii) Chattogram area |  |  | 1497 |  | MW | ii) Barishal area |  |  |  | 498 | MW
iii) Cumilla area |  |  | 1502.26 |  | MW | iii) Rajshahi area |  |  |  | 1655 | MW
iv) Mymensingh area |  |  | 1289 |  | MW | iv) Rangpur area |  |  |  | 1065 | MW
v) Sylhet area |  |  | 673 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14910.23 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 88 | 21:00 | 133 | Patuakhali | 92 | 00:00
2 | AKSML | 67 | 15:00 | 68 | Jaldhaka | 96 | 23:00 | 134 | Payra | 38 | 00:00
3 | Aftabnagar | 40 | 12:00 | 69 | Jamalpur | 143 | 23:00 | 135 | Postogola | 52 | 15:00
4 | Agargaon | 138 | 12:00 | 70 | Jashore | 156 | 00:00 | 136 | Purbachal | 21 | 00:00
5 | Agrabad | 90 | 18:30 | 71 | Jhenaidah | 137 | 23:00 | 137 | Purbasadipur | 147 | 23:00
6 | Amnura | 47 | 00:00 | 72 | Joydebpur | 137 | 12:00 | 138 | Rahanpur | 39 | 00:00
7 | Ashuganj | 109 | 16:00 | 73 | Joypurhat | 71 | 00:00 | 139 | Rahim | 21 | 14:00
8 | BSRM | 195 | 11:00 | 74 | Juldah | 13 | 15:00 | 140 | Rajbari | 88 | 00:00
9 | Bagerhat | 89 | 00:00 | 75 | KSRM | 21 | 06:00 | 141 | Rajendrapur | 128 | 20:00
10 | Bajitpur | 56 | 00:00 | 76 | Kabirpur | 219 | 16:00 | 142 | Rajshahi | 124 | 21:00
11 | Bakulia | 95 | 20:00 | 77 | Kachua | 104 | 00:00 | 143 | Rajshahi-230 | 113 | 00:00
12 | Banani | 38 | 11:00 | 78 | Kallyanpur | 105 | 00:00 | 144 | Ramganj | 112 | 04:00
13 | Bangabhaban | 21 | 11:00 | 79 | Kalurghat | 40 | 15:00 | 145 | Rampur | 44 | 00:00
14 | Barapukuria | 74 | 23:00 | 80 | Kamrangirchar | 52 | 13:00 | 146 | Rangamati | 17 | 21:00
15 | Barguna | 26 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 171 | 19:30
16 | Barishal | 118 | 02:00 | 82 | Kasba | 39 | 00:00 | 148 | Ruppur | 7.4 | 09:00
17 | Barishal-230 | 120 | 00:00 | 83 | Kazla | 77 | 00:00 | 149 | SSM | 9 | 23:00
18 | Baroaulia | 57 | 00:00 | 84 | Keranigonj | 96 | 00:00 | 150 | Saidpur | 122 | 19:30
19 | Baroirhat | 68 | 00:00 | 85 | Khagrachori | 32 | 00:00 | 151 | Satkhira | 152 | 20:00
20 | Bashundhara | 171 | 13:00 | 86 | Khulna | 73 | 00:00 | 152 | Satmasjid | 104 | 13:00
21 | BashundharaCement | 9 | 18:00 | 87 | Khulshi | 170 | 10:00 | 153 | Savar | 202 | 15:00
22 | Beanibazar | 88 | 00:00 | 88 | Kishoreganj | 162 | 23:00 | 154 | SevenRings | 12.87 | 23:00
23 | Benapole | 72 | 00:00 | 89 | Kodda | 270 | 09:00 | 155 | ShahCement | 19 | 00:00
24 | Bhaluka | 160 | 16:00 | 90 | Kulaura | 56 | 00:00 | 156 | Shahjadpur | 83 | 00:00
25 | Bhandaria | 61 | 00:00 | 91 | Kurigram | 74 | 20:00 | 157 | Shahjibazar | 135 | 00:00
26 | Bhangura | 43 | 21:00 | 92 | Kushtia | 168 | 00:00 | 158 | Shahmirpur | 65 | 00:00
27 | Bheramara(GK) | 73 | 21:00 | 93 | Lalbag | 36 | 18:00 | 159 | Shariatpur | 102 | 00:00
28 | Bhulta | 219 | 16:00 | 94 | Lalmonirhat | 73 | 20:00 | 160 | Sherpur | 180 | 23:00
29 | Bog-Sherpur | 70 | 00:00 | 95 | MI_Cement | 9.6 | 15:00 | 161 | Shikalbaha | 13 | 00:00
30 | Bogura | 177 | 00:00 | 96 | Madanganj | 34 | 00:00 | 162 | Shitalakhya | 85 | 15:00
31 | Borhanuddin | 92 | 01:00 | 97 | Madaripur | 124 | 00:00 | 163 | Sholosohor | 44 | 15:00
32 | Brahmanbaria | 140 | 20:00 | 98 | Madartek | 97.22 | 00:00 | 164 | Shyampur | 118 | 10:00
33 | Cantonment | 160 | 13:00 | 99 | Madunaghat | 58 | 19:30 | 165 | Siddhirganj | 113 | 15:00
34 | Chandina | 18.03 | 02:00 | 100 | Magura | 70 | 00:00 | 166 | Sirajganj | 115 | 00:00
35 | Chandpur | 94 | 00:00 | 101 | Mahasthangarh | 96 | 00:00 | 167 | Sonargaon | 93 | 16:00
36 | Chandraghona | 37 | 19:30 | 102 | Manikganj | 134 | 00:00 | 168 | Sreemongol | 86 | 00:00
37 | Chapai | 83 | 00:00 | 103 | Maniknagar | 68 | 12:00 | 169 | Sreepur | 91 | 19:30
38 | Charsaidpur | 39 | 12:00 | 104 | Matarbari | 54 | 01:00 | 170 | Srinagar | 51 | 23:00
39 | Chauddagram | 83 | 00:00 | 105 | Matuail | 52 | 23:00 | 171 | Sunamganj | 65 | 19:30
40 | Chhatak | 43 | 00:00 | 106 | Millgate | 83 | 11:00 | 172 | Sylhet | 52 | 00:00
41 | Chowmuhani | 236 | 21:00 | 107 | Mirpur | 119 | 12:00 | 173 | Sylhet-132 | 140 | 19:00
42 | Chuadanga | 131 | 01:00 | 108 | Mirsorai | 11 | 14:00 | 174 | TK | 35 | 23:00
43 | Coxsbazar | 138 | 19:00 | 109 | Mirzapur | 46 | 21:00 | 175 | Tangail | 192 | 22:00
44 | Cumilla(N) | 157 | 19:30 | 110 | Mithapukur | 69 | 04:00 | 176 | Thakurgaon | 115 | 21:00
45 | Cumilla(S) | 175 | 00:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 133 | 15:00
46 | Daudkandi | 156 | 00:00 | 112 | Mogbazar | 162.2 | 15:00 | 178 | Ullahpara | 42 | 21:00
47 | Dhaka | 68 | 13:00 | 113 | Mongla | 36 | 12:00 | 179 | Ullon | 57 | 00:00
48 | Dhamrai | 116 | 00:00 | 114 | Motijheel | 43 | 13:00 | 180 | Uttara | 102 | 12:00
49 | Dhanmondi | 162.2 | 13:00 | 115 | Muktagacha | 43 | 22:00 | 181 | UttaraNew | 61 | 00:00
50 | Dohazari | 115 | 19:30 | 116 | Munshiganj | 128 | 00:00 | 182 | Zigatola | 72 | 00:00
51 | Faridpur | 175 | 00:00 | 117 | Muradnagar | 32 | 00:00
52 | Fatullah | 80 | 15:00 | 118 | Mymensingh | 195 | 23:00
53 | Fenchuganj | 45 | 00:00 | 119 | Naogaon | 159 | 00:00
54 | Feni | 124 | 19:30 | 120 | Narail | 65 | 00:00
55 | GPH | 74 | 22:00 | 121 | Narinda | 74 | 13:00
56 | Ghatail | 84 | 19:30 | 122 | Narshingdi | 175 | 23:00
57 | Ghorashal | 17 | 15:00 | 123 | Natore | 175 | 00:00
58 | Ghorashal-230 | 75 | 20:00 | 124 | Nawabganj | 64 | 22:00
59 | Goalpara | 42 | 01:00 | 125 | Netrakona | 148 | 20:00
60 | Gollamari | 98 | 01:00 | 126 | New | 78.1 | 12:00
61 | Gopalganj | 118 | 00:00 | 127 | Niamatpur | 92 | 00:00
62 | Gulshan | 146 | 12:00 | 128 | Noapara | 50 | 01:00
63 | Halishahar | 87 | 15:00 | 129 | PHP | 10 | 12:00
64 | HaripurSBU | 146 | 16:00 | 130 | Pabna | 120 | 19:00
65 | Hasnabad | 50 | 00:00 | 131 | Palashbari | 130 | 00:00
66 | Hathazari | 86 | 19:00 | 132 | Panchagarh | 53 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 15-06-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15638.42 | 49 |  | 15689.63
1:00 | 15295.42 | 53 |  | 15350.81
2:00 | 15071.43 | 47 |  | 15120.55
3:00 | 14616.77 | 47 |  | 14665.89
4:00 | 14346.35 | 0 |  | 14346.35
5:00 | 13929.47 | 0 |  | 13929.47
6:00 | 13377.33 | 0 |  | 13377.33
7:00 | 13014.92 | 0 |  | 13014.92
8:00 | 13081.2 | 0 |  | 13081.2
9:00 | 13322.15 | 0 |  | 13322.15
10:00 | 13634.02 | 0 |  | 13634.02
11:00 | 13781.19 | 0 |  | 13781.19
12:00 | 14146.38 | 0 |  | 14146.38
13:00 | 14071.05 | 0 |  | 14071.05
14:00 | 14094.93 | 0 |  | 14094.93
15:00 | 13981.02 | 83 |  | 14068.02
16:00 | 14213.13 | 0 |  | 14213.13
17:00 | 13725.16 | 0 |  | 13725.16
18:00 | 13100.6 | 0 |  | 13100.6
19:00 | 14344.93 | 25 |  | 14370.93
19:30 | 15056.97 | 42 |  | 15100.97
20:00 | 15253.82 | 45 |  | 15300.85
21:00 | 15599.57 | 40 |  | 15641.57
22:00 | 15418.29 | 40 |  | 15460.09
23:00 | 15513.19 | 70 |  | 15586.34
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 15-06-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8652.2 | 6986.22 | 15638.42 | DAILY GENERATION CURVE
00:30 | 8533.7 | 6933.22 | 15466.92
01:00 | 8415.2 | 6880.22 | 15295.42 | 15-06-2025
01:30 | 8343.7 | 6839.725 | 15183.425
02:00 | 8272.2 | 6799.23 | 15071.43
02:30 | 8184.7 | 6659.4 | 14844.1
03:00 | 8097.2 | 6519.57 | 14616.77
03:30 | 7947.7 | 6533.86 | 14481.56
04:00 | 7798.2 | 6548.15 | 14346.35
04:30 | 7640.2 | 6497.71 | 14137.91
05:00 | 7482.2 | 6447.27 | 13929.47
05:30 | 7271.125 | 6382.275 | 13653.4
06:00 | 7060.05 | 6317.28 | 13377.33
06:30 | 6906.03 | 6290.095 | 13196.125
07:00 | 6752.01 | 6262.91 | 13014.92
07:30 | 6750.755 | 6297.305 | 13048.06
08:00 | 6749.5 | 6331.7 | 13081.2
08:30 | 6837.665 | 6364.01 | 13201.675
09:00 | 6925.83 | 6396.32 | 13322.15
09:30 | 6982.515 | 6495.57 | 13478.085
10:00 | 7039.2 | 6594.82 | 13634.02
10:30 | 7113.86 | 6593.745 | 13707.605
11:00 | 7188.52 | 6592.67 | 13781.19
11:30 | 7398.46 | 6565.325 | 13963.785
12:00 | 7608.4 | 6537.98 | 14146.38
12:30 | 7525.065 | 6583.65 | 14108.715
13:00 | 7441.73 | 6629.32 | 14071.05
13:30 | 7433.395 | 6649.595 | 14082.99
14:00 | 7425.06 | 6669.87 | 14094.93
14:30 | 7363.965 | 6674.01 | 14037.975
15:00 | 7302.87 | 6678.15 | 13981.02
15:30 | 7471.01 | 6626.065 | 14097.075
16:00 | 7639.15 | 6573.98 | 14213.13
16:30 | 7489.605 | 6479.54 | 13969.145
17:00 | 7340.06 | 6385.1 | 13725.16
17:30 | 7203.685 | 6209.195 | 13412.88
18:00 | 7067.31 | 6033.29 | 13100.6
18:30 | 7504.905 | 6217.86 | 13722.765
19:00 | 7942.5 | 6402.43 | 14344.93
19:30 | 8348.5 | 6708.47 | 15056.97
20:00 | 8353.2 | 6900.62 | 15253.82
20:30 | 8330.2 | 7096.495 | 15426.695 |  | Executive Engineer
21:00 | 8307.2 | 7292.37 | 15599.57 |  | Network Operation Division
21:30 | 8250.2 | 7258.73 | 15508.93
22:00 | 8193.2 | 7225.09 | 15418.29
22:30 | 8218.7 | 7247.04 | 15465.74
23:00 | 8244.2 | 7268.99 | 15513.19

## En-Curve
QF-LDC-12
Date | 15-06-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3676 | 1972 | 782 | 0 | 46 | 1437.02 | 172 | 4773.2 | 0 | 774 | 2000.2 | 0 | 0 | 6 | 49 | DAILY ENERGY CURVE
00:30 | 3620.5 | 1927 | 768 | 19 | 44 | 1445.62 | 172 | 4707.6 | 0 | 773 | 1979.2 | 0 | 0 | 11 | 51 | 15-06-2025
01:00 | 3565 | 1882 | 754 | 38 | 42 | 1454.22 | 172 | 4642 | 0 | 772 | 1958.2 | 0 | 0 | 16 | 53
01:30 | 3568 | 1896 | 754 | 38 | 43 | 1406.725 | 172 | 4589.5 | 0 | 754.5 | 1943.7 | 0 | 0 | 18 | 50 | Energy Generated | 345.1582 |  | MKWHr
02:00 | 3571 | 1910 | 754 | 38 | 44 | 1359.23 | 172 | 4537 | 0 | 737 | 1929.2 | 0 | 0 | 20 | 47 | Energy not Served | 0.499 |  | MKWHr
02:30 | 3586 | 1924 | 754 | 38 | 43 | 1336.4 | 172 | 4487.5 | 0 | 662.5 | 1826.2 | 0 | 0 | 14.5 | 47 | Total Energy Requirement | 345.6572 |  | MKWHr
03:00 | 3601 | 1938 | 754 | 38 | 42 | 1313.57 | 172 | 4438 | 0 | 588 | 1723.2 | 0 | 0 | 9 | 47
03:30 | 3615.5 | 1961.5 | 815.5 | 38 | 42 | 1264.86 | 172 | 4435 | 0 | 516.5 | 1607.7 | 0 | 0 | 13 | 23.5
04:00 | 3630 | 1985 | 877 | 38 | 42 | 1216.15 | 172 | 4432 | 0 | 445 | 1492.2 | 0 | 0 | 17 | 0
04:30 | 3614 | 1986.5 | 877 | 38 | 42 | 1218.21 | 172 | 4399.5 | 0 | 408.5 | 1367.2 | 0 | 0 | 15 | 0
05:00 | 3598 | 1988 | 877 | 38 | 42 | 1220.27 | 172 | 4367 | 0 | 372 | 1242.2 | 0 | 0 | 13 | 0
05:30 | 3535 | 1962.5 | 877 | 38 | 41 | 1211.75 | 172 | 4250.5 | 14.05 | 356.5 | 1184.6 | 0 | 0 | 10.5 | 0
06:00 | 3472 | 1937 | 877 | 38 | 40 | 1203.23 | 172 | 4134 | 28.1 | 341 | 1127 | 0 | 0 | 8 | 0
06:30 | 3446 | 1909 | 877 | 38 | 39 | 1204.835 | 172 | 4117.5 | 64.29 | 293.5 | 1030.5 | 0 | 0 | 4.5 | 0
07:00 | 3420 | 1881 | 877 | 38 | 38 | 1206.44 | 172 | 4101 | 100.48 | 246 | 934 | 0 | 0 | 1 | 0
07:30 | 3422.5 | 1871.6 | 877 | 38 | 38 | 1205.825 | 172 | 4106 | 150.135 | 244 | 918 | 0 | 0 | 5 | 0
08:00 | 3425 | 1862.2 | 877 | 38 | 38 | 1205.21 | 172 | 4111 | 199.79 | 242 | 902 | 0 | 0 | 9 | 0
08:30 | 3480 | 1877.6 | 878 | 38 | 37 | 1212.585 | 172 | 4104.5 | 253.99 | 263 | 875 | 0 | 0 | 10 | 0
09:00 | 3535 | 1893 | 879 | 38 | 36 | 1219.96 | 172 | 4098 | 308.19 | 284 | 848 | 0 | 0 | 11 | 0
09:30 | 3530.5 | 1894.25 | 879 | 38 | 34 | 1226.39 | 172 | 4138.5 | 360.945 | 310.5 | 879.5 | 0 | 0 | 14.5 | 0
10:00 | 3526 | 1895.5 | 879 | 38 | 32 | 1232.82 | 172 | 4179 | 413.7 | 337 | 911 | 0 | 0 | 18 | 0
10:30 | 3516.5 | 1887 | 884.5 | 38 | 34 | 1227.495 | 172 | 4131 | 510.61 | 337 | 950.5 | 0 | 0 | 19 | 0
11:00 | 3507 | 1878.5 | 890 | 38 | 36 | 1222.17 | 172 | 4083 | 607.52 | 337 | 990 | 0 | 0 | 20 | 0
11:30 | 3557 | 1993 | 890.5 | 38 | 36 | 1218.77 | 172 | 4123 | 528.015 | 340 | 1048 | 0 | 0 | 19.5 | 0
12:00 | 3607 | 2107.5 | 891 | 38 | 36 | 1215.37 | 172 | 4163 | 448.51 | 343 | 1106 | 0 | 0 | 19 | 0
12:30 | 3560.5 | 2072.5 | 891 | 38 | 36 | 1268.215 | 172 | 4139 | 452.4 | 325.5 | 1137.1 | 0 | 0 | 16.5 | 0
13:00 | 3514 | 2037.5 | 891 | 38 | 36 | 1321.06 | 172 | 4115 | 456.29 | 308 | 1168.2 | 0 | 0 | 14 | 0
13:30 | 3562.5 | 2034 | 890.5 | 38 | 38 | 1357.875 | 172 | 4103 | 430.515 | 283.5 | 1152.6 | 0 | 0 | 20.5 | 0
14:00 | 3611 | 2030.5 | 890 | 38 | 40 | 1394.69 | 172 | 4091 | 404.74 | 259 | 1137 | 0 | 0 | 27 | 0
14:30 | 3599 | 2047 | 891.5 | 38 | 41 | 1409.295 | 172 | 4149 | 353.68 | 252 | 1062.5 | 0 | 0 | 23 | 41.5
15:00 | 3587 | 2063.5 | 893 | 38 | 42 | 1423.9 | 172 | 4207 | 302.62 | 245 | 988 | 0 | 0 | 19 | 83
15:30 | 3641.5 | 2061 | 892.5 | 38 | 40 | 1421.755 | 172 | 4219 | 236.82 | 291.5 | 1068.5 | 0 | 0 | 14.5 | 41.5
16:00 | 3696 | 2058.5 | 892 | 38 | 38 | 1419.61 | 172 | 4231 | 171.02 | 338 | 1149 | 0 | 0 | 10 | 0
16:30 | 3617.5 | 2004 | 891.5 | 38 | 38 | 1415.16 | 172 | 4153 | 150.985 | 349 | 1129 | 0 | 0 | 11 | 0
17:00 | 3539 | 1949.5 | 891 | 38 | 38 | 1410.71 | 172 | 4075 | 130.95 | 360 | 1109 | 0 | 0 | 12 | 0
17:30 | 3494.5 | 1890 | 892 | 38 | 32 | 1359.085 | 172 | 3944 | 83.795 | 373.5 | 1121 | 0 | 0 | 13 | 0
18:00 | 3450 | 1830.5 | 893 | 38 | 26 | 1307.46 | 172 | 3813 | 36.64 | 387 | 1133 | 0 | 0 | 14 | 0
18:30 | 3605.5 | 1940.5 | 868 | 38 | 27 | 1354.445 | 172 | 3859.5 | 18.32 | 500.5 | 1323.5 | 0 | 0 | 15.5 | 12.5
19:00 | 3761 | 2050.5 | 843 | 38 | 28 | 1401.43 | 172 | 3906 | 0 | 614 | 1514 | 0 | 0 | 17 | 25
19:30 | 3728 | 1988 | 842 | 38 | 42 | 1420.47 | 172 | 4150 | 0 | 697 | 1956.5 | 0 | 0 | 23 | 42
20:00 | 3735 | 1968 | 842 | 38 | 40 | 1419.62 | 172 | 4282 | 0 | 783 | 1951.2 | 0 | 0 | 23 | 45
20:30 | 3836.5 | 1996 | 867.5 | 38 | 42 | 1434.745 | 172 | 4377.5 | 0 | 772 | 1872.45 | 0 | 0 | 18 | 42.5
21:00 | 3938 | 2024 | 893 | 38 | 44 | 1449.87 | 172 | 4473 | 0 | 761 | 1793.7 | 0 | 0 | 13 | 40
21:30 | 3986 | 2017.5 | 893 | 38 | 44 | 1450.48 | 172 | 4466.5 | 0 | 713 | 1713.95 | 0 | 0 | 14.5 | 40
22:00 | 4034 | 2011 | 893 | 38 | 44 | 1451.09 | 172 | 4460 | 0 | 665 | 1634.2 | 0 | 0 | 16 | 40
22:30 | 4056 | 2021 | 892 | 38 | 44 | 1449.54 | 172 | 4477 | 0 | 665 | 1631.7 | 0 | 0 | 19.5 | 55
23:00 | 4078 | 2031 | 891 | 38 | 44 | 1447.99 | 172 | 4494 | 0 | 665 | 1629.2 | 0 | 0 | 23 | 70
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 15-06-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 388 | 06:00 | 376 | 00:00 | Payra | 415 | 18:30 | 407 | 00:00
Ashuganj | 415 | 6:00 | 382 | 14:00 | Rahanpur | 405 | 18:00 | 388 | 00:00
Bhulta | 410 | 06:00 | 380 | 16:00 | Rampal | 402 | 18:00 | 384 | 00:00
Bibiana | 390 | 18:30 | 382 | 15:00
BIPTC | 400 | 06:00 | 386 | 23:00
Bogura | 394 | 18:30 | 372 | 00:00
Gopalganj | 399 | 18:30 | 382 | 00:00
Kaliakoir | 379 | 06:00 | 365 | 16:00
Madunaghat | 395 | 02:00 | 389 | 15:00
Meghnaghat | 390 | 06:00 | 381 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 229 | 06:00 | 218 | 15:00 | Keranigonj | 227 | 06:00 | 217 | 15:00
AKSML | 232 | 00:00 | 222 | 15:00 | Khulna(S) | 231 | 18:30 | 212 | 00:00
Aminbazar | 228 | 05:00 | 219 | 15:00 | Madunaghat | 232 | 02:00 | 226 | 13:00
Ashuganj | 239 | 06:00 | 226 | 14:00 | Madunaghat-400 | 232 | 02:00 | 226 | 15:00
Ashuganj-400 | 239 | 06:00 | 226 | 14:00 | Maniknagar | 225 | 05:00 | 218 | 15:00
Baghabari | 234 | 18:00 | 222 | 00:00 | Meghnaghat | 234 | 07:00 | 225 | 15:00
Barapukuria | 222 | 04:00 | 212 | 22:00 | Meghnaghat-400 | 229 | 06:00 | 222 | 15:00
Barapukuria-230 | 222 | 04:00 | 212 | 22:00 | Mirsorai | 228 | 03:00 | 221 | 13:00
Barishal | 235 | 18:00 | 215 | 00:00 | Rajshahi | 233 | 06:00 | 219 | 00:00
Bheramara | 234 | 06:00 | 220 | 00:00 | Rampal | 231 | 18:30 | 213 | 00:00
Bhulta | 239 | 06:00 | 219 | 15:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 228 | 06:00 | 222 | 00:00 | Rampura | 239 | 06:00 | 217 | 15:00
BIPTC | 236 | 18:30 | 219 | 00:00 | Shikalbaha | 230 | 01:00 | 223 | 15:00
Bogura | 230 | 06:00 | 218 | 00:00 | Shyampur | 228 | 06:00 | 219 | 16:00
Bogura-400 | 231 | 18:00 | 218 | 00:00 | Siddhirganj | 233 | 20:00 | 220 | 16:00
Borhanuddin | 239 | 18:00 | 218 | 00:00 | Sirajgonj | 239 | 06:00 | 231 | 00:00
BSRM | 228 | 06:00 | 220 | 15:00 | Sreepur | 233 | 06:00 | 222 | 00:00
Cumilla(N) | 226 | 06:00 | 218 | 15:00 | Tongi | 228 | 18:00 | 217 | 15:00
Faridpur | 234 | 18:30 | 217 | 00:00
Fenchuganj | 226 | 06:00 | 220 | 00:00
Ghorashal | 235 | 07:00 | 230 | 00:00
Ghorashal-230 | 235 | 06:00 | 219 | 01:00
Gopalganj | 235 | 18:30 | 220 | 00:00
GPH | 229 | 02:00 | 222 | 15:00
Haripur | 226 | 03:00 | 220 | 15:00
Hasnabad | 227 | 07:00 | 218 | 16:00
Hathazari | 231 | 18:30 | 226 | 15:00
Ishurdi | 236 | 18:00 | 221 | 00:00
Jhenaidah | 231 | 18:30 | 208 | 00:00
Kaliakoir | 236 | 06:00 | 223 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 06:00 | 124 | 15:00 | Madartek | 138 | 06:00 | 125 | 15:00
Agargaon | 132 | 06:00 | 126 | 15:00 | Madunaghat | 133 | 18:00 | 128 | 13:00
Agrabad | 132 | 01:00 | 127 | 14:00 | Magura | 135 | 18:00 | 117 | 00:00
AKS | 130 | 03:00 | 127 | 15:00 | Mahasthangarh | 132 | 18:00 | 121 | 00:00
Aminbazar | 131 | 03:00 | 122 | 15:00 | Manikganj | 132 | 06:00 | 121 | 00:00
Amnura | 137 | 18:30 | 123 | 00:00 | Maniknagar | 127 | 04:00 | 122 | 15:00
Ashuganj | 139 | 06:00 | 133 | 15:00 | Matarbari | 119 | 12:00 | 112 | 00:00
Bagerhat | 133 | 18:00 | 116 | 00:00 | Matuail | 132 | 04:00 | 128 | 15:00
Bajitpur | 131 | 06:00 | 123 | 00:00 | Millgate | 135 | 05:00 | 124 | 15:00
Bakulia | 133 | 03:00 | 127 | 15:00 | Mirpur | 131 | 01:00 | 120 | 16:00
Banani | 139 | 06:00 | 125 | 15:00 | Mirzapur | 132 | 18:30 | 122 | 00:00
Bangabhaban | 128 | 04:00 | 122 | 13:00 | Mithapukur | 129 | 06:00 | 118 | 23:00
Barapukuria | 135 | 04:00 | 122 | 23:00 | MI_Cement | 132 | 03:00 | 126 | 15:00
Barguna | 134 | 18:00 | 128 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 136 | 18:00 | 125 | 00:00 | Mogbazar | 140 | 06:00 | 125 | 13:00
Barishal-230 | 137 | 18:00 | 124 | 00:00 | Mongla | 133 | 18:00 | 116 | 00:00
Baroaulia | 132 | 00:00 | 128 | 14:00 | Motijheel | 128 | 04:00 | 122 | 15:00
Baroirhat | 128 | 18:30 | 119 | 02:00 | Muktagacha | 133 | 18:30 | 115 | 00:00
Bashundhara | 139 | 05:00 | 122 | 13:00 | Munshiganj | 131 | 02:00 | 126 | 15:00
BashundharaCement | 130 | 04:00 | 126 | 15:00 | Muradnagar | 129 | 18:30 | 123 | 00:00
Beanibazar | 129 | 06:00 | 122 | 00:00 | Mymensingh | 132 | 18:00 | 111 | 00:00
Benapole | 132 | 18:30 | 114 | 00:00 | Naogaon | 130 | 18:30 | 118 | 00:00
Bhaluka | 134 | 06:00 | 122 | 00:00 | Narail | 135 | 18:30 | 115 | 00:00
Bhandaria | 130 | 18:00 | 114 | 00:00 | Narinda | 127 | 04:00 | 122 | 15:00
Bhangura | 133 | 07:00 | 126 | 23:00 | Narshingdi | 138 | 05:00 | 120 | 23:00
Bheramara | 136 | 18:30 | 124 | 00:00 | Natore | 133 | 18:00 | 122 | 00:00
Bheramara(GK) | 135 | 18:00 | 124 | 00:00 | Nawabganj | 131 | 06:00 | 124 | 15:00
Bhulta | 127 | 18:00 | 123 | 16:00 | Netrakona | 127 | 09:00 | 109 | 00:00
Bog-Sherpur | 133 | 08:00 | 123 | 00:00 | New | 136 | 05:00 | 125 | 15:00
Bogura | 136 | 18:30 | 126 | 01:00 | Niamatpur | 136 | 18:00 | 130 | 22:00
Bogura-230 | 136 | 18:30 | 126 | 00:00 | Noapara | 135 | 18:30 | 119 | 00:00
Brahmanbaria | 133 | 07:00 | 126 | 00:00 | Pabna | 132 | 07:00 | 122 | 00:00
Cantonment | 132 | 18:30 | 126 | 14:00 | Palashbari | 128 | 18:00 | 116 | 00:00
Chandina | 131 | 18:30 | 125 | 01:00 | Panchagarh | 136 | 06:00 | 118 | 22:00
Chandpur | 133 | 18:30 | 123 | 23:00 | Patuakhali | 134 | 08:00 | 130 | 00:00
Chandraghona | 132 | 06:00 | 129 | 15:00 | Payra | 136 | 18:00 | 133 | 00:00
Chapai | 131 | 07:00 | 124 | 00:00 | PHP | 127 | 18:30 | 118 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 131 | 01:00 | 126 | 16:00 | Postogola | 133 | 04:00 | 128 | 15:00
Chauddagram | 127 | 18:00 | 119 | 23:00 | Purbachal | 139 | 06:00 | 125 | 15:00
Chhatak | 126 | 05:00 | 118 | 00:00 | Purbasadipur | 130 | 06:00 | 115 | 23:00
Chowmuhani | 123 | 18:00 | 111 | 01:00 | Rahanpur | 138 | 18:00 | 131 | 00:00
Chuadanga | 132 | 09:00 | 115 | 00:00 | Rahanpur-400 | 138 | 06:00 | 131 | 00:00
Coxsbazar | 122 | 08:00 | 113 | 00:00 | Rahim | 131 | 02:00 | 127 | 16:00
Cumilla(N) | 131 | 18:30 | 124 | 23:00 | Rajbari | 135 | 18:30 | 123 | 00:00
Cumilla(S) | 132 | 04:00 | 123 | 00:00 | Rajendrapur | 139 | 06:00 | 124 | 00:00
Daudkandi | 127 | 18:30 | 120 | 11:00 | Rajshahi | 134 | 18:00 | 126 | 22:00
Dhaka | 138 | 05:00 | 125 | 16:00 | Rajshahi-230 | 134 | 06:00 | 115 | 01:00
Dhamrai | 131 | 20:00 | 122 | 15:00 | Ramganj | 126 | 18:00 | 114 | 23:00
Dhanmondi | 139 | 05:00 | 125 | 15:00 | Rampur | 132 | 02:00 | 127 | 10:00
Dohazari | 127 | 11:00 | 122 | 15:00 | Rampura | 139 | 06:00 | 126 | 13:00
Faridpur | 136 | 18:30 | 125 | 00:00 | Rangamati | 131 | 02:00 | 128 | 10:00
Fatullah | 132 | 03:00 | 127 | 15:00 | Rangpur | 128 | 04:00 | 118 | 00:00
Fenchuganj | 134 | 06:00 | 130 | 00:00 | Ruppur | 136 | 18:00 | 126 | 00:00
Feni | 125 | 18:00 | 118 | 00:00 | Saidpur | 130 | 06:00 | 118 | 21:00
Ghatail | 130 | 18:00 | 114 | 00:00 | Satkhira | 132 | 18:00 | 113 | 00:00
Ghorashal | 142 | 04:00 | 132 | 15:00 | Satmasjid | 131 | 06:00 | 126 | 15:00
Goalpara | 137 | 18:00 | 124 | 01:00 | Savar | 131 | 01:00 | 120 | 15:00
Gollamari | 137 | 18:00 | 123 | 00:00 | SevenRings | 142 | 06:00 | 131 | 16:00
Gopalganj | 136 | 18:30 | 123 | 00:00 | ShahCement | 131 | 01:00 | 126 | 16:00
Gopalganj-400 | 138 | 18:30 | 129 | 00:00 | Shahjadpur | 135 | 03:00 | 130 | 00:00
Gulshan | 139 | 06:00 | 125 | 15:00 | Shahjibazar | 134 | 07:00 | 126 | 00:00
Halishahar | 134 | 02:00 | 126 | 10:00 | Shahmirpur | 133 | 00:00 | 128 | 15:00
Haripur | 132 | 02:00 | 128 | 15:00 | Shariatpur | 136 | 18:30 | 123 | 00:00
HaripurSBU | 132 | 03:00 | 128 | 15:00 | Sherpur | 136 | 18:30 | 114 | 00:00
Hasnabad | 134 | 05:00 | 128 | 15:00 | Shikalbaha | 122 | 00:00 | 118 | 13:00
Hathazari | 135 | 00:00 | 129 | 15:00 | Shikalbaha-230 | 133 | 00:00 | 129 | 15:00
Ishurdi | 137 | 18:30 | 127 | 00:00 | Shitalakhya | 132 | 03:00 | 126 | 15:00
Jaldhaka | 127 | 06:00 | 112 | 23:00 | Sholosohor | 133 | 03:00 | 126 | 15:00
Jamalpur | 138 | 18:30 | 118 | 00:00 | Shyampur | 131 | 06:00 | 125 | 16:00
Jashore | 135 | 18:00 | 115 | 00:00 | Shyampur-230 | 131 | 02:00 | 126 | 16:00
Jhenaidah | 137 | 18:00 | 110 | 00:00 | Siddhirganj | 132 | 01:00 | 128 | 13:00
Jhenaidah-230 | 137 | 18:00 | 119 | 00:00 | Sirajganj | 132 | 08:00 | 123 | 00:00
Joydebpur | 141 | 06:00 | 125 | 11:00 | Sonargaon | 131 | 00:00 | 126 | 16:00
Joypurhat | 128 | 18:30 | 113 | 00:00 | Sreemongol | 131 | 06:00 | 125 | 00:00
Juldah | 133 | 00:00 | 129 | 15:00 | Sreepur | 136 | 06:00 | 126 | 19:30
Kabirpur | 134 | 04:00 | 123 | 15:00 | Srinagar | 132 | 06:00 | 124 | 15:00
Kachua | 130 | 18:00 | 121 | 23:00 | SSM | 134 | 00:00 | 132 | 12:00
Kaliakoir | 136 | 18:30 | 125 | 15:00 | Sunamganj | 125 | 05:00 | 116 | 00:00
Kallyanpur | 131 | 04:00 | 122 | 13:00 | Sylhet | 128 | 06:00 | 123 | 00:00
Kalurghat | 131 | 00:00 | 127 | 10:00 | Sylhet-132 | 128 | 06:00 | 125 | 00:00
Kamrangirchar | 132 | 04:00 | 125 | 16:00 | Tangail | 129 | 13:00 | 118 | 00:00
Kaptai | 133 | 6:00 | 120 | 13:00 | Thakurgaon | 135 | 06:00 | 116 | 22:00
Kasba | 128 | 18:00 | 121 | 23:00 | TK | 131 | 06:00 | 127 | 14:00
Kazla | 127 | 03:00 | 122 | 15:00 | Tongi | 134 | 03:00 | 127 | 15:00
Keranigonj | 132 | 06:00 | 125 | 15:00 | Ullahpara | 133 | 06:00 | 125 | 00:00
Khagrachori | 131 | 06:00 | 127 | 10:00 | Ullon | 138 | 06:00 | 125 | 15:00
Khulna | 136 | 18:00 | 122 | 00:00 | Uttara | 135 | 06:00 | 119 | 15:00
Khulna(S) | 137 | 18:00 | 123 | 00:00 | UttaraNew | 131 | 02:00 | 120 | 15:00
Khulshi | 130 | 00:00 | 126 | 10:00 | Zigatola | 131 | 06:00 | 124 | 16:00
Kishoreganj | 127 | 06:00 | 116 | 00:00
Kodda | 138 | 06:00 | 124 | 14:00
KSRM | 133 | 07:00 | 129 | 15:00
Kulaura | 132 | 04:00 | 129 | 00:00
Kurigram | 125 | 06:00 | 112 | 23:00
Kushtia | 130 | 18:00 | 119 | 01:00
Lalbag | 132 | 06:00 | 125 | 15:00
Lalmonirhat | 125 | 17:00 | 114 | 22:00
Madanganj | 130 | 04:00 | 126 | 15:00
Madaripur | 135 | 09:00 | 127 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division