## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 20-06-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-06-2025 | during | 20-06-2025 | during | 20-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 280 | 334 | 400.75 | 400.75 | 380 | 380 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 250 | 450 | 450 | 420 | 420 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 140 | 138 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 18 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 176 | 170 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 90 | 8 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 80 | 146 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 0 | 7 | 33 | 33 | 25 | 25 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 11 | 10 | 15 | 15 | 15 | 15 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 33 | 25 | 52.19 | 52.19 | 35 | 35 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 180 | 277 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 72 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 60 | 88 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 50 | 50 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 108 | 108 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 34 | 0 | 20 | 0 | 20 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 125 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 1736 | 2147 | 5092.2 | 5104.2 | 3525.33 | 3537.33
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 23 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 14 | 0 | 6 | 0 | 6 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 172 | 172 | 172 | 172 | 172 | 172 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 218 | 221 | 221 | 221 | 221 | 221 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 57 | 102 | 105 | 105 | 94.5 | 94.5 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 32 | 70 | 56 | 82 | 56 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 8 | 66 | 65 | 65 | 65 | 65 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 76 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 0 | 8 | 0 | 0 | 0 | 0 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 5 | 0 | 1.39 | 0 | 1.39 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 70 | 138 | 300 | 300 | 270 | 270 | FGMO
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 54 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 45 | 100 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 75 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 72 | 144 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1140 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 62 | 17 | 40 | 35 | 40 | 35 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 210 | 0 | 575 | 575 | 545 | 545 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 2359 | 2580 | 3589.11 | 3602.72 | 3477.61 | 3491.22
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 196 | 183 | 221.43 | 221.43 | 221.43 | 221.43 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 340 | 340 | 340 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 10 | 10 | 46.7 | 46.7 | 29 | 29 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 5 | 5 | 55 | 55 | 50 | 50 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 185 | 185 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 128 | 137 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 30 | 45 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 143 | 168 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 28 | 32 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 9 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 42 | 88 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 29 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 65 | 114 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 3 | 0 | 25 | 0 | 25 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1067 | 1274.2 | 2072.83 | 2047.83 | 1891.63 | 1866.63
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-06-2025 | during | 20-06-2025 | during | 20-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 63 | 63 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.3 | 0 | 1.3 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 139 | 176 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 72 | 78 | 115 | 115 | 105 | 105 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 29.31 | 0 | 35 | 0 | 35 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 8 | 22 | 22 | 22 | 22 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 19 | 35 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 272.31 | 297 | 585.3 | 549 | 480.8 | 444.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 35 | 36 | 35 | 35 | 35 | 35 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 20 | 20 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 81 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 168 | 168 | 165 | 165 | 165 | 165 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 17 | 17 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 386 | 359 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1337 | 1297 | 1595 | 1595 | 1515 | 1515
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 924 | 924 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 5 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 246 | 246 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 105 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 91 | 0 | 55 | 0 | 55 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1020 | 1147 | 1234.2 | 1234.2 | 1194 | 1194 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2073 | 2236 | 3609.2 | 3554.2 | 3405 | 3350
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 32 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 9 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 130 | 130 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1120 | 1230 | 1244 | 1244 | 1240 | 1240 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 215 | 277 | 307 | 307 | 267 | 267 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.24 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1696.24 | 1933 | 2172 | 2171 | 2128 | 2127
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 47 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 5 | 32 | 32 | 30 | 30 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 192 | 192 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 128 | 121 | 220 | 220 | 200 | 200 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is in Standby as per NLDC request.
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 386 | 300 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 | 30 | 30 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 98 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0.8 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1301.97 | 1421 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 5.53 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 27 | 0 | 85 | 0 | 85 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 1849.3 | 2145 | 3178.37 | 3026.87 | 3134.37 | 2982.87
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 50 | 49 | 49 | 49 | 49 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 150 | 134 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 98 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 1 | 0 | 4.6 | 0 | 4.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 113 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 17 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 84 | 0 | 90.64 | 0 | 90.64 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 336 | 395 | 581.24 | 461 | 581.24 | 461
System Total |  |  |  |  | 28565.2 | 27084.055 | 12725.85 | 14304.2 | 22475.25 | 22111.82 | 20138.98 | 19775.55
Forecast Scenario (20-06-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13730 |  | 0 |  | 13730
|  |  |  | 1:00 | 13500 |  | 0 |  | 13500
|  |  |  | 2:00 | 13200 |  | 0 |  | 13200
|  |  |  | 3:00 | 12920 |  | 0 |  | 12920
|  |  |  | 4:00 | 12500 |  | 0 |  | 12500
|  |  |  | 5:00 | 12330 |  | 0 |  | 12330
|  |  |  | 6:00 | 11620 |  | 0 |  | 11620
|  |  |  | 7:00 | 11290 |  | 0 |  | 11290
|  |  |  | 8:00 | 11090 |  | 0 |  | 11090
|  |  |  | 9:00 | 10800 |  | 0 |  | 10800
|  |  |  | 10:00 | 10720 |  | 0 |  | 10720
|  |  |  | 11:00 | 10870 |  | 0 |  | 10870
|  |  |  | 12:00 | 11170 |  | 0 |  | 11170
|  |  |  | 13:00 | 11970 |  | 0 |  | 11970
|  |  |  | 14:00 | 11700 |  | 0 |  | 11700
|  |  |  | 15:00 | 11920 |  | 0 |  | 11920
|  |  |  | 16:00 | 11840 |  | 0 |  | 11840
|  |  |  | 17:00 | 11450 |  | 0 |  | 11450
|  |  |  | 18:00 | 10810 |  | 0 |  | 10810
|  |  |  | 18:30 | 11300 |  | 0 |  | 11300
|  |  |  | 19:00 | 11980 |  | 0 |  | 11980
|  |  |  | 19:30 | 13250 |  | 0 |  | 13250
|  |  |  | 20:00 | 13400 |  | 0 |  | 13400
|  |  |  | 21:00 | 13940 |  | 0 |  | 13940
|  |  |  | 22:00 | 14050 |  | 0 |  | 14050
|  |  |  | 23:00 | 14140 |  | 0 |  | 14140
Probable Maximum Temperature: |  |  | 29.00°C
Probable Maximum Demand at Day Peak: |  |  | 11170.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13940.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13940.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 292.94 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:53 hrs on 20-06-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 19-06-2025 | [28 empty] | Date: | 19-06-2025 | [28 empty] | Date: | 19-06-2025 | [28 empty] | Date: | 19-06-2025 | [28 empty] | Date: | 19-06-2025 | [12 empty] | Date: | 19-06-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [12 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 54 | 35 | 51 | 112 | 0 | 0 | 0 | 129 | 0 | 350 | 143 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 70 | 16 | 18 | 0 | 0 | 0 | 13 | 0 | 0 | 35 | 16 | 56 | 0 | 88 | 100 | 0 | 172 | 15 | 3 | 214 | 0 | 0 | 19 | 0 | 47 | 224 | 0 | 0 | 0 | 1150 | 0 | 51 | 143 | 8 | 0 | 0 | 330 | 49 | 192 | 28 | 45 | 0 | 181 | 10 | 20 | 102 | 34 | 43 | 0 | 38 | 310 | 320 | 363 | 34 | 0 | 0 | 8 | 0 | 81 | 20 | 0 | 0 | 167 | 17 | 92 | 177 | 0 | 0 | 0 | 9 | 6691 | 959 | 30 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1126 | 0 | 1413 | 0 | 0 | 0 | 113 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 125 | 0 | 0 | 0 | 370 | 0 | 0 | 165 | 49 | 70 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 9 | 130 | 220 | 0 | 563 | 1106 | 0 | 7061 | 13752 | 97.95
01:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 54 | 35 | 45 | 81 | 0 | 0 | 0 | 126 | 0 | 350 | 142 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 70 | 14 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 16 | 24 | 0 | 88 | 100 | 0 | 172 | 15 | 2 | 212 | 0 | 0 | 19 | 0 | 0 | 224 | 0 | 0 | 0 | 1105 | 0 | 51 | 145 | 8 | 0 | 0 | 340 | 49 | 186 | 27 | 34 | 0 | 180 | 9 | 20 | 97 | 34 | 43 | 0 | 38 | 305 | 320 | 359 | 34 | 0 | 0 | 8 | 0 | 81 | 20 | 0 | 0 | 168 | 17 | 93 | 168 | 0 | 0 | 0 | 12 | 6423 | 921 | 27 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 1422 | 0 | 0 | 0 | 70 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 123 | 0 | 0 | 0 | 340 | 0 | 0 | 160 | 49 | 54 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 8 | 130 | 220 | 0 | 592 | 1095 | 0 | 6919 | 13342 | 97.96
02:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 35 | 34 | 48 | 0 | 0 | 0 | 90 | 0 | 350 | 143 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 70 | 14 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 16 | 0 | 0 | 88 | 100 | 0 | 172 | 0 | 2 | 212 | 0 | 0 | 19 | 0 | 0 | 224 | 0 | 0 | 0 | 1140 | 0 | 51 | 50 | 8 | 0 | 0 | 340 | 49 | 206 | 26 | 30 | 0 | 181 | 9 | 20 | 101 | 26 | 43 | 0 | 38 | 305 | 320 | 365 | 34 | 0 | 0 | 8 | 0 | 81 | 20 | 0 | 0 | 168 | 17 | 83 | 174 | 0 | 0 | 0 | 12 | 6215 | 922 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 1416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 123 | 0 | 0 | 0 | 300 | 0 | 0 | 163 | 50 | 54 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 11 | 130 | 220 | 0 | 610 | 1092 | 0 | 6615 | 12830 | 97.97
03:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 35 | 34 | 48 | 0 | 0 | 0 | 84 | 0 | 350 | 145 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 52 | 14 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 16 | 0 | 0 | 88 | 100 | 0 | 172 | 0 | 2 | 212 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 1105 | 0 | 51 | 0 | 8 | 0 | 0 | 340 | 49 | 203 | 26 | 31 | 0 | 181 | 9 | 20 | 103 | 32 | 43 | 0 | 38 | 310 | 320 | 386 | 34 | 0 | 0 | 8 | 0 | 81 | 20 | 0 | 0 | 168 | 17 | 83 | 182 | 0 | 0 | 0 | 12 | 6140 | 921 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1002 | 0 | 1317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 122 | 0 | 0 | 0 | 220 | 0 | 0 | 158 | 50 | 54 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 7 | 130 | 220 | 0 | 622 | 1050 | 0 | 6288 | 12428 | 97.98
04:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 34 | 48 | 0 | 0 | 0 | 54 | 0 | 330 | 143 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 62 | 74 | 0 | 172 | 0 | 2 | 213 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1063 | 0 | 51 | 0 | 8 | 0 | 0 | 340 | 49 | 197 | 26 | 32 | 0 | 181 | 9 | 20 | 101 | 30 | 25 | 0 | 0 | 315 | 320 | 362 | 34 | 0 | 0 | 8 | 0 | 81 | 20 | 0 | 0 | 168 | 17 | 45 | 177 | 0 | 0 | 0 | 12 | 5786 | 921 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 938 | 0 | 1310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 124 | 0 | 0 | 0 | 220 | 0 | 0 | 158 | 48 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 9 | 130 | 220 | 0 | 622 | 1044 | 0 | 6149 | 11935 | 97.99
05:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 17 | 34 | 48 | 0 | 0 | 0 | 0 | 0 | 330 | 150 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 17 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 36 | 74 | 0 | 172 | 0 | 4 | 213 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1010 | 0 | 51 | 0 | 8 | 0 | 0 | 340 | 49 | 193 | 26 | 30 | 0 | 155 | 9 | 20 | 69 | 28 | 8 | 0 | 0 | 320 | 320 | 383 | 34 | 0 | 0 | 8 | 0 | 81 | 20 | 0 | 0 | 168 | 17 | 45 | 167 | 0 | 0 | 0 | 12 | 5562 | 921 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 857 | 0 | 1317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 127 | 0 | 0 | 0 | 220 | 0 | 0 | 157 | 48 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 9 | 130 | 220 | 0 | 622 | 948 | 0 | 5844 | 11406 | 98
06:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 17 | 34 | 48 | 0 | 0 | 0 | 0 | 0 | 300 | 142 | 0 | 0 | 0 | 230 | 0 | 0 | 1 | 17 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 36 | 48 | 0 | 172 | 0 | 2 | 212 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 925 | 1 | 51 | 0 | 0 | 0 | 0 | 340 | 44 | 189 | 26 | 31 | 0 | 85 | 9 | 20 | 16 | 22 | 0 | 2 | 0 | 315 | 320 | 375 | 34 | 0 | 0 | 8 | 0 | 81 | 20 | 0 | 0 | 168 | 17 | 45 | 171 | 0 | 0 | 2.24 | 12 | 5231.24 | 921 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4 | 768 | 0 | 1220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58 | 0 | 0 | 133 | 0 | 0 | 0 | 300 | 0 | 0 | 155 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0.04 | 0 | 172 | 8 | 130 | 220 | 0 | 622 | 850 | 0 | 5596.62 | 10827.86 | 98.01
07:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 18 | 34 | 48 | 0 | 0 | 0 | 0 | 0 | 300 | 141 | 0 | 0 | 0 | 220 | 0 | 0 | 3 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 12 | 24 | 1 | 172 | 0 | 5 | 212 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 859 | 1 | 51 | 0 | 0 | 0 | 0 | 340 | 35 | 189 | 26 | 32 | 0 | 34 | 9 | 20 | 4 | 22 | 0 | 2 | 0 | 320 | 320 | 396 | 34 | 0 | 0 | 8 | 0 | 81 | 20 | 0 | 0 | 168 | 17 | 45 | 105 | 0 | 0 | 10.96 | 12 | 4983.96 | 921 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 13 | 796 | 0 | 1223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 21.05 | 0 | 0 | 138 | 0 | 0 | 0 | 414 | 0 | 0 | 153 | 48 | 0 | 4 | 0 | 0 | 0 | 0.5 | 43 | 0.06 | 0 | 202 | 7 | 130 | 220 | 0 | 621 | 847 | 0 | 5842.61 | 10826.57 | 98.02
08:00 | 0 | 40 | 25 | 0 | 0 | 0 | 0 | 0 | 287 | 0 | 0 | 0 | 35 | 34 | 48 | 0 | 0 | 0 | 12 | 0 | 300 | 140 | 0 | 0 | 0 | 180 | 0 | 0 | 5 | 0 | 7 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 12 | 12 | 2 | 172 | 0 | 0 | 214 | 0 | 0 | 1 | 0 | 0 | 222 | 0 | 0 | 0 | 1095 | 6 | 51 | 0 | 0 | 0 | 0 | 340 | 35 | 189 | 26 | 35 | 0 | 30 | 9 | 20 | 0 | 24 | 0 | 2 | 0 | 320 | 320 | 398 | 34 | 0 | 0 | 8 | 0 | 81 | 20 | 0 | 0 | 168 | 17 | 73 | 120 | 0 | 1 | 10.92 | 2 | 5245.92 | 921 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 20 | 896 | 0 | 1363.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 6.11 | 0 | 0 | 141 | 0 | 0 | 0 | 414 | 0 | 0 | 150 | 51 | 0 | 8 | 0 | 0 | 0 | 0.6 | 38 | 0.05 | 0 | 202 | 7 | 130 | 220 | 0 | 471 | 900 | 0 | 5997.59 | 11243.51 | 98.03
09:00 | 0 | 52 | 27 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 15 | 35 | 38 | 48 | 0 | 0 | 10 | 33 | 0 | 300 | 138 | 0 | 0 | 0 | 177 | 0 | 0 | 2 | 17 | 6.8 | 13 | 0 | 0 | 0 | 14 | 0 | 0 | 38 | 0 | 0 | 0 | 36 | 88 | 2 | 172 | 0 | 0 | 215 | 0 | 0 | 46 | 0 | 11 | 217 | 0 | 0 | 0 | 1167 | 9 | 51 | 12 | 0 | 0 | 0 | 340 | 22 | 186 | 26 | 46 | 0 | 69 | 9 | 20 | 0 | 26 | 0 | 2 | 0 | 315 | 320 | 360 | 35 | 0 | 0 | 8 | 0 | 80 | 20 | 0 | 0 | 168 | 17 | 55 | 110 | 0 | 1 | 17.64 | 4 | 5531.44 | 921 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 34 | 952 | 0 | 1338.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 3.09 | 0 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0 | 148 | 50 | 0 | 3 | 0 | 0 | 0 | 1 | 55 | 0.07 | 0 | 213 | 6 | 130 | 180 | 0 | 326 | 950 | 0 | 5912.76 | 11444.2 | 98.04
10:00 | 0 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 49 | 41 | 52 | 48 | 60 | 0 | 53 | 105 | 18 | 300 | 140 | 0 | 0 | 35 | 176 | 0 | 0 | 26 | 52 | 6.6 | 13 | 0 | 0 | 0 | 55 | 0 | 0 | 41 | 0 | 0 | 0 | 36 | 100 | 0 | 172 | 27 | 0 | 212 | 17 | 0 | 0 | 1 | 44 | 218 | 0 | 0 | 0 | 1153 | 10 | 51 | 73 | 0 | 0 | 0 | 340 | 7 | 190 | 10 | 50 | 0 | 109 | 9 | 20 | 15 | 24 | 8 | 9 | 0 | 315 | 320 | 367 | 35 | 0 | 0 | 8 | 0 | 80 | 20 | 0 | 0 | 168 | 17 | 55 | 110 | 0 | 1 | 28 | 8 | 6073.6 | 921 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 33 | 945 | 0 | 1203.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 18.04 | 0 | 0 | 137 | 0 | 0 | 0 | 414 | 0 | 0 | 150 | 50 | 0 | 11 | 34 | 0 | 0 | 3.8 | 70 | 0 | 0 | 198 | 6 | 130 | 180 | 0 | 247 | 1010 | 0 | 5812.99 | 11886.59 | 98.05
11:00 | 0 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 54 | 55 | 52 | 48 | 60 | 9 | 55 | 72 | 34 | 300 | 142 | 0 | 0 | 35 | 176 | 0 | 0 | 6 | 52 | 0 | 11 | 0 | 0 | 0 | 60 | 0 | 0 | 52 | 0 | 9 | 0 | 50 | 100 | 0 | 172 | 46 | 0 | 212 | 17 | 0 | 50 | 8 | 46 | 218 | 0 | 0 | 0 | 1174 | 0 | 51 | 123 | 0 | 0 | 0 | 340 | 5 | 196 | 10 | 52 | 0 | 130 | 9 | 20 | 15 | 24 | 8 | 8 | 23 | 310 | 320 | 390 | 35 | 0 | 0 | 8 | 0 | 80 | 20 | 0 | 0 | 168 | 17 | 55 | 122 | 0 | 0 | 5.29 | 7 | 6291.29 | 924 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 100 | 975 | 0 | 1233.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 9.42 | 0 | 0 | 132 | 0 | 0 | 0 | 350 | 0 | 0 | 151 | 50 | 0 | 16 | 34 | 0 | 0 | 5.8 | 65 | 0.13 | 0 | 203 | 6 | 130 | 220 | 0 | 170 | 1055 | 0 | 5877.41 | 12168.7 | 98.06
12:00 | 0 | 60 | 33 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 17 | 55 | 72 | 80 | 180 | 18 | 35 | 108 | 50 | 300 | 140 | 0 | 0 | 35 | 176 | 0 | 0 | 34 | 52 | 0 | 11 | 0 | 0 | 0 | 70 | 0 | 0 | 62 | 8 | 32 | 0 | 76 | 100 | 5 | 172 | 45 | 0 | 210 | 72 | 0 | 50 | 8 | 57 | 218 | 0 | 0 | 0 | 1160 | 14 | 51 | 128 | 0 | 0 | 0 | 340 | 5 | 196 | 10 | 65 | 0 | 143 | 9 | 9 | 42 | 28 | 8 | 3 | 30 | 320 | 320 | 386 | 35 | 0 | 0 | 8 | 0 | 80 | 20 | 0 | 0 | 168 | 19 | 72 | 139 | 0 | 1 | 29.31 | 12 | 6771.31 | 924 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 91 | 1020 | 0 | 1301.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 5.53 | 0 | 0 | 128 | 0 | 0 | 0 | 386 | 0 | 0.8 | 150 | 50 | 0 | 17 | 34 | 0 | 0 | 1 | 84 | 0.24 | 0 | 215 | 0 | 130 | 220 | 0 | 11 | 1120 | 0 | 5954.54 | 12725.85 | 98.06
13:00 | 22 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 279 | 0 | 0 | 17 | 55 | 110 | 80 | 206 | 30 | 35 | 108 | 50 | 300 | 140 | 0 | 0 | 35 | 176 | 0 | 0 | 32 | 70 | 6.5 | 11 | 0 | 0 | 0 | 118 | 0 | 0 | 60 | 55 | 32 | 0 | 89 | 100 | 0 | 172 | 46 | 0 | 212 | 72 | 0 | 50 | 8 | 76 | 219 | 0 | 0 | 0 | 1142 | 6 | 51 | 135 | 0 | 0 | 0 | 340 | 5 | 191 | 10 | 70 | 0 | 166 | 9 | 19 | 40 | 28 | 34 | 3 | 45 | 315 | 320 | 360 | 35 | 0 | 0 | 8 | 0 | 80 | 20 | 0 | 0 | 168 | 35 | 71 | 128 | 0 | 1 | 7.12 | 4 | 7020.62 | 924 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 22 | 1163 | 0 | 1345.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 20.89 | 0 | 0 | 127 | 0 | 0 | 0 | 359 | 0 | 2.04 | 190 | 50 | 0 | 16 | 34 | 0 | 0 | 1.7 | 136 | 0 | 0 | 273 | 5 | 130 | 220 | 0 | 0 | 1120 | 0 | 6190.45 | 13211.07 | 98.07
14:00 | 24 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 277 | 0 | 0 | 17 | 55 | 146 | 80 | 261 | 30 | 35 | 108 | 50 | 300 | 142 | 0 | 0 | 35 | 176 | 0 | 0 | 17 | 70 | 6.5 | 11 | 0 | 0 | 0 | 45 | 0 | 0 | 64 | 65 | 42 | 0 | 60 | 100 | 0 | 172 | 46 | 0 | 213 | 72 | 0 | 50 | 8 | 68 | 223 | 0 | 0 | 0 | 1160 | 9 | 51 | 133 | 0 | 0 | 0 | 280 | 5 | 186 | 10 | 63 | 0 | 154 | 9 | 19 | 48 | 30 | 34 | 11 | 44 | 300 | 320 | 333 | 35 | 0 | 0 | 8 | 0 | 80 | 20 | 0 | 0 | 168 | 35 | 71 | 138 | 0 | 1 | 18.03 | 10 | 6954.53 | 924 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 45 | 1103 | 0 | 1374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 15.52 | 0 | 0 | 125 | 0 | 0 | 0 | 300 | 0 | 1.81 | 191 | 50 | 0 | 15 | 34 | 0 | 0 | 0.3 | 21 | 0.24 | 0 | 231 | 6 | 130 | 180 | 0 | 0 | 1070 | 0 | 5874.87 | 12829.4 | 98.07
15:00 | 24 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 282 | 0 | 0 | 17 | 55 | 149 | 80 | 261 | 30 | 35 | 108 | 50 | 300 | 143 | 0 | 0 | 35 | 176 | 0 | 0 | 10 | 70 | 7 | 11 | 0 | 0 | 0 | 45 | 0 | 0 | 50 | 66 | 43 | 0 | 60 | 100 | 1 | 172 | 52 | 2 | 212 | 72 | 0 | 50 | 8 | 68 | 222 | 0 | 0 | 0 | 1180 | 6 | 51 | 133 | 0 | 0 | 0 | 320 | 5 | 187 | 10 | 52 | 0 | 170 | 9 | 19 | 50 | 26 | 34 | 26 | 43 | 310 | 320 | 351 | 35 | 0 | 0 | 8 | 0 | 77 | 20 | 0 | 0 | 168 | 35 | 74 | 138 | 0 | 0 | 24.26 | 8 | 7032.26 | 924 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 30 | 1134 | 0 | 1376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 13.58 | 0 | 0 | 125 | 0 | 0 | 0 | 300 | 0 | 1.34 | 186 | 51 | 0 | 3 | 34 | 0 | 0 | 1.3 | 27 | 0.26 | 0 | 230 | 6 | 130 | 220 | 0 | 0 | 1070 | 0 | 5916.48 | 12948.74 | 98.08
16:00 | 32 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 282 | 0 | 0 | 17 | 55 | 149 | 80 | 261 | 30 | 35 | 108 | 50 | 300 | 142 | 0 | 0 | 35 | 176 | 0 | 0 | 7 | 70 | 7 | 6 | 0 | 0 | 0 | 41 | 0 | 0 | 51 | 66 | 53 | 0 | 60 | 88 | 1 | 172 | 53 | 2 | 212 | 72 | 0 | 50 | 8 | 68 | 222 | 0 | 0 | 0 | 1185 | 0 | 51 | 135 | 0 | 0 | 0 | 340 | 5 | 187 | 10 | 59 | 0 | 168 | 9 | 20 | 44 | 26 | 34 | 13 | 44 | 310 | 320 | 343 | 35 | 0 | 0 | 8 | 0 | 76 | 20 | 0 | 0 | 168 | 35 | 70 | 137 | 0 | 0 | 27.56 | 2 | 7019.56 | 924 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 16 | 1090 | 0 | 1348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 1.27 | 0 | 0 | 125 | 0 | 0 | 0 | 339 | 0 | 0.18 | 190 | 51 | 0 | 8 | 34 | 0 | 0 | 1.4 | 74 | 0.27 | 0 | 222 | 6 | 100 | 220 | 0 | 0 | 1079 | 0 | 5873.12 | 12892.68 | 98.08
17:00 | 32 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 17 | 55 | 149 | 79 | 261 | 30 | 35 | 108 | 50 | 250 | 140 | 0 | 0 | 35 | 170 | 0 | 0 | 0 | 70 | 7 | 10 | 0 | 0 | 0 | 43 | 0 | 0 | 3 | 66 | 70 | 0 | 60 | 75 | 0 | 172 | 47 | 2 | 212 | 72 | 0 | 0 | 8 | 68 | 222 | 0 | 0 | 0 | 1065 | 0 | 51 | 135 | 0 | 0 | 0 | 340 | 5 | 182 | 10 | 77 | 0 | 153 | 9 | 20 | 45 | 26 | 34 | 9 | 44 | 305 | 320 | 341 | 35 | 0 | 0 | 8 | 0 | 76 | 20 | 0 | 0 | 168 | 35 | 78 | 173 | 0 | 0 | 4.39 | 3 | 6785.39 | 921 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12 | 1002 | 0 | 1357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 4.8 | 0 | 0 | 124 | 0 | 0 | 0 | 300 | 0 | 0 | 195 | 51 | 0 | 2 | 34 | 0 | 0 | 1.1 | 28 | 0.08 | 0 | 178 | 6 | 100 | 220 | 0 | 0 | 1093 | 0 | 5668.98 | 12454.37 | 98.09
18:00 | 32 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 55 | 149 | 79 | 261 | 30 | 35 | 108 | 50 | 250 | 143 | 0 | 0 | 35 | 170 | 0 | 0 | 0 | 125 | 7 | 10 | 0 | 0 | 0 | 43 | 0 | 0 | 8 | 66 | 70 | 17 | 100 | 100 | 0 | 172 | 51 | 2 | 0 | 72 | 0 | 0 | 8 | 65 | 221 | 0 | 0 | 0 | 1035 | 0 | 51 | 130 | 0 | 0 | 0 | 285 | 5 | 184 | 10 | 89 | 0 | 162 | 15 | 20 | 45 | 26 | 34 | 1 | 45 | 310 | 320 | 324 | 35 | 0 | 0 | 8 | 0 | 80 | 20 | 0 | 0 | 168 | 35 | 78 | 174 | 0 | 0 | 3.34 | 6 | 6646.34 | 924 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5 | 1022 | 0 | 1347 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 328 | 0 | 0 | 161 | 51 | 0 | 0 | 35 | 0 | 0 | 0.3 | 2 | 0.02 | 0 | 247 | 6 | 100 | 220 | 0 | 0 | 1102 | 0 | 5712.32 | 12358.66 | 98.09
19:00 | 40 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 0 | 55 | 149 | 145 | 261 | 35 | 35 | 108 | 50 | 250 | 145 | 0 | 0 | 35 | 170 | 0 | 0 | 0 | 125 | 7 | 10 | 0 | 0 | 17 | 130 | 0 | 0 | 22 | 66 | 70 | 44 | 100 | 100 | 0 | 172 | 51 | 3 | 0 | 144 | 0 | 33 | 11 | 84 | 221 | 0 | 0 | 0 | 1170 | 0 | 51 | 132 | 0 | 0 | 0 | 316 | 5 | 178 | 10 | 89 | 0 | 153 | 27 | 20 | 96 | 30 | 38 | 0 | 45 | 310 | 320 | 367 | 36 | 0 | 0 | 8 | 0 | 81 | 20 | 0 | 0 | 168 | 35 | 78 | 175 | 0 | 0 | 0 | 6 | 7246 | 924 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 60 | 0 | 1051 | 17 | 1427 | 0 | 44 | 0 | 35 | 4 | 38 | 35 | 13 | 0 | 0 | 30 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 280 | 0 | 0 | 145 | 51 | 70 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 7 | 130 | 180 | 0 | 0 | 1120 | 18 | 6168 | 13414 | 98.1
19:30 | 48 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 55 | 149 | 147 | 277 | 55 | 35 | 108 | 50 | 250 | 140 | 0 | 0 | 35 | 170 | 0 | 0 | 0 | 125 | 7 | 10 | 0 | 0 | 45 | 150 | 0 | 0 | 17 | 66 | 70 | 54 | 100 | 100 | 0 | 172 | 68 | 8 | 0 | 144 | 0 | 50 | 17 | 84 | 221 | 0 | 0 | 0 | 1163 | 0 | 51 | 137 | 0 | 0 | 0 | 340 | 5 | 183 | 10 | 115 | 0 | 173 | 28 | 20 | 95 | 32 | 52.2 | 0 | 45 | 310 | 320 | 385 | 36 | 0 | 0 | 8 | 0 | 81 | 20 | 0 | 0 | 168 | 35 | 78 | 168 | 0 | 0 | 0 | 7 | 7560.2 | 924 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 1184 | 17 | 1441 | 0 | 47 | 0 | 35 | 5 | 42 | 35 | 19 | 8 | 0 | 30 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 320 | 0 | 0 | 140 | 51 | 110 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 11 | 278 | 9 | 130 | 220 | 0 | 0 | 1244 | 35 | 6697 | 14257.2
20:00 | 90 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 55 | 149 | 146 | 277 | 55 | 35 | 108 | 50 | 250 | 138 | 0 | 0 | 35 | 170 | 0 | 0 | 0 | 125 | 7 | 10 | 0 | 0 | 75 | 138 | 0 | 0 | 17 | 66 | 70 | 54 | 100 | 100 | 0 | 172 | 100 | 8 | 0 | 144 | 0 | 50 | 23 | 102 | 221 | 0 | 0 | 0 | 1140 | 0 | 51 | 137 | 0 | 0 | 0 | 340 | 5 | 183 | 10 | 114 | 0 | 168 | 29 | 20 | 88 | 32 | 52.2 | 0 | 45 | 305 | 320 | 359 | 36 | 0 | 0 | 8 | 0 | 81 | 20 | 0 | 0 | 168 | 35 | 78 | 176 | 0 | 0 | 0 | 8 | 7595.2 | 924 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 1147 | 17 | 1421 | 0 | 47 | 0 | 35 | 5 | 98 | 35 | 37 | 16 | 0 | 30 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 300 | 0 | 0 | 134 | 50 | 113 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 32 | 277 | 9 | 130 | 220 | 0 | 0 | 1230 | 35 | 6709 | 14304.2 | 98.11
21:00 | 90 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 55 | 149 | 110 | 277 | 55 | 0 | 108 | 51 | 250 | 142 | 0 | 0 | 35 | 182 | 0 | 0 | 0 | 108 | 7 | 10 | 0 | 0 | 70 | 126 | 14 | 0 | 13 | 66 | 70 | 54 | 100 | 100 | 0 | 172 | 100 | 3 | 0 | 144 | 0 | 50 | 25.5 | 92 | 222 | 0 | 0 | 0 | 1098 | 0 | 43 | 142 | 0 | 0 | 0 | 340 | 5 | 190 | 10 | 115 | 0 | 154 | 29 | 20 | 97 | 26 | 52.2 | 0 | 46 | 305 | 320 | 315 | 36 | 0 | 0 | 8 | 0 | 81 | 20 | 0 | 0 | 168 | 35 | 78 | 167 | 0 | 0 | 0 | 12 | 7378.7 | 927 | 0 | 0 | 21 | 24 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 1067 | 17 | 1405.75 | 0 | 47 | 0 | 92 | 21 | 98 | 35 | 37 | 43 | 0 | 30 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 280 | 0 | 0 | 160 | 50 | 115 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 32 | 269 | 10 | 130 | 220 | 0 | 0 | 1244 | 72 | 6808.75 | 14187.45 | 98.12
22:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 287 | 0 | 0 | 0 | 55 | 122 | 110 | 277 | 15 | 0 | 108 | 50 | 250 | 142 | 0 | 0 | 17 | 182 | 0 | 0 | 0 | 90 | 6.5 | 10 | 0 | 0 | 70 | 139 | 39 | 0 | 24 | 66 | 70 | 54 | 100 | 100 | 0 | 172 | 94 | 16 | 0 | 53 | 0 | 19 | 8 | 95 | 222 | 0 | 0 | 0 | 1153 | 0 | 51 | 140 | 0 | 0 | 0 | 300 | 5 | 208 | 10 | 95 | 0 | 156 | 28 | 20 | 63 | 28 | 52.2 | 0 | 46 | 310 | 320 | 318 | 36 | 0 | 0 | 8 | 0 | 81 | 20 | 0 | 0 | 168 | 35 | 82 | 169 | 0 | 0 | 0 | 5 | 7082.7 | 926 | 0 | 0 | 35 | 29 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 1130 | 17 | 1409.19 | 0 | 47 | 0 | 113 | 25 | 99 | 35 | 37 | 6 | 0 | 30 | 0 | 0 | 0 | 126 | 0 | 0 | 0 | 280 | 0 | 0 | 160 | 50 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 32 | 277 | 10 | 100 | 180 | 0 | 0 | 1244 | 72 | 6825.19 | 13907.89 | 98.13
23:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 55 | 88 | 110 | 277 | 0 | 0 | 108 | 50 | 300 | 143 | 0 | 0 | 0 | 257 | 0 | 0 | 0 | 108 | 6.5 | 11 | 0 | 0 | 70 | 140 | 40 | 0 | 13 | 66 | 70 | 54 | 100 | 100 | 0 | 182 | 97 | 21 | 0 | 53 | 0 | 19 | 8 | 90 | 222 | 0 | 0 | 0 | 1159 | 0 | 51 | 142 | 0 | 0 | 0 | 300 | 5 | 215 | 10 | 59 | 0 | 166 | 28 | 20 | 78 | 34 | 52.2 | 0 | 45 | 305 | 320 | 332 | 36 | 0 | 0 | 8 | 0 | 81 | 20 | 0 | 0 | 169 | 35 | 82 | 169 | 0 | 0 | 0 | 12 | 7189.7 | 928 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 1113 | 17 | 1421.88 | 0 | 47 | 0 | 113 | 25 | 99 | 0 | 37 | 0 | 0 | 30 | 0 | 0 | 0 | 126 | 0 | 0 | 0 | 280 | 0 | 0 | 160 | 50 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 11 | 120 | 220 | 0 | 0 | 1244 | 72 | 6747.88 | 13937.58 | 98.14
Total KWH | 344736 | 1423680 | 648960 | 0 | 0 | 0 | 0 | 0 | 7333200 | 0 | 0 | 324000 | 1109160 | 2103840 | 1817280 | 3301713 | 388069 | 462862 | 2031840 | 713280 | 6586000 | 3404335 | 0 | 0 | 465004 | 4916984 | 0 | 0 | 111538 | 1512000 | 197400 | 45923 | 0 | 0 | 375109 | 1372473 | 117312 | 0 | 870720 | 782080 | 787320 | 296189 | 1696320 | 2121600 | 16621 | 4129140 | 995300 | 85920 | 3723636.36 | 1012000 | 0 | 664800 | 191538 | 1193490 | 5249887 | 0 | 0 | 0 | 26645452 | 58320 | 1186000 | 2241454 | 50181.81 | 0 | 0 | 7928000 | 462720 | 4667000 | 409464 | 1400640 | 0 | 3548160 | 346920 | 451810 | 1396500 | 659520 | 707789 | 83636 | 692320 | 7580500 | 7654800 | 9012000 | 833000 | 0 | 0 | 182736 | 0 | 1916160 | 480000 | 0 | 0 | 4476180 | 644040 | 1687200 | 3650400 | 0 | 6900 | 218690 | 212880 | 156414632.17 | 22343272 | 53568 | 0 | 43680 | 50048 | 912000 | 0 | 0 | 0 | 0 | 626400 | 411840 | 24501820 | 91200 | 32379818 | 0 | 212780 | 0 | 643968 | 80056 | 577088 | 145728 | 133929 | 51677 | 145540 | 145821 | 126744 | 625182 | 0 | 3266491 | 0 | 0 | 0 | 7751418 | 0 | 5580 | 3963000 | 1154181 | 868949 | 101683 | 1108089 | 0 | 0 | 19558.08 | 596880 | 1687 | 86208 | 5520000 | 179664 | 2969000 | 5346960 | 0 | 5912727 | 26536727.27 | 328800 | 150019761.35 | 306434393.52

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 19-06-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12725.85 | MW | 12:00 Hr. | Energy Generated |  |  | 306.4344 |  | MKWHr.
| Day Peak Demand |  |  | 12725.85 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.103 |  | MKWHr.
| Evening Peak Generation |  |  | 14304.2 | MW | 20:00 Hr. | Energy Demand |  |  | 306.5374 |  | MKWHr.
| Evening Peak Demand |  |  | 14304.2 | MW | 20:00 Hr. | Maximum Temperature |  |  | 31.5 |  | °C
| Minimum Generation of the Day |  |  | 10826.57 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 689.56 |  | MMCFD
| Maximum Generation of the Day |  |  | 14304.2 | MW | 20:00 Hr. | Production Cost per KWHr |  |  | 7.2703 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 22.4838 | 0 | 16.6464 | 0 | 0 | 0.11154 | 0 | 0 | 39.2418 | Gas | 95.3025 | Gas | 339304361.4877
| Chattogram Zone |  |  | 5.3358 | 30.3691 | 11.6055 | 0 | 4.1291 | 0.074941 | 0 | 0.87072 | 52.3852 | Coal | 97.9575 | Coal | 628007119.5085
| Cumilla Zone |  |  | 15.1552 | 0 | 10.3338 | 0 | 0 | 0.083636 | 0.65952 | 0 | 26.2321 | HFO | 49.9747 | HFO | 935816771
| Mymensingh Zone |  |  | 0 | 0 | 6.1945 | 0 | 0 | 0.22559 | 0 | 0 | 6.4201 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 32.1354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.1354 | Hydro | 4.1291 | Hydro | 412914
| Khulna Zone |  |  | 0.053568 | 24.5018 | 0.81133 | 0 | 0 | 0.41184 | 23.2553 | 0 | 49.0338 | Solar | 1.9052 | Solar | 32690454.5288
| Barishal Zone |  |  | 8.4956 | 37.9695 | 0.41501 | 0 | 0 | 0.001687 | 0 | 0 | 46.8818 | Import | 56.2946 | Import | 278877181.08
| Rajshahi Zone |  |  | 11.6431 | 0 | 1.991 | 0 | 0 | 0.27786 | 32.3798 | 0 | 46.2918 | Wind | 0.87072 | Wind | 12747340.8
| Rangpur Zone |  |  | 0 | 5.1172 | 1.977 | 0 | 0 | 0.71812 | 0 | 0 | 7.8123
| Total |  |  | 95.3025 | 97.9575 | 49.9747 | 0 | 4.1291 | 1.9052 | 56.2946 | 0.87072 | 306.4344
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 339304361.4877 |  | Hydro | 412914
|  |  |  | Coal | 628007119.5085 |  | Solar | 32690454.5288
|  |  |  | HFO | 935816771 |  | Import | 278877181.08
|  |  |  | HSD | 0 |  | Wind | 12747340.8
[5 empty] | Total: | 222,78,56,142 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.3433 | Peak Hr Flow | 924.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 54319672.84 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 32.3798 | Peak Hr Flow | 1421.00 MW at 20:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 832 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.65952 | Peak Hr Flow | 32.00 MW at 20:00 hrs.
Maximum Power Flow: |  |  | MW: | 998 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 55.3826 | Peak Hr Flow | 2377.00 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5119
|  |  |  | Chattogram |  | 0 |  | 1387
|  |  |  | Cumilla |  | 0 |  | 1315
|  |  |  | Mymensingh |  | 0 |  | 1093
|  |  |  | Sylhet |  | 0 |  | 587
|  |  |  | Khulna |  | 0 |  | 1569
|  |  |  | Barishal |  | 0 |  | 434
|  |  |  | Rajshahi |  | 0 |  | 1236
|  |  |  | Rangpur |  | 0 |  | 913
|  |  |  | Total |  | 0 |  | 13653
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[5 empty] | Total | 300 |  |  |  | Total | 476
|  |  |  | Total Unavailable Capacity |  |  |  | 776
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:25 | 09:23 | Jamalpur 132/33kV S/S T-3 LT Scheduled S/D Due to Red hot remove work of 33kv Shahapur | [7 empty] | 12.0MW load
|  |  | feeder incoming D.S. | [7 empty] | interrup.
| 08:25 | 09:23 | Jamalpur 132/33kV S/S T-3 HT Scheduled S/D Due to Red hot remove work of 33kv Shahapur | [7 empty] | 12.0MW load
|  |  | feeder incoming D.S. | [7 empty] | interrup.
|  | 08:49 | Mymensingh 132/33kV S/S Transformer-2 (414T) LT is restored.
|  | 08:49 | Mymensingh 132/33kV S/S Transformer-2 (414T) HT is restored.
| 09:10 | 12:20 | Mymensingh 132/33kV S/S Capacitor Bank-2 Forced S/D Due to Red hot on 33 Y Bus DS
| 09:16 | 12:13 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Scheduled S/D from Beanibazar 132/33kV
end Due to CB maintenance
| 09:37 | 12:16 | Mymensingh 132/33kV S/S Transformer-2 (414T) LT Forced S/D Due to Red hot on 33 Y Bus DS
| 09:40 | 12:16 | Mymensingh 132/33kV S/S Transformer-2 (414T) HT Forced S/D Due to Red hot on 33 Y Bus DS
| 09:41 |  | Raozan 25 MW PP Synchronized
|  | 11:25 | Rangamati 132/33kV S/S Power Transformer TR1 (405T) HT is restored.
| 11:26 | 13:38 | Gopalganj- Gopalganj(N) 132kV Ckt-2 Forced S/D from Gopalganj 132/33kV end Due to তার
পরিবর্তন and from Gopalganj 400/132kVend.
| 12:00 |  | Day Peak Generation: 12723 MW.
| 12:03 |  | Patuakhali 1320 MW (RNPL) Unit-1 was forced shutdown due to boiler tube leakage.
|  | 12:06 | Rangamati 132/33kV S/S Power Transformer TR1 (405T) LT is restored.
| 13:30 | 20:49 | Goalpara 132/33kV S/S Bus 2 Project Work S/D Due to protechtion test by SPMD WITH T-7
| 14:37 |  | Bashundhara-Rampura 132 kV Ckt-2 Project Work S/D from Rampura 230/132kV end Due to New
1200sqmm XLPE UG Cable installation work
| 15:52 | 16:56 | Hathazari 230/132/33kV S/S MT-01 LT Forced S/D Due to oil level alarm
| 15:52 | 16:56 | Hathazari 230/132/33kV S/S MT-01 HT Forced S/D Due to oil level alarm
| 16:49 | 17:27 | Chhatak 132/33kV S/S T-2 HT Forced S/D Due to Transformer-02 DS status cheack.
| 17:25 |  | Matarbari 2*600 MW (CPGCBL) Tripped with remarks:- unit-1
| 17:25 |  | Matarbari 2*600 MW (CPGCBL) Unit-1 tripped due to the tripping of Main cooling water
pump.
| 20:00 |  | Evening Peak Generation 14304 MW
| 01:35 |  | Raozan 25 MW PP Shutdown
| 04:15 | 04:34 | Gopalganj 132/33kV S/S T2 LT Tripped showing Siprotec 7sj82 relays Due to REB-5 trip | [7 empty] | 50.0MW load
interrup.
| 05:43 |  | Jhenaidah 230/132kV S/S Transformer- 2 LT Scheduled S/D Due to Maintenance Work
| 05:44 |  | Jhenaidah 230/132kV S/S Transformer- 2 HT Scheduled S/D Due to Maintenance Work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 19-06-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 334 | 7333200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 250 | 6586000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 138 | 3404335 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 388069 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 170 | 4916984 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 90 | 344736 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 324000 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 146 | 1817280 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 462862 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 465004 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 7 | 197400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 10 | 45923 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 648960 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 277 | 3301713 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2103840 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1423680 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 50 | 713280 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 2031840 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 111538 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1109160 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | None
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 125 | 1512000 | -
Dhaka Area Total |  |  |  |  | 5939.724 | 2147 | 39241804
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 23 | 191538 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 58320 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 664800 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 172 | 4129140 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 221 | 5249887 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 102 | 1193490 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 70 | 787320 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 782080 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1696320 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 8 | 85920 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 117312 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 16621 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 138 | 1372473 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 54 | 296189 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 100 | 995300 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2121600 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 75 | 375109 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 144 | 1012000 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1140 | 26645452 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 17 | 870720 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 0 | 3723636.36 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4895.72 | 2580 | 52385227.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 183 | 4667000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 7928000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 10 | 409464 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 462720 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 50181.81 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1186000 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 137 | 2241454 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 45 | 692320 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 168 | 3548160 | -
| Import (Tripura) |  | Import | 0 | 160 | 32 | 659520 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 707789 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 451810 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 88 | 1396500 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 29 | 346920 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 114 | 1400640 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 83636 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1274.2 | 26232114.81
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 6900 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 176 | 3650400 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 78 | 1687200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 218690 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 8 | 212880 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 644040 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 297 | 6420110
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 36 | 833000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 20 | 480000 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1916160 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 168 | 4476180 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 182736 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7580500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 359 | 9012000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7654800 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1297 | 32135376
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 924 | 22343272 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 43680 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 5 | 50048 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 53568 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 91200 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 626400 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 411840 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1147 | 24501820 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2236 | 49033828
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 0 | 5912727 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 32 | 86208 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 9 | 179664 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 2969000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1230 | 26536727.27 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5346960 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 328800 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 277 | 5520000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1687 | -
Barishal Area Total |  |  |  |  | 2236 | 1933 | 46881773.27
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 47 | 212780 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 5 | 80056 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 133929 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 625182 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 121 | 3266491 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 300 | 7751418 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 145821 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 16 | 51677 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 98 | 577088 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 643968 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 145728 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 5580 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1421 | 32379818 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 126744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 145540 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2145 | 46291820
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1154181 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 134 | 3963000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 1108089 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 19558.08 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 113 | 868949 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 101683 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 596880 | -
Rangpur Area Total |  |  |  |  | 950 | 395 | 7812340.08
Eastern Grid Total |  |  |  |  | 16705.895 | 7595.2 | 156414632.17
Western Grid Total |  |  |  |  | 10378.16 | 6709 | 150019761.35
National Grid Total |  |  |  |  | 27084.055 | 14304.2 | 306434393.52
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 19-06-2025
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9500.88 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4152.5 | MW
i) Dhaka area |  |  | 5118.68 |  | MW | i) Khulna area |  |  |  | 1569.4 | MW
ii) Chattogram area |  |  | 1387 |  | MW | ii) Barishal area |  |  |  | 434.5 | MW
iii) Cumilla area |  |  | 1315.2 |  | MW | iii) Rajshahi area |  |  |  | 1235.6 | MW
iv) Mymensingh area |  |  | 1093 |  | MW | iv) Rangpur area |  |  |  | 913 | MW
v) Sylhet area |  |  | 587 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13653.38 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 69 | 20:00 | 133 | Patuakhali | 76 | 22:00
2 | AKSML | 142 | 06:00 | 68 | Jaldhaka | 74 | 19:30 | 134 | Payra | 32 | 23:00
3 | Aftabnagar | 38 | 13:00 | 69 | Jamalpur | 114 | 19:30 | 135 | Postogola | 55 | 13:00
4 | Agargaon | 129 | 13:00 | 70 | Jashore | 128 | 22:00 | 136 | Purbachal | 19 | 19:00
5 | Agrabad | 86 | 11:00 | 71 | Jhenaidah | 112 | 19:30 | 137 | Purbasadipur | 121 | 00:00
6 | Amnura | 35 | 00:00 | 72 | Joydebpur | 138 | 13:00 | 138 | Rahanpur | 26 | 00:00
7 | Ashuganj | 101 | 21:00 | 73 | Joypurhat | 55 | 00:00 | 139 | Rahim | 53 | 16:00
8 | BSRM | 211 | 09:00 | 74 | Juldah | 14.5 | 23:00 | 140 | Rajbari | 70 | 20:00
9 | Bagerhat | 77 | 20:00 | 75 | KSRM | 15 | 06:00 | 141 | Rajendrapur | 126 | 19:30
10 | Bajitpur | 61 | 21:00 | 76 | Kabirpur | 248 | 18:00 | 142 | Rajshahi | 98 | 00:00
11 | Bakulia | 103 | 13:00 | 77 | Kachua | 84 | 19:00 | 143 | Rajshahi-230 | 74 | 01:00
12 | Banani | 20 | 13:00 | 78 | Kallyanpur | 93 | 00:00 | 144 | Ramganj | 110 | 20:00
13 | Bangabhaban | 16 | 10:00 | 79 | Kalurghat | 36 | 18:30 | 145 | Rampur | 37 | 12:00
14 | Barapukuria | 62 | 00:00 | 80 | Kamrangirchar | 61 | 17:00 | 146 | Rangamati | 15 | 19:00
15 | Barguna | 22 | 21:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 152 | 20:00
16 | Barishal | 105 | 21:00 | 82 | Kasba | 34 | 22:00 | 148 | Ruppur | 6 | 16:00
17 | Barishal-230 | 98 | 23:00 | 83 | Kazla | 84 | 19:30 | 149 | SSM | 15 | 08:00
18 | Baroaulia | 55 | 18:00 | 84 | Keranigonj | 67 | 21:00 | 150 | Saidpur | 103 | 19:30
19 | Baroirhat | 55 | 19:00 | 85 | Khagrachori | 32 | 19:00 | 151 | Satkhira | 122 | 22:00
20 | Bashundhara | 160 | 13:00 | 86 | Khulna | 67 | 14:00 | 152 | Satmasjid | 96 | 12:00
21 | BashundharaCement | 1 | 00:00 | 87 | Khulshi | 184 | 12:00 | 153 | Savar | 224 | 15:00
22 | Beanibazar | 74 | 00:00 | 88 | Kishoreganj | 140 | 22:00 | 154 | SevenRings | 16.27 | 04:00
23 | Benapole | 64 | 22:00 | 89 | Kodda | 317 | 15:00 | 155 | ShahCement | 39 | 03:00
24 | Bhaluka | 152 | 12:00 | 90 | Kulaura | 49 | 00:00 | 156 | Shahjadpur | 61 | 19:00
25 | Bhandaria | 54 | 22:00 | 91 | Kurigram | 65 | 19:30 | 157 | Shahjibazar | 125 | 00:00
26 | Bhangura | 31 | 19:30 | 92 | Kushtia | 128 | 00:00 | 158 | Shahmirpur | 63 | 19:00
27 | Bheramara(GK) | 54 | 00:00 | 93 | Lalbag | 52 | 12:00 | 159 | Shariatpur | 88 | 22:00
28 | Bhulta | 248 | 23:00 | 94 | Lalmonirhat | 62 | 19:30 | 160 | Sherpur | 144 | 00:00
29 | Bog-Sherpur | 60 | 00:00 | 95 | MI_Cement | 6.6 | 02:00 | 161 | Shikalbaha | 8 | 09:00
30 | Bogura | 152 | 22:00 | 96 | Madanganj | 42 | 19:30 | 162 | Shitalakhya | 81.7 | 16:00
31 | Borhanuddin | 86 | 22:00 | 97 | Madaripur | 109 | 00:00 | 163 | Sholosohor | 47 | 12:00
32 | Brahmanbaria | 122 | 21:00 | 98 | Madartek | 83.12 | 21:00 | 164 | Shyampur | 164 | 12:00
33 | Cantonment | 154 | 13:00 | 99 | Madunaghat | 56 | 19:30 | 165 | Siddhirganj | 110 | 11:00
34 | Chandina | 12.94 | 19:30 | 100 | Magura | 54 | 21:00 | 166 | Sirajganj | 86 | 19:30
35 | Chandpur | 74 | 00:00 | 101 | Mahasthangarh | 80 | 00:00 | 167 | Sonargaon | 120 | 23:00
36 | Chandraghona | 34 | 19:00 | 102 | Manikganj | 107 | 02:00 | 168 | Sreemongol | 79 | 00:00
37 | Chapai | 69 | 00:00 | 103 | Maniknagar | 80 | 13:00 | 169 | Sreepur | 99 | 10:00
38 | Charsaidpur | 31 | 17:00 | 104 | Matarbari | 45 | 22:00 | 170 | Srinagar | 45.82 | 22:00
39 | Chauddagram | 63 | 19:00 | 105 | Matuail | 58 | 10:00 | 171 | Sunamganj | 60 | 23:00
40 | Chhatak | 36 | 21:00 | 106 | Millgate | 97 | 09:00 | 172 | Sylhet | 46 | 00:00
41 | Chowmuhani | 215 | 20:00 | 107 | Mirpur | 115 | 18:30 | 173 | Sylhet-132 | 120 | 19:00
42 | Chuadanga | 90 | 00:00 | 108 | Mirsorai | 9 | 15:00 | 174 | TK | 31 | 23:00
43 | Coxsbazar | 120 | 19:30 | 109 | Mirzapur | 36 | 01:00 | 175 | Tangail | 144 | 19:30
44 | Cumilla(N) | 147 | 23:00 | 110 | Mithapukur | 54 | 00:00 | 176 | Thakurgaon | 92 | 00:00
45 | Cumilla(S) | 151 | 19:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 137 | 09:00
46 | Daudkandi | 139 | 19:30 | 112 | Mogbazar | 149.9 | 13:00 | 178 | Ullahpara | 34 | 19:30
47 | Dhaka | 62 | 12:00 | 113 | Mongla | 47 | 16:00 | 179 | Ullon | 38 | 21:00
48 | Dhamrai | 138 | 23:00 | 114 | Motijheel | 38 | 12:00 | 180 | Uttara | 92 | 16:00
49 | Dhanmondi | 149 | 13:00 | 115 | Muktagacha | 37 | 19:00 | 181 | UttaraNew | 55 | 21:00
50 | Dohazari | 95 | 20:00 | 116 | Munshiganj | 110 | 00:00 | 182 | Zigatola | 70 | 13:00
51 | Faridpur | 152 | 22:00 | 117 | Muradnagar | 28 | 22:00
52 | Fatullah | 98 | 12:00 | 118 | Mymensingh | 202 | 19:30
53 | Fenchuganj | 41 | 00:00 | 119 | Naogaon | 121 | 00:00
54 | Feni | 102 | 19:00 | 120 | Narail | 55 | 19:30
55 | GPH | 86 | 17:00 | 121 | Narinda | 74 | 13:00
56 | Ghatail | 72 | 19:00 | 122 | Narshingdi | 169 | 20:00
57 | Ghorashal | 16 | 00:00 | 123 | Natore | 132 | 00:00
58 | Ghorashal-230 | 92 | 21:00 | 124 | Nawabganj | 53.6 | 23:00
59 | Goalpara | 36 | 13:00 | 125 | Netrakona | 140 | 21:00
60 | Gollamari | 88 | 19:30 | 126 | New | 86 | 12:00
61 | Gopalganj | 105 | 22:00 | 127 | Niamatpur | 67 | 00:00
62 | Gulshan | 142 | 13:00 | 128 | Noapara | 45 | 19:30
63 | Halishahar | 107 | 11:00 | 129 | PHP | 10 | 06:00
64 | HaripurSBU | 175 | 12:00 | 130 | Pabna | 105 | 21:00
65 | Hasnabad | 73 | 15:00 | 131 | Palashbari | 108 | 20:00
66 | Hathazari | 73 | 22:00 | 132 | Panchagarh | 56 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 19-06-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13752 | 17 |  | 13770
1:00 | 13342 | 36 |  | 13380
2:00 | 12830 | 29 |  | 12860
3:00 | 12428 | 21 |  | 12450
4:00 | 11935 | 0 |  | 11935
5:00 | 11406 | 0 |  | 11406
6:00 | 10827.86 | 0 |  | 10827.86
7:00 | 10826.57 | 0 |  | 10826.57
8:00 | 11243.51 | 0 |  | 11243.51
9:00 | 11444.2 | 0 |  | 11444.2
10:00 | 11886.59 | 0 |  | 11886.59
11:00 | 12168.7 | 0 |  | 12168.7
12:00 | 12725.85 | 0 |  | 12725.85
13:00 | 13211.07 | 0 |  | 13211.07
14:00 | 12829.4 | 0 |  | 12829.4
15:00 | 12948.74 | 0 |  | 12948.74
16:00 | 12892.68 | 0 |  | 12892.68
17:00 | 12454.37 | 0 |  | 12454.37
18:00 | 12358.66 | 0 |  | 12358.66
19:00 | 13414 | 0 |  | 13414
19:30 | 14257.2 | 0 |  | 14257.2
20:00 | 14304.2 | 0 |  | 14304.2
21:00 | 14187.45 | 0 |  | 14187.45
22:00 | 13907.89 | 0 |  | 13907.89
23:00 | 13937.58 | 0 |  | 13937.58
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 19-06-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6691 | 7061 | 13752 | DAILY GENERATION CURVE
00:30 | 6557 | 6990 | 13547
01:00 | 6423 | 6919 | 13342 | 19-06-2025
01:30 | 6319 | 6767 | 13086
02:00 | 6215 | 6615 | 12830
02:30 | 6177.5 | 6451.5 | 12629
03:00 | 6140 | 6288 | 12428
03:30 | 5963 | 6218.5 | 12181.5
04:00 | 5786 | 6149 | 11935
04:30 | 5674 | 5996.5 | 11670.5
05:00 | 5562 | 5844 | 11406
05:30 | 5396.62 | 5720.31 | 11116.93
06:00 | 5231.24 | 5596.62 | 10827.86
06:30 | 5107.6 | 5719.615 | 10827.215
07:00 | 4983.96 | 5842.61 | 10826.57
07:30 | 5114.94 | 5920.1 | 11035.04
08:00 | 5245.92 | 5997.59 | 11243.51
08:30 | 5388.68 | 5955.175 | 11343.855
09:00 | 5531.44 | 5912.76 | 11444.2
09:30 | 5802.52 | 5862.875 | 11665.395
10:00 | 6073.6 | 5812.99 | 11886.59
10:30 | 6182.445 | 5845.2 | 12027.645
11:00 | 6291.29 | 5877.41 | 12168.7
11:30 | 6531.3 | 5915.975 | 12447.275
12:00 | 6771.31 | 5954.54 | 12725.85
12:30 | 6895.965 | 6072.495 | 12968.46
13:00 | 7020.62 | 6190.45 | 13211.07
13:30 | 6987.575 | 6032.66 | 13020.235
14:00 | 6954.53 | 5874.87 | 12829.4
14:30 | 6993.395 | 5895.675 | 12889.07
15:00 | 7032.26 | 5916.48 | 12948.74
15:30 | 7025.91 | 5894.8 | 12920.71
16:00 | 7019.56 | 5873.12 | 12892.68
16:30 | 6902.475 | 5771.05 | 12673.525
17:00 | 6785.39 | 5668.98 | 12454.37
17:30 | 6715.865 | 5690.65 | 12406.515
18:00 | 6646.34 | 5712.32 | 12358.66
18:30 | 6946.17 | 5940.16 | 12886.33
19:00 | 7246 | 6168 | 13414
19:30 | 7560.2 | 6697 | 14257.2
20:00 | 7595.2 | 6709 | 14304.2
20:30 | 7486.95 | 6758.875 | 14245.825 |  | Executive Engineer
21:00 | 7378.7 | 6808.75 | 14187.45 |  | Network Operation Division
21:30 | 7230.7 | 6816.97 | 14047.67
22:00 | 7082.7 | 6825.19 | 13907.89
22:30 | 7136.2 | 6786.535 | 13922.735
23:00 | 7189.7 | 6747.88 | 13937.58

## En-Curve
QF-LDC-12
Date | 19-06-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3042 | 1286 | 959 | 38 | 34 | 1413 | 172 | 4650 | 0 | 493 | 1630 | 0 | 0 | 35 | 17 | DAILY ENERGY CURVE
00:30 | 3019 | 1281 | 940 | 38 | 34 | 1417.5 | 172 | 4624 | 0 | 430 | 1555.5 | 0 | 0 | 36 | 26.5 | 19-06-2025
01:00 | 2996 | 1276 | 921 | 38 | 34 | 1422 | 172 | 4598 | 0 | 367 | 1481 | 0 | 0 | 37 | 36
01:30 | 2974 | 1277.5 | 921.5 | 38 | 30 | 1419 | 172 | 4587.5 | 0 | 299.5 | 1325 | 0 | 0 | 42 | 32.5 | Energy Generated | 306.4344 |  | MKWHr
02:00 | 2952 | 1279 | 922 | 38 | 26 | 1416 | 172 | 4577 | 0 | 232 | 1169 | 0 | 0 | 47 | 29 | Energy not Served | 0.103 |  | MKWHr
02:30 | 2925 | 1280.5 | 921.5 | 38 | 29 | 1366.5 | 172 | 4488.5 | 0 | 223 | 1137 | 0 | 0 | 48 | 25 | Total Energy Requirement | 306.5374 |  | MKWHr
03:00 | 2898 | 1282 | 921 | 38 | 32 | 1317 | 172 | 4400 | 0 | 214 | 1105 | 0 | 0 | 49 | 21
03:30 | 2886.5 | 1265.5 | 921 | 38 | 31 | 1313.5 | 172 | 4328.5 | 0 | 169.5 | 1007 | 0 | 0 | 49 | 10.5
04:00 | 2875 | 1249 | 921 | 38 | 30 | 1310 | 172 | 4257 | 0 | 125 | 909 | 0 | 0 | 49 | 0
04:30 | 2820 | 1256 | 921 | 38 | 29 | 1313.5 | 172 | 4143.5 | 0 | 125 | 808.5 | 0 | 0 | 44 | 0
05:00 | 2765 | 1263 | 921 | 38 | 28 | 1317 | 172 | 4030 | 0 | 125 | 708 | 0 | 0 | 39 | 0
05:30 | 2783.5 | 1233 | 921 | 38 | 25 | 1268.5 | 172 | 3891 | 8.93 | 125 | 614.5 | 0 | 0 | 36.5 | 0
06:00 | 2802 | 1203 | 921 | 38 | 22 | 1220 | 172 | 3752 | 17.86 | 125 | 521 | 0 | 0 | 34 | 0
06:30 | 2861.5 | 1201.5 | 921 | 38 | 22 | 1221.5 | 172 | 3745 | 60.215 | 116.5 | 433.5 | 0 | 0 | 34.5 | 0
07:00 | 2921 | 1200 | 921 | 38 | 22 | 1223 | 172 | 3738 | 102.57 | 108 | 346 | 0 | 0 | 35 | 0
07:30 | 2895 | 1201 | 921 | 38 | 23 | 1293.415 | 172 | 3858.5 | 111.125 | 110.5 | 369 | 0 | 0 | 42.5 | 0
08:00 | 2869 | 1202 | 921 | 38 | 24 | 1363.83 | 172 | 3979 | 119.68 | 113 | 392 | 0 | 0 | 50 | 0
08:30 | 2843.5 | 1170.9 | 921 | 38 | 25 | 1351.215 | 172 | 4000 | 129.74 | 128.5 | 520 | 0 | 0 | 44 | 0
09:00 | 2818 | 1139.8 | 921 | 38 | 26 | 1338.6 | 172 | 4021 | 139.8 | 144 | 648 | 0 | 0 | 38 | 0
09:30 | 2812 | 1133.2 | 921 | 38 | 25 | 1270.875 | 172 | 3993 | 181.82 | 164.5 | 914.5 | 0 | 0 | 39.5 | 0
10:00 | 2806 | 1126.6 | 921 | 38 | 24 | 1203.15 | 172 | 3965 | 223.84 | 185 | 1181 | 0 | 0 | 41 | 0
10:30 | 2785.5 | 1139.8 | 922.5 | 38 | 24 | 1218.105 | 172 | 3977.5 | 224.74 | 201 | 1278 | 0 | 0 | 46.5 | 0
11:00 | 2765 | 1153 | 924 | 38 | 24 | 1233.06 | 172 | 3990 | 225.64 | 217 | 1375 | 0 | 0 | 52 | 0
11:30 | 2779 | 1148.5 | 924 | 38 | 26 | 1267.515 | 172 | 3963 | 269.26 | 256 | 1547 | 0 | 0 | 57 | 0
12:00 | 2793 | 1144 | 924 | 38 | 28 | 1301.97 | 172 | 3936 | 312.88 | 295 | 1719 | 0 | 0 | 62 | 0
12:30 | 2763.5 | 1152.25 | 924 | 38 | 28 | 1323.895 | 172 | 4043 | 286.815 | 340 | 1836 | 0 | 0 | 61 | 0
13:00 | 2734 | 1160.5 | 924 | 38 | 28 | 1345.82 | 172 | 4150 | 260.75 | 385 | 1953 | 0 | 0 | 60 | 0
13:30 | 2658.5 | 1134.5 | 924 | 38 | 29 | 1359.91 | 172 | 4084 | 217.825 | 394.5 | 1946 | 0 | 0 | 62 | 0
14:00 | 2583 | 1108.5 | 924 | 38 | 30 | 1374 | 172 | 4018 | 174.9 | 404 | 1939 | 0 | 0 | 64 | 0
14:30 | 2614.5 | 1133.75 | 924 | 38 | 28 | 1375 | 172 | 4040.5 | 167.32 | 391.5 | 1947.5 | 0 | 0 | 57 | 0
15:00 | 2646 | 1159 | 924 | 38 | 26 | 1376 | 172 | 4063 | 159.74 | 379 | 1956 | 0 | 0 | 50 | 0
15:30 | 2656.5 | 1156 | 924 | 38 | 26 | 1362 | 172 | 4046 | 157.71 | 384.5 | 1947.5 | 0 | 0 | 50.5 | 0
16:00 | 2667 | 1153 | 924 | 38 | 26 | 1348 | 172 | 4029 | 155.68 | 390 | 1939 | 0 | 0 | 51 | 0
16:30 | 2659 | 1126.5 | 922.5 | 38 | 26 | 1352.5 | 172 | 3912.5 | 109.525 | 398 | 1930 | 0 | 0 | 27 | 0
17:00 | 2651 | 1100 | 921 | 38 | 26 | 1357 | 172 | 3796 | 63.37 | 406 | 1921 | 0 | 0 | 3 | 0
17:30 | 2620 | 1106 | 922.5 | 38 | 26 | 1352 | 172 | 3707 | 37.515 | 452 | 1968 | 0 | 0 | 5.5 | 0
18:00 | 2589 | 1112 | 924 | 38 | 26 | 1347 | 172 | 3618 | 11.66 | 498 | 2015 | 0 | 0 | 8 | 0
18:30 | 2603.5 | 1094.5 | 924 | 38 | 28 | 1387 | 172 | 3718 | 5.83 | 625.5 | 2275 | 0 | 0 | 15 | 0
19:00 | 2618 | 1077 | 924 | 38 | 30 | 1427 | 172 | 3818 | 0 | 753 | 2535 | 0 | 0 | 22 | 0
19:30 | 2779 | 1119 | 924 | 38 | 32 | 1441 | 172 | 4060 | 0 | 814 | 2861.2 | 0 | 0 | 17 | 0
20:00 | 2712 | 1112 | 924 | 38 | 32 | 1421 | 172 | 3978 | 0 | 892 | 3006.2 | 0 | 0 | 17 | 0
20:30 | 2675.5 | 1108 | 925.5 | 38 | 29 | 1413.375 | 172 | 3933 | 0 | 894 | 3042.45 | 0 | 0 | 15 | 0
21:00 | 2639 | 1104 | 927 | 38 | 26 | 1405.75 | 172 | 3888 | 0 | 896 | 3078.7 | 0 | 0 | 13 | 0
21:30 | 2608 | 1096.75 | 926.5 | 38 | 27 | 1407.47 | 172 | 3951 | 0 | 899 | 2903.45 | 0 | 0 | 18.5 | 0
22:00 | 2577 | 1089.5 | 926 | 38 | 28 | 1409.19 | 172 | 4014 | 0 | 902 | 2728.2 | 0 | 0 | 24 | 0
22:30 | 2634.5 | 1136 | 927 | 38 | 31 | 1415.535 | 177 | 4009 | 0 | 878.5 | 2657.7 | 0 | 0 | 18.5 | 0
23:00 | 2692 | 1182.5 | 928 | 38 | 34 | 1421.88 | 182 | 4004 | 0 | 855 | 2587.2 | 0 | 0 | 13 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 19-06-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 382 | 18:00 | 368 | 00:00 | Payra | 414 | 18:30 | 406 | 13:00
Ashuganj | 388 | 18:00 | 364 | 11:00 | Rahanpur | 403 | 06:00 | 390 | 19:30
Bhulta | 386 | 18:30 | 364 | 11:00 | Rampal | 402 | 06:00 | 390 | 00:00
Bibiana | 389 | 18:30 | 378 | 02:00
BIPTC | 404 | 06:00 | 395 | 21:00
Bogura | 389 | 10:00 | 374 | 19:30
Gopalganj | 396 | 18:00 | 382 | 00:00
Kaliakoir | 376 | 18:00 | 362 | 00:00
Madunaghat | 395 | 19:00 | 384 | 02:00
Meghnaghat | 383 | 18:00 | 370 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 224 | 18:30 | 215 | 09:00 | Keranigonj | 222 | 18:30 | 213 | 09:00
AKSML | 233 | 19:00 | 222 | 01:00 | Khulna(S) | 232 | 06:00 | 221 | 01:00
Aminbazar | 224 | 18:00 | 216 | 08:00 | Madunaghat | 236 | 21:00 | 226 | 01:00
Ashuganj | 230 | 18:00 | 220 | 00:00 | Madunaghat-400 | 236 | 21:00 | 224 | 08:00
Ashuganj-400 | 230 | 18:00 | 220 | 00:00 | Maniknagar | 218 | 18:00 | 211 | 11:00
Baghabari | 234 | 05:00 | 225 | 00:00 | Meghnaghat | 228 | 18:00 | 221 | 11:00
Barapukuria | 225 | 10:00 | 218 | 02:00 | Meghnaghat-400 | 223 | 18:30 | 216 | 11:00
Barapukuria-230 | 225 | 10:00 | 218 | 02:00 | Mirsorai | 234 | 21:00 | 218 | 09:00
Barishal | 234 | 18:30 | 225 | 00:00 | Rajshahi | 235 | 06:00 | 223 | 01:00
Bheramara | 233 | 05:00 | 222 | 00:00 | Rampal | 231 | 06:00 | 220 | 00:00
Bhulta | 225 | 06:00 | 212 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 226 | 18:00 | 219 | 00:00 | Rampura | 230 | 16:00 | 211 | 11:00
BIPTC | 237 | 06:00 | 222 | 00:00 | Shikalbaha | 236 | 20:00 | 223 | 02:00
Bogura | 235 | 06:00 | 228 | 00:00 | Shyampur | 224 | 18:30 | 214 | 09:00
Bogura-400 | 236 | 10:00 | 228 | 02:00 | Siddhirganj | 219 | 20:00 | 214 | 11:00
Borhanuddin | 240 | 07:00 | 232 | 00:00 | Sirajgonj | 238 | 05:00 | 233 | 02:00
BSRM | 231 | 21:00 | 217 | 09:00 | Sreepur | 229 | 18:30 | 220 | 00:00
Cumilla(N) | 224 | 18:00 | 215 | 08:00 | Tongi | 225 | 19:30 | 214 | 09:00
Faridpur | 232 | 18:00 | 224 | 02:00
Fenchuganj | 226 | 18:30 | 220 | 00:00
Ghorashal | 230 | 00:00 | 230 | 00:00
Ghorashal-230 | 226 | 18:30 | 212 | 11:00
Gopalganj | 233 | 18:00 | 224 | 00:00
GPH | 234 | 21:00 | 221 | 08:00
Haripur | 220 | 18:30 | 213 | 09:00
Hasnabad | 222 | 18:00 | 214 | 11:00
Hathazari | 237 | 21:00 | 222 | 08:00
Ishurdi | 235 | 05:00 | 224 | 00:00
Jhenaidah | 234 | 05:00 | 218 | 00:00
Kaliakoir | 232 | 18:00 | 221 | 01:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 131 | 05:00 | 119 | 11:00 | Madartek | 129 | 05:00 | 120 | 11:00
Agargaon | 130 | 06:00 | 125 | 11:00 | Madunaghat | 134 | 21:00 | 126 | 07:00
Agrabad | 136 | 21:00 | 127 | 08:00 | Magura | 137 | 06:00 | 126 | 00:00
AKS | 132 | 18:00 | 126 | 01:00 | Mahasthangarh | 137 | 06:00 | 125 | 18:30
Aminbazar | 133 | 18:00 | 126 | 08:00 | Manikganj | 130 | 20:00 | 121 | 01:00
Amnura | 138 | 21:00 | 128 | 00:00 | Maniknagar | 130 | 04:00 | 119 | 09:00
Ashuganj | 137 | 18:30 | 133 | 00:00 | Matarbari | 129 | 14:00 | 114 | 00:00
Bagerhat | 134 | 06:00 | 122 | 00:00 | Matuail | 128 | 18:00 | 123 | 11:00
Bajitpur | 131 | 18:00 | 123 | 23:00 | Millgate | 132 | 18:00 | 123 | 11:00
Bakulia | 136 | 21:00 | 128 | 08:00 | Mirpur | 131 | 18:00 | 125 | 08:00
Banani | 130 | 05:00 | 119 | 11:00 | Mirzapur | 130 | 18:00 | 123 | 08:00
Bangabhaban | 129 | 18:00 | 119 | 09:00 | Mithapukur | 133 | 06:00 | 126 | 00:00
Barapukuria | 137 | 10:00 | 131 | 14:00 | MI_Cement | 128 | 21:00 | 123 | 09:00
Barguna | 136 | 21:00 | 131 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 136 | 18:00 | 130 | 00:00 | Mogbazar | 131 | 04:00 | 121 | 11:00
Barishal-230 | 137 | 18:00 | 130 | 00:00 | Mongla | 135 | 05:00 | 122 | 00:00
Baroaulia | 135 | 18:30 | 130 | 00:00 | Motijheel | 129 | 18:00 | 119 | 09:00
Baroirhat | 127 | 18:30 | 118 | 00:00 | Muktagacha | 160 | 04:00 | 123 | 19:00
Bashundhara | 132 | 18:30 | 120 | 11:00 | Munshiganj | 127 | 18:00 | 122 | 11:00
BashundharaCement | 127 | 18:00 | 123 | 09:00 | Muradnagar | 127 | 18:30 | 120 | 00:00
Beanibazar | 127 | 18:00 | 122 | 00:00 | Mymensingh | 133 | 05:00 | 115 | 22:00
Benapole | 137 | 05:00 | 123 | 00:00 | Naogaon | 134 | 05:00 | 128 | 00:00
Bhaluka | 134 | 18:30 | 123 | 00:00 | Narail | 138 | 06:00 | 125 | 00:00
Bhandaria | 133 | 09:00 | 122 | 00:00 | Narinda | 130 | 04:00 | 119 | 09:00
Bhangura | 134 | 05:00 | 129 | 01:00 | Narshingdi | 136 | 18:30 | 116 | 23:00
Bheramara | 136 | 05:00 | 129 | 00:00 | Natore | 134 | 04:00 | 129 | 00:00
Bheramara(GK) | 136 | 05:00 | 129 | 00:00 | Nawabganj | 128 | 18:00 | 123 | 00:00
Bhulta | 123 | 18:00 | 119 | 09:00 | Netrakona | 127 | 10:00 | 112 | 22:00
Bog-Sherpur | 137 | 06:00 | 131 | 00:00 | New | 133 | 18:00 | 125 | 09:00
Bogura | 139 | 06:00 | 134 | 02:00 | Niamatpur | 137 | 10:00 | 131 | 00:00
Bogura-230 | 139 | 06:00 | 134 | 00:00 | Noapara | 136 | 06:00 | 126 | 00:00
Brahmanbaria | 131 | 18:00 | 124 | 00:00 | Pabna | 135 | 05:00 | 128 | 02:00
Cantonment | 130 | 05:00 | 125 | 11:00 | Palashbari | 133 | 06:00 | 124 | 01:00
Chandina | 129 | 18:30 | 122 | 00:00 | Panchagarh | 137 | 21:00 | 124 | 01:00
Chandpur | 131 | 18:30 | 112 | 08:00 | Patuakhali | 137 | 18:30 | 131 | 00:00
Chandraghona | 135 | 21:00 | 129 | 08:00 | Payra | 136 | 21:00 | 133 | 00:00
Chapai | 133 | 10:00 | 127 | 19:00 | PHP | 125 | 18:00 | 117 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 128 | 18:00 | 123 | 11:00 | Postogola | 130 | 18:00 | 125 | 09:00
Chauddagram | 125 | 18:00 | 117 | 00:00 | Purbachal | 131 | 05:00 | 120 | 11:00
Chhatak | 126 | 08:00 | 119 | 23:00 | Purbasadipur | 132 | 21:00 | 122 | 01:00
Chowmuhani | 122 | 18:30 | 111 | 00:00 | Rahanpur | 138 | 10:00 | 132 | 19:00
Chuadanga | 137 | 05:00 | 123 | 00:00 | Rahanpur-400 | 138 | 10:00 | 133 | 19:30
Coxsbazar | 128 | 16:00 | 117 | 03:00 | Rahim | 127 | 06:00 | 124 | 09:00
Cumilla(N) | 129 | 18:00 | 122 | 08:00 | Rajbari | 136 | 06:00 | 129 | 00:00
Cumilla(S) | 133 | 05:00 | 120 | 00:00 | Rajendrapur | 136 | 18:30 | 121 | 12:00
Daudkandi | 126 | 18:30 | 119 | 00:00 | Rajshahi | 135 | 04:00 | 129 | 00:00
Dhaka | 131 | 05:00 | 120 | 11:00 | Rajshahi-230 | 136 | 06:00 | 122 | 01:00
Dhamrai | 130 | 18:00 | 123 | 11:00 | Ramganj | 133 | 02:00 | 110 | 00:00
Dhanmondi | 131 | 05:00 | 119 | 11:00 | Rampur | 135 | 21:00 | 127 | 08:00
Dohazari | 133 | 14:00 | 125 | 00:00 | Rampura | 130 | 06:00 | 121 | 11:00
Faridpur | 136 | 07:00 | 131 | 00:00 | Rangamati | 133 | 18:30 | 128 | 00:00
Fatullah | 128 | 18:00 | 123 | 11:00 | Rangpur | 133 | 10:00 | 123 | 08:00
Fenchuganj | 133 | 17:00 | 129 | 00:00 | Ruppur | 138 | 05:00 | 130 | 13:00
Feni | 123 | 18:00 | 116 | 00:00 | Saidpur | 132 | 05:00 | 124 | 01:00
Ghatail | 131 | 06:00 | 122 | 19:30 | Satkhira | 136 | 05:00 | 126 | 00:00
Ghorashal | 136 | 18:30 | 130 | 00:00 | Satmasjid | 134 | 12:00 | 124 | 11:00
Goalpara | 138 | 05:00 | 128 | 01:00 | Savar | 132 | 18:00 | 123 | 08:00
Gollamari | 138 | 05:00 | 130 | 00:00 | SevenRings | 137 | 18:30 | 127 | 11:00
Gopalganj | 136 | 06:00 | 128 | 00:00 | ShahCement | 128 | 18:00 | 123 | 11:00
Gopalganj-400 | 137 | 11:00 | 131 | 00:00 | Shahjadpur | 138 | 04:00 | 133 | 00:00
Gulshan | 130 | 04:00 | 120 | 11:00 | Shahjibazar | 132 | 18:30 | 124 | 00:00
Halishahar | 137 | 21:00 | 126 | 08:00 | Shahmirpur | 136 | 18:00 | 128 | 07:00
Haripur | 128 | 18:00 | 124 | 09:00 | Shariatpur | 135 | 17:00 | 127 | 00:00
HaripurSBU | 128 | 18:00 | 124 | 09:00 | Sherpur | 138 | 12:00 | 125 | 19:30
Hasnabad | 130 | 18:00 | 125 | 09:00 | Shikalbaha | 124 | 18:30 | 117 | 08:00
Hathazari | 137 | 21:00 | 129 | 08:00 | Shikalbaha-230 | 138 | 21:00 | 129 | 08:00
Ishurdi | 138 | 05:00 | 131 | 00:00 | Shitalakhya | 128 | 21:00 | 123 | 09:00
Jaldhaka | 131 | 10:00 | 122 | 01:00 | Sholosohor | 136 | 21:00 | 126 | 01:00
Jamalpur | 140 | 12:00 | 128 | 19:30 | Shyampur | 130 | 19:30 | 124 | 11:00
Jashore | 140 | 05:00 | 124 | 00:00 | Shyampur-230 | 128 | 18:30 | 122 | 09:00
Jhenaidah | 139 | 05:00 | 122 | 19:30 | Siddhirganj | 128 | 07:00 | 124 | 11:00
Jhenaidah-230 | 140 | 05:00 | 129 | 00:00 | Sirajganj | 134 | 06:00 | 130 | 00:00
Joydebpur | 140 | 18:30 | 126 | 11:00 | Sonargaon | 126 | 06:00 | 119 | 03:00
Joypurhat | 132 | 06:00 | 126 | 00:00 | Sreemongol | 131 | 18:30 | 124 | 00:00
Juldah | 138 | 21:00 | 129 | 07:00 | Sreepur | 134 | 18:30 | 125 | 04:00
Kabirpur | 133 | 18:30 | 122 | 09:00 | Srinagar | 128 | 18:30 | 123 | 00:00
Kachua | 129 | 18:30 | 116 | 00:00 | SSM | 135 | 00:00 | 132 | 03:00
Kaliakoir | 134 | 18:00 | 127 | 00:00 | Sunamganj | 124 | 16:00 | 118 | 23:00
Kallyanpur | 133 | 18:00 | 126 | 07:00 | Sylhet | 128 | 07:00 | 124 | 00:00
Kalurghat | 133 | 18:30 | 127 | 02:00 | Sylhet-132 | 128 | 17:00 | 125 | 00:00
Kamrangirchar | 127 | 04:00 | 122 | 15:00 | Tangail | 129 | 18:00 | 123 | 19:30
Kaptai | 129 | 6:00 | 121 | 21:00 | Thakurgaon | 136 | 21:00 | 122 | 01:00
Kasba | 126 | 18:00 | 119 | 00:00 | TK | 133 | 18:30 | 128 | 00:00
Kazla | 129 | 18:30 | 119 | 10:00 | Tongi | 135 | 19:30 | 126 | 09:00
Keranigonj | 128 | 06:00 | 123 | 00:00 | Ullahpara | 136 | 05:00 | 130 | 00:00
Khagrachori | 132 | 14:00 | 127 | 08:00 | Ullon | 130 | 06:00 | 120 | 11:00
Khulna | 138 | 05:00 | 128 | 00:00 | Uttara | 131 | 18:00 | 124 | 09:00
Khulna(S) | 139 | 06:00 | 130 | 00:00 | UttaraNew | 131 | 18:00 | 125 | 07:00
Khulshi | 134 | 20:00 | 126 | 07:00 | Zigatola | 127 | 05:00 | 122 | 13:00
Kishoreganj | 131 | 18:00 | 122 | 00:00
Kodda | 135 | 18:00 | 121 | 02:00
KSRM | 137 | 21:00 | 129 | 06:00
Kulaura | 132 | 18:00 | 128 | 02:00
Kurigram | 131 | 11:00 | 124 | 02:00
Kushtia | 136 | 04:00 | 125 | 19:00
Lalbag | 128 | 18:30 | 123 | 00:00
Lalmonirhat | 130 | 20:00 | 123 | 01:00
Madanganj | 127 | 18:00 | 123 | 09:00
Madaripur | 135 | 05:00 | 130 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division