## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 21-06-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-06-2025 | during | 21-06-2025 | during | 21-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 380 | 375 | 400.75 | 400.75 | 385 | 385 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 450 | 450 | 450 | 300 | 300 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 142 | 148 | 335 | 335 | 150 | 150 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 323 | 330 | 335 | 335 | 220 | 220 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 50 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 32 | 80 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 8 | 13 | 33 | 33 | 25 | 25 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 22 | 22 | 15 | 15 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 24 | 52.19 | 52.19 | 35 | 35 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 18 | 51 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 70 | 105 | 105 | 80 | 80 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 33 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 28 | 139 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 150 | 150 | None
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 70 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 1454 | 1931 | 5122.4 | 5126.4 | 2694.33 | 2698.33
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 3 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 182 | 182 | 172 | 172 | 172 | 172 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 221 | 221 | 221 | 221 | 221 | 221 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 1 | 86 | 105 | 105 | 94.5 | 94.5 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 79 | 48 | 80 | 56 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 65 | 65 | 65 | 65 | 65 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 80 | 60 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 23 | 34 | 2 | 25 | 2 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2 | 0 | 4.71 | 0 | 4.71 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 13 | 45 | 300 | 300 | 270 | 270 | FGMO
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 50 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 75 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1161 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 46 | 6 | 18 | 31 | 18 | 31 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 0 | 0 | 575 | 575 | 0 | 0 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1825 | 2108 | 3568.43 | 3621.72 | 2919.93 | 2967.22
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 204 | 209 | 221.43 | 221.43 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 353.35 | 353.35 | 0 | 0 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 340 | 340 | 340 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 20 | 24 | 46.7 | 46.7 | 29 | 29 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 5 | 44 | 55 | 55 | 50 | 50 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 145 | 195 | 195 | 150 | 150 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 1 | 138 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 46 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 151 | 200 | 200 | 150 | 150 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 30 | 30 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 16 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 19 | 17.75 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 113 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 18 | 28 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 115 | 115 | 115 | 51 | 115 | Fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 40 | 0 | 40 | 0 | 40 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 896 | 1487 | 2271.43 | 2238.18 | 1607.2 | 1631.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-06-2025 | during | 21-06-2025 | during | 21-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.2 | 0 | 1.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 135 | 150 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 80 | 102 | 115 | 115 | 105 | 105 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 28.25 | 0 | 39 | 0 | 39 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 22 | 22 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 267.25 | 275 | 589.2 | 549 | 421.7 | 381.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 36 | 36 | 35 | 35 | 35 | 35 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 60 | 163 | 163 | 0 | 0 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 81 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 169 | 168 | 165 | 165 | 165 | 165 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 220 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 388 | 390 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1251 | 1403 | 1565 | 1565 | 1305 | 1305
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 934 | 934 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 9.1 | 0 | 30 | 0 | 30 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1202 | 1234.2 | 1234.2 | 1234.2 | 1234 | 1234 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2183.1 | 2223.2 | 3479.2 | 3449.2 | 3174 | 3144
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 6 | 10 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1120 | 1120 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Station will be under shutdown for STG MI
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 200 | 201 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.22 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1666.22 | 1671 | 2172 | 2171 | 2120 | 2119
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 45 | 47 | 47 | 31 | 31 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 30 | 30 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 148 | 177 | 220 | 220 | 180 | 180 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is in Standby as per NLDC request.
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 | 30 | 30 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 96 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 102 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.23 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1218.92 | 1456.58 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 62.72 | 0 | 45 | 0 | 45 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 32 | 0 | 90 | 0 | 90 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 1878.87 | 2357.58 | 3167.37 | 3026.87 | 2853.58 | 2713.08
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 49 | 50 | 49 | 49 | 50 | 50 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 160 | 163 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 90 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.9 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 20 | 0 | 20 | 0 | 20 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 58 | 0 | 87.06 | 0 | 87.06 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 293.9 | 418 | 584.66 | 471 | 585.66 | 472
System Total |  |  |  |  | 28565.2 | 27084.055 | 11715.34 | 13873.78 | 22519.69 | 22218.37 | 17681.4 | 17431.33
Forecast Scenario (21-06-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13850 |  | 0 |  | 13850
|  |  |  | 1:00 | 13620 |  | 0 |  | 13620
|  |  |  | 2:00 | 13080 |  | 0 |  | 13080
|  |  |  | 3:00 | 12930 |  | 0 |  | 12930
|  |  |  | 4:00 | 12660 |  | 0 |  | 12660
|  |  |  | 5:00 | 12300 |  | 0 |  | 12300
|  |  |  | 6:00 | 11430 |  | 0 |  | 11430
|  |  |  | 7:00 | 11180 |  | 0 |  | 11180
|  |  |  | 8:00 | 11030 |  | 0 |  | 11030
|  |  |  | 9:00 | 10910 |  | 0 |  | 10910
|  |  |  | 10:00 | 11180 |  | 0 |  | 11180
|  |  |  | 11:00 | 11050 |  | 0 |  | 11050
|  |  |  | 12:00 | 11500 |  | 0 |  | 11500
|  |  |  | 13:00 | 11980 |  | 0 |  | 11980
|  |  |  | 14:00 | 12100 |  | 0 |  | 12100
|  |  |  | 15:00 | 12320 |  | 0 |  | 12320
|  |  |  | 16:00 | 12150 |  | 0 |  | 12150
|  |  |  | 17:00 | 11770 |  | 0 |  | 11770
|  |  |  | 18:00 | 10890 |  | 0 |  | 10890
|  |  |  | 18:30 | 11600 |  | 0 |  | 11600
|  |  |  | 19:00 | 12280 |  | 0 |  | 12280
|  |  |  | 19:30 | 12945 |  | 0 |  | 12945
|  |  |  | 20:00 | 13380 |  | 0 |  | 13380
|  |  |  | 21:00 | 13680 |  | 0 |  | 13680
|  |  |  | 22:00 | 13720 |  | 0 |  | 13720
|  |  |  | 23:00 | 13810 |  | 0 |  | 13810
Probable Maximum Temperature: |  |  | 31.10°C
Probable Maximum Demand at Day Peak: |  |  | 11500.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13680.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13680.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 294.80 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:33 hrs on 21-06-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 20-06-2025 | [28 empty] | Date: | 20-06-2025 | [28 empty] | Date: | 20-06-2025 | [28 empty] | Date: | 20-06-2025 | [28 empty] | Date: | 20-06-2025 | [12 empty] | Date: | 20-06-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [12 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 55 | 68 | 110 | 145 | 0 | 0 | 108 | 50 | 300 | 144 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 108 | 6.5 | 11 | 0 | 0 | 71 | 140 | 0 | 0 | 23 | 0 | 70 | 54.36 | 75 | 100 | 0 | 182 | 100 | 25 | 0 | 0 | 0 | 19 | 8 | 95 | 222 | 0 | 0 | 0 | 1149 | 0 | 51 | 138 | 0 | 0 | 0 | 300 | 5 | 215 | 10 | 38 | 0 | 171 | 29 | 20 | 113 | 34 | 52.2 | 0 | 45 | 310 | 320 | 344 | 36 | 0 | 0 | 8 | 0 | 81 | 30 | 0 | 0 | 169 | 35 | 82 | 167 | 0 | 0 | 0 | 12 | 6983.06 | 928 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 1128 | 17 | 1424.2 | 0 | 0 | 0 | 113 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 280 | 0 | 0 | 158 | 50 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 7 | 120 | 220 | 0 | 0 | 1244 | 72 | 6622.2 | 13605.26 | 98.15
01:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 55 | 67 | 110 | 30 | 0 | 0 | 108 | 50 | 300 | 144 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 108 | 6.5 | 11 | 0 | 0 | 80 | 130 | 0 | 0 | 22 | 0 | 70 | 17 | 75 | 100 | 0 | 182 | 99 | 25 | 0 | 0 | 0 | 19 | 8 | 95 | 224 | 0 | 0 | 0 | 1108 | 0 | 51 | 140 | 0 | 0 | 0 | 300 | 5 | 192 | 10 | 34 | 0 | 181 | 10 | 20 | 113 | 32 | 52.2 | 0 | 45 | 310 | 320 | 357 | 34 | 0 | 0 | 8 | 0 | 81 | 30 | 0 | 0 | 169 | 35 | 82 | 159 | 0 | 0 | 0 | 12 | 6762.7 | 928 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 1117 | 17 | 1423.89 | 0 | 0 | 0 | 113 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 0 | 0 | 280 | 0 | 0 | 160 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 8 | 120 | 220 | 0 | 0 | 1244 | 72 | 6552.89 | 13315.59 | 98.16
02:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 55 | 68 | 110 | 0 | 0 | 0 | 17 | 50 | 300 | 143 | 0 | 0 | 35 | 332 | 0 | 0 | 0 | 108 | 7 | 12 | 0 | 0 | 30 | 135 | 0 | 0 | 22 | 0 | 41 | 0 | 75 | 100 | 0 | 182 | 95 | 22 | 0 | 0 | 0 | 19 | 0 | 90 | 225 | 0 | 0 | 0 | 1140 | 0 | 51 | 143 | 0 | 0 | 0 | 300 | 5 | 196 | 10 | 34 | 0 | 175 | 9 | 20 | 113 | 32 | 52.2 | 0 | 45 | 305 | 320 | 380 | 34 | 0 | 0 | 8 | 0 | 81 | 30 | 0 | 0 | 169 | 35 | 83 | 159 | 0 | 0 | 0 | 12 | 6587.2 | 935 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 17 | 1410.66 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 280 | 0 | 0 | 160 | 49 | 110 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 10 | 120 | 220 | 0 | 0 | 1244 | 72 | 6334.66 | 12921.86 | 98.16
03:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 55 | 68 | 110 | 0 | 0 | 0 | 17 | 50 | 300 | 144 | 0 | 0 | 35 | 332 | 0 | 0 | 0 | 108 | 7 | 12 | 0 | 0 | 0 | 42 | 0 | 0 | 17 | 0 | 0 | 0 | 75 | 88 | 0 | 182 | 34 | 25 | 0 | 0 | 0 | 19 | 0 | 95 | 223 | 0 | 0 | 0 | 1138 | 0 | 51 | 143 | 0 | 0 | 0 | 300 | 5 | 195 | 10 | 34 | 0 | 163 | 9 | 20 | 113 | 30 | 52.2 | 0 | 46 | 310 | 320 | 372 | 34 | 0 | 0 | 8 | 0 | 78 | 30 | 0 | 0 | 169 | 35 | 83 | 150 | 0 | 0 | 0 | 12 | 6337.2 | 934 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1114 | 17 | 1415.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 280 | 0 | 0 | 165 | 49 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 10 | 120 | 220 | 0 | 0 | 1244 | 54 | 6111.79 | 12448.99 | 98.17
04:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 55 | 68 | 64 | 0 | 0 | 0 | 17 | 16 | 300 | 143 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 108 | 7 | 12 | 0 | 0 | 0 | 15 | 0 | 0 | 31 | 0 | 0 | 0 | 75 | 88 | 0 | 182 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 51 | 223 | 0 | 0 | 0 | 1143 | 0 | 51 | 20 | 0 | 0 | 0 | 300 | 5 | 200 | 10 | 36 | 0 | 163 | 9 | 20 | 113 | 30 | 52.2 | 0 | 46 | 310 | 320 | 374 | 34 | 0 | 0 | 8 | 0 | 81 | 30 | 0 | 0 | 169 | 35 | 92 | 159 | 0 | 0 | 0 | 12 | 6022.2 | 934 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1115 | 0 | 1425.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 280 | 0 | 0 | 166 | 49 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 10 | 120 | 220 | 0 | 0 | 1244 | 0 | 6008.7 | 12030.9 | 98.17
05:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 55 | 63 | 32 | 0 | 0 | 0 | 17 | 16 | 350 | 144 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 70 | 7 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 62 | 62 | 0 | 182 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 17 | 223 | 0 | 0 | 0 | 1115 | 0 | 51 | 0 | 0 | 0 | 0 | 300 | 5 | 189 | 10 | 35 | 0 | 163 | 9 | 20 | 113 | 30 | 52.2 | 0 | 16 | 305 | 320 | 357 | 34 | 0 | 0 | 8 | 0 | 81 | 30 | 0 | 0 | 169 | 17 | 92 | 105 | 0 | 0 | 0 | 12 | 5711.2 | 935 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1132 | 0 | 1306.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 320 | 0 | 0 | 166 | 49 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 6 | 120 | 220 | 0 | 0 | 1244 | 0 | 5905.89 | 11617.09 | 98.18
06:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 55 | 50 | 32 | 0 | 0 | 0 | 17 | 16 | 350 | 145 | 0 | 0 | 0 | 330 | 0 | 0 | 1 | 70 | 7.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 24 | 24 | 0 | 182 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1022 | 0 | 51 | 0 | 0 | 0 | 0 | 300 | 5 | 196 | 10 | 34 | 0 | 164 | 9 | 20 | 113 | 28 | 8 | 1 | 16 | 300 | 320 | 353 | 34 | 0 | 0 | 8 | 0 | 81 | 30 | 0 | 0 | 169 | 17 | 65 | 105 | 0 | 0 | 2.43 | 12 | 5434.93 | 935 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 1068 | 0 | 1206.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1.37 | 0 | 0 | 144 | 0 | 0 | 0 | 320 | 0 | 0.11 | 164 | 49 | 35 | 0 | 0 | 0 | 0 | 0.2 | 2 | 0.02 | 0 | 199 | 6 | 120 | 220 | 0 | 0 | 1120 | 0 | 5632.17 | 11067.1 | 98.18
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 55 | 43 | 16 | 0 | 0 | 0 | 17 | 16 | 350 | 147 | 0 | 0 | 0 | 330 | 0 | 0 | 1 | 35 | 8 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 75 | 88 | 1 | 182 | 0 | 25 | 0 | 0 | 0 | 5 | 0 | 0 | 223 | 0 | 0 | 0 | 1017 | 6 | 51 | 0 | 0 | 0 | 0 | 300 | 5 | 197 | 10 | 34 | 0 | 120 | 9 | 17 | 59 | 26 | 8 | 3 | 0 | 310 | 320 | 367 | 34 | 0 | 0 | 8 | 0 | 81 | 20 | 0 | 0 | 169 | 17 | 65 | 105 | 0 | 0 | 8.32 | 12 | 5377.32 | 933 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 8 | 971 | 0 | 1116.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 1.06 | 0 | 0 | 147 | 0 | 0 | 0 | 320 | 0 | 0.1 | 165 | 49 | 35 | 2 | 0 | 0 | 0 | 1 | 7 | 0.13 | 0 | 200 | 8 | 120 | 220 | 0 | 0 | 1090 | 0 | 5441.67 | 10818.99 | 98.19
08:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 55 | 20 | 16 | 0 | 0 | 0 | 17 | 16 | 350 | 146 | 0 | 0 | 0 | 331 | 0 | 0 | 4 | 17 | 8 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 48 | 88 | 2 | 182 | 0 | 10 | 0 | 0 | 0 | 24 | 0 | 0 | 223 | 0 | 0 | 0 | 1035 | 6 | 51 | 0 | 0 | 0 | 0 | 300 | 5 | 195 | 10 | 34 | 0 | 118 | 9 | 17 | 52 | 26 | 0 | 14 | 0 | 300 | 320 | 367 | 34 | 0 | 0 | 8 | 0 | 81 | 20 | 0 | 0 | 169 | 17 | 65 | 105 | 0 | 0 | 4.2 | 2 | 5315.2 | 934 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 19 | 938 | 0 | 1105.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 15.53 | 0 | 0 | 148 | 0 | 0 | 0 | 320 | 0 | 1.69 | 163 | 49 | 35 | 2 | 0 | 0 | 0 | 1.6 | 7 | 0.24 | 0 | 198 | 7 | 120 | 220 | 0 | 0 | 1120 | 0 | 5472.25 | 10787.45 | 98.19
09:00 | 0 | 17 | 2 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 300 | 141 | 0 | 0 | 0 | 310 | 0 | 0 | 5 | 0 | 8 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 48 | 62 | 3 | 182 | 0 | 20 | 0 | 0 | 0 | 20 | 0 | 0 | 222 | 0 | 0 | 0 | 1100 | 10 | 51 | 0 | 0 | 0 | 0 | 340 | 5 | 206 | 10 | 36 | 0 | 51 | 9 | 17 | 16 | 26 | 0 | 40 | 0 | 210 | 320 | 360 | 37 | 0 | 0 | 8 | 0 | 81 | 30 | 0 | 0 | 169 | 17 | 63 | 105 | 0 | 0 | 4.04 | 5 | 5095.04 | 934 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6 | 945 | 0 | 1175.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 10.15 | 0 | 0 | 148 | 0 | 0 | 0 | 414 | 0 | 0.78 | 166 | 49 | 0 | 10 | 0 | 0 | 0 | 3.5 | 59 | 0.47 | 0 | 202 | 7 | 120 | 220 | 0 | 0 | 1120 | 0 | 5637.97 | 10733.01 | 98.2
10:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 17 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 300 | 149 | 0 | 0 | 0 | 240 | 0 | 0 | 6 | 0 | 8 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 12 | 12 | 3 | 182 | 0 | 23 | 0 | 0 | 0 | 6 | 0 | 0 | 222 | 0 | 0 | 0 | 1186 | 7 | 51 | 0 | 0 | 0 | 0 | 340 | 5 | 213 | 10 | 51 | 0 | 17 | 9 | 17 | 17 | 24 | 0 | 42 | 0 | 160 | 320 | 369 | 36 | 0 | 0 | 8 | 0 | 80 | 30 | 0 | 0 | 169 | 17 | 63 | 105 | 0 | 1 | 6.82 | 6 | 5010.82 | 934 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6.91 | 992 | 0 | 1211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 25.03 | 0 | 0 | 148 | 0 | 0 | 0 | 414 | 0 | 1.86 | 164 | 49 | 0 | 8 | 0 | 0 | 0 | 3.6 | 12 | 0.23 | 0 | 205 | 7 | 120 | 220 | 0 | 0 | 1120 | 0 | 5702.63 | 10713.45 | 98.2
11:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 17 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 144 | 0 | 0 | 0 | 326 | 0 | 0 | 16 | 0 | 8 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 36 | 12 | 2 | 182 | 0 | 23 | 0 | 0 | 0 | 7 | 0 | 0 | 222 | 0 | 0 | 0 | 1156 | 6 | 51 | 0 | 0 | 0 | 0 | 340 | 5 | 203 | 10 | 51 | 0 | 17 | 10 | 17 | 27 | 28 | 7 | 72 | 0 | 160 | 320 | 390 | 36 | 0 | 0 | 8 | 0 | 80 | 30 | 0 | 0 | 169 | 17 | 63 | 105 | 0 | 1 | 14.24 | 6 | 5228.24 | 934 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 11.66 | 1132 | 0 | 1168.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 60.05 | 0 | 0 | 148 | 0 | 0 | 0 | 414 | 0 | 6.45 | 164 | 49 | 0 | 28 | 0 | 0 | 0 | 6.9 | 53 | 0.49 | 0 | 202 | 7 | 120 | 220 | 0 | 0 | 1120 | 0 | 5933.96 | 11162.2 | 98.21
12:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 17 | 18 | 32 | 0 | 0 | 0 | 28 | 0 | 420 | 142 | 0 | 0 | 0 | 323 | 0 | 0 | 30 | 0 | 8 | 14 | 0 | 0 | 0 | 13 | 0 | 0 | 46 | 0 | 0 | 0 | 80 | 75 | 2 | 182 | 0 | 23 | 0 | 0 | 0 | 19 | 0 | 1 | 221 | 0 | 0 | 0 | 1160 | 3 | 51 | 1 | 0 | 0 | 0 | 340 | 5 | 204 | 20 | 51 | 0 | 51 | 18 | 17 | 52 | 30 | 16 | 40 | 0 | 220 | 320 | 388 | 36 | 0 | 0 | 8 | 0 | 80 | 30 | 0 | 0 | 169 | 17 | 80 | 135 | 0 | 1 | 28.25 | 6 | 5693.25 | 934 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9.1 | 1202 | 0 | 1218.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 62.72 | 0 | 0 | 148 | 0 | 0 | 0 | 414 | 0 | 3.23 | 160 | 49 | 0 | 20 | 0 | 0 | 0 | 6.9 | 58 | 0.22 | 0 | 200 | 6 | 120 | 220 | 0 | 0 | 1120 | 0 | 6022.09 | 11715.34 | 98.21
13:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 54 | 23 | 34 | 32 | 0 | 0 | 0 | 61 | 0 | 420 | 135 | 0 | 0 | 0 | 327 | 0 | 0 | 21 | 17 | 8.5 | 14 | 0 | 0 | 0 | 42 | 0 | 0 | 18 | 0 | 0 | 0 | 88 | 100 | 1 | 182 | 19 | 23 | 0 | 0 | 0 | 32 | 0 | 27 | 222 | 0 | 0 | 0 | 1160 | 13 | 51 | 28 | 0 | 0 | 0 | 340 | 5 | 203 | 20 | 54 | 0 | 121 | 17 | 17 | 104 | 32 | 16 | 19 | 37 | 310 | 320 | 343 | 36 | 0 | 0 | 8 | 0 | 80 | 30 | 0 | 0 | 169 | 17 | 86 | 139 | 0 | 2 | 16.7 | 6 | 6156.2 | 934 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14.23 | 1210 | 0 | 1391.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 11.12 | 0 | 0 | 143 | 0 | 0 | 0 | 414 | 0 | 1.62 | 163 | 49 | 35 | 9 | 0 | 0 | 0 | 6.4 | 162 | 0.09 | 0 | 202 | 7 | 120 | 220 | 0 | 0 | 1120 | 0 | 6266.09 | 12422.29 | 98.22
14:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 51 | 17 | 24 | 16 | 0 | 0 | 0 | 54 | 0 | 350 | 150 | 0 | 0 | 0 | 333 | 0 | 0 | 5 | 17 | 11 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 10 | 0 | 0 | 0 | 48 | 75 | 1 | 182 | 30 | 30 | 0 | 0 | 0 | 19 | 0 | 45 | 219 | 0 | 0 | 0 | 1102 | 0 | 51 | 20 | 0 | 0 | 0 | 340 | 5 | 207 | 23 | 70 | 0 | 144 | 18 | 17 | 109 | 34 | 8 | 49 | 45 | 310 | 320 | 330 | 36 | 0 | 0 | 8 | 0 | 77 | 30 | 0 | 0 | 168 | 17 | 86 | 138 | 0 | 2 | 26.07 | 2 | 5899.07 | 934 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9.43 | 1090 | 0 | 1409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 29.42 | 0 | 0 | 145 | 0 | 0 | 0 | 300 | 0 | 2.85 | 160 | 49 | 0 | 13 | 0 | 0 | 0 | 3.7 | 129 | 0.13 | 0 | 173 | 7 | 120 | 220 | 0 | 0 | 1050 | 0 | 5918.53 | 11817.6 | 98.22
15:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 17 | 17 | 17 | 16 | 0 | 0 | 0 | 51 | 0 | 350 | 149 | 0 | 0 | 0 | 330 | 0 | 0 | 8 | 17 | 10 | 7 | 0 | 0 | 0 | 15 | 0 | 0 | 2 | 0 | 0 | 0 | 48 | 48 | 2 | 182 | 0 | 25 | 0 | 0 | 0 | 19 | 0 | 15 | 218 | 0 | 0 | 0 | 1108 | 0 | 43 | 10 | 16 | 0 | 0 | 340 | 6 | 208 | 21 | 70 | 0 | 148 | 9 | 17 | 105 | 30 | 8 | 23 | 44 | 320 | 320 | 390 | 36 | 0 | 0 | 8 | 0 | 74 | 30 | 0 | 0 | 167 | 17 | 87 | 136 | 0 | 0 | 24.94 | 8 | 5805.94 | 934 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7.21 | 1126 | 0 | 1307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 2.9 | 0 | 0 | 148 | 0 | 0 | 0 | 344 | 0 | 0.31 | 164 | 50 | 0 | 25 | 0 | 0 | 0 | 0.9 | 72 | 0.08 | 0 | 173 | 5 | 120 | 220 | 0 | 0 | 1050 | 0 | 5818.4 | 11624.34 | 98.23
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 17 | 17 | 17 | 16 | 0 | 0 | 0 | 17 | 0 | 350 | 141 | 0 | 0 | 0 | 333 | 0 | 0 | 2 | 17 | 10 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 1 | 182 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 15 | 218 | 0 | 0 | 0 | 1083 | 1 | 43 | 10 | 53 | 0 | 0 | 340 | 15 | 196 | 21 | 69 | 0 | 141 | 9 | 19 | 96 | 28 | 8 | 8 | 44 | 315 | 320 | 363 | 36 | 0 | 0 | 8 | 0 | 77 | 30 | 0 | 0 | 167 | 0 | 65 | 95 | 0 | 0 | 3.17 | 12 | 5454.17 | 934 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 17.97 | 1078 | 0 | 1307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0.41 | 0 | 0 | 149 | 0 | 0 | 0 | 350 | 0 | 0.02 | 165 | 50 | 0 | 16 | 0 | 0 | 0 | 1.7 | 49 | 0.09 | 0 | 170 | 5 | 120 | 220 | 0 | 0 | 1020 | 0 | 5700.19 | 11154.36 | 98.23
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 17 | 17 | 17 | 16 | 0 | 0 | 0 | 15 | 0 | 350 | 144 | 0 | 0 | 0 | 330 | 0 | 0 | 1 | 17 | 10 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 17 | 218 | 0 | 0 | 0 | 1025 | 0 | 51 | 10 | 53 | 0 | 0 | 340 | 15 | 201 | 23 | 69 | 0 | 100 | 9 | 19 | 67 | 24 | 8 | 3 | 44 | 310 | 320 | 390 | 36 | 0 | 0 | 8 | 0 | 77 | 30 | 0 | 0 | 167 | 0 | 65 | 95 | 0 | 0 | 0.23 | 12 | 5339.23 | 934 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 13.6 | 1001 | 0 | 1166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 1.68 | 0 | 0 | 153 | 0 | 0 | 0 | 350 | 0 | 0 | 166 | 49 | 0 | 3 | 0 | 0 | 0 | 2.8 | 19 | 0.1 | 0 | 173 | 5 | 120 | 220 | 0 | 0 | 1001 | 0 | 5422.18 | 10761.41 | 98.24
18:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 17 | 17 | 17 | 16 | 0 | 0 | 0 | 15 | 0 | 350 | 151 | 0 | 0 | 0 | 328 | 0 | 0 | 1 | 17 | 16 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 17 | 219 | 0 | 0 | 0 | 1035 | 0 | 51 | 10 | 63 | 0 | 0 | 340 | 15 | 211 | 24 | 69 | 0 | 98 | 20 | 19 | 71 | 28 | 8 | 1 | 45 | 310 | 320 | 390 | 36 | 0 | 0 | 8 | 0 | 81 | 30 | 0 | 0 | 168 | 0.72 | 65 | 95 | 0 | 0 | 0.58 | 12 | 5436.3 | 935 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5.37 | 1023 | 0 | 1209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71 | 0 | 0 | 161 | 0 | 0 | 0 | 350 | 0 | 0.08 | 164 | 49 | 0 | 1 | 0 | 0 | 0 | 0.4 | 7 | 0.04 | 0 | 179 | 7 | 120 | 220 | 0 | 0 | 990 | 0 | 5459.6 | 10895.9 | 98.24
19:00 | 0 | 40 | 24 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 26 | 21 | 20 | 64 | 15 | 0 | 10 | 100 | 30 | 400 | 147 | 0 | 0 | 17 | 290 | 0 | 0 | 0 | 70 | 17 | 7 | 0 | 0 | 0 | 45 | 0 | 0 | 9 | 65 | 40 | 0 | 50 | 56 | 0 | 182 | 20 | 30 | 0 | 0 | 0 | 4 | 0 | 27 | 219 | 0 | 0 | 0 | 1167 | 0 | 51 | 58 | 63 | 0 | 0 | 340 | 19 | 212 | 24 | 86 | 0 | 103 | 36 | 19 | 114 | 32 | 34 | 0 | 46 | 305 | 320 | 390 | 36 | 0 | 0 | 8 | 0 | 81 | 30 | 0 | 0 | 168 | 17 | 75 | 122 | 0 | 0 | 0 | 12 | 6398 | 934 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1040 | 14 | 1344 | 0 | 0 | 0 | 18 | 0 | 87 | 0 | 12 | 0 | 0 | 30 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 300 | 0 | 0 | 160 | 49 | 90 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 9 | 120 | 180 | 0 | 0 | 1020 | 0 | 5891 | 12289 | 98.25
19:30 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 52 | 35 | 50 | 80 | 15 | 0 | 17 | 135 | 32 | 450 | 145 | 0 | 0 | 17 | 330 | 0 | 0 | 0 | 70 | 13 | 13 | 0 | 0 | 0 | 45 | 0 | 0 | 10 | 65 | 55 | 0 | 60 | 100 | 0 | 182 | 30 | 34 | 0 | 0 | 0 | 18 | 0 | 48 | 221 | 0 | 0 | 0 | 1155 | 0 | 51 | 125 | 100 | 0 | 0 | 340 | 25 | 208 | 24 | 115 | 0 | 153 | 28 | 19 | 111 | 32 | 34 | 0 | 39 | 320 | 320 | 390 | 36 | 0 | 0 | 8 | 0 | 81 | 30 | 0 | 0 | 168 | 17 | 81 | 141 | 0 | 0 | 0 | 12 | 6951 | 934 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1188 | 17 | 1367 | 0 | 0 | 0 | 35 | 0 | 96 | 0 | 12 | 0 | 0 | 30 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 414 | 0 | 0 | 162 | 50 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 9 | 120 | 220 | 0 | 0 | 1120 | 0 | 6371 | 13322
20:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 51 | 35 | 51 | 80 | 15 | 0 | 17 | 125 | 32 | 450 | 148 | 0 | 0 | 17 | 331 | 0 | 0 | 0 | 70 | 13 | 14 | 0 | 0 | 0 | 43 | 0 | 0 | 12 | 65 | 77 | 0 | 60 | 100 | 0 | 182 | 51 | 34 | 0 | 0 | 0 | 19 | 0 | 51 | 221 | 0 | 0 | 0 | 1148 | 0 | 51 | 120 | 108 | 0 | 0 | 340 | 41 | 203 | 24 | 115 | 0 | 151 | 27 | 20 | 105 | 32 | 34 | 0 | 46 | 315 | 320 | 390 | 36 | 0 | 2.6 | 8 | 0 | 81 | 30 | 0 | 0 | 168 | 17 | 100 | 141 | 0 | 0 | 0 | 12 | 7020.6 | 934 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 1433 | 0 | 0 | 0 | 52 | 0 | 96 | 0 | 37 | 0 | 0 | 30 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 414 | 0 | 0 | 162 | 50 | 115 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 9 | 120 | 220 | 0 | 0 | 1101 | 0 | 6518.2 | 13538.8 | 98.25
21:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 50 | 35 | 51 | 80 | 15 | 0 | 17 | 139 | 33 | 450 | 148 | 0 | 0 | 17 | 330 | 0 | 0 | 0 | 70 | 13 | 14 | 0 | 0 | 0 | 45 | 0 | 0 | 6 | 65 | 79 | 0 | 60 | 100 | 0 | 182 | 50 | 34 | 0 | 0 | 0 | 19 | 0 | 86 | 221 | 0 | 0 | 0 | 1161 | 0 | 51 | 138 | 145 | 0 | 0 | 340 | 44 | 209 | 24 | 115 | 0 | 151 | 28 | 19 | 113 | 30 | 34 | 0 | 46 | 310 | 320 | 390 | 36 | 0 | 60 | 8 | 0 | 81 | 30 | 0 | 0 | 168 | 17 | 102 | 150 | 0 | 0 | 0 | 6 | 7204 | 934 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 1456.58 | 0 | 45 | 0 | 102 | 0 | 96 | 0 | 37 | 0 | 0 | 30 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 414 | 0 | 0 | 163 | 50 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 10 | 120 | 220 | 0 | 0 | 1120 | 0 | 6669.78 | 13873.78 | 98.26
22:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 51 | 35 | 51 | 95 | 15 | 0 | 17 | 144 | 39 | 450 | 180 | 0 | 0 | 17 | 329 | 0 | 0 | 0 | 70 | 18 | 14 | 0 | 65 | 0 | 45 | 0 | 0 | 10 | 61 | 79 | 0 | 85 | 100 | 0 | 182 | 48 | 32 | 0 | 0 | 0 | 19 | 0 | 99 | 221 | 0 | 0 | 0 | 1152 | 0 | 51 | 143 | 145 | 0 | 0 | 340 | 45 | 209 | 24 | 106 | 0 | 151 | 29 | 19 | 108 | 34 | 34 | 0 | 46 | 310 | 320 | 392 | 36 | 0 | 17 | 8 | 0 | 81 | 30 | 0 | 0 | 168 | 17 | 102 | 150 | 0 | 0 | 0 | 0 | 7324 | 934 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1220 | 17 | 1446.11 | 0 | 31 | 0 | 113 | 0 | 96 | 0 | 37 | 0 | 0 | 30 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 414 | 0 | 0 | 163 | 50 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 10 | 120 | 220 | 0 | 0 | 1120 | 0 | 6644.11 | 13968.11 | 98.26
23:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 51 | 35 | 51 | 95 | 15 | 0 | 17 | 145 | 50 | 450 | 302 | 0 | 0 | 17 | 329 | 0 | 0 | 0 | 70 | 18 | 14 | 0 | 68 | 0 | 48 | 0 | 0 | 3 | 65 | 79 | 0 | 85 | 100 | 0 | 182 | 51 | 32 | 0 | 0 | 0 | 19 | 0 | 105 | 220 | 0 | 0 | 0 | 1152 | 0 | 51 | 142 | 145 | 0 | 0 | 335 | 46 | 207 | 24 | 50 | 0 | 155 | 28 | 19 | 108 | 32 | 52.2 | 0 | 46 | 315 | 320 | 389 | 36 | 0 | 17 | 8 | 0 | 81 | 30 | 0 | 0 | 168 | 17 | 102 | 150 | 20 | 0 | 0 | 0 | 7450.2 | 935 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1205 | 17 | 1435.5 | 0 | 31 | 0 | 113 | 0 | 96 | 0 | 37 | 0 | 0 | 30 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 414 | 0 | 0 | 163 | 50 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 10 | 120 | 220 | 0 | 0 | 1140 | 0 | 6642.5 | 14092.7 | 98.27
Total KWH | 0 | 1023360 | 382560 | 0 | 0 | 0 | 0 | 0 | 8528400 | 0 | 0 | 421560 | 895680 | 935424 | 1235040 | 183665 | 0 | 96995 | 1284480 | 475200 | 8726000 | 3649222 | 0 | 0 | 223991 | 7836312 | 0 | 0 | 101178 | 1150800 | 256200 | 280080 | 0 | 167727.27 | 141764 | 757745 | 0 | 0 | 497280 | 331159 | 531984 | 52243 | 1312320 | 1627200 | 13203 | 4343560 | 584618 | 625440 | 0 | 0 | 0 | 356160 | 11140.2 | 988581 | 5255359 | 0 | 0 | 0 | 26749088 | 45090 | 1145256 | 1456945 | 853091 | 0 | 0 | 7914000 | 369600 | 4917000 | 409032 | 1385280 | 0 | 3141120 | 368760 | 423680 | 2085060 | 705600 | 610042 | 311755 | 733104 | 7028000 | 7709000 | 9341000 | 840000 | 0 | 114791 | 184008 | 0 | 1914240 | 713184 | 0 | 0 | 3927160 | 478440 | 1936800 | 3052800 | 16320 | 9050 | 162220 | 196320 | 146530466.47 | 22604364 | 0 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 92304 | 0 | 26421820 | 152640 | 31521191 | 0 | 125937 | 0 | 733728 | 0 | 702640 | 0 | 142769 | 0 | 276050 | 155336 | 192000 | 0 | 0 | 3874545 | 0 | 0 | 0 | 8614545 | 0 | 16860 | 3969000 | 1164218 | 1190507 | 115400 | 811104 | 0 | 0 | 38187.12 | 700560 | 0 | 480 | 4909000 | 184712 | 2888000 | 5458980 | 0 | 0 | 27565090.91 | 231600 | 145765568.03 | 292296034.5

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 20-06-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11715.34 | MW | 12:00 Hr. | Energy Generated |  |  | 292.296 |  | MKWHr.
| Day Peak Demand |  |  | 11756.1 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.221 |  | MKWHr.
| Evening Peak Generation |  |  | 13873.78 | MW | 21:00 Hr. | Energy Demand |  |  | 292.517 |  | MKWHr.
| Evening Peak Demand |  |  | 13873.78 | MW | 21:00 Hr. | Maximum Temperature |  |  | 32 |  | °C
| Minimum Generation of the Day |  |  | 10713.45 | MW | 10:00 Hr. | Total Gas Supplied |  |  | 808.98 |  | MMCFD
| Maximum Generation of the Day |  |  | 14092.7 | MW | 23:00 Hr. | Production Cost per KWHr |  |  | 6.683 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 29.4439 | 0 | 8.3088 | 0 | 0 | 0.10118 | 0 | 0 | 37.8539 | Gas | 104.1649 | Gas | 371947169.6959
| Chattogram Zone |  |  | 5.8808 | 26.7491 | 6.6949 | 0 | 4.3436 | 0.058293 | 0 | 0.49728 | 44.2239 | Coal | 90.7782 | Coal | 620706072.8405
| Cumilla Zone |  |  | 16.0317 | 0 | 9.7803 | 0 | 0 | 0.31176 | 0.7056 | 0 | 26.8293 | HFO | 34.7874 | HFO | 646860306.534
| Mymensingh Zone |  |  | 0.01632 | 0 | 5.6644 | 0 | 0 | 0.17127 | 0 | 0 | 5.852 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 31.7714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.7714 | Hydro | 4.3436 | Hydro | 434356
| Khulna Zone |  |  | 0 | 26.4218 | 0.24494 | 0 | 0 | 0 | 23.5164 | 0 | 50.1831 | Solar | 1.9816 | Solar | 31920346.5932
| Barishal Zone |  |  | 8.5317 | 32.4741 | 0.23208 | 0 | 0 | 0 | 0 | 0 | 41.2379 | Import | 55.7432 | Import | 274261348.26
| Rajshahi Zone |  |  | 12.4891 | 0 | 1.8604 | 0 | 0 | 0.48491 | 31.5212 | 0 | 46.3556 | Wind | 0.49728 | Wind | 7280179.2
| Rangpur Zone |  |  | 0 | 5.1332 | 2.0016 | 0 | 0 | 0.85415 | 0 | 0 | 7.989
| Total |  |  | 104.1649 | 90.7782 | 34.7874 | 0 | 4.3436 | 1.9816 | 55.7432 | 0.49728 | 292.296
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 371947169.6959 |  | Hydro | 434356
|  |  |  | Coal | 620706072.8405 |  | Solar | 31920346.5932
|  |  |  | HFO | 646860306.534 |  | Import | 274261348.26
|  |  |  | HSD | 0 |  | Wind | 7280179.2
[5 empty] | Total: | 195,34,09,779 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.6044 | Peak Hr Flow | 934.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 49822454.65 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 31.5212 | Peak Hr Flow | 1456.58 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 826 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.7056 | Peak Hr Flow | 30.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 960 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 54.8312 | Peak Hr Flow | 2420.58 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4577
|  |  |  | Chattogram |  | 0 |  | 1366
|  |  |  | Cumilla |  | 0 |  | 1327
|  |  |  | Mymensingh |  | 0 |  | 1122
|  |  |  | Sylhet |  | 0 |  | 603
|  |  |  | Khulna |  | 0 |  | 1672
|  |  |  | Barishal |  | 0 |  | 444
|  |  |  | Rajshahi |  | 0 |  | 1341
|  |  |  | Rangpur |  | 0 |  | 921
|  |  |  | Total |  | 0 |  | 13373
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[5 empty] | Total | 300 |  |  |  | Total | 476
|  |  |  | Total Unavailable Capacity |  |  |  | 776
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:26 | 12:45 | Satkhira 132/33kV S/S Transformer-1 (T-1) LT Scheduled S/D Due to Change T clamp
| 08:27 | 12:45 | Satkhira 132/33kV S/S Transformer-1 (T-1) HT Scheduled S/D Due to Change T clamp
| 08:40 | 12:45 | Chandpur 132/33kV S/S 412T HT Scheduled S/D Due to Maintenance work | [7 empty] | 12.5MW load
interrup.
| 08:40 | 11:40 | Chandpur 132/33kV S/S 422T LT Scheduled S/D Due to Maintenance work | [7 empty] | 12.5MW load
interrup.
| 09:03 | 10:05 | Chandraghona 132/33kV S/S TR-01(406T) LT Scheduled S/D Due to maintenance and | [7 empty] | 20.0MW load
|  |  | installation Of Rajastali feeder bus isolator by PDB | [7 empty] | interrup.
| 09:03 | 10:05 | Chandraghona 132/33kV S/S TR-01(406T) LT Scheduled S/D Due to maintenance and | [7 empty] | 20.0MW load
|  |  | installation Of Rajastali feeder bus isolator by PDB | [7 empty] | interrup.
| 09:04 | 10:05 | Chandraghona 132/33kV S/S TR-01(406T) HT Scheduled S/D Due to maintenance and | [7 empty] | 20.0MW load
|  |  | installation of Rajastali feeder bus isolator by PDB | [7 empty] | interrup.
| 09:33 | 12:50 | Magura 132/33kV S/S T-3 (425T) LT Scheduled S/D Due to 33kV Bay extension | [7 empty] | 20.0MW load
interrup.
| 09:34 | 12:46 | Magura 132/33kV S/S T-3 (425T) HT Scheduled S/D Due to 33kV Bay extension | [7 empty] | 20.0MW load
interrup.
| 09:36 | 14:57 | Sunamganj 132/33kV S/S Chhatak-Sunamgonj CKT-2 Scheduled S/D
| 09:38 | 15:21 | Bogura 230/132kV S/S T-01 HT Tripped showing General Trip, Diff L1,Diff L2,Diff L3,
relays Due to Auxilary Transformer Brust
| 09:38 | 15:22 | Bogura 230/132kV S/S T-01 LT Tripped showing No Relay show relays Due to Auxilary
Transformer Brust
|  | 10:04 | Jhenaidah 230/132kV S/S Transformer- 2 HT is restored.
| 10:06 | 14:55 | Mirpur 132/33kV S/S Main Bus Scheduled S/D Due to Earthing Boring for T3 Bay by G2G
project
|  | 10:10 | Jhenaidah 230/132kV S/S Transformer- 2 LT is restored.
| 10:44 | 12:12 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT Scheduled S/D Due to Oil
felling
| 10:44 | 12:14 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) LT Scheduled S/D Due to Oil
felling
| 10:55 | 11:15 | Khulna (S)-Satkhira 132kV Ckt-1 Tripped from Satkhira 132/33kV end showing Distance relay | [7 empty] | 17.5MW load
|  |  | relays. | [7 empty] | interrup. Satkhira
132/33kV end
| 10:55 | 11:17 | Khulna (S)-Satkhira 132kV Ckt-2 Tripped from Satkhira 132/33kV end showing Distance relay | [7 empty] | 17.5MW load
|  |  | relays. | [7 empty] | interrup. Satkhira
132/33kV end
| 12:00 |  | Day peak generation: 11714 MW
| 12:27 |  | The 400/230kV Transformer-2 was shut down at Bogura 400kV SS on an emergency basis (230kV
side was opened) with the consent of the respective protection department, due to a
malfunction (not showing data) of the B-phase CT on the 400kV side.
|  | 12:45 | Chandpur 132/33kV S/S 412T LT is restored.
|  | 12:46 | Chandpur 132/33kV S/S 200KVA Aux. T-2 LT is restored.
| 12:47 |  | Chandpur 132/33kV S/S 402T LT Forced S/D Due to No load condition
| 12:49 |  | Chandpur 132/33kV S/S 200KVA Aux. T-1 LT Forced S/D
|  | 14:10 | Baroaulia-Hathazari 132 kV Ckt-2 is restored.
|  | 14:10 | Baroaulia-Hathazari 132 kV Ckt-1 is restored.
| 15:14 | 16:59 | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to Due to mehendigonj 33 kv feeder Bus DS | [7 empty] | 20.0MW load
|  |  | repair maintenance. | [7 empty] | interrup.
| 15:15 | 16:57 | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to Due to mehendigonj 33 kv feeder Bus DS | [7 empty] | 20.0MW load
|  |  | repair maintenance. | [7 empty] | interrup.
| 16:58 | 19:51 | Naogaon 132/33kV S/S T-3 LT Tripped showing MCGG OC/EF (50). Inst. (t) relays Due to
Atrai 33KV PBS feeder BKR Y-phase Bus DS loop open.
| 18:40 | 19:49 | Naogaon 132/33kV S/S T-3 HT Forced S/D Due to Atrai 33KV PBS feeder BKR Y-phase Bus DS
loop maintenance
| 19:53 |  | Kushiara 163MW CCPP GT was sync.
| 21:00 |  | Peak generation 13873 MW
| 21:15 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- GT1
| 21:15 |  | Meghnaghat Summit 335 MW CCPP GT-1 was sync.
| 21:15 |  | Meghnaghat CCPP(Summit) GT-1 Synchronized with remarks:- GT1 synch as per NLDC demand
| 21:33 |  | Unique Meghnaghat Power Limited (UMPL) GT Synchronized with remarks:- GT Synchronized at
21:33 hrs.
| 21:33 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized with remarks:- GT
| 21:33 |  | Unique Meghnaghat Power 584 MW CCPP GT was sync.
| 00:27 |  | Bogura 400/230kV S/S ATR-02 LT Forced S/D Due to ATR-02 400 kV side CT( B Phase) Problem
| 00:42 |  | Unique Meghnaghat Power Limited (UMPL) ST Synchronized with remarks:- ST Synch at 00:42
hrs.
| 00:42 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized with remarks:- ST
| 00:42 |  | Unique Meghnaghat Power 584 MW CCPP ST was sync.
| 03:07 |  | Ashuganj (N) CCPP GT was synch.
| 05:22 | 07:43 | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to Auxillary Transformer-1 maintenance | [7 empty] | 29.0MW load
interrup.
| 05:23 | 07:43 | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to Auxillary Transformer-1 maintenance | [7 empty] | 29.0MW load
interrup.
| 05:57 |  | Kushiara 163MW CCPP ST was sync.
| 06:00 |  | Min. Generation 11547 MW.
| 07:33 |  | BSRM-Cumilla(N) 230 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end.
| 07:55 |  | Kulaura 132/33kV S/S TR-2 LT Project Work S/D Due to PDB Bay Extension Project Work | [7 empty] | 13.0MW load
interrup.
| 08:00 |  | Kulaura 132/33kV S/S TR-2 HT Project Work S/D Due to PDB Bay Extension Project Work | [7 empty] | 13.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 20-06-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 375 | 8528400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8726000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 148 | 3649222 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 7836312 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 50 | 421560 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 80 | 1235040 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 96995 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 223991 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 13 | 256200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 280080 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 24 | 382560 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 15 | 183665 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 51 | 935424 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1023360 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 33 | 475200 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 139 | 1284480 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 101178 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 895680 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 167727.27 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 70 | 1150800 | -
Dhaka Area Total |  |  |  |  | 5939.724 | 1931 | 37853874.27
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 11140.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 45090 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 356160 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 182 | 4343560 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 221 | 5255359 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 86 | 988581 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 79 | 531984 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 331159 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 60 | 1312320 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 34 | 625440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 13203 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 45 | 757745 | FGMO
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 52243 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 50 | 584618 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1627200 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 141764 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1161 | 26749088 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 6 | 497280 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 0 | 0 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4895.72 | 2108 | 44223934.2
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 209 | 4917000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 7914000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 24 | 409032 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 44 | 369600 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 145 | 853091 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1145256 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 138 | 1456945 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 46 | 733104 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 151 | 3141120 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 30 | 705600 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 34 | 610042 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 423680 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 113 | 2085060 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 368760 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1385280 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 311755 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1487 | 26829325
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 16320 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9050 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 150 | 3052800 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 102 | 1936800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 162220 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 196320 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 478440 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 275 | 5851950
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 36 | 840000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 60 | 114791 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 713184 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1914240 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 168 | 3927160 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 184008 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7028000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 390 | 9341000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7709000 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1403 | 31771383
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 934 | 22604364 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 152640 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 92304 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 0 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1234.2 | 26421820 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2223.2 | 50183128
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 480 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 10 | 184712 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2888000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1120 | 27565090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5458980 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 231600 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 201 | 4909000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 2236 | 1671 | 41237862.91
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 45 | 125937 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 142769 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 177 | 3874545 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Plant is in Standby as per NLDC request.
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8614545 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 155336 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 702640 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 102 | 733728 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 16860 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1456.58 | 31521191 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 192000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 276050 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2357.58 | 46355601
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1164218 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 163 | 3969000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 90 | 811104 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 38187.12 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1190507 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 115400 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 700560 | -
Rangpur Area Total |  |  |  |  | 950 | 418 | 7988976.12
Eastern Grid Total |  |  |  |  | 16705.895 | 7204 | 146530466.47
Western Grid Total |  |  |  |  | 10378.16 | 6669.78 | 145765568.03
National Grid Total |  |  |  |  | 27084.055 | 13873.78 | 292296034.5
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 20-06-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8995.64 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4378.1 | MW
i) Dhaka area |  |  | 4577.15 |  | MW | i) Khulna area |  |  |  | 1672 | MW
ii) Chattogram area |  |  | 1366 |  | MW | ii) Barishal area |  |  |  | 444.5 | MW
iii) Cumilla area |  |  | 1327.49 |  | MW | iii) Rajshahi area |  |  |  | 1340.6 | MW
iv) Mymensingh area |  |  | 1122 |  | MW | iv) Rangpur area |  |  |  | 921 | MW
v) Sylhet area |  |  | 603 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13373.74 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 69 | 20:00 | 133 | Patuakhali | 74.5 | 23:00
2 | AKSML | 119 | 14:00 | 68 | Jaldhaka | 82 | 23:00 | 134 | Payra | 32 | 23:00
3 | Aftabnagar | 37 | 21:00 | 69 | Jamalpur | 118 | 21:00 | 135 | Postogola | 51 | 13:00
4 | Agargaon | 115 | 13:00 | 70 | Jashore | 132 | 23:00 | 136 | Purbachal | 20 | 00:00
5 | Agrabad | 78 | 19:30 | 71 | Jhenaidah | 115 | 23:00 | 137 | Purbasadipur | 127 | 20:00
6 | Amnura | 35 | 21:00 | 72 | Joydebpur | 118 | 19:30 | 138 | Rahanpur | 29 | 22:00
7 | Ashuganj | 96 | 23:00 | 73 | Joypurhat | 55 | 21:00 | 139 | Rahim | 52 | 01:00
8 | BSRM | 204 | 12:00 | 74 | Juldah | 14.5 | 00:00 | 140 | Rajbari | 74 | 20:00
9 | Bagerhat | 80 | 19:30 | 75 | KSRM | 17 | 17:00 | 141 | Rajendrapur | 120 | 00:00
10 | Bajitpur | 58 | 20:00 | 76 | Kabirpur | 226 | 00:00 | 142 | Rajshahi | 102 | 21:00
11 | Bakulia | 78 | 20:00 | 77 | Kachua | 92 | 22:00 | 143 | Rajshahi-230 | 74 | 23:00
12 | Banani | 14 | 12:00 | 78 | Kallyanpur | 93 | 00:00 | 144 | Ramganj | 108 | 00:00
13 | Bangabhaban | 4 | 10:00 | 79 | Kalurghat | 28 | 00:00 | 145 | Rampur | 37 | 23:00
14 | Barapukuria | 59 | 21:00 | 80 | Kamrangirchar | 54 | 00:00 | 146 | Rangamati | 15 | 19:00
15 | Barguna | 26 | 20:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 139 | 21:00
16 | Barishal | 96 | 00:00 | 82 | Kasba | 36 | 21:00 | 148 | Ruppur | 6.2 | 10:00
17 | Barishal-230 | 106 | 19:30 | 83 | Kazla | 86 | 13:00 | 149 | SSM | 0 | 00:00
18 | Baroaulia | 54 | 22:00 | 84 | Keranigonj | 71 | 23:00 | 150 | Saidpur | 97 | 20:00
19 | Baroirhat | 56 | 19:30 | 85 | Khagrachori | 30 | 19:00 | 151 | Satkhira | 123 | 21:00
20 | Bashundhara | 148 | 12:00 | 86 | Khulna | 66 | 23:00 | 152 | Satmasjid | 87 | 19:30
21 | BashundharaCement | 1 | 00:00 | 87 | Khulshi | 161 | 21:00 | 153 | Savar | 178 | 00:00
22 | Beanibazar | 76 | 23:00 | 88 | Kishoreganj | 145 | 22:00 | 154 | SevenRings | 17.29 | 12:00
23 | Benapole | 66 | 21:00 | 89 | Kodda | 291 | 00:00 | 155 | ShahCement | 31 | 00:00
24 | Bhaluka | 125 | 19:30 | 90 | Kulaura | 50 | 23:00 | 156 | Shahjadpur | 74 | 21:00
25 | Bhandaria | 54 | 00:00 | 91 | Kurigram | 66 | 19:30 | 157 | Shahjibazar | 122 | 23:00
26 | Bhangura | 33 | 21:00 | 92 | Kushtia | 131 | 21:00 | 158 | Shahmirpur | 51 | 00:00
27 | Bheramara(GK) | 60 | 19:30 | 93 | Lalbag | 46 | 01:00 | 159 | Shariatpur | 88 | 22:00
28 | Bhulta | 242 | 00:00 | 94 | Lalmonirhat | 64 | 19:30 | 160 | Sherpur | 138 | 00:00
29 | Bog-Sherpur | 58 | 19:30 | 95 | MI_Cement | 13.2 | 13:00 | 161 | Shikalbaha | 7 | 00:00
30 | Bogura | 156 | 23:00 | 96 | Madanganj | 40 | 00:00 | 162 | Shitalakhya | 59.4 | 00:00
31 | Borhanuddin | 87 | 23:00 | 97 | Madaripur | 112 | 23:00 | 163 | Sholosohor | 36 | 00:00
32 | Brahmanbaria | 129 | 22:00 | 98 | Madartek | 82.08 | 13:00 | 164 | Shyampur | 140 | 12:00
33 | Cantonment | 136 | 12:00 | 99 | Madunaghat | 49 | 20:00 | 165 | Siddhirganj | 93 | 00:00
34 | Chandina | 14.4 | 22:00 | 100 | Magura | 62 | 21:00 | 166 | Sirajganj | 86 | 22:00
35 | Chandpur | 72 | 00:00 | 101 | Mahasthangarh | 72 | 22:00 | 167 | Sonargaon | 116 | 03:00
36 | Chandraghona | 34 | 19:30 | 102 | Manikganj | 120 | 22:00 | 168 | Sreemongol | 79 | 22:00
37 | Chapai | 67 | 19:30 | 103 | Maniknagar | 72 | 13:00 | 169 | Sreepur | 82 | 01:00
38 | Charsaidpur | 34 | 23:00 | 104 | Matarbari | 47 | 21:00 | 170 | Srinagar | 46.5 | 22:00
39 | Chauddagram | 66 | 23:00 | 105 | Matuail | 56 | 00:00 | 171 | Sunamganj | 62 | 21:00
40 | Chhatak | 35 | 01:00 | 106 | Millgate | 118 | 13:00 | 172 | Sylhet | 46 | 00:00
41 | Chowmuhani | 206 | 19:30 | 107 | Mirpur | 108 | 13:00 | 173 | Sylhet-132 | 113 | 22:00
42 | Chuadanga | 104 | 23:00 | 108 | Mirsorai | 9 | 19:00 | 174 | TK | 30 | 19:30
43 | Coxsbazar | 120 | 21:00 | 109 | Mirzapur | 40 | 20:00 | 175 | Tangail | 162 | 22:00
44 | Cumilla(N) | 150 | 00:00 | 110 | Mithapukur | 60 | 19:30 | 176 | Thakurgaon | 95 | 22:00
45 | Cumilla(S) | 147 | 00:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 121 | 00:00
46 | Daudkandi | 141 | 22:00 | 112 | Mogbazar | 113.1 | 12:00 | 178 | Ullahpara | 33 | 19:30
47 | Dhaka | 30 | 13:00 | 113 | Mongla | 37 | 05:00 | 179 | Ullon | 38 | 21:00
48 | Dhamrai | 136 | 00:00 | 114 | Motijheel | 31 | 12:00 | 180 | Uttara | 82 | 13:00
49 | Dhanmondi | 113 | 19:00 | 115 | Muktagacha | 33 | 23:00 | 181 | UttaraNew | 55 | 13:00
50 | Dohazari | 96 | 23:00 | 116 | Munshiganj | 110 | 00:00 | 182 | Zigatola | 68 | 12:00
51 | Faridpur | 158 | 22:00 | 117 | Muradnagar | 28 | 20:00
52 | Fatullah | 78 | 00:00 | 118 | Mymensingh | 190 | 00:00
53 | Fenchuganj | 41 | 19:30 | 119 | Naogaon | 125 | 21:00
54 | Feni | 108 | 22:00 | 120 | Narail | 58.5 | 23:00
55 | GPH | 90 | 15:00 | 121 | Narinda | 52 | 12:00
56 | Ghatail | 70 | 19:00 | 122 | Narshingdi | 173 | 21:00
57 | Ghorashal | 15 | 00:00 | 123 | Natore | 131 | 20:00
58 | Ghorashal-230 | 86 | 01:00 | 124 | Nawabganj | 56.6 | 23:00
59 | Goalpara | 36 | 00:00 | 125 | Netrakona | 132 | 19:30
60 | Gollamari | 86 | 00:00 | 126 | New | 69 | 00:00
61 | Gopalganj | 108 | 22:00 | 127 | Niamatpur | 66 | 22:00
62 | Gulshan | 102 | 12:00 | 128 | Noapara | 44 | 23:00
63 | Halishahar | 37 | 15:00 | 129 | PHP | 9 | 07:00
64 | HaripurSBU | 154 | 00:00 | 130 | Pabna | 106 | 20:00
65 | Hasnabad | 66 | 00:00 | 131 | Palashbari | 100 | 21:00
66 | Hathazari | 75 | 22:00 | 132 | Panchagarh | 57 | 23:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 20-06-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13605.26 | 0 |  | 13605.26
1:00 | 13315.59 | 0 |  | 13315.59
2:00 | 12921.86 | 0 |  | 12921.86
3:00 | 12448.99 | 0 |  | 12448.99
4:00 | 12030.9 | 0 |  | 12030.9
5:00 | 11617.09 | 0 |  | 11617.09
6:00 | 11067.1 | 0 |  | 11067.1
7:00 | 10818.99 | 0 |  | 10818.99
8:00 | 10787.45 | 38 |  | 10827.45
9:00 | 10733.01 | 47 |  | 10782.01
10:00 | 10713.45 | 29 |  | 10743.45
11:00 | 11162.2 | 68 |  | 11233.2
12:00 | 11715.34 | 39 |  | 11756.1
13:00 | 12422.29 | 0 |  | 12422.29
14:00 | 11817.6 | 0 |  | 11817.6
15:00 | 11624.34 | 0 |  | 11624.34
16:00 | 11154.36 | 0 |  | 11154.36
17:00 | 10761.41 | 0 |  | 10761.41
18:00 | 10895.9 | 0 |  | 10895.9
19:00 | 12289 | 0 |  | 12289
19:30 | 13322 | 0 |  | 13322
20:00 | 13538.8 | 0 |  | 13538.8
21:00 | 13873.78 | 0 |  | 13873.78
22:00 | 13968.11 | 0 |  | 13968.11
23:00 | 14092.7 | 0 |  | 14092.7
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 20-06-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6983.06 | 6622.2 | 13605.26 | DAILY GENERATION CURVE
00:30 | 6872.88 | 6587.545 | 13460.425
01:00 | 6762.7 | 6552.89 | 13315.59 | 20-06-2025
01:30 | 6674.95 | 6443.775 | 13118.725
02:00 | 6587.2 | 6334.66 | 12921.86
02:30 | 6462.2 | 6223.225 | 12685.425
03:00 | 6337.2 | 6111.79 | 12448.99
03:30 | 6179.7 | 6060.245 | 12239.945
04:00 | 6022.2 | 6008.7 | 12030.9
04:30 | 5866.7 | 5957.295 | 11823.995
05:00 | 5711.2 | 5905.89 | 11617.09
05:30 | 5573.065 | 5769.03 | 11342.095
06:00 | 5434.93 | 5632.17 | 11067.1
06:30 | 5406.125 | 5536.92 | 10943.045
07:00 | 5377.32 | 5441.67 | 10818.99
07:30 | 5346.26 | 5456.96 | 10803.22
08:00 | 5315.2 | 5472.25 | 10787.45
08:30 | 5205.12 | 5555.11 | 10760.23
09:00 | 5095.04 | 5637.97 | 10733.01
09:30 | 5052.93 | 5670.3 | 10723.23
10:00 | 5010.82 | 5702.63 | 10713.45
10:30 | 5119.53 | 5818.295 | 10937.825
11:00 | 5228.24 | 5933.96 | 11162.2
11:30 | 5460.745 | 5978.025 | 11438.77
12:00 | 5693.25 | 6022.09 | 11715.34
12:30 | 5924.725 | 6144.09 | 12068.815
13:00 | 6156.2 | 6266.09 | 12422.29
13:30 | 6027.635 | 6092.31 | 12119.945
14:00 | 5899.07 | 5918.53 | 11817.6
14:30 | 5852.505 | 5868.465 | 11720.97
15:00 | 5805.94 | 5818.4 | 11624.34
15:30 | 5630.055 | 5759.295 | 11389.35
16:00 | 5454.17 | 5700.19 | 11154.36
16:30 | 5396.7 | 5561.185 | 10957.885
17:00 | 5339.23 | 5422.18 | 10761.41
17:30 | 5387.765 | 5440.89 | 10828.655
18:00 | 5436.3 | 5459.6 | 10895.9
18:30 | 5917.15 | 5675.3 | 11592.45
19:00 | 6398 | 5891 | 12289
19:30 | 6951 | 6371 | 13322
20:00 | 7020.6 | 6518.2 | 13538.8
20:30 | 7112.3 | 6593.99 | 13706.29 |  | Executive Engineer
21:00 | 7204 | 6669.78 | 13873.78 |  | Network Operation Division
21:30 | 7264 | 6656.945 | 13920.945
22:00 | 7324 | 6644.11 | 13968.11
22:30 | 7387.1 | 6643.305 | 14030.405
23:00 | 7450.2 | 6642.5 | 14092.7

## En-Curve
QF-LDC-12
Date | 20-06-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2787 | 1188.5 | 928 | 38 | 34 | 1424.2 | 182 | 4010 | 0 | 650 | 2340.56 | 0 | 0 | 23 | 0 | DAILY ENERGY CURVE
00:30 | 2800.5 | 1189 | 928 | 38 | 33 | 1424.045 | 182 | 3981 | 0 | 591.5 | 2270.88 | 0 | 0 | 22.5 | 0 | 20-06-2025
01:00 | 2814 | 1189.5 | 928 | 38 | 32 | 1423.89 | 182 | 3952 | 0 | 533 | 2201.2 | 0 | 0 | 22 | 0
01:30 | 2831 | 1186.75 | 931.5 | 38 | 32 | 1417.275 | 182 | 3959.5 | 0 | 485.5 | 2033.2 | 0 | 0 | 22 | 0 | Energy Generated | 292.296 |  | MKWHr
02:00 | 2848 | 1184 | 935 | 38 | 32 | 1410.66 | 182 | 3967 | 0 | 438 | 1865.2 | 0 | 0 | 22 | 0 | Energy not Served | 0.221 |  | MKWHr
02:30 | 2852 | 1187 | 934.5 | 38 | 31 | 1413.225 | 182 | 3937.5 | 0 | 376.5 | 1714.2 | 0 | 0 | 19.5 | 0 | Total Energy Requirement | 292.517 |  | MKWHr
03:00 | 2856 | 1190 | 934 | 38 | 30 | 1415.79 | 182 | 3908 | 0 | 315 | 1563.2 | 0 | 0 | 17 | 0
03:30 | 2861 | 1191 | 934 | 38 | 30 | 1420.745 | 182 | 3913 | 0 | 292 | 1354.2 | 0 | 0 | 24 | 0
04:00 | 2866 | 1192 | 934 | 38 | 30 | 1425.7 | 182 | 3918 | 0 | 269 | 1145.2 | 0 | 0 | 31 | 0
04:30 | 2875 | 1213.5 | 934.5 | 38 | 30 | 1366.295 | 182 | 3909 | 0 | 215 | 1035.2 | 0 | 0 | 25.5 | 0
05:00 | 2884 | 1235 | 935 | 38 | 30 | 1306.89 | 182 | 3900 | 0 | 161 | 925.2 | 0 | 0 | 20 | 0
05:30 | 2873.5 | 1233.75 | 935 | 38 | 29 | 1256.68 | 182 | 3761 | 6.065 | 161 | 836.6 | 0 | 0 | 29.5 | 0
06:00 | 2863 | 1232.5 | 935 | 38 | 28 | 1206.47 | 182 | 3622 | 12.13 | 161 | 748 | 0 | 0 | 39 | 0
06:30 | 2868 | 1238.25 | 934 | 38 | 27 | 1161.425 | 182 | 3557 | 30.37 | 118.5 | 755.5 | 0 | 0 | 33 | 0
07:00 | 2873 | 1244 | 933 | 38 | 26 | 1116.38 | 182 | 3492 | 48.61 | 76 | 763 | 0 | 0 | 27 | 0
07:30 | 2878.5 | 1230.5 | 933.5 | 38 | 26 | 1110.785 | 182 | 3497.5 | 77.935 | 63 | 734 | 0 | 0 | 31.5 | 19
08:00 | 2884 | 1217 | 934 | 38 | 26 | 1105.19 | 182 | 3503 | 107.26 | 50 | 705 | 0 | 0 | 36 | 38
08:30 | 2952.5 | 1149.5 | 934 | 38 | 26 | 1140.13 | 182 | 3542.5 | 134.6 | 42.5 | 585 | 0 | 0 | 33.5 | 42.5
09:00 | 3021 | 1082 | 934 | 38 | 26 | 1175.07 | 182 | 3582 | 161.94 | 35 | 465 | 0 | 0 | 31 | 47
09:30 | 3005 | 1062 | 934 | 38 | 25 | 1193.035 | 182 | 3649 | 154.195 | 38 | 406.5 | 0 | 0 | 36.5 | 38
10:00 | 2989 | 1042 | 934 | 38 | 24 | 1211 | 182 | 3716 | 146.45 | 41 | 348 | 0 | 0 | 42 | 29
10:30 | 3047.5 | 1064.5 | 934 | 38 | 26 | 1189.705 | 182 | 3769.5 | 237.62 | 41 | 369.5 | 0 | 0 | 38.5 | 48.5
11:00 | 3106 | 1087 | 934 | 38 | 28 | 1168.41 | 182 | 3823 | 328.79 | 41 | 391 | 0 | 0 | 35 | 68
11:30 | 3109.5 | 1150.5 | 934 | 38 | 29 | 1193.665 | 182 | 3857 | 312.605 | 57.5 | 534.5 | 0 | 0 | 40.5 | 53.5
12:00 | 3113 | 1214 | 934 | 38 | 30 | 1218.92 | 182 | 3891 | 296.42 | 74 | 678 | 0 | 0 | 46 | 39
12:30 | 3090.5 | 1256.25 | 934 | 38 | 31 | 1305.275 | 182 | 3897.5 | 294.29 | 117.5 | 890.5 | 0 | 0 | 32 | 19.5
13:00 | 3068 | 1298.5 | 934 | 38 | 32 | 1391.63 | 182 | 3904 | 292.16 | 161 | 1103 | 0 | 0 | 18 | 0
13:30 | 2984.5 | 1267.25 | 934 | 38 | 33 | 1400.315 | 182 | 3764 | 299.38 | 157 | 1046.5 | 0 | 0 | 14 | 0
14:00 | 2901 | 1236 | 934 | 38 | 34 | 1409 | 182 | 3624 | 306.6 | 153 | 990 | 0 | 0 | 10 | 0
14:30 | 2958.5 | 1243 | 934 | 38 | 32 | 1358 | 182 | 3647.5 | 251.97 | 152.5 | 917.5 | 0 | 0 | 6 | 0
15:00 | 3016 | 1250 | 934 | 38 | 30 | 1307 | 182 | 3671 | 197.34 | 152 | 845 | 0 | 0 | 2 | 0
15:30 | 2992 | 1269 | 934 | 38 | 29 | 1307 | 182 | 3618.5 | 153.35 | 127 | 716.5 | 0 | 0 | 23 | 0
16:00 | 2968 | 1288 | 934 | 38 | 28 | 1307 | 182 | 3566 | 109.36 | 102 | 588 | 0 | 0 | 44 | 0
16:30 | 2988 | 1293.5 | 934 | 38 | 26 | 1236.5 | 182 | 3490.5 | 79.885 | 102 | 553 | 0 | 0 | 34.5 | 0
17:00 | 3008 | 1299 | 934 | 38 | 24 | 1166 | 182 | 3415 | 50.41 | 102 | 518 | 0 | 0 | 25 | 0
17:30 | 3035.5 | 1313.5 | 934.5 | 38 | 26 | 1187.5 | 182 | 3427.5 | 33.795 | 102.5 | 524.86 | 0 | 0 | 23 | 0
18:00 | 3063 | 1328 | 935 | 38 | 28 | 1209 | 182 | 3440 | 17.18 | 103 | 531.72 | 0 | 0 | 21 | 0
18:30 | 3029 | 1332 | 934.5 | 38 | 30 | 1276.5 | 182 | 3545.5 | 8.59 | 290.5 | 910.86 | 0 | 0 | 15 | 0
19:00 | 2995 | 1336 | 934 | 38 | 32 | 1344 | 182 | 3651 | 0 | 478 | 1290 | 0 | 0 | 9 | 0
19:30 | 3145 | 1488 | 934 | 38 | 32 | 1367 | 182 | 3877 | 0 | 541 | 1708 | 0 | 0 | 10 | 0
20:00 | 3149 | 1514.6 | 934 | 38 | 32 | 1433 | 182 | 3896.2 | 0 | 595 | 1753 | 0 | 0 | 12 | 0
20:30 | 3151.5 | 1560.8 | 934 | 38 | 31 | 1444.79 | 182 | 3912.7 | 0 | 618.5 | 1824 | 0 | 0 | 9 | 0
21:00 | 3154 | 1607 | 934 | 38 | 30 | 1456.58 | 182 | 3929.2 | 0 | 642 | 1895 | 0 | 0 | 6 | 0
21:30 | 3154.5 | 1636 | 934 | 38 | 32 | 1451.345 | 182 | 3918.1 | 0 | 649.5 | 1917.5 | 0 | 0 | 8 | 0
22:00 | 3155 | 1665 | 934 | 38 | 34 | 1446.11 | 182 | 3907 | 0 | 657 | 1940 | 0 | 0 | 10 | 0
22:30 | 3162.5 | 1730.5 | 934.5 | 38 | 33 | 1440.805 | 182 | 3909.5 | 0 | 659 | 1934.1 | 0 | 0 | 6.5 | 0
23:00 | 3170 | 1796 | 935 | 38 | 32 | 1435.5 | 182 | 3912 | 0 | 661 | 1928.2 | 0 | 0 | 3 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 20-06-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 382 | 18:00 | 373 | 10:00 | Payra | 413 | 08:00 | 408 | 22:00
Ashuganj | 388 | 18:30 | 364 | 12:00 | Rahanpur | 400 | 08:00 | 387 | 22:00
Bhulta | 387 | 07:00 | 368 | 12:00 | Rampal | 402 | 07:00 | 391 | 02:00
Bibiana | 386 | 06:00 | 380 | 02:00
BIPTC | 403 | 05:00 | 393 | 20:00
Bogura | 388 | 07:00 | 374 | 21:00
Gopalganj | 396 | 07:00 | 387 | 00:00
Kaliakoir | 374 | 07:00 | 363 | 11:00
Madunaghat | 392 | 00:00 | 386 | 11:00
Meghnaghat | 383 | 18:30 | 374 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 224 | 07:00 | 216 | 11:00 | Keranigonj | 222 | 07:00 | 214 | 12:00
AKSML | 228 | 00:00 | 223 | 10:00 | Khulna(S) | 232 | 10:00 | 221 | 21:00
Aminbazar | 225 | 18:00 | 219 | 02:00 | Madunaghat | 231 | 00:00 | 225 | 10:00
Ashuganj | 228 | 18:00 | 218 | 12:00 | Madunaghat-400 | 233 | 00:00 | 226 | 11:00
Ashuganj-400 | 228 | 18:00 | 218 | 12:00 | Maniknagar | 219 | 07:00 | 213 | 00:00
Baghabari | 235 | 16:00 | 225 | 00:00 | Meghnaghat | 228 | 06:00 | 221 | 00:00
Barapukuria | 226 | 18:30 | 220 | 04:00 | Meghnaghat-400 | 224 | 18:30 | 217 | 10:00
Barapukuria-230 | 226 | 18:30 | 220 | 04:00 | Mirsorai | 226 | 07:00 | 219 | 12:00
Barishal | 234 | 07:00 | 227 | 22:00 | Rajshahi | 235 | 18:30 | 223 | 22:00
Bheramara | 234 | 17:00 | 222 | 21:00 | Rampal | 231 | 07:00 | 220 | 23:00
Bhulta | 228 | 07:00 | 214 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 228 | 07:00 | 221 | 00:00 | Rampura | 226 | 07:00 | 213 | 12:00
BIPTC | 237 | 17:00 | 221 | 22:00 | Shikalbaha | 232 | 01:00 | 224 | 10:00
Bogura | 236 | 18:30 | 227 | 13:00 | Shyampur | 222 | 07:00 | 215 | 11:00
Bogura-400 | 236 | 07:00 | 225 | 22:00 | Siddhirganj | 222 | 06:00 | 215 | 10:00
Borhanuddin | 239 | 07:00 | 233 | 22:00 | Sirajgonj | 239 | 07:00 | 233 | 00:00
BSRM | 225 | 07:00 | 218 | 12:00 | Sreepur | 226 | 08:00 | 218 | 12:00
Cumilla(N) | 222 | 06:00 | 215 | 12:00 | Tongi | 224 | 17:00 | 216 | 13:00
Faridpur | 232 | 06:00 | 224 | 22:00
Fenchuganj | 225 | 09:00 | 217 | 01:00
Ghorashal | 230 | 00:00 | 225 | 13:00
Ghorashal-230 | 225 | 07:00 | 216 | 12:00
Gopalganj | 234 | 07:00 | 221 | 15:00
GPH | 228 | 07:00 | 223 | 04:00
Haripur | 221 | 18:30 | 215 | 00:00
Hasnabad | 222 | 18:00 | 215 | 11:00
Hathazari | 231 | 00:00 | 219 | 03:00
Ishurdi | 236 | 17:00 | 224 | 21:00
Jhenaidah | 233 | 17:00 | 217 | 22:00
Kaliakoir | 233 | 01:00 | 221 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 131 | 07:00 | 124 | 11:00 | Madartek | 131 | 06:00 | 123 | 12:00
Agargaon | 132 | 06:00 | 126 | 11:00 | Madunaghat | 131 | 00:00 | 127 | 10:00
Agrabad | 133 | 07:00 | 127 | 10:00 | Magura | 136 | 17:00 | 123 | 22:00
AKS | 130 | 00:00 | 125 | 11:00 | Mahasthangarh | 137 | 18:30 | 130 | 22:00
Aminbazar | 133 | 18:00 | 126 | 11:00 | Manikganj | 130 | 14:00 | 121 | 21:00
Amnura | 139 | 18:30 | 124 | 01:00 | Maniknagar | 131 | 06:00 | 127 | 12:00
Ashuganj | 135 | 03:00 | 132 | 12:00 | Matarbari | 127 | 09:00 | 117 | 19:30
Bagerhat | 135 | 17:00 | 124 | 02:00 | Matuail | 128 | 08:00 | 124 | 00:00
Bajitpur | 131 | 16:00 | 123 | 00:00 | Millgate | 133 | 06:00 | 126 | 12:00
Bakulia | 133 | 01:00 | 129 | 10:00 | Mirpur | 131 | 06:00 | 124 | 11:00
Banani | 133 | 07:00 | 123 | 12:00 | Mirzapur | 130 | 15:00 | 123 | 21:00
Bangabhaban | 131 | 18:00 | 127 | 11:00 | Mithapukur | 133 | 06:00 | 125 | 21:00
Barapukuria | 139 | 18:30 | 130 | 09:00 | MI_Cement | 128 | 17:00 | 124 | 00:00
Barguna | 137 | 17:00 | 130 | 22:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 137 | 17:00 | 130 | 23:00 | Mogbazar | 132 | 07:00 | 123 | 15:00
Barishal-230 | 137 | 16:00 | 131 | 23:00 | Mongla | 135 | 17:00 | 125 | 22:00
Baroaulia | 132 | 00:00 | 132 | 00:00 | Motijheel | 131 | 18:00 | 127 | 11:00
Baroirhat | 125 | 06:00 | 117 | 10:00 | Muktagacha | 134 | 15:00 | 122 | 19:30
Bashundhara | 132 | 05:00 | 124 | 12:00 | Munshiganj | 128 | 18:30 | 123 | 00:00
BashundharaCement | 128 | 18:30 | 123 | 11:00 | Muradnagar | 125 | 07:00 | 120 | 00:00
Beanibazar | 127 | 07:00 | 122 | 23:00 | Mymensingh | 134 | 12:00 | 120 | 05:00
Benapole | 133 | 17:00 | 122 | 22:00 | Naogaon | 136 | 17:00 | 128 | 13:00
Bhaluka | 130 | 05:00 | 123 | 13:00 | Narail | 135 | 06:00 | 122 | 23:00
Bhandaria | 134 | 16:00 | 124 | 22:00 | Narinda | 130 | 14:00 | 121 | 21:00
Bhangura | 134 | 06:00 | 129 | 20:00 | Narshingdi | 133 | 06:00 | 119 | 13:00
Bheramara | 136 | 17:00 | 128 | 21:00 | Natore | 136 | 18:30 | 128 | 21:00
Bheramara(GK) | 136 | 17:00 | 128 | 21:00 | Nawabganj | 128 | 06:00 | 123 | 00:00
Bhulta | 124 | 13:00 | 119 | 00:00 | Netrakona | 129 | 16:00 | 113 | 00:00
Bog-Sherpur | 137 | 06:00 | 131 | 21:00 | New | 133 | 06:00 | 127 | 12:00
Bogura | 140 | 17:00 | 134 | 21:00 | Niamatpur | 135 | 06:00 | 129 | 22:00
Bogura-230 | 140 | 18:30 | 134 | 02:00 | Noapara | 137 | 17:00 | 126 | 22:00
Brahmanbaria | 131 | 08:00 | 124 | 00:00 | Pabna | 135 | 17:00 | 127 | 21:00
Cantonment | 131 | 05:00 | 126 | 11:00 | Palashbari | 132 | 06:00 | 125 | 21:00
Chandina | 127 | 06:00 | 121 | 12:00 | Panchagarh | 139 | 18:30 | 123 | 10:00
Chandpur | 127 | 19:00 | 115 | 10:00 | Patuakhali | 136 | 00:00 | 130 | 22:00
Chandraghona | 132 | 01:00 | 129 | 11:00 | Payra | 136 | 18:30 | 134 | 04:00
Chapai | 132 | 06:00 | 127 | 20:00 | PHP | 123 | 07:00 | 116 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 18:30 | 124 | 00:00 | Postogola | 131 | 18:30 | 126 | 00:00
Chauddagram | 123 | 06:00 | 115 | 10:00 | Purbachal | 132 | 07:00 | 123 | 12:00
Chhatak | 127 | 18:00 | 119 | 00:00 | Purbasadipur | 135 | 18:30 | 121 | 09:00
Chowmuhani | 120 | 06:00 | 108 | 23:00 | Rahanpur | 137 | 07:00 | 131 | 22:00
Chuadanga | 136 | 17:00 | 120 | 22:00 | Rahanpur-400 | 137 | 17:00 | 132 | 20:00
Coxsbazar | 125 | 13:00 | 117 | 01:00 | Rahim | 129 | 19:00 | 125 | 00:00
Cumilla(N) | 135 | 04:00 | 122 | 00:00 | Rajbari | 136 | 06:00 | 130 | 23:00
Cumilla(S) | 133 | 04:00 | 119 | 10:00 | Rajendrapur | 132 | 20:00 | 122 | 17:00
Daudkandi | 125 | 16:00 | 116 | 19:00 | Rajshahi | 136 | 08:00 | 129 | 22:00
Dhaka | 132 | 05:00 | 125 | 12:00 | Rajshahi-230 | 136 | 18:30 | 121 | 21:00
Dhamrai | 130 | 07:00 | 124 | 11:00 | Ramganj | 120 | 15:00 | 110 | 10:00
Dhanmondi | 132 | 07:00 | 125 | 12:00 | Rampur | 132 | 08:00 | 127 | 10:00
Dohazari | 130 | 07:00 | 125 | 11:00 | Rampura | 132 | 07:00 | 123 | 12:00
Faridpur | 137 | 07:00 | 133 | 13:00 | Rangamati | 131 | 00:00 | 128 | 11:00
Fatullah | 129 | 18:30 | 124 | 00:00 | Rangpur | 134 | 10:00 | 126 | 05:00
Fenchuganj | 134 | 09:00 | 129 | 02:00 | Ruppur | 137 | 07:00 | 129 | 22:00
Feni | 124 | 06:00 | 116 | 10:00 | Saidpur | 134 | 18:30 | 125 | 09:00
Ghatail | 131 | 15:00 | 119 | 22:00 | Satkhira | 137 | 09:00 | 123 | 23:00
Ghorashal | 134 | 04:00 | 129 | 11:00 | Satmasjid | 131 | 06:00 | 125 | 12:00
Goalpara | 139 | 18:00 | 129 | 02:00 | Savar | 131 | 06:00 | 124 | 10:00
Gollamari | 139 | 17:00 | 130 | 02:00 | SevenRings | 135 | 07:00 | 128 | 11:00
Gopalganj | 136 | 09:00 | 129 | 21:00 | ShahCement | 129 | 18:30 | 124 | 00:00
Gopalganj-400 | 137 | 07:00 | 133 | 02:00 | Shahjadpur | 138 | 05:00 | 132 | 21:00
Gulshan | 131 | 06:00 | 123 | 12:00 | Shahjibazar | 131 | 08:00 | 124 | 00:00
Halishahar | 134 | 00:00 | 128 | 11:00 | Shahmirpur | 134 | 13:00 | 130 | 17:00
Haripur | 129 | 18:30 | 124 | 00:00 | Shariatpur | 136 | 17:00 | 129 | 23:00
HaripurSBU | 129 | 18:30 | 125 | 00:00 | Sherpur | 136 | 03:00 | 125 | 22:00
Hasnabad | 131 | 01:00 | 125 | 12:00 | Shikalbaha | 124 | 00:00 | 119 | 16:00
Hathazari | 136 | 19:30 | 129 | 11:00 | Shikalbaha-230 | 136 | 23:00 | 130 | 10:00
Ishurdi | 138 | 17:00 | 130 | 21:00 | Shitalakhya | 128 | 17:00 | 124 | 00:00
Jaldhaka | 133 | 18:30 | 121 | 10:00 | Sholosohor | 133 | 01:00 | 127 | 04:00
Jamalpur | 139 | 15:00 | 129 | 21:00 | Shyampur | 128 | 18:30 | 123 | 12:00
Jashore | 137 | 06:00 | 124 | 21:00 | Shyampur-230 | 128 | 18:30 | 123 | 00:00
Jhenaidah | 138 | 17:00 | 120 | 21:00 | Siddhirganj | 130 | 18:30 | 124 | 00:00
Jhenaidah-230 | 138 | 17:00 | 127 | 22:00 | Sirajganj | 135 | 06:00 | 128 | 22:00
Joydebpur | 136 | 07:00 | 127 | 15:00 | Sonargaon | 129 | 18:30 | 122 | 09:00
Joypurhat | 134 | 17:00 | 125 | 22:00 | Sreemongol | 130 | 06:00 | 125 | 00:00
Juldah | 134 | 07:00 | 130 | 10:00 | Sreepur | 132 | 08:00 | 125 | 02:00
Kabirpur | 132 | 07:00 | 124 | 11:00 | Srinagar | 128 | 18:00 | 123 | 12:00
Kachua | 125 | 06:00 | 115 | 10:00 | SSM | 135 | 00:00 | 134 | 11:00
Kaliakoir | 133 | 18:30 | 126 | 11:00 | Sunamganj | 125 | 07:00 | 119 | 00:00
Kallyanpur | 131 | 01:00 | 126 | 11:00 | Sylhet | 129 | 09:00 | 124 | 00:00
Kalurghat | 131 | 01:00 | 128 | 04:00 | Sylhet-132 | 128 | 06:00 | 125 | 00:00
Kamrangirchar | 128 | 18:30 | 124 | 00:00 | Tangail | 129 | 15:00 | 120 | 21:00
Kaptai | 129 | 6:00 | 121 | 12:00 | Thakurgaon | 138 | 18:30 | 120 | 09:00
Kasba | 125 | 07:00 | 118 | 00:00 | TK | 131 | 19:30 | 128 | 04:00
Kazla | 131 | 07:00 | 127 | 00:00 | Tongi | 135 | 04:00 | 129 | 11:00
Keranigonj | 129 | 07:00 | 124 | 00:00 | Ullahpara | 136 | 18:30 | 129 | 22:00
Khagrachori | 131 | 07:00 | 127 | 11:00 | Ullon | 132 | 07:00 | 122 | 12:00
Khulna | 137 | 08:00 | 127 | 21:00 | Uttara | 132 | 17:00 | 123 | 11:00
Khulna(S) | 139 | 17:00 | 130 | 21:00 | UttaraNew | 131 | 06:00 | 124 | 11:00
Khulshi | 132 | 20:00 | 127 | 10:00 | Zigatola | 129 | 18:30 | 123 | 00:00
Kishoreganj | 130 | 07:00 | 120 | 22:00
Kodda | 131 | 07:00 | 121 | 11:00
KSRM | 133 | 00:00 | 127 | 11:00
Kulaura | 132 | 06:00 | 128 | 00:00
Kurigram | 131 | 18:30 | 122 | 10:00
Kushtia | 133 | 05:00 | 123 | 22:00
Lalbag | 129 | 07:00 | 124 | 00:00
Lalmonirhat | 131 | 18:30 | 124 | 19:30
Madanganj | 128 | 18:30 | 123 | 11:00
Madaripur | 137 | 17:00 | 131 | 22:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division