## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 22-06-2025 | [28 empty] | Date: | 22-06-2025 | [28 empty] | Date: | 22-06-2025 | [28 empty] | Date: | 22-06-2025 | [28 empty] | Date: | 22-06-2025 | [12 empty] | Date: | 22-06-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [12 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 31 | 88 | 146 | 195 | 0 | 17 | 35 | 51 | 380 | 293 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 70 | 20 | 22 | 0 | 450 | 43 | 172 | 0 | 0 | 13 | 65 | 79 | 0 | 100 | 100 | 0 | 182 | 101 | 23 | 133 | 0 | 0 | 19 | 8 | 86 | 221 | 0 | 0 | 0 | 1160 | 0 | 51 | 138 | 175 | 0 | 352 | 340 | 47 | 200 | 18 | 51 | 0 | 200 | 12 | 18 | 114 | 42 | 52.2 | 0 | 39 | 305 | 320 | 385 | 37 | 20 | 135 | 8 | 0 | 81 | 30 | 0 | 0 | 169 | 17 | 101 | 147 | 83 | 0 | 0 | 12 | 8800.2 | 879 | 340 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1041 | 53 | 1453.75 | 0 | 0 | 0 | 113 | 0 | 95 | 0 | 35 | 0 | 0 | 30 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 406 | 0 | 0 | 155 | 50 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 11 | 120 | 220 | 0 | 0 | 1106 | 0 | 6731.75 | 15531.95 | 98.39
01:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 20 | 88 | 146 | 195 | 0 | 17 | 17 | 51 | 380 | 289 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 52 | 20 | 22 | 0 | 450 | 43 | 170 | 0 | 0 | 10 | 65 | 79 | 0 | 100 | 100 | 0 | 182 | 102 | 26 | 133 | 0 | 0 | 33 | 8 | 96 | 220 | 0 | 0 | 0 | 1145 | 0 | 51 | 137 | 175 | 0 | 355 | 340 | 47 | 196 | 18 | 34 | 0 | 199 | 10 | 18 | 114 | 38 | 52.2 | 0 | 39 | 305 | 320 | 361 | 37 | 20 | 138 | 8 | 0 | 81 | 30 | 0 | 0 | 169 | 17 | 101 | 148 | 98 | 0 | 0 | 11 | 8675.2 | 879 | 344 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 53 | 1440.16 | 0 | 0 | 0 | 113 | 0 | 95 | 0 | 28 | 0 | 0 | 30 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 403 | 0 | 0 | 190 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 10 | 120 | 220 | 0 | 0 | 1105 | 0 | 6458.16 | 15133.36 | 98.4
02:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 29 | 79 | 112 | 0 | 0 | 0 | 17 | 51 | 380 | 294 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 20 | 22 | 0 | 450 | 0 | 98 | 0 | 0 | 3 | 0 | 79 | 0 | 100 | 100 | 0 | 182 | 51 | 26 | 215 | 0 | 0 | 20 | 0 | 51 | 220 | 0 | 0 | 0 | 1160 | 0 | 51 | 138 | 175 | 0 | 353 | 340 | 47 | 203 | 18 | 34 | 0 | 199 | 9 | 18 | 105 | 38 | 52.2 | 0 | 39 | 300 | 320 | 388 | 37 | 20 | 133 | 8 | 0 | 81 | 30 | 0 | 0 | 169 | 17 | 100 | 148 | 98 | 0 | 0 | 12 | 8212.2 | 880 | 351 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 741 | 0 | 1466.4 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 414 | 0 | 0 | 189 | 50 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 10 | 120 | 220 | 0 | 0 | 1098 | 0 | 6212.4 | 14424.6 | 98.41
03:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 28 | 45 | 95 | 0 | 0 | 0 | 17 | 51 | 380 | 293 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 20 | 22 | 0 | 450 | 0 | 15 | 0 | 0 | 11 | 0 | 71 | 0 | 100 | 100 | 0 | 182 | 26 | 26 | 213 | 0 | 0 | 19 | 0 | 17 | 223 | 0 | 0 | 0 | 1160 | 0 | 51 | 70 | 174 | 0 | 353 | 340 | 48 | 198 | 16 | 34 | 0 | 179 | 9 | 18 | 98 | 38 | 52.2 | 0 | 39 | 305 | 320 | 385 | 37 | 20 | 138 | 8 | 0 | 81 | 30 | 0 | 0 | 169 | 17 | 101 | 148 | 100 | 0 | 0 | 12 | 7919.2 | 880 | 354 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 1452.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 414 | 0 | 0 | 186 | 50 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 10 | 120 | 220 | 0 | 0 | 1102 | 0 | 6164.75 | 14083.95 | 98.42
04:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 29 | 32 | 80 | 0 | 0 | 0 | 17 | 51 | 380 | 290 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 20 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 7 | 0 | 40 | 0 | 100 | 100 | 0 | 182 | 0 | 26 | 217 | 0 | 0 | 15 | 0 | 0 | 223 | 0 | 0 | 0 | 1160 | 0 | 51 | 70 | 175 | 0 | 356 | 340 | 48 | 194 | 16 | 36 | 0 | 173 | 9 | 18 | 98 | 38 | 52.2 | 0 | 39 | 300 | 320 | 362 | 37 | 20 | 133 | 8 | 0 | 81 | 30 | 0 | 0 | 169 | 17 | 101 | 139 | 101 | 0 | 0 | 6 | 7736.2 | 879 | 354 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 740 | 0 | 1447.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 170 | 0 | 0 | 0 | 335 | 0 | 0 | 188 | 50 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 9 | 120 | 220 | 0 | 0 | 1101 | 0 | 6074.02 | 13810.22 | 98.43
05:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 29 | 32 | 80 | 0 | 0 | 0 | 17 | 17 | 380 | 290 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 20 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 11 | 0 | 10 | 0 | 48 | 100 | 0 | 182 | 0 | 26 | 217 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1080 | 0 | 51 | 20 | 175 | 0 | 356 | 340 | 48 | 189 | 16 | 34 | 0 | 197 | 8 | 18 | 92 | 36 | 52.2 | 0 | 31 | 305 | 320 | 345 | 37 | 20 | 132 | 8 | 0 | 81 | 30 | 0 | 0 | 170 | 17 | 101 | 139 | 101 | 0 | 0 | 10 | 7466.2 | 879 | 354 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 738 | 0 | 1355.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 169 | 0 | 0 | 0 | 328 | 0 | 0 | 188 | 50 | 92 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 9 | 120 | 220 | 0 | 0 | 1100 | 0 | 5959.74 | 13425.94 | 98.44
06:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 29 | 32 | 80 | 0 | 0 | 0 | 0 | 0 | 340 | 288 | 0 | 0 | 0 | 280 | 0 | 0 | 1 | 35 | 20 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 12 | 12 | 0 | 182 | 0 | 26 | 216 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 175 | 0 | 356 | 340 | 47 | 192 | 16 | 34 | 0 | 199 | 9 | 18 | 93 | 24 | 8 | 7 | 30 | 300 | 320 | 355 | 37 | 20 | 132 | 8 | 0 | 81 | 30 | 0 | 0 | 169 | 17 | 55 | 90 | 101 | 0 | 0.81 | 6 | 6954.81 | 879 | 351 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 740 | 0 | 1257.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 169 | 0 | 0 | 0 | 331 | 0 | 0.18 | 187 | 50 | 35 | 1 | 70 | 0 | 0 | 0.2 | 3 | 0.02 | 0 | 196 | 8 | 120 | 220 | 0 | 0 | 1050 | 0 | 5740.16 | 12694.97 | 98.45
07:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 1 | 29 | 33 | 80 | 0 | 0 | 0 | 0 | 0 | 340 | 290 | 0 | 0 | 0 | 280 | 0 | 0 | 4 | 17 | 20 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 1 | 182 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 175 | 0 | 355 | 340 | 48 | 197 | 16 | 34 | 0 | 141 | 9 | 18 | 96 | 34 | 8 | 19 | 30 | 290 | 320 | 365 | 37 | 20 | 131 | 8 | 0 | 81 | 30 | 0 | 0 | 170 | 17 | 55 | 90 | 93 | 0 | 4.64 | 12 | 6909.64 | 880 | 351 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4 | 739 | 0 | 1266.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 6.06 | 52 | 0 | 168 | 0 | 0 | 0 | 338 | 0 | 0.83 | 188 | 49 | 35 | 3 | 37 | 0 | 0 | 0.6 | 7 | 0.09 | 0 | 200 | 8 | 120 | 220 | 0 | 0 | 1040 | 0 | 5762.47 | 12672.11 | 98.46
08:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 17 | 19 | 33 | 64 | 0 | 0 | 0 | 0 | 0 | 340 | 292 | 0 | 0 | 0 | 280 | 0 | 0 | 5 | 17 | 20 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 6 | 215 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 965 | 5 | 51 | 0 | 175 | 0 | 300 | 340 | 47 | 197 | 16 | 34 | 0 | 155 | 9 | 19 | 39 | 28 | 8 | 22 | 0 | 300 | 320 | 375 | 37 | 20 | 130 | 8 | 0 | 81 | 30 | 0 | 0 | 170 | 17 | 55 | 90 | 94 | 1 | 7.7 | 12 | 6692.7 | 880 | 364 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 29.45 | 737 | 0 | 1281.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 13.85 | 122 | 0 | 164 | 0 | 0 | 0 | 340 | 0 | 1.17 | 192 | 49 | 35 | 4 | 45 | 0 | 0 | 1.6 | 40 | 0.39 | 0 | 191 | 7 | 120 | 180 | 0 | 0 | 1000 | 0 | 5875.05 | 12567.75 | 98.47
09:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 17 | 29 | 48 | 80 | 0 | 0 | 7 | 17 | 0 | 340 | 296 | 0 | 0 | 0 | 280 | 0 | 0 | 16 | 52 | 26 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 24 | 3 | 182 | 0 | 2 | 215 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 968 | 6 | 51 | 0 | 175 | 0 | 344 | 340 | 47 | 210 | 16 | 36 | 0 | 120 | 9 | 19 | 33 | 28 | 8 | 36 | 0 | 305 | 320 | 390 | 36 | 20 | 146 | 8 | 0 | 80 | 30 | 0 | 0 | 170 | 17 | 73 | 117 | 81 | 2 | 25.59 | 5 | 6978.59 | 880 | 364 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7 | 772 | 0 | 1286.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 16.62 | 178 | 0 | 181 | 0 | 0 | 0 | 383 | 0 | 1.42 | 149 | 49 | 35 | 10 | 49 | 0 | 0 | 1.6 | 52 | 0.59 | 0 | 174 | 6 | 120 | 180 | 0 | 0 | 994 | 0 | 5961.67 | 12940.26 | 98.48
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 17 | 29 | 50 | 79 | 0 | 0 | 20 | 17 | 0 | 340 | 300 | 0 | 0 | 0 | 330 | 0 | 0 | 16 | 52 | 26 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 24 | 4 | 182 | 0 | 3 | 215 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 960 | 9 | 51 | 0 | 174 | 0 | 345 | 340 | 47 | 201 | 14 | 51 | 0 | 120 | 9 | 16 | 42 | 30 | 8 | 66 | 0 | 305 | 320 | 390 | 36 | 20 | 147 | 8 | 0 | 59 | 30 | 0 | 0 | 169 | 17 | 75 | 118 | 71 | 1 | 14.8 | 3 | 7155.8 | 879 | 362 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 67 | 761 | 0 | 1266.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 28.07 | 176 | 0 | 181 | 0 | 0 | 0 | 366 | 0 | 3.74 | 136 | 49 | 35 | 13 | 34 | 0 | 0 | 3.3 | 104 | 0.29 | 0 | 173 | 6 | 120 | 220 | 0 | 0 | 1001 | 0 | 6106.2 | 13262 | 98.49
11:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 17 | 19 | 50 | 79 | 0 | 3 | 35 | 27 | 0 | 340 | 305 | 0 | 0 | 17 | 326 | 0 | 0 | 33 | 52 | 26 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 24 | 48 | 5 | 172 | 0 | 3 | 206 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 950 | 3 | 51 | 0 | 174 | 0 | 337 | 340 | 46 | 209 | 16 | 51 | 0 | 130 | 9 | 13 | 69 | 32 | 8 | 71 | 0 | 300 | 320 | 386 | 36 | 20 | 144 | 8 | 0 | 59 | 30 | 0 | 0 | 169 | 17 | 65 | 118 | 72 | 1 | 17.71 | 11 | 7253.71 | 880 | 362 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 90 | 756 | 0 | 1230.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 19.97 | 172 | 0 | 194 | 0 | 0 | 0 | 388 | 0 | 1.71 | 135 | 48 | 35 | 13 | 0 | 0 | 0 | 8 | 143 | 0.52 | 0 | 175 | 5 | 120 | 220 | 0 | 0 | 1001 | 0 | 6138.31 | 13392.02 | 98.5
12:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 17 | 28 | 51 | 79 | 0 | 15 | 35 | 50 | 3 | 340 | 301 | 0 | 0 | 17 | 325 | 0 | 0 | 33 | 70 | 26 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 48 | 75 | 2 | 172 | 0 | 2 | 205 | 0 | 0 | 0 | 0 | 7 | 216 | 0 | 0 | 0 | 1081 | 18 | 51 | 3 | 174 | 0 | 335 | 340 | 42 | 208 | 16 | 51 | 0 | 148 | 9 | 19 | 68 | 32 | 18 | 22 | 0 | 310 | 320 | 381 | 36 | 30 | 149 | 8 | 0 | 58 | 30 | 0 | 0 | 168 | 17 | 65 | 132 | 72 | 1 | 14.98 | 11 | 7520.98 | 880 | 360 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 81 | 764 | 0 | 1239.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 69.69 | 176 | 0 | 205 | 0 | 0 | 0 | 387 | 0 | 3.79 | 200 | 48 | 0 | 26 | 0 | 0 | 0 | 7.4 | 213 | 0.2 | 0 | 204 | 7 | 120 | 220 | 0 | 0 | 1038 | 0 | 6329.42 | 13850.4 | 98.51
13:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 17 | 0 | 62 | 79 | 0 | 15 | 35 | 79 | 16 | 340 | 299 | 0 | 0 | 17 | 325 | 0 | 0 | 32 | 66 | 26 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 88 | 100 | 1 | 172 | 0 | 10 | 205 | 0 | 0 | 0 | 0 | 32 | 216 | 0 | 0 | 0 | 1100 | 15 | 51 | 30 | 174 | 0 | 333 | 340 | 41 | 202 | 16 | 51 | 0 | 157 | 9 | 19 | 79 | 32 | 25 | 70 | 37 | 305 | 320 | 389 | 36 | 30 | 157 | 8 | 0 | 58 | 30 | 0 | 0 | 168 | 17 | 65 | 125 | 72 | 1 | 24.43 | 0 | 7776.43 | 880 | 360 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 79 | 760 | 0 | 1265.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 10.28 | 174 | 0 | 207 | 0 | 0 | 0 | 374 | 0 | 1.38 | 198 | 49 | 35 | 27 | 0 | 0 | 0 | 2.5 | 142 | 0.34 | 0 | 202 | 7 | 120 | 220 | 0 | 0 | 1107 | 0 | 6331.27 | 14107.7 | 98.53
14:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 0 | 56 | 78 | 0 | 20 | 35 | 88 | 16 | 340 | 303 | 0 | 0 | 17 | 280 | 0 | 0 | 29 | 108 | 26 | 22 | 0 | 520 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 88 | 100 | 0 | 172 | 0 | 6 | 203 | 0 | 0 | 0 | 0 | 51 | 216 | 0 | 0 | 0 | 1160 | 8 | 51 | 46 | 174 | 0 | 338 | 340 | 41 | 200 | 16 | 51 | 0 | 187 | 9 | 12 | 96 | 32 | 27 | 65 | 41 | 305 | 320 | 373 | 36 | 30 | 144 | 8 | 0 | 58 | 15 | 0 | 0 | 167 | 17 | 65 | 126 | 67 | 1 | 23.38 | 0 | 7879.38 | 880 | 320 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 79 | 753 | 0 | 1365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 33.3 | 175 | 0 | 180 | 0 | 0 | 0 | 404 | 0 | 5.72 | 200 | 49 | 35 | 32 | 0 | 0 | 0 | 4.3 | 185 | 0.2 | 0 | 201 | 7 | 120 | 220 | 0 | 42 | 1110 | 0 | 6524.52 | 14403.9 | 98.55
15:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 17 | 47 | 50 | 78 | 0 | 30 | 35 | 89 | 16 | 340 | 297 | 0 | 0 | 17 | 280 | 0 | 0 | 12 | 108 | 26 | 22 | 0 | 520 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 88 | 100 | 4 | 172 | 0 | 4 | 203 | 0 | 0 | 0 | 0 | 50 | 214 | 0 | 0 | 0 | 1170 | 10 | 51 | 50 | 174 | 0 | 330 | 335 | 42 | 206 | 16 | 57 | 0 | 198 | 9 | 19 | 94 | 30 | 43 | 20 | 45 | 300 | 320 | 376 | 35 | 30 | 147 | 8 | 0 | 59 | 15 | 0 | 0 | 167 | 17 | 65 | 107 | 67 | 1 | 26.89 | 0 | 7920.89 | 881 | 320 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 30 | 770 | 0 | 1386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 10.08 | 177 | 0 | 178 | 0 | 0 | 0 | 405 | 0 | 1.52 | 190 | 48 | 35 | 25 | 0 | 0 | 0 | 6.2 | 162 | 0.21 | 0 | 204 | 6 | 120 | 220 | 0 | 137 | 1106 | 0 | 6543.01 | 14463.9 | 98.57
16:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 17 | 55 | 50 | 110 | 0 | 30 | 35 | 89 | 16 | 340 | 289 | 0 | 0 | 17 | 280 | 0 | 0 | 8 | 108 | 26 | 22 | 0 | 520 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 88 | 100 | 2 | 172 | 0 | 6 | 203 | 0 | 0 | 0 | 0 | 51 | 214 | 0 | 0 | 0 | 1165 | 4 | 51 | 50 | 164 | 0 | 332 | 335 | 40 | 203 | 16 | 69 | 0 | 197 | 8 | 19 | 100 | 36 | 52.2 | 37 | 45 | 300 | 320 | 376 | 35 | 30 | 145 | 8 | 0 | 59 | 15 | 0 | 0 | 166 | 17 | 85 | 116 | 67 | 0 | 18.41 | 0 | 7988.61 | 880 | 336 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 28 | 745 | 0 | 1356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 13.18 | 174 | 0 | 176 | 0 | 0 | 0 | 414 | 0 | 0.76 | 167 | 48 | 35 | 13 | 0 | 0 | 0 | 1.2 | 117 | 0.24 | 0 | 202 | 7 | 120 | 220 | 0 | 200 | 1107 | 0 | 6424.38 | 14412.99 | 98.59
17:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 17 | 35 | 50 | 110 | 0 | 15 | 35 | 54 | 0 | 340 | 285 | 0 | 0 | 0 | 280 | 0 | 0 | 3 | 90 | 25.7 | 22 | 0 | 520 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 88 | 100 | 1 | 172 | 0 | 9 | 200 | 0 | 0 | 0 | 0 | 47 | 214 | 0 | 0 | 0 | 1140 | 2 | 51 | 0 | 164 | 0 | 338 | 340 | 41 | 192 | 16 | 69 | 0 | 196 | 8 | 19 | 113 | 34 | 52.2 | 11 | 43 | 300 | 320 | 354 | 35 | 30 | 136 | 8 | 0 | 59 | 15 | 0 | 0 | 166 | 17 | 85 | 125 | 67 | 1 | 8.12 | 0 | 7701.02 | 880 | 340 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12 | 728 | 0 | 1357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 17.43 | 165 | 0 | 170 | 0 | 0 | 0 | 393 | 0 | 1.4 | 197 | 48 | 0 | 4 | 0 | 0 | 0 | 0.6 | 33 | 0.08 | 0 | 198 | 7 | 120 | 220 | 0 | 277 | 1100 | 0 | 6328.51 | 14029.53 | 98.61
18:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 17 | 35 | 50 | 110 | 0 | 15 | 35 | 47 | 0 | 340 | 285 | 0 | 0 | 0 | 280 | 0 | 0 | 1 | 70 | 26 | 22 | 0 | 520 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 70 | 72 | 1 | 172 | 0 | 13 | 200 | 0 | 0 | 0 | 0 | 45 | 216 | 0 | 0 | 0 | 960 | 1 | 51 | 0 | 172 | 0 | 340 | 340 | 42 | 193 | 16 | 69 | 0 | 155 | 13 | 19 | 78 | 30 | 34 | 2 | 43 | 295 | 320 | 365 | 35 | 30 | 130 | 8 | 0 | 59 | 15 | 0 | 0 | 167 | 17 | 85 | 134 | 67 | 0 | 8.05 | 0 | 7361.05 | 880 | 336 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 730 | 0 | 1267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1.67 | 166 | 0 | 164 | 0 | 0 | 0 | 400 | 0 | 0.19 | 197 | 48 | 35 | 1 | 35 | 0 | 0 | 0.3 | 6 | 0.02 | 0 | 171 | 7 | 120 | 220 | 0 | 278 | 950 | 0 | 6055.18 | 13416.23 | 98.62
19:00 | 8 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 22 | 35 | 70 | 110 | 0 | 15 | 55 | 51 | 8 | 360 | 305 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 90 | 26.5 | 22 | 0 | 450 | 2 | 14 | 0 | 0 | 11 | 58 | 40 | 2 | 70 | 72 | 0 | 172 | 3 | 13 | 202 | 17 | 0 | 3 | 0 | 48 | 216 | 0 | 0 | 0 | 980 | 0 | 51 | 7 | 172 | 0 | 343 | 340 | 43 | 194 | 16 | 81 | 0 | 147 | 27 | 19 | 100 | 38 | 52.2 | 0 | 42 | 300 | 320 | 372 | 35 | 30 | 138 | 8 | 0 | 59 | 15 | 0 | 0 | 166 | 17 | 85 | 134 | 70 | 0 | 0 | 0 | 7763.7 | 879 | 324 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1101 | 50 | 1404 | 0 | 3 | 0 | 1 | 0 | 72 | 15 | 8 | 0 | 0 | 24 | 0 | 173 | 0 | 174 | 0 | 0 | 0 | 399 | 0 | 0 | 201 | 48 | 70 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 236 | 10 | 120 | 220 | 0 | 278 | 978 | 0 | 6913 | 14676.7 | 98.63
19:30 | 16 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 35 | 35 | 85 | 118 | 45 | 15 | 55 | 130 | 20 | 360 | 299 | 0 | 0 | 17 | 329 | 0 | 0 | 0 | 125 | 26.5 | 22 | 0 | 450 | 10 | 14 | 0 | 0 | 16 | 66 | 42 | 17 | 88 | 100 | 0 | 172 | 15 | 13 | 200 | 17 | 0 | 50 | 2 | 48 | 216 | 0 | 0 | 0 | 980 | 0 | 51 | 80 | 172 | 0 | 343 | 335 | 44 | 195 | 16 | 115 | 0 | 172 | 28 | 19 | 100 | 36 | 52.2 | 0 | 42 | 300 | 320 | 355 | 35 | 30 | 154 | 8 | 0 | 59 | 15 | 0 | 0 | 168 | 17 | 85 | 134 | 70 | 0 | 0 | 0 | 8271.7 | 879 | 323 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1185 | 53 | 1417 | 0 | 31 | 0 | 25 | 0 | 96 | 35 | 12 | 0 | 0 | 30 | 0 | 189 | 0 | 190 | 0 | 0 | 0 | 405 | 0 | 0 | 200 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 268 | 10 | 120 | 220 | 0 | 279 | 1100 | 0 | 7366 | 15637.7 | 98.63
20:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 35 | 35 | 91 | 146 | 0 | 15 | 55 | 129 | 32 | 360 | 300 | 0 | 0 | 17 | 329 | 0 | 0 | 0 | 130 | 26.5 | 22 | 0 | 450 | 0 | 14 | 0 | 0 | 18 | 66 | 56 | 0 | 88 | 100 | 0 | 172 | 15 | 13 | 200 | 0 | 0 | 48 | 6 | 47 | 216 | 0 | 0 | 0 | 980 | 0 | 51 | 80 | 165 | 0 | 346 | 340 | 43 | 212 | 16 | 115 | 0 | 178 | 27 | 19 | 99 | 34 | 52.2 | 0 | 42 | 295 | 320 | 365 | 35 | 30 | 154 | 8 | 0 | 59 | 15 | 0 | 0 | 167 | 17 | 85 | 134 | 71 | 0 | 0 | 0 | 8258.7 | 879 | 318 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 53 | 1406 | 0 | 45 | 0 | 30 | 0 | 96 | 0 | 24 | 0 | 0 | 30 | 0 | 187 | 0 | 187 | 0 | 0 | 0 | 402 | 0 | 0 | 200 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 11 | 120 | 220 | 0 | 283 | 1105 | 0 | 7332 | 15590.7 | 98.64
21:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 54 | 35 | 120 | 146 | 0 | 0 | 17 | 132 | 16 | 360 | 304 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 142 | 20.5 | 22 | 0 | 450 | 0 | 14 | 0 | 0 | 11 | 66 | 56 | 0 | 100 | 100 | 0 | 172 | 15 | 19 | 200 | 0 | 0 | 19 | 8 | 48 | 216 | 0 | 0 | 0 | 990 | 0 | 51 | 80 | 165 | 0 | 343 | 340 | 45 | 205 | 16 | 115 | 0 | 174 | 29 | 19 | 109 | 30 | 52.2 | 0 | 42 | 295 | 320 | 377 | 35 | 30 | 154 | 8 | 0 | 59 | 15 | 0 | 0 | 167 | 0 | 85 | 142 | 70 | 0 | 0 | 0 | 8222.7 | 880 | 312 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 35 | 1424.83 | 0 | 44 | 0 | 35 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 188 | 0 | 0 | 0 | 414 | 0 | 0 | 196 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 11 | 120 | 220 | 0 | 282 | 1100 | 0 | 7322.83 | 15545.53 | 98.65
22:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 54 | 35 | 120 | 146 | 0 | 0 | 0 | 138 | 16 | 360 | 291 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 142 | 25.5 | 22 | 0 | 450 | 0 | 14 | 0 | 0 | 4 | 66 | 32 | 0 | 100 | 100 | 0 | 172 | 16 | 19 | 200 | 0 | 0 | 19 | 8 | 49 | 216 | 0 | 0 | 0 | 965 | 0 | 30 | 80 | 152 | 0 | 351 | 340 | 46 | 186 | 16 | 111 | 0 | 186 | 28 | 19 | 92 | 36 | 52.2 | 0 | 42 | 290 | 320 | 310 | 34 | 30 | 155 | 8 | 0 | 59 | 15 | 0 | 0 | 168 | 4 | 85 | 165 | 68 | 0 | 0 | 0 | 8063.7 | 879 | 276 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1170 | 17 | 1411.91 | 0 | 44 | 0 | 35 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 190 | 0 | 0 | 0 | 332 | 0 | 0 | 197 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 11 | 114 | 220 | 0 | 346 | 1102 | 0 | 7198.91 | 15262.61 | 98.66
23:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 54 | 35 | 131 | 146 | 0 | 0 | 0 | 126 | 16 | 360 | 291 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 142 | 25.5 | 22 | 0 | 450 | 0 | 13 | 0 | 0 | 7 | 65 | 32 | 0 | 100 | 100 | 0 | 172 | 14 | 27 | 200 | 0 | 0 | 19 | 8 | 46 | 222 | 0 | 0 | 0 | 1017 | 0 | 51 | 80 | 162 | 0 | 352 | 335 | 47 | 215 | 16 | 68 | 0 | 163 | 29 | 19 | 98 | 38 | 52.2 | 0 | 45 | 285 | 320 | 319 | 34 | 30 | 148 | 8 | 0 | 59 | 15 | 0 | 0 | 166 | 17 | 85 | 166 | 67 | 0 | 0 | 0 | 8112.7 | 880 | 290 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 17 | 1410.24 | 0 | 44 | 0 | 35 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 178 | 0 | 0 | 0 | 332 | 0 | 0 | 192 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 10 | 120 | 220 | 0 | 347 | 1090 | 0 | 7095.24 | 15207.94 | 98.67
Total KWH | 12384 | 1330560 | 586080 | 0 | 0 | 0 | 0 | 0 | 8348400 | 0 | 0 | 453600 | 392040 | 1604880 | 2466720 | 307865 | 189651 | 462423 | 1355040 | 396480 | 8617000 | 7076305 | 0 | 0 | 147441 | 7489640 | 0 | 0 | 204567 | 1814400 | 564000 | 519480 | 0 | 11417727.27 | 82800 | 474218 | 0 | 0 | 319200 | 447707 | 560784 | 18538 | 1592640 | 1835520 | 25426 | 4269180 | 326182 | 382560 | 4872727.27 | 6691 | 0 | 254400 | 53127 | 818799 | 5255362 | 0 | 0 | 0 | 25270907 | 92880 | 1161171 | 1175927 | 4098182 | 0 | 8571800 | 8214000 | 1078560 | 4922000 | 394704 | 1384320 | 0 | 4093920 | 322560 | 417270 | 2140920 | 806400 | 895120 | 486136 | 760720 | 7242000 | 7670000 | 9233000 | 583000 | 574800 | 3421145 | 183840 | 0 | 1632000 | 560352 | 0 | 0 | 4475930 | 408240 | 1899600 | 3081600 | 1835520 | 7050 | 188810 | 114480 | 186751408.54 | 21105454 | 8186112 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 491040 | 20072726 | 266400 | 32486545 | 0 | 207187 | 0 | 437088 | 0 | 652656 | 34272 | 65695 | 0 | 691160 | 97443 | 249000 | 3102909 | 0 | 4522373 | 0 | 0 | 0 | 9123054 | 0 | 21000 | 4477000 | 1124072 | 1629787 | 165057 | 1361625 | 0 | 0 | 36797.28 | 1174320 | 3916 | 0 | 5062000 | 203195 | 2873000 | 5375750 | 0 | 2625192 | 26203636.36 | 0 | 155039461.64 | 341790870.18

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 23-06-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-06-2025 | during | 23-06-2025 | during | 23-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 357 | 360 | 400.75 | 400.75 | 371 | 371 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 340 | 360 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 301 | 299 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 325 | 329 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 16 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 79 | 118 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 17 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 26 | 26.5 | 33 | 33 | 26.5 | 26.5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 45 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 51 | 85 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 88 | 105 | 105 | 88 | 88 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 3 | 20 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 50 | 130 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 34 | 0 | 34 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 28 | 35 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 500 | 450 | 584 | 584 | 584 | 584 | None
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 125 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2346 | 2655.5 | 5113.2 | 5173.2 | 3542.83 | 3602.83
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 2 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 8 | 0 | 8 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 172 | 172 | 182 | 182 | 182 | 182 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 216 | 221 | 221 | 221 | 221 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 7 | 48 | 105 | 105 | 94.5 | 94.5 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 42 | 48 | 80 | 56 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 66 | 65 | 65 | 65 | 65 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 48 | 88 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 13 | 2 | 20 | 2 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2 | 0 | 0.71 | 0 | 0.71 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 14 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 17 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 15 | 110 | 110 | 99 | 99 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 75 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 10 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 17 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1081 | 980 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 10 | 16 | 16 | 20 | 16 | 20 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 205 | 200 | 215 | 215 | 215 | 215 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1836 | 2066 | 3210.43 | 3255.72 | 3196.93 | 3236.22
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 208 | 195 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 335 | 343 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 335 | 340 | 340 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 16 | 16 | 46.7 | 46.7 | 24 | 24 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 42 | 44 | 55 | 55 | 49 | 49 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 174 | 172 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 3 | 80 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 42 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 148 | 172 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 32 | 36 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 18 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 68 | 100 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 28 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 115 | 115 | 115 | 52 | 115 | Fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 22 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1536 | 1800.2 | 2450.75 | 2400.75 | 2071.55 | 2084.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-06-2025 | during | 23-06-2025 | during | 23-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 72 | 70 | 157.5 | 157.5 | 101 | 101 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.2 | 0 | 1.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 132 | 134 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 65 | 85 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 14.98 | 0 | 25 | 0 | 25 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 11 | 0 | 22 | 22 | 22 | 22 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 312.98 | 306 | 575.2 | 549 | 518.7 | 492.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 36 | 35 | 35 | 35 | 35 | 35 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 0 | 0 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 149 | 154 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 15 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 58 | 59 | 64 | 64 | 64 | 64 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 168 | 168 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 381 | 355 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1490 | 1444 | 1541 | 1541 | 1458 | 1458
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 880 | 879 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 360 | 323 | 410 | 410 | 364 | 364 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 53 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 81 | 0 | 65 | 0 | 65 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 764 | 1185 | 750 | 1234.2 | 750 | 1234.2 | Coal Unloading problem due to bad weather
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2123 | 2478 | 3135 | 3554.2 | 3089 | 3508.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 0 | 279 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 7 | 10 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1038 | 1100 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 204 | 268 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.2 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1589.2 | 1997 | 2172 | 2171 | 2160 | 2159
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 31 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 30 | 30 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 12 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 176 | 189 | 214 | 214 | 192 | 192 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 205 | 190 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is in Standby as per NLDC request.
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 387 | 405 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 | 30 | 30 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 96 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 25 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 28 | 28 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.79 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1239.34 | 1417 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 69.69 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 42 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 2122.82 | 2430 | 3193.47 | 3026.87 | 3020.68 | 2854.08
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 48 | 50 | 50 | 50 | 50 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 150 | 150 | 150 | 150 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 98 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.4 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 26 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 213 | 0 | 143.3 | 0 | 143.3 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 494.4 | 461 | 636.9 | 462 | 636.9 | 462
System Total |  |  |  |  | 28565.2 | 27084.055 | 13850.4 | 15637.7 | 22027.95 | 22133.74 | 19694.59 | 19857.38
Forecast Scenario (23-06-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15280 |  | 0 |  | 15280
|  |  |  | 1:00 | 14885 |  | 0 |  | 14885
|  |  |  | 2:00 | 14166 |  | 0 |  | 14166
|  |  |  | 3:00 | 13784 |  | 0 |  | 13784
|  |  |  | 4:00 | 13510 |  | 0 |  | 13510
|  |  |  | 5:00 | 13126 |  | 0 |  | 13126
|  |  |  | 6:00 | 12395 |  | 0 |  | 12395
|  |  |  | 7:00 | 12372 |  | 0 |  | 12372
|  |  |  | 8:00 | 12268 |  | 0 |  | 12268
|  |  |  | 9:00 | 12640 |  | 0 |  | 12640
|  |  |  | 10:00 | 12962 |  | 0 |  | 12962
|  |  |  | 11:00 | 13092 |  | 0 |  | 13092
|  |  |  | 12:00 | 13550 |  | 0 |  | 13550
|  |  |  | 13:00 | 13808 |  | 0 |  | 13808
|  |  |  | 14:00 | 14104 |  | 0 |  | 14104
|  |  |  | 15:00 | 14164 |  | 0 |  | 14164
|  |  |  | 16:00 | 14113 |  | 0 |  | 14113
|  |  |  | 17:00 | 13730 |  | 0 |  | 13730
|  |  |  | 18:00 | 13116 |  | 0 |  | 13116
|  |  |  | 18:30 | 13600 |  | 0 |  | 13600
|  |  |  | 19:00 | 14377 |  | 0 |  | 14377
|  |  |  | 19:30 | 15338 |  | 0 |  | 15338
|  |  |  | 20:00 | 15331 |  | 0 |  | 15331
|  |  |  | 21:00 | 15282 |  | 0 |  | 15282
|  |  |  | 22:00 | 14963 |  | 0 |  | 14963
|  |  |  | 23:00 | 14852 |  | 0 |  | 14852
Probable Maximum Temperature: |  |  | 30.00°C
Probable Maximum Demand at Day Peak: |  |  | 13550.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 15338.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15338.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 331.87 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:24 hrs on 23-06-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 22-06-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13850.4 | MW | 12:00 Hr. | Energy Generated |  |  | 341.7909 |  | MKWHr.
| Day Peak Demand |  |  | 13850.4 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.287 |  | MKWHr.
| Evening Peak Generation |  |  | 15637.7 | MW | 19:30 Hr. | Energy Demand |  |  | 342.0779 |  | MKWHr.
| Evening Peak Demand |  |  | 15637.7 | MW | 19:30 Hr. | Maximum Temperature |  |  | 34.2 |  | °C
| Minimum Generation of the Day |  |  | 12567.75 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 1062.27 |  | MMCFD
| Maximum Generation of the Day |  |  | 15637.7 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.423 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 44.0326 | 0 | 11.5196 | 0 | 0 | 0.20457 | 0 | 0 | 55.7567 | Gas | 149.3261 | Gas | 528357230.5459
| Chattogram Zone |  |  | 5.6379 | 30.1436 | 6.4714 | 0 | 4.2692 | 0.11831 | 0 | 0.3192 | 46.9596 | Coal | 89.7083 | Coal | 591394124.213
| Cumilla Zone |  |  | 28.8577 | 0 | 10.7735 | 0 | 0 | 0.48614 | 0.8064 | 0 | 40.9237 | HFO | 39.0205 | HFO | 730849392.28
| Mymensingh Zone |  |  | 1.8355 | 0 | 5.5039 | 0 | 0 | 0.19586 | 0 | 0 | 7.5353 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 35.5761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.5761 | Hydro | 4.2692 | Hydro | 426918
| Khulna Zone |  |  | 8.1861 | 20.0727 | 0.2664 | 0 | 0 | 0.49104 | 22.0175 | 0 | 51.0337 | Solar | 3.8372 | Solar | 61788195.9208
| Barishal Zone |  |  | 8.4519 | 33.8908 | 0 | 0 | 0 | 0.003916 | 0 | 0 | 42.3467 | Import | 55.3104 | Import | 277823969.4
| Rajshahi Zone |  |  | 16.7483 | 0 | 1.4943 | 0 | 0 | 0.96116 | 32.4865 | 0 | 51.6904 | Wind | 0.3192 | Wind | 4673088
| Rangpur Zone |  |  | 0 | 5.6011 | 2.9914 | 0 | 0 | 1.3762 | 0 | 0 | 9.9687
| Total |  |  | 149.3261 | 89.7083 | 39.0205 | 0 | 4.2692 | 3.8372 | 55.3104 | 0.3192 | 341.7909
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 528357230.5459 |  | Hydro | 426918
|  |  |  | Coal | 591394124.213 |  | Solar | 61788195.9208
|  |  |  | HFO | 730849392.28 |  | Import | 277823969.4
|  |  |  | HSD | 0 |  | Wind | 4673088
[5 empty] | Total: | 219,53,12,918 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.1055 | Peak Hr Flow | 879.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 39635727.36 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 32.4865 | Peak Hr Flow | 1417.00 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 892 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.8064 | Peak Hr Flow | 36.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 1010 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 54.3984 | Peak Hr Flow | 2332.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5480
|  |  |  | Chattogram |  | 0 |  | 1418
|  |  |  | Cumilla |  | 0 |  | 1422
|  |  |  | Mymensingh |  | 0 |  | 1153
|  |  |  | Sylhet |  | 0 |  | 655
|  |  |  | Khulna |  | 0 |  | 1863
|  |  |  | Barishal |  | 0 |  | 453
|  |  |  | Rajshahi |  | 0 |  | 1516
|  |  |  | Rangpur |  | 0 |  | 1013
|  |  |  | Total |  | 0 |  | 14973
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[5 empty] | Total | 300 |  |  |  | Total | 476
|  |  |  | Total Unavailable Capacity |  |  |  | 776
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:02 | 09:17 | Noapara 132/33kV S/S Bus Section-2 Scheduled S/D | [7 empty] | 16.0MW load
interrup.
|  | 08:41 | Ramganj 132/33kV S/S Transformer -02 LT is restored.
|  | 09:23 | Noapara 132/33kV S/S T-2 HT is restored.
|  | 09:24 | Noapara 132/33kV S/S T-2 LT is restored.
| 09:24 |  | Madunaghat 132/33kV S/S ATR-1(705T) HT Scheduled S/D Due to Fire protection maintenance
work by CNTIC.
| 09:24 |  | Madunaghat 132/33kV S/S ATR-1(705T) LT Scheduled S/D Due to Fire protection maintenance
work by CNTIC.
| 09:54 | 12:56 | Shikalbaha 132/33 kV transformer T-4 S/D due to red hot maintenance | [7 empty] | 5MW load interrup.
|  | 10:07 | Ishurdi 230/132kV S/S 230/132 kV T-01 LT is restored.
|  | 10:07 | Ishurdi 230/132kV S/S 230/132 kV T-01 HT is restored.
|  | 10:28 | Daudkandi 132/33kV S/S Transformer-2 HT is restored.
| 10:29 | 11:55 | Ishurdi 132/33kV S/S 132 kV Bus-2 Scheduled S/D Due to For DSEPL work
|  | 10:30 | Daudkandi 132/33kV S/S Transformer-2 LT is restored.
| 10:52 | 18:05 | Goalpara 132/33kV S/S Goalpara-NWPGCL Scheduled S/D Due to Busbar protection testing
| 13:07 | 16:08 | BIPTC S/S 10CF15 Tripped showing 60/61 instant relays Due to C1 unbalance 60/61 instant
L1 Trip
| 14:01 | 14:17 | Naogaon 132/33kV S/S T-3 LT Tripped showing MCGG, Over current A,B (t) relays Due to
Atrai 33KV PBS feeder BKR ,CT to BKR Connecting loop flashing and burn out.
| 15:03 | 16:59 | Chhatak 132/33kV S/S T-3 HT Forced S/D Due to 132KV T-3 GCB Hydraulic System Oil Leakage
Problem.
| 15:03 | 16:59 | Chhatak 132/33kV S/S T-3 LT Forced S/D Due to Oil Leakage Problem of 132KV T-3 GCB
Hydraulic Oil System.
| 15:19 | 15:52 | Pabna 132/33kV S/S T-2 LT Forced S/D Due to 33 kv kashinathpur feeder Incoming D/S red | [7 empty] | 35.0MW load
|  |  | hot maintenance work. | [7 empty] | interrup.
| 15:20 | 15:53 | Pabna 132/33kV S/S T-2 HT Forced S/D Due to Red hot maintenance work. | [7 empty] | 35.0MW load
interrup.
| 15:52 | 19:19 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-01 HT Scheduled S/D Due to PRD
Checking and Fire Detection alarm Checking and reset.
| 19:14 |  | Raozan 25 MW PP Synchronized
| 19:30 |  | Evening Peak Generation 15637 MW.
| 19:30 |  | Evening peak Generation is 15637 MW
| 21:43 | 22:52 | Rampura 230/132kV S/S Auto Transformer - 03 LT Tripped showing Lockout Relay 1&2 CB-665B, | [7 empty] | 208.0MW load
|  |  | CB-668B relays Due to T2-132kV jack BUS Insulator failure. 132kv Bus-2 fail. | [7 empty] | interrup.
| 21:43 | 22:33 | Rampura 230/132kV S/S Auto Transformer - 04 HT Tripped showing Lockout Relay 1&2 CB-655B | [7 empty] | 208.0MW load
|  |  | , CB-658B (SQA2) Siprotec 7UT86 relays Due to T2-132kV jack BUS Insulator failure. | [7 empty] | interrup.
132kv Bus-2 fail.
| 21:43 |  | Rampura 230/132kV S/S Auto Transformer - 02 HT Tripped showing lockout1&2 | [7 empty] | 208.0MW load
|  |  | CB-638B, Siprotec & 7UT86 relays Due to T2-132kV jack BUS Insulator failure. 132kv | [7 empty] | interrup.
Bus-2 fail.
| 21:43 |  | Rampura 230/132kV S/S Auto Transformer - 02 LT Tripped showing Biased Differential Relay | [7 empty] | 208.0MW load
|  |  | Trip, Restricted Earth Fault , Main-2 General Trip , Lockout Relay 1&2 CB-845B, Lockout | [7 empty] | interrup.
Relay 1&2 CB-848B relays Due to T2-132kV jack BUS Insulator failure. 132kv Bus-2 fail.
| 21:43 | 22:33 | Rampura 230/132kV S/S Auto Transformer - 04 LT Tripped showing Lockout relay 1&2 CB-655B | [7 empty] | 208.0MW load
|  |  | relays Due to T2-132kV jack BUS Insulator failure. 132kv Bus-2 fail. | [7 empty] | interrup.
| 23:04 |  | Hasnabad 230/132kV S/S AUTO TR-2 HT Tripped showing LOR-
86T1 LOR-86T2 LOR-86L1 LOR-86L2 relays Due to OLTC PROTECT TRIP signal at Control
Panel Lock out Relay operate at Relay Panel
| 23:04 |  | Hasnabad 230/132kV S/S AUTO TR-2 LT Tripped showing No RELAY operated relays Due to OLTC
PROTECT TRIP for LOR-86T ,LOR86-L
| 04:17 |  | Raozan 25 MW PP Shutdown
| 06:27 | 06:59 | Rajbari 132/33kV S/S Transformer-3 LT Tripped showing 86.1&86.2 relays Due to E/F | [7 empty] | 17.0MW load
interrup.
| 06:45 |  | Ramganj 132/33kV S/S Transformer-01 LT Scheduled S/D Due to Red Hot Maintenance | [7 empty] | 10.0MW load
interrup.
| 06:46 |  | Ramganj 132/33kV S/S Transformer-01 HT Scheduled S/D Due to Red hot maintenance | [7 empty] | 10.0MW load
interrup.
| 07:00 |  | Minimum generation 12732 MW
| 07:03 |  | Goalpara 132/33kV S/S T-5 LT Scheduled S/D Due to 3rd transformer Installation. | [7 empty] | 3.0MW load
interrup.
| 07:03 |  | Goalpara 132/33kV S/S T-5 HT Scheduled S/D Due to 3rd transformer Installation. | [7 empty] | 3.0MW load
interrup.
| 07:05 |  | Goalpara 132/33kV S/S T-6 LT Scheduled S/D Due to 3rd transformer Installation. | [7 empty] | 3.0MW load
interrup.
| 07:05 |  | Goalpara 132/33kV S/S T-6 HT Scheduled S/D Due to 3rd transformer Installation. | [7 empty] | 3.0MW load
interrup.
| 07:31 |  | Coxsbazar 132/33kV S/S 415T-T2 HT Tripped showing Differential Relay relays Due to PBS | [7 empty] | 40.0MW load
|  |  | UKHIYA 33KV FEEDER FAILED TO TRIP( O/C & E/F) | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 22-06-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 360 | 8348400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 360 | 8617000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 299 | 7076305 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 189651 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 329 | 7489640 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 12384 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 453600 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 118 | 2466720 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 462423 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 147441 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 26.5 | 564000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 519480 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 586080 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 45 | 307865 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 85 | 1604880 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1330560 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 20 | 396480 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 130 | 1355040 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 204567 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 392040 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 450 | 11417727.27 | None
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 125 | 1814400 | -
Dhaka Area Total |  |  |  |  | 5939.724 | 2655.5 | 55756683.27
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 2 | 53127 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 92880 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 254400 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 172 | 4269180 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 216 | 5255362 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 48 | 818799 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 42 | 560784 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 447707 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 88 | 1592640 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 13 | 382560 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 25426 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 14 | 474218 | FGMO
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 17 | 18538 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 15 | 326182 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1835520 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 10 | 82800 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 17 | 6691 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 980 | 25270907 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 16 | 319200 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 200 | 4872727.27 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4895.72 | 2066 | 46959648.27
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 195 | 4922000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 343 | 8571800 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 335 | 8214000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 16 | 394704 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 44 | 1078560 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 172 | 4098182 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1161171 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 80 | 1175927 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 42 | 760720 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 172 | 4093920 | -
| Import (Tripura) |  | Import | 0 | 160 | 36 | 806400 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 895120 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 417270 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 2140920 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 322560 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1384320 | Fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 486136 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1800.2 | 40923710
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 70 | 1835520 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7050 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 134 | 3081600 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 85 | 1899600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 188810 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 114480 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 408240 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 306 | 7535300
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 35 | 583000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 574800 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 154 | 3421145 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 15 | 560352 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 59 | 1632000 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 168 | 4475930 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 183840 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7242000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 355 | 9233000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7670000 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1444 | 35576067
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 879 | 21105454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 323 | 8186112 | Plant is in standby due to scarcity of fuel gas
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 266400 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 491040 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1185 | 20072726 | Coal Unloading problem due to bad weather
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2478 | 51033732
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 279 | 2625192 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 10 | 203195 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2873000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1100 | 26203636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5375750 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 268 | 5062000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3916 | -
Barishal Area Total |  |  |  |  | 2236 | 1997 | 42346689.36
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 31 | 207187 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 12 | 65695 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 189 | 3102909 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 190 | 4522373 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Plant is in Standby as per NLDC request.
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 405 | 9123054 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 97443 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 652656 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 25 | 437088 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 34272 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 21000 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1417 | 32486545 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 249000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 691160 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2430 | 51690382
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 48 | 1124072 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4477000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 1361625 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 36797.28 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1629787 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 165057 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1174320 | -
Rangpur Area Total |  |  |  |  | 950 | 461 | 9968658.28
Eastern Grid Total |  |  |  |  | 16705.895 | 8271.7 | 186751408.54
Western Grid Total |  |  |  |  | 10378.16 | 7366 | 155039461.64
National Grid Total |  |  |  |  | 27084.055 | 15637.7 | 341790870.18
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 22-06-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10126.92 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4845 | MW
i) Dhaka area |  |  | 5479.85 |  | MW | i) Khulna area |  |  |  | 1863 | MW
ii) Chattogram area |  |  | 1417.5 |  | MW | ii) Barishal area |  |  |  | 453 | MW
iii) Cumilla area |  |  | 1421.57 |  | MW | iii) Rajshahi area |  |  |  | 1516 | MW
iv) Mymensingh area |  |  | 1153 |  | MW | iv) Rangpur area |  |  |  | 1013 | MW
v) Sylhet area |  |  | 655 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14971.92 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 86 | 19:30 | 133 | Patuakhali | 78 | 21:00
2 | AKSML | 71 | 02:00 | 68 | Jaldhaka | 88 | 21:00 | 134 | Payra | 32 | 00:00
3 | Aftabnagar | 42 | 13:00 | 69 | Jamalpur | 136 | 00:00 | 135 | Postogola | 59 | 18:30
4 | Agargaon | 138 | 13:00 | 70 | Jashore | 150 | 19:30 | 136 | Purbachal | 22 | 00:00
5 | Agrabad | 90 | 19:00 | 71 | Jhenaidah | 134 | 00:00 | 137 | Purbasadipur | 142 | 00:00
6 | Amnura | 41 | 00:00 | 72 | Joydebpur | 149 | 19:30 | 138 | Rahanpur | 34 | 00:00
7 | Ashuganj | 108 | 00:00 | 73 | Joypurhat | 66 | 22:00 | 139 | Rahim | 41 | 16:00
8 | BSRM | 207 | 01:00 | 74 | Juldah | 15 | 13:00 | 140 | Rajbari | 88 | 19:30
9 | Bagerhat | 86 | 00:00 | 75 | KSRM | 23 | 15:00 | 141 | Rajendrapur | 140 | 21:00
10 | Bajitpur | 58 | 21:00 | 76 | Kabirpur | 261 | 12:00 | 142 | Rajshahi | 121 | 00:00
11 | Bakulia | 92 | 16:00 | 77 | Kachua | 94 | 23:00 | 143 | Rajshahi-230 | 89 | 21:00
12 | Banani | 22 | 13:00 | 78 | Kallyanpur | 105 | 00:00 | 144 | Ramganj | 120 | 22:00
13 | Bangabhaban | 20 | 14:00 | 79 | Kalurghat | 38 | 12:00 | 145 | Rampur | 40 | 00:00
14 | Barapukuria | 74 | 21:00 | 80 | Kamrangirchar | 65.8 | 13:00 | 146 | Rangamati | 19 | 19:00
15 | Barguna | 22 | 21:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 159 | 22:00
16 | Barishal | 115 | 20:00 | 82 | Kasba | 39 | 22:00 | 148 | Ruppur | 7.4 | 16:00
17 | Barishal-230 | 104 | 23:00 | 83 | Kazla | 84 | 23:00 | 149 | SSM | 14 | 03:00
18 | Baroaulia | 62 | 10:00 | 84 | Keranigonj | 87 | 20:00 | 150 | Saidpur | 116 | 23:00
19 | Baroirhat | 62 | 21:00 | 85 | Khagrachori | 34 | 20:00 | 151 | Satkhira | 136 | 01:00
20 | Bashundhara | 193 | 14:00 | 86 | Khulna | 77 | 23:00 | 152 | Satmasjid | 105 | 14:00
21 | BashundharaCement | 9 | 11:00 | 87 | Khulshi | 161 | 10:00 | 153 | Savar | 230 | 12:00
22 | Beanibazar | 86 | 20:00 | 88 | Kishoreganj | 152 | 22:00 | 154 | SevenRings | 17.12 | 16:00
23 | Benapole | 74 | 00:00 | 89 | Kodda | 302 | 23:00 | 155 | ShahCement | 32 | 04:00
24 | Bhaluka | 151 | 19:00 | 90 | Kulaura | 53 | 00:00 | 156 | Shahjadpur | 84 | 21:00
25 | Bhandaria | 55 | 22:00 | 91 | Kurigram | 68 | 21:00 | 157 | Shahjibazar | 138 | 23:00
26 | Bhangura | 48 | 22:00 | 92 | Kushtia | 166 | 21:00 | 158 | Shahmirpur | 64 | 16:00
27 | Bheramara(GK) | 71 | 20:00 | 93 | Lalbag | 54 | 18:30 | 159 | Shariatpur | 96 | 23:00
28 | Bhulta | 241 | 22:00 | 94 | Lalmonirhat | 71 | 19:30 | 160 | Sherpur | 162 | 00:00
29 | Bog-Sherpur | 70 | 00:00 | 95 | MI_Cement | 17.7 | 16:00 | 161 | Shikalbaha | 13 | 15:00
30 | Bogura | 178 | 21:00 | 96 | Madanganj | 38 | 20:00 | 162 | Shitalakhya | 87.5 | 16:00
31 | Borhanuddin | 92 | 21:00 | 97 | Madaripur | 118 | 23:00 | 163 | Sholosohor | 46 | 15:00
32 | Brahmanbaria | 138 | 22:00 | 98 | Madartek | 93.76 | 00:00 | 164 | Shyampur | 152 | 10:00
33 | Cantonment | 162 | 13:00 | 99 | Madunaghat | 55 | 14:00 | 165 | Siddhirganj | 119 | 16:00
34 | Chandina | 17.17 | 23:00 | 100 | Magura | 68 | 00:00 | 166 | Sirajganj | 106 | 21:00
35 | Chandpur | 82 | 00:00 | 101 | Mahasthangarh | 84 | 00:00 | 167 | Sonargaon | 108 | 00:00
36 | Chandraghona | 37 | 19:30 | 102 | Manikganj | 132 | 20:00 | 168 | Sreemongol | 85 | 23:00
37 | Chapai | 81 | 19:30 | 103 | Maniknagar | 86 | 13:00 | 169 | Sreepur | 106 | 21:00
38 | Charsaidpur | 50 | 12:00 | 104 | Matarbari | 50 | 19:30 | 170 | Srinagar | 51.99 | 22:00
39 | Chauddagram | 72 | 19:00 | 105 | Matuail | 63 | 23:00 | 171 | Sunamganj | 65 | 22:00
40 | Chhatak | 38 | 23:00 | 106 | Millgate | 99 | 15:00 | 172 | Sylhet | 52 | 19:30
41 | Chowmuhani | 207 | 19:00 | 107 | Mirpur | 125 | 19:00 | 173 | Sylhet-132 | 133 | 19:00
42 | Chuadanga | 126 | 00:00 | 108 | Mirsorai | 11 | 11:00 | 174 | TK | 31 | 00:00
43 | Coxsbazar | 131 | 19:30 | 109 | Mirzapur | 42 | 21:00 | 175 | Tangail | 190 | 19:30
44 | Cumilla(N) | 163 | 01:00 | 110 | Mithapukur | 72 | 01:00 | 176 | Thakurgaon | 116 | 22:00
45 | Cumilla(S) | 166 | 17:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 136 | 11:00
46 | Daudkandi | 150 | 19:30 | 112 | Mogbazar | 161.3 | 12:00 | 178 | Ullahpara | 41 | 19:00
47 | Dhaka | 74 | 13:00 | 113 | Mongla | 35 | 15:00 | 179 | Ullon | 41 | 00:00
48 | Dhamrai | 134 | 23:00 | 114 | Motijheel | 43 | 13:00 | 180 | Uttara | 101 | 11:00
49 | Dhanmondi | 160 | 13:00 | 115 | Muktagacha | 37 | 00:00 | 181 | UttaraNew | 64 | 23:00
50 | Dohazari | 107 | 19:30 | 116 | Munshiganj | 122 | 23:00 | 182 | Zigatola | 78 | 16:00
51 | Faridpur | 170 | 00:00 | 117 | Muradnagar | 33 | 23:00
52 | Fatullah | 103 | 15:00 | 118 | Mymensingh | 214 | 00:00
53 | Fenchuganj | 50 | 19:00 | 119 | Naogaon | 141 | 23:00
54 | Feni | 118 | 22:00 | 120 | Narail | 60.5 | 20:00
55 | GPH | 78 | 21:00 | 121 | Narinda | 74 | 12:00
56 | Ghatail | 80 | 21:00 | 122 | Narshingdi | 193 | 22:00
57 | Ghorashal | 16 | 00:00 | 123 | Natore | 156 | 23:00
58 | Ghorashal-230 | 91 | 22:00 | 124 | Nawabganj | 66.4 | 22:00
59 | Goalpara | 40 | 00:00 | 125 | Netrakona | 144 | 20:00
60 | Gollamari | 96 | 19:30 | 126 | New Tongi | 88 | 15:00
61 | Gopalganj | 114 | 20:00 | 127 | Niamatpur | 78 | 21:00
62 | Gulshan | 154 | 13:00 | 128 | Noapara | 49 | 00:00
63 | Halishahar | 80 | 15:00 | 129 | PHP | 9 | 13:00
64 | HaripurSBU | 170 | 00:00 | 130 | Pabna | 131 | 19:30
65 | Hasnabad | 69 | 20:00 | 131 | Palashbari | 120 | 18:00
66 | Hathazari | 82 | 23:00 | 132 | Panchagarh | 65 | 23:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 22-06-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15531.95 | 33 |  | 15566.44
1:00 | 15133.36 | 50 |  | 15185.36
2:00 | 14424.6 | 39 |  | 14465.6
3:00 | 14083.95 | 0 |  | 14083.95
4:00 | 13810.22 | 0 |  | 13810.22
5:00 | 13425.94 | 0 |  | 13425.94
6:00 | 12694.97 | 0 |  | 12694.97
7:00 | 12672.11 | 0 |  | 12672.11
8:00 | 12567.75 | 0 |  | 12567.75
9:00 | 12940.26 | 0 |  | 12940.26
10:00 | 13262 | 0 |  | 13262
11:00 | 13392.02 | 0 |  | 13392.02
12:00 | 13850.4 | 0 |  | 13850.4
13:00 | 14107.7 | 0 |  | 14107.7
14:00 | 14403.9 | 0 |  | 14403.9
15:00 | 14463.9 | 0 |  | 14463.9
16:00 | 14412.99 | 0 |  | 14412.99
17:00 | 14029.53 | 0 |  | 14029.53
18:00 | 13416.23 | 0 |  | 13416.23
19:00 | 14676.7 | 0 |  | 14676.7
19:30 | 15637.7 | 0 |  | 15637.7
20:00 | 15590.7 | 38 |  | 15630.41
21:00 | 15545.53 | 34 |  | 15581.06
22:00 | 15262.61 | 42 |  | 15306.61
23:00 | 15207.94 | 51 |  | 15260.94
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 22-06-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8800.2 | 6731.75 | 15531.95 | DAILY GENERATION CURVE
00:30 | 8737.7 | 6594.955 | 15332.655
01:00 | 8675.2 | 6458.16 | 15133.36 | 22-06-2025
01:30 | 8443.7 | 6335.28 | 14778.98
02:00 | 8212.2 | 6212.4 | 14424.6
02:30 | 8065.7 | 6188.575 | 14254.275
03:00 | 7919.2 | 6164.75 | 14083.95
03:30 | 7827.7 | 6119.385 | 13947.085
04:00 | 7736.2 | 6074.02 | 13810.22
04:30 | 7601.2 | 6016.88 | 13618.08
05:00 | 7466.2 | 5959.74 | 13425.94
05:30 | 7210.505 | 5849.95 | 13060.455
06:00 | 6954.81 | 5740.16 | 12694.97
06:30 | 6932.225 | 5751.315 | 12683.54
07:00 | 6909.64 | 5762.47 | 12672.11
07:30 | 6801.17 | 5818.76 | 12619.93
08:00 | 6692.7 | 5875.05 | 12567.75
08:30 | 6835.645 | 5918.36 | 12754.005
09:00 | 6978.59 | 5961.67 | 12940.26
09:30 | 7067.195 | 6033.935 | 13101.13
10:00 | 7155.8 | 6106.2 | 13262
10:30 | 7204.755 | 6122.255 | 13327.01
11:00 | 7253.71 | 6138.31 | 13392.02
11:30 | 7387.345 | 6233.865 | 13621.21
12:00 | 7520.98 | 6329.42 | 13850.4
12:30 | 7648.705 | 6330.345 | 13979.05
13:00 | 7776.43 | 6331.27 | 14107.7
13:30 | 7827.905 | 6427.895 | 14255.8
14:00 | 7879.38 | 6524.52 | 14403.9
14:30 | 7900.135 | 6533.765 | 14433.9
15:00 | 7920.89 | 6543.01 | 14463.9
15:30 | 7954.75 | 6483.695 | 14438.445
16:00 | 7988.61 | 6424.38 | 14412.99
16:30 | 7844.815 | 6376.445 | 14221.26
17:00 | 7701.02 | 6328.51 | 14029.53
17:30 | 7531.035 | 6191.845 | 13722.88
18:00 | 7361.05 | 6055.18 | 13416.23
18:30 | 7562.375 | 6484.09 | 14046.465
19:00 | 7763.7 | 6913 | 14676.7
19:30 | 8271.7 | 7366 | 15637.7
20:00 | 8258.7 | 7332 | 15590.7
20:30 | 8240.7 | 7327.415 | 15568.115 |  | Executive Engineer
21:00 | 8222.7 | 7322.83 | 15545.53 |  | Network Operation Division
21:30 | 8143.2 | 7260.87 | 15404.07
22:00 | 8063.7 | 7198.91 | 15262.61
22:30 | 8088.2 | 7147.075 | 15235.275
23:00 | 8112.7 | 7095.24 | 15207.94

## En-Curve
QF-LDC-12
Date | 22-06-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3881 | 2239 | 879 | 38 | 42 | 1453.75 | 182 | 3846 | 0 | 672 | 2286.2 | 0 | 0 | 13 | 33 | DAILY ENERGY CURVE
00:30 | 3879 | 2239.5 | 879 | 38 | 40 | 1446.955 | 182 | 3711 | 0 | 633 | 2272.7 | 0 | 0 | 11.5 | 41.5 | 22-06-2025
01:00 | 3877 | 2240 | 879 | 38 | 38 | 1440.16 | 182 | 3576 | 0 | 594 | 2259.2 | 0 | 0 | 10 | 50
01:30 | 3894.5 | 2237.5 | 879.5 | 38 | 38 | 1453.28 | 182 | 3615.5 | 0 | 468 | 1966.2 | 0 | 0 | 6.5 | 44.5 | Energy Generated | 341.7909 |  | MKWHr
02:00 | 3912 | 2235 | 880 | 38 | 38 | 1466.4 | 182 | 3655 | 0 | 342 | 1673.2 | 0 | 0 | 3 | 39 | Energy not Served | 0.287 |  | MKWHr
02:30 | 3918.5 | 2239.5 | 880 | 38 | 38 | 1459.575 | 182 | 3658.5 | 0 | 321 | 1512.2 | 0 | 0 | 7 | 19.5 | Total Energy Requirement | 342.0779 |  | MKWHr
03:00 | 3925 | 2244 | 880 | 38 | 38 | 1452.75 | 182 | 3662 | 0 | 300 | 1351.2 | 0 | 0 | 11 | 0
03:30 | 3873.5 | 2237.5 | 879.5 | 38 | 38 | 1449.885 | 182 | 3658 | 0 | 277 | 1304.7 | 0 | 0 | 9 | 0
04:00 | 3822 | 2231 | 879 | 38 | 38 | 1447.02 | 182 | 3654 | 0 | 254 | 1258.2 | 0 | 0 | 7 | 0
04:30 | 3811.5 | 2233 | 879 | 38 | 37 | 1401.38 | 182 | 3611.5 | 0 | 235 | 1180.7 | 0 | 0 | 9 | 0
05:00 | 3801 | 2235 | 879 | 38 | 36 | 1355.74 | 182 | 3569 | 0 | 216 | 1103.2 | 0 | 0 | 11 | 0
05:30 | 3783.5 | 2210.5 | 879 | 38 | 30 | 1306.75 | 182 | 3504 | 7.105 | 210.5 | 902.1 | 0 | 0 | 7 | 0
06:00 | 3766 | 2186 | 879 | 38 | 24 | 1257.76 | 182 | 3439 | 14.21 | 205 | 701 | 0 | 0 | 3 | 0
06:30 | 3780 | 2181.5 | 879.5 | 38 | 29 | 1262.325 | 182 | 3435 | 37.715 | 204.5 | 649 | 0 | 0 | 5 | 0
07:00 | 3794 | 2177 | 880 | 38 | 34 | 1266.89 | 182 | 3431 | 61.22 | 204 | 597 | 0 | 0 | 7 | 0
07:30 | 3808.5 | 2127.5 | 880 | 38 | 31 | 1274.24 | 182 | 3390 | 115.69 | 181 | 582.5 | 0 | 0 | 9.5 | 0
08:00 | 3823 | 2078 | 880 | 38 | 28 | 1281.59 | 182 | 3349 | 170.16 | 158 | 568 | 0 | 0 | 12 | 0
08:30 | 3926 | 2090.5 | 880 | 38 | 28 | 1284.015 | 182 | 3335 | 190.99 | 183.5 | 606 | 0 | 0 | 10 | 0
09:00 | 4029 | 2103 | 880 | 38 | 28 | 1286.44 | 182 | 3321 | 211.82 | 209 | 644 | 0 | 0 | 8 | 0
09:30 | 4033.5 | 2163.5 | 879.5 | 38 | 29 | 1276.62 | 182 | 3308 | 312.51 | 208.5 | 656.5 | 0 | 0 | 13.5 | 0
10:00 | 4038 | 2224 | 879 | 38 | 30 | 1266.8 | 182 | 3295 | 413.2 | 208 | 669 | 0 | 0 | 19 | 0
10:30 | 4049.5 | 2220 | 879.5 | 38 | 31 | 1248.455 | 177 | 3283 | 461.555 | 208 | 711 | 0 | 0 | 20 | 0
11:00 | 4061 | 2216 | 880 | 38 | 32 | 1230.11 | 172 | 3271 | 509.91 | 208 | 753 | 0 | 0 | 21 | 0
11:30 | 4071.5 | 2222.5 | 880 | 38 | 32 | 1234.725 | 172 | 3405.5 | 521.985 | 217 | 810.5 | 0 | 0 | 15.5 | 0
12:00 | 4082 | 2229 | 880 | 38 | 32 | 1239.34 | 172 | 3540 | 534.06 | 226 | 868 | 0 | 0 | 10 | 0
12:30 | 4073.5 | 2233 | 880 | 38 | 32 | 1252.555 | 172 | 3580.5 | 505.995 | 242.5 | 961 | 0 | 0 | 8 | 0
13:00 | 4065 | 2237 | 880 | 38 | 32 | 1265.77 | 172 | 3621 | 477.93 | 259 | 1054 | 0 | 0 | 6 | 0
13:30 | 4006 | 2237 | 880 | 38 | 32 | 1315.385 | 172 | 3669.5 | 514.915 | 281.5 | 1100.5 | 0 | 0 | 9 | 0
14:00 | 3947 | 2237 | 880 | 38 | 32 | 1365 | 172 | 3718 | 551.9 | 304 | 1147 | 0 | 0 | 12 | 0
14:30 | 3945.5 | 2236 | 880.5 | 38 | 31 | 1375.5 | 172 | 3773 | 473.9 | 306 | 1180.5 | 0 | 0 | 22 | 0
15:00 | 3944 | 2235 | 881 | 38 | 30 | 1386 | 172 | 3828 | 395.9 | 308 | 1214 | 0 | 0 | 32 | 0
15:30 | 3950.5 | 2225.5 | 880.5 | 38 | 33 | 1371 | 172 | 3832.5 | 332.345 | 324 | 1245.6 | 0 | 0 | 33.5 | 0
16:00 | 3957 | 2216 | 880 | 38 | 36 | 1356 | 172 | 3837 | 268.79 | 340 | 1277.2 | 0 | 0 | 35 | 0
16:30 | 3922.5 | 2211.35 | 880 | 38 | 35 | 1356.5 | 172 | 3862.5 | 192.71 | 330 | 1191.7 | 0 | 0 | 29 | 0
17:00 | 3888 | 2206.7 | 880 | 38 | 34 | 1357 | 172 | 3888 | 116.63 | 320 | 1106.2 | 0 | 0 | 23 | 0
17:30 | 3892.5 | 2207.85 | 880 | 38 | 32 | 1312 | 172 | 3711 | 71.43 | 310 | 1073.6 | 0 | 0 | 22.5 | 0
18:00 | 3897 | 2209 | 880 | 38 | 30 | 1267 | 172 | 3534 | 26.23 | 300 | 1041 | 0 | 0 | 22 | 0
18:30 | 3941.5 | 2202.75 | 879.5 | 38 | 34 | 1335.5 | 172 | 3779 | 13.115 | 430 | 1204.6 | 0 | 0 | 16.5 | 0
19:00 | 3986 | 2196.5 | 879 | 38 | 38 | 1404 | 172 | 4024 | 0 | 560 | 1368.2 | 0 | 0 | 11 | 0
19:30 | 4014 | 2207.5 | 879 | 38 | 36 | 1417 | 172 | 4260 | 0 | 675 | 1923.2 | 0 | 0 | 16 | 0
20:00 | 4036 | 2196.5 | 879 | 38 | 34 | 1406 | 172 | 4253 | 0 | 748 | 1810.2 | 0 | 0 | 18 | 38
20:30 | 4037 | 2199.5 | 879.5 | 38 | 32 | 1415.415 | 172 | 4275 | 0 | 726.5 | 1778.7 | 0 | 0 | 14.5 | 36
21:00 | 4038 | 2202.5 | 880 | 38 | 30 | 1424.83 | 172 | 4297 | 0 | 705 | 1747.2 | 0 | 0 | 11 | 34
21:30 | 3943 | 2180 | 879.5 | 38 | 33 | 1418.37 | 172 | 4298 | 0 | 692.5 | 1742.2 | 0 | 0 | 7.5 | 38
22:00 | 3848 | 2157.5 | 879 | 38 | 36 | 1411.91 | 172 | 4299 | 0 | 680 | 1737.2 | 0 | 0 | 4 | 42
22:30 | 3853 | 2171 | 879.5 | 38 | 37 | 1411.075 | 172 | 4280 | 0 | 677 | 1711.2 | 0 | 0 | 5.5 | 46.5
23:00 | 3858 | 2184.5 | 880 | 38 | 38 | 1410.24 | 172 | 4261 | 0 | 674 | 1685.2 | 0 | 0 | 7 | 51
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 22-06-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 385 | 06:00 | 373 | 15:00 | Payra | 413 | 06:00 | 409 | 01:00
Ashuganj | 408 | 6:00 | 375 | 15:00 | Rahanpur | 394 | 18:00 | 382 | 21:00
Bhulta | 404 | 06:00 | 370 | 15:00 | Rampal | 402 | 08:00 | 389 | 21:00
Bibiana | 390 | 07:00 | 382 | 15:00
BIPTC | 402 | 08:00 | 389 | 23:00
Bogura | 381 | 06:00 | 367 | 21:00
Gopalganj | 398 | 06:00 | 387 | 21:00
Kaliakoir | 375 | 04:00 | 362 | 15:00
Madunaghat | 397 | 00:00 | 389 | 15:00
Meghnaghat | 387 | 07:00 | 377 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 225 | 07:00 | 215 | 12:00 | Keranigonj | 223 | 06:00 | 214 | 12:00
AKSML | 232 | 01:00 | 223 | 10:00 | Khulna(S) | 231 | 08:00 | 219 | 19:30
Aminbazar | 226 | 07:00 | 216 | 15:00 | Madunaghat | 235 | 00:00 | 226 | 12:00
Ashuganj | 236 | 06:00 | 222 | 15:00 | Madunaghat-400 | 236 | 00:00 | 227 | 10:00
Ashuganj-400 | 236 | 06:00 | 222 | 15:00 | Maniknagar | 220 | 04:00 | 213 | 12:00
Baghabari | 234 | 05:00 | 225 | 21:00 | Meghnaghat | 231 | 04:00 | 221 | 12:00
Barapukuria | 221 | 05:00 | 215 | 17:00 | Meghnaghat-400 | 225 | 07:00 | 217 | 13:00
Barapukuria-230 | 221 | 05:00 | 215 | 17:00 | Mirsorai | 228 | 00:00 | 220 | 15:00
Barishal | 234 | 06:00 | 226 | 22:00 | Rajshahi | 234 | 05:00 | 223 | 21:00
Bheramara | 235 | 05:00 | 223 | 19:30 | Rampal | 230 | 08:00 | 218 | 22:00
Bhulta | 235 | 06:00 | 213 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 230 | 05:00 | 222 | 15:00 | Rampura | 235 | 06:00 | 210 | 15:00
BIPTC | 236 | 05:00 | 223 | 21:00 | Shikalbaha | 235 | 00:00 | 223 | 11:00
Bogura | 231 | 06:00 | 222 | 21:00 | Shyampur | 222 | 04:00 | 215 | 12:00
Bogura-400 | 231 | 06:00 | 223 | 21:00 | Siddhirganj | 220 | 04:00 | 215 | 13:00
Borhanuddin | 239 | 06:00 | 233 | 22:00 | Sirajgonj | 238 | 06:00 | 233 | 00:00
BSRM | 227 | 01:00 | 220 | 16:00 | Sreepur | 230 | 04:00 | 219 | 19:00
Cumilla(N) | 224 | 06:00 | 216 | 12:00 | Tongi | 229 | 04:00 | 214 | 15:00
Faridpur | 232 | 06:00 | 223 | 21:00
Fenchuganj | 233 | 19:00 | 224 | 01:00
Ghorashal | 230 | 00:00 | 220 | 15:00
Ghorashal-230 | 231 | 05:00 | 212 | 15:00
Gopalganj | 234 | 06:00 | 226 | 19:30
GPH | 232 | 01:00 | 222 | 15:00
Haripur | 221 | 04:00 | 214 | 00:00
Hasnabad | 224 | 07:00 | 214 | 15:00
Hathazari | 236 | 00:00 | 224 | 15:00
Ishurdi | 236 | 05:00 | 225 | 21:00
Jhenaidah | 230 | 10:00 | 216 | 21:00
Kaliakoir | 231 | 01:00 | 220 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 06:00 | 121 | 12:00 | Madartek | 136 | 05:00 | 121 | 14:00
Agargaon | 132 | 07:00 | 124 | 12:00 | Madunaghat | 133 | 00:00 | 127 | 12:00
Agrabad | 135 | 00:00 | 127 | 08:00 | Magura | 132 | 09:00 | 121 | 21:00
AKS | 131 | 00:00 | 126 | 10:00 | Mahasthangarh | 133 | 10:00 | 125 | 21:00
Aminbazar | 132 | 05:00 | 126 | 12:00 | Manikganj | 131 | 07:00 | 121 | 15:00
Amnura | 136 | 00:00 | 122 | 00:00 | Maniknagar | 131 | 04:00 | 125 | 13:00
Ashuganj | 137 | 05:00 | 132 | 15:00 | Matarbari | 120 | 00:00 | 111 | 19:00
Bagerhat | 133 | 07:00 | 120 | 23:00 | Matuail | 128 | 05:00 | 123 | 17:00
Bajitpur | 131 | 05:00 | 123 | 19:00 | Millgate | 134 | 03:00 | 122 | 15:00
Bakulia | 136 | 00:00 | 128 | 11:00 | Mirpur | 130 | 02:00 | 125 | 11:00
Banani | 137 | 05:00 | 121 | 13:00 | Mirzapur | 131 | 05:00 | 123 | 21:00
Bangabhaban | 132 | 07:00 | 125 | 12:00 | Mithapukur | 129 | 10:00 | 118 | 21:00
Barapukuria | 135 | 05:00 | 125 | 12:00 | MI_Cement | 127.9 | 06:00 | 123 | 12:00
Barguna | 135 | 05:00 | 130 | 19:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 135 | 05:00 | 130 | 01:00 | Mogbazar | 138 | 06:00 | 123 | 12:00
Barishal-230 | 136 | 05:00 | 130 | 22:00 | Mongla | 132 | 05:00 | 121 | 23:00
Baroaulia | 135 | 00:00 | 128 | 10:00 | Motijheel | 132 | 07:00 | 125 | 12:00
Baroirhat | 126 | 07:00 | 118 | 15:00 | Muktagacha | 138 | 17:00 | 128 | 21:00
Bashundhara | 137 | 06:00 | 121 | 15:00 | Munshiganj | 127 | 07:00 | 121 | 12:00
BashundharaCement | 127 | 09:00 | 122 | 11:00 | Muradnagar | 125 | 06:00 | 120 | 11:00
Beanibazar | 128 | 05:00 | 122 | 19:00 | Mymensingh | 136 | 17:00 | 114 | 19:30
Benapole | 131 | 09:00 | 119 | 23:00 | Naogaon | 132 | 18:00 | 123 | 21:00
Bhaluka | 131 | 06:00 | 122 | 19:00 | Narail | 132 | 07:00 | 119 | 19:30
Bhandaria | 134 | 06:00 | 119 | 02:00 | Narinda | 131 | 04:00 | 125 | 13:00
Bhangura | 133 | 06:00 | 127 | 22:00 | Narshingdi | 137 | 06:00 | 116 | 00:00
Bheramara | 137 | 04:00 | 132 | 21:00 | Natore | 134 | 03:00 | 127 | 21:00
Bheramara(GK) | 137 | 05:00 | 132 | 00:00 | Nawabganj | 133 | 05:00 | 126 | 12:00
Bhulta | 123 | 06:00 | 118 | 12:00 | Netrakona | 127 | 06:00 | 111 | 19:30
Bog-Sherpur | 134 | 10:00 | 127 | 21:00 | New | 136 | 03:00 | 123 | 14:00
Bogura | 136 | 07:00 | 129 | 21:00 | Niamatpur | 133 | 18:00 | 127 | 21:00
Bogura-230 | 136 | 06:00 | 129 | 21:00 | Noapara | 135 | 09:00 | 124 | 23:00
Brahmanbaria | 132 | 05:00 | 125 | 12:00 | Pabna | 134 | 08:00 | 128 | 19:30
Cantonment | 132 | 05:00 | 123 | 12:00 | Palashbari | 129 | 10:00 | 117 | 21:00
Chandina | 127 | 06:00 | 121 | 15:00 | Panchagarh | 140 | 05:00 | 114 | 12:00
Chandpur | 127 | 18:30 | 117 | 00:00 | Patuakhali | 134 | 04:00 | 131 | 16:00
Chandraghona | 133 | 00:00 | 128 | 10:00 | Payra | 136 | 08:00 | 133 | 12:00
Chapai | 130 | 18:00 | 123 | 00:00 | PHP | 123 | 18:30 | 116 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 128 | 07:00 | 123 | 12:00 | Postogola | 130 | 02:00 | 124 | 12:00
Chauddagram | 123 | 05:00 | 117 | 15:00 | Purbachal | 137 | 05:00 | 122 | 12:00
Chhatak | 129 | 06:00 | 120 | 19:00 | Purbasadipur | 132 | 05:00 | 113 | 12:00
Chowmuhani | 119 | 18:00 | 109 | 15:00 | Rahanpur | 134 | 06:00 | 129 | 00:00
Chuadanga | 132 | 06:00 | 119 | 21:00 | Rahanpur-400 | 134 | 06:00 | 130 | 00:00
Coxsbazar | 121 | 17:00 | 114 | 22:00 | Rahim | 128 | 02:00 | 124 | 13:00
Cumilla(N) | 128 | 07:00 | 122 | 12:00 | Rajbari | 136 | 06:00 | 129 | 00:00
Cumilla(S) | 131 | 04:00 | 120 | 11:00 | Rajendrapur | 134 | 23:00 | 120 | 15:00
Daudkandi | 125 | 08:00 | 117 | 12:00 | Rajshahi | 134 | 06:00 | 129 | 15:00
Dhaka | 137 | 04:00 | 123 | 12:00 | Rajshahi-230 | 135 | 05:00 | 116 | 00:00
Dhamrai | 131 | 03:00 | 122 | 15:00 | Ramganj | 121 | 18:00 | 112 | 15:00
Dhanmondi | 137 | 06:00 | 123 | 12:00 | Rampur | 134 | 00:00 | 127 | 09:00
Dohazari | 131 | 01:00 | 124 | 08:00 | Rampura | 137 | 06:00 | 122 | 12:00
Faridpur | 136 | 06:00 | 131 | 00:00 | Rangamati | 132 | 01:00 | 127 | 15:00
Fatullah | 128 | 04:00 | 123 | 12:00 | Rangpur | 128 | 20:00 | 118 | 17:00
Fenchuganj | 135 | 08:00 | 131 | 20:00 | Ruppur | 137 | 03:00 | 132 | 19:30
Feni | 122 | 06:00 | 115 | 12:00 | Saidpur | 131 | 05:00 | 117 | 12:00
Ghatail | 131 | 07:00 | 122 | 21:00 | Satkhira | 136 | 09:00 | 121 | 22:00
Ghorashal | 137 | 06:00 | 127 | 16:00 | Satmasjid | 131 | 04:00 | 123 | 13:00
Goalpara | 137 | 08:00 | 127 | 23:00 | Savar | 130 | 06:00 | 125 | 11:00
Gollamari | 137 | 06:00 | 128 | 22:00 | SevenRings | 137 | 01:00 | 126 | 15:00
Gopalganj | 135 | 06:00 | 128 | 19:30 | ShahCement | 128 | 07:00 | 123 | 12:00
Gopalganj-400 | 137 | 06:00 | 132 | 19:30 | Shahjadpur | 135 | 03:00 | 131 | 21:00
Gulshan | 136 | 05:00 | 122 | 12:00 | Shahjibazar | 133 | 07:00 | 125 | 15:00
Halishahar | 137 | 00:00 | 127 | 09:00 | Shahmirpur | 136 | 00:00 | 127 | 07:00
Haripur | 129 | 05:00 | 124 | 12:00 | Shariatpur | 135 | 06:00 | 128 | 23:00
HaripurSBU | 129 | 05:00 | 114 | 22:00 | Sherpur | 136 | 05:00 | 127 | 00:00
Hasnabad | 130 | 03:00 | 125 | 12:00 | Shikalbaha | 124 | 00:00 | 117 | 08:00
Hathazari | 136 | 00:00 | 130 | 11:00 | Shikalbaha-230 | 137 | 01:00 | 129 | 10:00
Ishurdi | 138 | 08:00 | 132 | 21:00 | Shitalakhya | 128 | 06:00 | 123 | 12:00
Jaldhaka | 129 | 04:00 | 115 | 12:00 | Sholosohor | 136 | 01:00 | 126 | 15:00
Jamalpur | 138 | 12:00 | 129 | 21:00 | Shyampur | 127 | 00:00 | 125 | 09:00
Jashore | 135 | 10:00 | 119 | 19:30 | Shyampur-230 | 128 | 08:00 | 122 | 13:00
Jhenaidah | 135 | 09:00 | 122 | 19:30 | Siddhirganj | 129 | 04:00 | 124 | 12:00
Jhenaidah-230 | 136 | 10:00 | 126 | 19:30 | Sirajganj | 132 | 06:00 | 126 | 19:00
Joydebpur | 135 | 23:00 | 122 | 15:00 | Sonargaon | 126 | 01:00 | 121 | 12:00
Joypurhat | 131 | 18:00 | 120 | 21:00 | Sreemongol | 132 | 06:00 | 125 | 19:30
Juldah | 137 | 00:00 | 128 | 07:00 | Sreepur | 133 | 04:00 | 125 | 19:00
Kabirpur | 133 | 05:00 | 120 | 15:00 | Srinagar | 133 | 04:00 | 127 | 12:00
Kachua | 125 | 18:30 | 118 | 13:00 | SSM | 139 | 00:00 | 131 | 08:00
Kaliakoir | 133 | 01:00 | 125 | 15:00 | Sunamganj | 127 | 08:00 | 118 | 21:00
Kallyanpur | 132 | 04:00 | 126 | 12:00 | Sylhet | 129 | 06:00 | 125 | 19:30
Kalurghat | 134 | 01:00 | 127 | 15:00 | Sylhet-132 | 130 | 06:00 | 126 | 19:00
Kamrangirchar | 134 | 05:00 | 127 | 12:00 | Tangail | 128 | 03:00 | 121 | 21:00
Kaptai | 135 | 1:00 | 132 | 11:00 | Thakurgaon | 138 | 05:00 | 112 | 12:00
Kasba | 125 | 08:00 | 119 | 11:00 | TK | 132 | 00:00 | 127 | 10:00
Kazla | 131 | 04:00 | 124 | 13:00 | Tongi | 136 | 04:00 | 126 | 11:00
Keranigonj | 134 | 06:00 | 127 | 12:00 | Ullahpara | 134 | 06:00 | 128 | 21:00
Khagrachori | 131 | 00:00 | 126 | 11:00 | Ullon | 136 | 04:00 | 122 | 13:00
Khulna | 136 | 09:00 | 125 | 22:00 | Uttara | 130 | 04:00 | 125 | 11:00
Khulna(S) | 138 | 09:00 | 128 | 23:00 | UttaraNew | 131 | 05:00 | 124 | 12:00
Khulshi | 134 | 01:00 | 126 | 10:00 | Zigatola | 134 | 06:00 | 126 | 13:00
Kishoreganj | 129 | 06:00 | 120 | 19:30
Kodda | 134 | 23:00 | 119 | 15:00
KSRM | 134 | 00:00 | 127 | 10:00
Kulaura | 134 | 06:00 | 130 | 15:00
Kurigram | 126 | 05:00 | 117 | 17:00
Kushtia | 133 | 08:00 | 127 | 19:30
Lalbag | 134 | 06:00 | 126 | 12:00
Lalmonirhat | 127 | 05:00 | 117 | 17:00
Madanganj | 127 | 09:00 | 122 | 11:00
Madaripur | 136 | 05:00 | 131 | 19:30
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division