## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 24-06-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-06-2025 | during | 24-06-2025 | during | 24-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 353 | 325 | 400.75 | 400.75 | 371 | 371 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 400 | 450 | 450 | 300 | 300 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 299 | 294 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 327 | 330 | 335 | 335 | 100 | 100 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 80 | 147 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 5 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23.8 | 25 | 33 | 33 | 26.5 | 26.5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 30 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 68 | 88 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 88 | 105 | 105 | 88 | 88 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 51 | 104 | 104 | 50 | 50 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 60 | 108 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 26 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 41 | 55 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 486 | 500 | 584 | 584 | 451 | 451 | None
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 142 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2389.8 | 2788 | 5124.4 | 5188.4 | 2966.83 | 3030.83
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 14 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 172 | 172 | 172 | 172 | 172 | 172 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 216 | 215 | 215 | 214 | 214 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 5 | 46 | 105 | 105 | 94.5 | 94.5 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 40 | 72 | 72 | 72 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 65 | 65 | 65 | 65 | 65 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 62 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 3 | 12 | 2 | 20 | 2 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4 | 0 | 1.53 | 0 | 1.53 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 30 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 15 | 110 | 110 | 99 | 99 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 960 | 1127 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 7 | 23 | 48 | 52 | 48 | 52 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 205 | 201 | 575 | 575 | 200 | 200 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1752 | 2169 | 3613.25 | 3623.72 | 3185.75 | 3196.22
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 206 | 213 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 340 | 351 | 353.35 | 353.35 | 335 | 335 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 340 | 340 | 340 | 340 | 340 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 15 | 28 | 46.7 | 46.7 | 18 | 18 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 47 | 46 | 55 | 55 | 42 | 42 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 155 | 165 | 195 | 195 | 195 | 195
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 2 | 50 | 150 | 150 | 145 | 145 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 42 | 44 | 46 | 46 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 124 | 180 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 30 | 40 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 19 | 24.5 | 24.5 | 17 | 17 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 82 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 28 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 115 | 115 | 115 | 51 | 115
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 68 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1575 | 1836.2 | 2469.75 | 2399.75 | 2051.2 | 2045.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-06-2025 | during | 24-06-2025 | during | 24-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 59 | 48 | 157.5 | 157.5 | 48 | 48 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.6 | 0 | 1.6 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 120 | 175 | 200 | 200 | 160 | 160 | Fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 55 | 102 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 3.67 | 0 | 25 | 0 | 25 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 22 | 22 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 255.67 | 342 | 575.6 | 549 | 426.1 | 399.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 35 | 37 | 35 | 35 | 35 | 35 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 157 | 154 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 28 | 30 | 30 | 30 | 30 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 58 | 58 | 64 | 64 | 55 | 55 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 168 | 166 | 160 | 160 | 160 | 160 | Machine Problem
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 385 | 314 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 350 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1531 | 1420 | 1571 | 1571 | 1449 | 1449
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 879 | 880 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 46 | 46 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 284 | 258 | 410 | 410 | 280 | 280 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 34 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 97.65 | 0 | 65 | 0 | 65 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 791 | 1028 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2089.65 | 2238 | 3621.2 | 3556.2 | 3489 | 3424
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 518 | 614 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 7 | 8 | 10 | 10 | 6 | 6 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 753 | 1100 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 172 | 225 | 307 | 307 | 277 | 277 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.46 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1790.46 | 2287 | 2172 | 2171 | 2076 | 2075
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 38 | 47 | 47 | 44 | 44 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 30 | 30 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 179 | 169 | 214 | 214 | 192 | 192 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 195 | 169 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is in Standby as per NLDC request.
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 335 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 | 30 | 30 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 33 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 28 | 28 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.83 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1076.4 | 1410.45 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 26.4 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 91 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 1983.63 | 2154.45 | 3193.47 | 3026.87 | 2797.68 | 2631.08
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 46 | 48 | 48 | 48 | 48 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 190 | 187 | 150 | 150 | 150 | 150 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 98 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.8 | 0 | 4.6 | 0 | 4.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 70 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 19 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 109 | 0 | 104.78 | 0 | 104.78 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 475.8 | 446 | 599.38 | 460 | 599.38 | 460
System Total |  |  |  |  | 28565.2 | 27084.055 | 13843.01 | 15680.65 | 22940.05 | 22545.94 | 19040.94 | 18710.83
Forecast Scenario (24-06-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15560 |  | 0 |  | 15560
|  |  |  | 1:00 | 15180 |  | 0 |  | 15180
|  |  |  | 2:00 | 14460 |  | 0 |  | 14460
|  |  |  | 3:00 | 14080 |  | 0 |  | 14080
|  |  |  | 4:00 | 13810 |  | 0 |  | 13810
|  |  |  | 5:00 | 13420 |  | 0 |  | 13420
|  |  |  | 6:00 | 12690 |  | 0 |  | 12690
|  |  |  | 7:00 | 12670 |  | 0 |  | 12670
|  |  |  | 8:00 | 12560 |  | 0 |  | 12560
|  |  |  | 9:00 | 12940 |  | 0 |  | 12940
|  |  |  | 10:00 | 13260 |  | 0 |  | 13260
|  |  |  | 11:00 | 13390 |  | 0 |  | 13390
|  |  |  | 12:00 | 13850 |  | 0 |  | 13850
|  |  |  | 13:00 | 14100 |  | 0 |  | 14100
|  |  |  | 14:00 | 14400 |  | 0 |  | 14400
|  |  |  | 15:00 | 14460 |  | 0 |  | 14460
|  |  |  | 16:00 | 14410 |  | 0 |  | 14410
|  |  |  | 17:00 | 14030 |  | 0 |  | 14030
|  |  |  | 18:00 | 13410 |  | 0 |  | 13410
|  |  |  | 18:30 | 14100 |  | 0 |  | 14100
|  |  |  | 19:00 | 14670 |  | 0 |  | 14670
|  |  |  | 19:30 | 15630 |  | 0 |  | 15630
|  |  |  | 20:00 | 15630 |  | 0 |  | 15630
|  |  |  | 21:00 | 15580 |  | 0 |  | 15580
|  |  |  | 22:00 | 15300 |  | 0 |  | 15300
|  |  |  | 23:00 | 15260 |  | 0 |  | 15260
Probable Maximum Temperature: |  |  | 31.70°C
Probable Maximum Demand at Day Peak: |  |  | 13850.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 15630.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15630.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 339.12 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:06 hrs on 24-06-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 23-06-2025 | [28 empty] | Date: | 23-06-2025 | [28 empty] | Date: | 23-06-2025 | [28 empty] | Date: | 23-06-2025 | [28 empty] | Date: | 23-06-2025 | [12 empty] | Date: | 23-06-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [12 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 35 | 24 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 35 | 149 | 146 | 0 | 0 | 0 | 120 | 16 | 360 | 297 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 142 | 25.5 | 22 | 0 | 450 | 0 | 14 | 0 | 0 | 1 | 65 | 32 | 0 | 100 | 100 | 0 | 172 | 15 | 29 | 204 | 0 | 0 | 19 | 8 | 46 | 222 | 0 | 0 | 0 | 1045 | 0 | 51 | 80 | 170 | 0 | 353 | 335 | 48 | 214 | 16 | 51 | 0 | 168 | 13 | 19 | 95 | 36 | 52.2 | 0 | 45 | 295 | 320 | 347 | 34 | 30 | 150 | 8 | 0 | 59 | 15 | 0 | 0 | 166 | 17 | 85 | 165 | 72 | 0 | 0 | 0 | 8080.7 | 917 | 290 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1091 | 17 | 1404.49 | 0 | 44 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 182 | 0 | 0 | 0 | 336 | 0 | 0 | 190 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 11 | 120 | 220 | 0 | 404 | 1095 | 0 | 7108.49 | 15189.19 | 98.68
01:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 35 | 149 | 146 | 0 | 0 | 0 | 80 | 16 | 360 | 298 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 142 | 23 | 22 | 0 | 450 | 0 | 14 | 0 | 0 | 4 | 65 | 32 | 0 | 100 | 100 | 0 | 172 | 15 | 29 | 203 | 0 | 0 | 19 | 8 | 48 | 220 | 0 | 0 | 0 | 1150 | 0 | 51 | 80 | 170 | 0 | 351 | 340 | 48 | 214 | 16 | 38 | 0 | 180 | 9 | 19 | 98 | 40 | 52.2 | 0 | 39 | 305 | 320 | 341 | 34 | 30 | 155 | 8 | 0 | 59 | 15 | 0 | 0 | 168 | 17 | 85 | 148 | 72 | 0 | 0 | 0 | 8154.2 | 880 | 291 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 826 | 17 | 1414.24 | 0 | 44 | 0 | 35 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 188 | 0 | 0 | 0 | 348 | 0 | 0 | 187 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 11 | 120 | 220 | 0 | 480 | 1107 | 0 | 7020.24 | 15174.44 | 98.68
02:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 35 | 137 | 146 | 0 | 0 | 0 | 15 | 16 | 360 | 297 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 23 | 22 | 0 | 450 | 0 | 42 | 0 | 0 | 3 | 34 | 0 | 0 | 60 | 100 | 0 | 172 | 20 | 29 | 203 | 0 | 0 | 19 | 8 | 51 | 222 | 0 | 0 | 0 | 1150 | 0 | 51 | 20 | 175 | 0 | 353 | 340 | 48 | 215 | 13 | 34 | 0 | 165 | 9 | 19 | 113 | 34 | 52.2 | 0 | 45 | 305 | 320 | 338 | 34 | 30 | 150 | 8 | 0 | 59 | 30 | 0 | 0 | 168 | 17 | 85 | 141 | 72 | 0 | 0 | 0 | 7873.2 | 880 | 291 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 731 | 17 | 1412.45 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 181 | 0 | 0 | 0 | 342 | 0 | 0 | 191 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 11 | 120 | 220 | 0 | 566 | 1096 | 0 | 6828.45 | 14701.65 | 98.68
03:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 35 | 85 | 146 | 0 | 0 | 0 | 14 | 0 | 360 | 290 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 23 | 22 | 0 | 450 | 0 | 40 | 0 | 0 | 32 | 17 | 0 | 0 | 60 | 100 | 0 | 172 | 0 | 29 | 201 | 0 | 0 | 19 | 8 | 60 | 222 | 0 | 0 | 0 | 1010 | 0 | 51 | 0 | 175 | 0 | 355 | 340 | 48 | 215 | 13 | 34 | 0 | 164 | 10 | 19 | 90 | 38 | 52.2 | 0 | 45 | 310 | 320 | 332 | 34 | 30 | 149 | 8 | 0 | 60 | 30 | 0 | 0 | 168 | 17 | 85 | 148 | 72 | 0 | 0 | 0 | 7623.2 | 880 | 291 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 730 | 0 | 1301.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 181 | 0 | 0 | 0 | 330 | 0 | 0 | 188 | 48 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 11 | 114 | 220 | 0 | 602 | 1095 | 0 | 6606.83 | 14230.03 | 98.68
04:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 17 | 85 | 130 | 0 | 0 | 0 | 0 | 0 | 360 | 294 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 23 | 22 | 0 | 450 | 0 | 15 | 0 | 0 | 9 | 0 | 0 | 0 | 60 | 100 | 0 | 172 | 0 | 30 | 201 | 0 | 0 | 19 | 8 | 61 | 222 | 0 | 0 | 0 | 1024 | 0 | 51 | 0 | 175 | 0 | 355 | 340 | 48 | 215 | 11 | 34 | 0 | 163 | 9 | 19 | 92 | 38 | 52.2 | 0 | 45 | 305 | 320 | 346 | 34 | 30 | 149 | 8 | 0 | 60 | 30 | 0 | 0 | 169 | 17 | 85 | 148 | 72 | 0 | 0 | 0 | 7499.2 | 880 | 293 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 734 | 0 | 1109.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 180 | 0 | 0 | 0 | 334 | 0 | 0 | 189 | 48 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 10 | 120 | 220 | 0 | 617 | 1050 | 0 | 6403.09 | 13902.29 | 98.68
05:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 17 | 83 | 113 | 0 | 0 | 0 | 0 | 0 | 360 | 294 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 23 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 60 | 60 | 0 | 172 | 0 | 30 | 203 | 0 | 0 | 0 | 0 | 17 | 223 | 0 | 0 | 0 | 1036 | 0 | 51 | 0 | 175 | 0 | 357 | 335 | 48 | 215 | 9 | 37 | 0 | 163 | 9 | 19 | 90 | 38 | 52.2 | 0 | 45 | 305 | 320 | 349 | 34 | 30 | 151 | 8 | 0 | 60 | 30 | 0 | 0 | 169 | 17 | 75 | 148 | 71 | 0 | 0 | 0 | 7366.2 | 879 | 292 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 737 | 0 | 1117.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 183 | 0 | 0 | 0 | 339 | 0 | 0 | 186 | 47 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 9 | 116 | 220 | 0 | 498 | 1030 | 0 | 6254.9 | 13621.1 | 98.68
06:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 17 | 68 | 113 | 0 | 0 | 0 | 0 | 0 | 360 | 277 | 0 | 0 | 0 | 335 | 0 | 0 | 1 | 52 | 23 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 60 | 60 | 0 | 172 | 0 | 30 | 200 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 895 | 0 | 43 | 0 | 175 | 0 | 356 | 340 | 48 | 216 | 9 | 35 | 0 | 163 | 9 | 19 | 90 | 36 | 52.2 | 3 | 45 | 295 | 320 | 301 | 34 | 30 | 145 | 8 | 0 | 60 | 30 | 0 | 0 | 169 | 17 | 55 | 120 | 71 | 0 | 1.46 | 0 | 7044.66 | 880 | 297 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4 | 735 | 0 | 964.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1.35 | 180 | 0 | 177 | 0 | 0 | 0 | 324 | 0 | 0.09 | 190 | 47 | 115 | 1 | 34 | 0 | 0 | 0 | 14 | 0.04 | 0 | 157 | 9 | 110 | 220 | 0 | 520 | 930 | 0 | 5951.88 | 12996.54 | 98.68
07:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 2 | 17 | 68 | 113 | 0 | 0 | 0 | 0 | 0 | 300 | 287 | 0 | 0 | 0 | 335 | 0 | 0 | 3 | 35 | 22 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 60 | 60 | 0 | 172 | 0 | 23 | 200 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 926 | 4 | 43 | 0 | 175 | 0 | 357 | 340 | 48 | 215 | 11 | 34 | 0 | 163 | 9 | 19 | 94 | 32 | 52.2 | 9 | 45 | 300 | 320 | 304 | 34 | 30 | 130 | 8 | 0 | 60 | 30 | 0 | 0 | 169 | 17 | 55 | 120 | 58 | 0 | 5.25 | 0 | 7000.45 | 880 | 297 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 17 | 740 | 0 | 857.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 6.29 | 162 | 0 | 166 | 0 | 0 | 0 | 330 | 0 | 0.5 | 190 | 47 | 115 | 4 | 34 | 0 | 0 | 0 | 25 | 0.15 | 0 | 163 | 8 | 112 | 220 | 0 | 521 | 790 | 0 | 5733.62 | 12734.07 | 98.68
08:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 17 | 17 | 68 | 80 | 0 | 0 | 0 | 0 | 0 | 300 | 284 | 0 | 0 | 0 | 332 | 0 | 0 | 18 | 35 | 26 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 60 | 60 | 2 | 172 | 0 | 11 | 200 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 955 | 2 | 43 | 0 | 175 | 0 | 351 | 340 | 47 | 215 | 11 | 34 | 0 | 120 | 9 | 19 | 60 | 26 | 8 | 9 | 43 | 310 | 320 | 331 | 34 | 30 | 130 | 8 | 0 | 60 | 30 | 0 | 0 | 169 | 10 | 55 | 120 | 59 | 1 | 15.58 | 0 | 6923.58 | 879 | 298 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 53 | 737 | 0 | 876.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 6.48 | 164 | 0 | 167 | 0 | 0 | 0 | 345 | 0 | 0.7 | 191 | 48 | 70 | 5 | 34 | 0 | 0 | 0 | 58 | 0.39 | 0 | 172 | 7 | 120 | 220 | 0 | 510 | 752 | 0 | 5773.97 | 12697.55 | 98.68
09:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 17 | 48 | 68 | 80 | 0 | 0 | 5 | 0 | 0 | 300 | 305 | 0 | 0 | 0 | 330 | 0 | 0 | 23 | 35 | 24.5 | 22 | 0 | 485 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 60 | 60 | 1 | 172 | 0 | 7 | 200 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 960 | 3 | 43 | 0 | 165 | 0 | 346 | 340 | 48 | 212 | 11 | 35 | 0 | 120 | 9 | 19 | 65 | 24 | 8 | 56 | 42 | 310 | 320 | 345 | 34 | 30 | 143 | 8 | 0 | 60 | 30 | 0 | 0 | 168 | 17 | 55 | 120 | 59 | 1 | 18.41 | 0 | 7116.91 | 880 | 297 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 64.71 | 772 | 0 | 886.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 22.31 | 174 | 0 | 178 | 0 | 0 | 0 | 378 | 0 | 1.18 | 195 | 48 | 70 | 9 | 34 | 0 | 0 | 0 | 151 | 0.34 | 0 | 174 | 7 | 120 | 220 | 0 | 520 | 751 | 0 | 6018.36 | 13135.27 | 98.68
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 0 | 68 | 80 | 0 | 0 | 17 | 40 | 0 | 400 | 304 | 0 | 0 | 0 | 329 | 0 | 0 | 13 | 70 | 25 | 0 | 0 | 468 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 60 | 60 | 2 | 172 | 0 | 4 | 200 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 950 | 11 | 35 | 0 | 165 | 0 | 347 | 340 | 48 | 204 | 11 | 50 | 0 | 120 | 9 | 13 | 66 | 26 | 8 | 14 | 42 | 315 | 320 | 340 | 35 | 30 | 147 | 8 | 0 | 57 | 30 | 0 | 0 | 168 | 17 | 55 | 120 | 59 | 2 | 32.45 | 0 | 7191.45 | 880 | 296 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 92.09 | 788 | 0 | 874.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 30.72 | 178 | 0 | 182 | 0 | 0 | 0 | 380 | 0 | 4.85 | 194 | 48 | 70 | 17 | 34 | 0 | 0 | 1.8 | 180 | 0.72 | 0 | 173 | 7 | 120 | 220 | 0 | 520 | 743 | 0 | 6145.68 | 13337.13 | 98.68
11:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 17 | 38 | 68 | 80 | 0 | 0 | 34 | 45 | 0 | 400 | 302 | 0 | 0 | 0 | 330 | 0 | 0 | 25 | 70 | 24.6 | 22 | 0 | 477 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 60 | 88 | 2 | 172 | 0 | 3 | 203 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 950 | 15 | 43 | 0 | 155 | 0 | 345 | 340 | 48 | 204 | 11 | 51 | 0 | 113 | 9 | 13 | 63 | 32 | 8 | 22 | 42 | 315 | 320 | 387 | 35 | 30 | 150 | 8 | 0 | 57 | 30 | 0 | 0 | 168 | 17 | 55 | 120 | 59 | 0 | 51.53 | 0 | 7398.13 | 880 | 287 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 98.27 | 790 | 0 | 878.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 13.54 | 179 | 0 | 183 | 0 | 0 | 0 | 380 | 0 | 1.03 | 189 | 48 | 70 | 23 | 34 | 0 | 0 | 4.4 | 128 | 0.23 | 0 | 173 | 7 | 120 | 220 | 0 | 520 | 744 | 0 | 6055.35 | 13453.48 | 98.68
12:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 17 | 41 | 68 | 80 | 0 | 0 | 35 | 60 | 0 | 400 | 299 | 0 | 0 | 5 | 327 | 0 | 0 | 26 | 70 | 23.8 | 22 | 0 | 486 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 62 | 100 | 4 | 172 | 0 | 3 | 205 | 0 | 0 | 0 | 0 | 5 | 214 | 0 | 0 | 0 | 960 | 20 | 43 | 2 | 155 | 0 | 340 | 340 | 47 | 206 | 15 | 51 | 0 | 124 | 9 | 13 | 82 | 30 | 8 | 68 | 42 | 310 | 350 | 385 | 35 | 30 | 157 | 8 | 0 | 58 | 30 | 0 | 0 | 168 | 17 | 55 | 120 | 59 | 1 | 3.67 | 0 | 7503.47 | 879 | 284 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 97.65 | 791 | 0 | 1076.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 26.4 | 179 | 0 | 195 | 0 | 0 | 0 | 414 | 0 | 1.83 | 190 | 48 | 70 | 19 | 34 | 0 | 0 | 5.8 | 109 | 0.46 | 0 | 172 | 7 | 120 | 220 | 0 | 518 | 753 | 0 | 6339.54 | 13843.01 | 98.68
13:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 17 | 55 | 68 | 95 | 0 | 0 | 35 | 108 | 24 | 400 | 296 | 0 | 0 | 17 | 327 | 0 | 0 | 28 | 70 | 19.5 | 22 | 0 | 450 | 0 | 45 | 0 | 0 | 12 | 0 | 0 | 0 | 64 | 100 | 4 | 172 | 0 | 2 | 202 | 0 | 0 | 0 | 0 | 51 | 215 | 0 | 0 | 0 | 950 | 20 | 43 | 28 | 155 | 0 | 337 | 340 | 46 | 201 | 22 | 51 | 0 | 125 | 12 | 17 | 98 | 32 | 8 | 37 | 42 | 305 | 320 | 385 | 35 | 30 | 154 | 8 | 0 | 58 | 30 | 0 | 0 | 166 | 17 | 75 | 136 | 30 | 0 | 31.9 | 0 | 7665.4 | 879 | 278 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 90.44 | 770 | 0 | 1222.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 35.64 | 195 | 0 | 191 | 0 | 0 | 0 | 369 | 0 | 3.84 | 188 | 48 | 70 | 16 | 34 | 0 | 0 | 5.7 | 128 | 0.25 | 0 | 172 | 7 | 120 | 220 | 0 | 519 | 830 | 0 | 6530.06 | 14195.46 | 98.68
14:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 17 | 55 | 68 | 95 | 0 | 0 | 35 | 108 | 49 | 400 | 301 | 0 | 0 | 17 | 325 | 0 | 0 | 28 | 70 | 24 | 21 | 0 | 400 | 0 | 45 | 0 | 0 | 19 | 0 | 0 | 0 | 77 | 100 | 5 | 172 | 0 | 2 | 202 | 0 | 0 | 0 | 0 | 51 | 215 | 0 | 0 | 0 | 975 | 13 | 51 | 80 | 155 | 0 | 336 | 340 | 45 | 204 | 22 | 58 | 0 | 163 | 13 | 17 | 105 | 28 | 8 | 14 | 42 | 310 | 320 | 350 | 35 | 30 | 143 | 8 | 0 | 58 | 30 | 0 | 0 | 167 | 17 | 75 | 163 | 31 | 0 | 15.44 | 0 | 7744.44 | 880 | 270 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 79.54 | 777 | 0 | 1215.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 56.23 | 181 | 0 | 177 | 0 | 0 | 0 | 376 | 0 | 5.03 | 190 | 48 | 70 | 24 | 34 | 0 | 0 | 4.7 | 99 | 0.28 | 0 | 172 | 8 | 120 | 220 | 0 | 519 | 845 | 0 | 6501.48 | 14245.92 | 98.68
15:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 17 | 55 | 68 | 95 | 0 | 0 | 35 | 108 | 51 | 400 | 300 | 0 | 0 | 17 | 320 | 0 | 0 | 24 | 83 | 24 | 21 | 0 | 450 | 0 | 45 | 0 | 0 | 29 | 0 | 0 | 0 | 77 | 88 | 1 | 172 | 0 | 4 | 200 | 0 | 0 | 0 | 0 | 50 | 214 | 0 | 0 | 0 | 960 | 12 | 51 | 113 | 167 | 0 | 338 | 340 | 44 | 206 | 22 | 69 | 0 | 161 | 9 | 17 | 107 | 34 | 8 | 34 | 42 | 310 | 320 | 360 | 35 | 30 | 148 | 8 | 0 | 58 | 30 | 0 | 0 | 167 | 0 | 75 | 143 | 33 | 1 | 13.88 | 0 | 7847.88 | 880 | 267 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 59.91 | 781 | 0 | 1227.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 34.31 | 181 | 0 | 180 | 0 | 0 | 0 | 414 | 0 | 2.76 | 187 | 47 | 70 | 17 | 34 | 0 | 0 | 7.6 | 126 | 0.43 | 0 | 174 | 6 | 120 | 220 | 0 | 577 | 871 | 0 | 6597.45 | 14445.33 | 98.68
16:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 17 | 55 | 68 | 95 | 0 | 0 | 35 | 108 | 51 | 400 | 300 | 0 | 0 | 35 | 322 | 0 | 0 | 13 | 108 | 0 | 21 | 0 | 450 | 0 | 45 | 0 | 0 | 20 | 0 | 0 | 0 | 77 | 88 | 0 | 172 | 0 | 3 | 201 | 0 | 0 | 0 | 0 | 51 | 218 | 0 | 0 | 0 | 960 | 8 | 51 | 125 | 175 | 0 | 337 | 340 | 43 | 201 | 22 | 69 | 0 | 161 | 9 | 17 | 103 | 38 | 21 | 29 | 42 | 305 | 320 | 345 | 36 | 30 | 153 | 8 | 0 | 58 | 30 | 0 | 0 | 166 | 0 | 75 | 145 | 33 | 1 | 14.27 | 0 | 7851.27 | 880 | 262 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 62.97 | 770 | 0 | 1215.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 22.52 | 181 | 0 | 178 | 0 | 0 | 0 | 414 | 0 | 2.14 | 188 | 48 | 70 | 6 | 34 | 0 | 0 | 4.4 | 39 | 0.24 | 0 | 176 | 6 | 120 | 220 | 0 | 615 | 898 | 0 | 6472.31 | 14323.58 | 98.68
17:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 35 | 55 | 68 | 95 | 0 | 6 | 35 | 108 | 51 | 360 | 301 | 0 | 0 | 17 | 324 | 0 | 0 | 0 | 90 | 23 | 21 | 0 | 400 | 0 | 30 | 0 | 0 | 18 | 0 | 0 | 0 | 89 | 88 | 1 | 172 | 0 | 5 | 203 | 0 | 0 | 0 | 0 | 51 | 217 | 0 | 0 | 0 | 910 | 4 | 51 | 80 | 145 | 0 | 336 | 300 | 43 | 202 | 21 | 70 | 0 | 161 | 9 | 17 | 95 | 36 | 25 | 16 | 42 | 300 | 320 | 345 | 36 | 30 | 159 | 8 | 0 | 58 | 30 | 0 | 0 | 166 | 15 | 75 | 145 | 33 | 1 | 9.71 | 0 | 7580.71 | 880 | 262 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 22.6 | 760 | 0 | 1111.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 13.17 | 177 | 0 | 176 | 0 | 0 | 0 | 375 | 0 | 1.15 | 187 | 47 | 70 | 2 | 34 | 0 | 0 | 1.1 | 33 | 0.21 | 0 | 173 | 6 | 120 | 220 | 0 | 615 | 898 | 0 | 6240.15 | 13820.86 | 98.68
18:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 54 | 55 | 68 | 95 | 15 | 15 | 35 | 72 | 51 | 320 | 292 | 0 | 0 | 17 | 280 | 0 | 0 | 2 | 90 | 19.5 | 21 | 0 | 400 | 0 | 30 | 0 | 0 | 24 | 0 | 0 | 0 | 89 | 88 | 0 | 172 | 0 | 10 | 202 | 0 | 0 | 0 | 0 | 48 | 217 | 0 | 0 | 0 | 880 | 1 | 51 | 80 | 145 | 0 | 300 | 300 | 44 | 190 | 28 | 69 | 0 | 164 | 16 | 17 | 99 | 34 | 25 | 3 | 42 | 295 | 320 | 321 | 36 | 30 | 151 | 8 | 0 | 58 | 30 | 0 | 0 | 167 | 17 | 75 | 145 | 33 | 0 | 2.39 | 0 | 7395.89 | 880 | 258 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3.97 | 742 | 17 | 1111.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 1.95 | 170 | 0 | 170 | 0 | 0 | 0 | 314 | 0 | 0.15 | 187 | 47 | 70 | 0 | 50 | 0 | 0 | 0 | 2 | 0.03 | 0 | 168 | 6 | 120 | 220 | 0 | 615 | 890 | 0 | 6088.04 | 13483.93 | 98.68
19:00 | 8 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 54 | 55 | 68 | 110 | 30 | 15 | 35 | 72 | 51 | 400 | 302 | 0 | 0 | 35 | 326 | 0 | 0 | 0 | 90 | 24 | 21 | 0 | 450 | 0 | 30 | 0 | 0 | 26 | 65 | 14 | 0 | 100 | 88 | 0 | 172 | 4 | 19 | 205 | 0 | 0 | 0 | 1 | 46 | 217 | 0 | 0 | 0 | 1040 | 0 | 51 | 80 | 164 | 0 | 335 | 340 | 44 | 209 | 28 | 74 | 0 | 163 | 27 | 17 | 99 | 42 | 25 | 0 | 42 | 300 | 320 | 357 | 36 | 30 | 132 | 8 | 0 | 58 | 30 | 0 | 0 | 166 | 17 | 103 | 165 | 49 | 0 | 0 | 0 | 8137 | 880 | 257 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 876 | 20 | 1281.44 | 0 | 17 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 164 | 0 | 0 | 0 | 356 | 0 | 0 | 186 | 48 | 90 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 9 | 120 | 220 | 0 | 615 | 924 | 0 | 6599.44 | 14736.44 | 98.68
19:30 | 8 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 54 | 55 | 90 | 146 | 30 | 15 | 55 | 108 | 51 | 400 | 300 | 0 | 0 | 35 | 328 | 0 | 0 | 0 | 125 | 24 | 21 | 0 | 500 | 0 | 30 | 0 | 0 | 11 | 65 | 32 | 0 | 100 | 88 | 0 | 172 | 15 | 8 | 202 | 0 | 0 | 10 | 8 | 46 | 216 | 0 | 0 | 0 | 1160 | 0 | 51 | 80 | 164 | 0 | 346 | 340 | 46 | 212 | 28 | 115 | 0 | 180 | 28 | 19 | 114 | 42 | 52.2 | 0 | 36 | 305 | 320 | 334 | 36 | 30 | 146 | 8 | 0 | 58 | 28 | 0 | 0 | 166 | 17 | 101 | 174 | 48 | 0 | 0 | 0 | 8563.2 | 879 | 257 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1031 | 17 | 1406.12 | 0 | 36 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 173 | 0 | 0 | 0 | 345 | 0 | 0 | 188 | 48 | 115 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 10 | 120 | 220 | 0 | 615 | 1085 | 0 | 7101.12 | 15664.32
20:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 54 | 55 | 88 | 147 | 30 | 15 | 55 | 108 | 51 | 400 | 294 | 0 | 0 | 35 | 330 | 0 | 0 | 0 | 142 | 25 | 21 | 0 | 500 | 0 | 30 | 0 | 0 | 23 | 65 | 40 | 0 | 100 | 100 | 0 | 172 | 15 | 12 | 201 | 0 | 0 | 14 | 8 | 46 | 216 | 0 | 0 | 0 | 1127 | 0 | 51 | 50 | 165 | 0 | 351 | 340 | 46 | 213 | 28 | 115 | 0 | 180 | 28 | 19 | 114 | 40 | 52.2 | 0 | 44 | 305 | 320 | 314 | 37 | 30 | 154 | 8 | 0 | 58 | 28 | 0 | 0 | 166 | 17 | 102 | 175 | 48 | 0 | 0 | 0 | 8555.2 | 880 | 258 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1028 | 34 | 1410.45 | 0 | 38 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 169 | 0 | 0 | 0 | 335 | 0 | 0 | 187 | 46 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 8 | 120 | 220 | 0 | 614 | 1100 | 0 | 7125.45 | 15680.65 | 98.68
21:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 54 | 55 | 105 | 147 | 15 | 0 | 55 | 90 | 51 | 400 | 301 | 0 | 0 | 35 | 332 | 0 | 0 | 0 | 142 | 25 | 21 | 0 | 500 | 0 | 0 | 0 | 0 | 16 | 65 | 48 | 0 | 100 | 100 | 0 | 172 | 0 | 10 | 201 | 0 | 0 | 19 | 8 | 17 | 218 | 0 | 0 | 0 | 1150 | 0 | 51 | 20 | 127 | 0 | 350 | 340 | 46 | 207 | 28 | 115 | 0 | 180 | 29 | 19 | 114 | 36 | 52.2 | 0 | 44 | 295 | 320 | 321 | 37 | 30 | 151 | 8 | 0 | 56 | 28 | 0 | 0 | 166 | 17 | 102 | 175 | 48 | 0 | 0 | 2 | 8392.2 | 879 | 258 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1044 | 34 | 1407.29 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 164 | 0 | 0 | 0 | 396 | 0 | 0 | 184 | 46 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 257 | 11 | 120 | 220 | 0 | 616 | 1090 | 0 | 7179.29 | 15571.49 | 98.68
22:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 54 | 55 | 105 | 146 | 0 | 0 | 0 | 90 | 51 | 350 | 302 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 125 | 25 | 21 | 0 | 500 | 0 | 0 | 0 | 0 | 14 | 65 | 48 | 0 | 60 | 100 | 0 | 172 | 0 | 17 | 204 | 0 | 0 | 19 | 0 | 0 | 219 | 0 | 0 | 0 | 1165 | 0 | 51 | 20 | 87 | 0 | 346 | 340 | 47 | 192 | 28 | 111 | 0 | 165 | 28 | 19 | 114 | 40 | 52.2 | 0 | 45 | 295 | 320 | 360 | 37 | 30 | 136 | 8 | 0 | 59 | 28 | 0 | 0 | 167 | 17 | 112 | 175 | 48 | 0 | 0 | 0 | 8109.2 | 880 | 258 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1063 | 34 | 1425.69 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 165 | 0 | 0 | 0 | 414 | 0 | 0 | 181 | 46 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 261 | 11 | 120 | 220 | 0 | 616 | 1095 | 0 | 7244.69 | 15353.89 | 98.68
23:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 55 | 105 | 146 | 0 | 0 | 0 | 90 | 51 | 350 | 303 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 125 | 26 | 21 | 0 | 500 | 0 | 0 | 0 | 0 | 23 | 66 | 48 | 0 | 60 | 100 | 0 | 172 | 0 | 21 | 204 | 0 | 0 | 19 | 0 | 0 | 220 | 0 | 0 | 0 | 1176 | 0 | 51 | 23 | 86 | 0 | 345 | 335 | 47 | 185 | 28 | 72 | 0 | 147 | 29 | 19 | 114 | 46 | 52.2 | 0 | 46 | 290 | 320 | 371 | 36 | 30 | 152 | 8 | 0 | 59 | 25 | 0 | 0 | 166 | 17 | 112 | 174 | 48 | 0 | 0 | 0 | 8074.2 | 880 | 259 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1135 | 34 | 1423.05 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 177 | 0 | 0 | 0 | 414 | 0 | 0 | 185 | 46 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 264 | 11 | 120 | 220 | 0 | 617 | 1110 | 0 | 7361.05 | 15435.25 | 98.68
Total KWH | 11808 | 1325760 | 540960 | 0 | 0 | 0 | 0 | 0 | 8334000 | 0 | 0 | 453600 | 1065960 | 2057184 | 2707680 | 101367 | 57889 | 462379 | 1389600 | 589440 | 8787000 | 7171316 | 0 | 0 | 303823 | 7744522 | 0 | 0 | 193156 | 2109600 | 546000 | 481320 | 0 | 10709090.91 | 0 | 491782 | 0 | 0 | 394560 | 487692 | 270624 | 0 | 1760640 | 2130240 | 21258 | 4164760 | 90327 | 406560 | 4894545.46 | 0 | 0 | 174240 | 55530 | 705891 | 5125614 | 0 | 0 | 0 | 24414543 | 109485 | 1114538 | 1047127 | 3746909 | 0 | 8632900 | 8148000 | 1113600 | 5025000 | 448200 | 1399680 | 0 | 3705600 | 337680 | 387870 | 2316480 | 845760 | 806208 | 312382 | 1036016 | 7349500 | 7698000 | 8743000 | 828000 | 680520 | 3554754 | 184392 | 0 | 1416000 | 676992 | 0 | 0 | 3471250 | 393480 | 1857600 | 3434400 | 1194240 | 9650 | 232880 | 2880 | 184993234.37 | 21296000 | 6577632 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 660960 | 20138190 | 219360 | 28227273 | 0 | 260884 | 0 | 79104 | 0 | 208784 | 0 | 0 | 0 | 665150 | 0 | 292496 | 4273818 | 0 | 4479145 | 0 | 0 | 0 | 8791854 | 0 | 25800 | 4590000 | 1103999 | 2320784 | 162720 | 1485657 | 0 | 0 | 33851.25 | 1103760 | 3972 | 0 | 4952000 | 209835 | 2858000 | 5385500 | 0 | 13498181.81 | 23170909.09 | 0 | 157987619.15 | 342980853.52

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 23-06-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13843.01 | MW | 12:00 Hr. | Energy Generated |  |  | 342.9809 |  | MKWHr.
| Day Peak Demand |  |  | 13843.01 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.338 |  | MKWHr.
| Evening Peak Generation |  |  | 15680.65 | MW | 20:00 Hr. | Energy Demand |  |  | 343.3189 |  | MKWHr.
| Evening Peak Demand |  |  | 15680.65 | MW | 20:00 Hr. | Maximum Temperature |  |  | 31.5 |  | °C
| Minimum Generation of the Day |  |  | 12697.55 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 1041.82 |  | MMCFD
| Maximum Generation of the Day |  |  | 15680.65 | MW | 20:00 Hr. | Production Cost per KWHr |  |  | 6.2958 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 43.7732 | 0 | 13.177 | 0 | 0 | 0.19316 | 0 | 0 | 57.1435 | Gas | 146.2949 | Gas | 518831667.8947
| Chattogram Zone |  |  | 5.5322 | 29.3091 | 6.167 | 0 | 4.1648 | 0.13074 | 0 | 0.39456 | 45.6983 | Coal | 96.7624 | Coal | 566063225.6795
| Cumilla Zone |  |  | 28.617 | 0 | 10.6488 | 0 | 0 | 0.31238 | 0.84576 | 0 | 40.4239 | HFO | 40.2557 | HFO | 755275518.34
| Mymensingh Zone |  |  | 1.1942 | 0 | 5.6884 | 0 | 0 | 0.24253 | 0 | 0 | 7.1251 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 34.6024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.6024 | Hydro | 4.1648 | Hydro | 416476
| Khulna Zone |  |  | 6.5776 | 20.1382 | 0.21936 | 0 | 0 | 0.66096 | 22.208 | 0 | 49.8041 | Solar | 3.8275 | Solar | 62669806.405
| Barishal Zone |  |  | 8.4533 | 41.6211 | 0 | 0 | 0 | 0.003972 | 0 | 0 | 50.0784 | Import | 51.281 | Import | 250316242.98
| Rajshahi Zone |  |  | 17.5448 | 0 | 0.54877 | 0 | 0 | 0.98345 | 28.2273 | 0 | 47.3043 | Wind | 0.39456 | Wind | 5776358.4
| Rangpur Zone |  |  | 0 | 5.694 | 3.8064 | 0 | 0 | 1.3003 | 0 | 0 | 10.8008
| Total |  |  | 146.2949 | 96.7624 | 40.2557 | 0 | 4.1648 | 3.8275 | 51.281 | 0.39456 | 342.9809
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 518831667.8947 |  | Hydro | 416476
|  |  |  | Coal | 566063225.6795 |  | Solar | 62669806.405
|  |  |  | HFO | 755275518.34 |  | Import | 250316242.98
|  |  |  | HSD | 0 |  | Wind | 5776358.4
[5 empty] | Total: | 215,93,49,295 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.296 | Peak Hr Flow | 880.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 43607818.26 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 28.2273 | Peak Hr Flow | 1410.45 MW at 20:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 662 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.84576 | Peak Hr Flow | 40.00 MW at 20:00 hrs.
Maximum Power Flow: |  |  | MW: | 868 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.369 | Peak Hr Flow | 2330.45 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5404
|  |  |  | Chattogram |  | 0 |  | 1412
|  |  |  | Cumilla |  | 0 |  | 1399
|  |  |  | Mymensingh |  | 0 |  | 1236
|  |  |  | Sylhet |  | 0 |  | 585
|  |  |  | Khulna |  | 0 |  | 1851
|  |  |  | Barishal |  | 0 |  | 474
|  |  |  | Rajshahi |  | 0 |  | 1524
|  |  |  | Rangpur |  | 0 |  | 996
|  |  |  | Total |  | 0 |  | 14881
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[5 empty] | Total | 300 |  |  |  | Total | 476
|  |  |  | Total Unavailable Capacity |  |  |  | 776
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:09 | 08:46 | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to For red hot removed on TR1AB 33kv | [7 empty] | 25.0MW load
|  |  | side DS | [7 empty] | interrup.
| 08:09 | 08:46 | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to For red hot removed on TR1AB 33kv | [7 empty] | 25.0MW load
|  |  | side DS | [7 empty] | interrup.
|  | 08:17 | Coxsbazar 132/33kV S/S 415T-T2 HT is restored.
|  | 08:57 | Ramganj 132/33kV S/S Transformer-01 HT is restored.
|  | 08:57 | Ramganj 132/33kV S/S Transformer-01 LT is restored.
| 09:05 | 13:35 | Ishurdi 230/132kV S/S 230/132 kV T-03 LT Scheduled S/D Due to DC Cable Replacement issue
| 09:42 | 11:57 | Chowmuhani-Ramganj 132 kV Ckt-1 Project Work S/D from Chowmuhani 132/33kV end Due to
71-72 tower loop removal for remove T-connection of chow-Ramgonj & Chow-kacua.
|  | 09:43 | Goalpara 132/33kV S/S T-6 HT is restored.
|  | 09:44 | Goalpara 132/33kV S/S T-6 LT is restored.
|  | 09:50 | Goalpara 132/33kV S/S T-5 HT is restored.
|  | 09:50 | Goalpara 132/33kV S/S T-5 LT is restored.
| 10:27 | 11:02 | Sunamganj 132/33kV S/S Tr-1 HT Scheduled S/D Due to Tr-1 Shutdown due t incoming CB | [7 empty] | 15.0MW load
|  |  | closing coil change. | [7 empty] | interrup.
| 11:03 | 17:42 | Bogura 400/230kV S/S ATR-01 HT Project Work S/D Due to ATR-01 Paint Work
|  | 11:25 | Rampura 230/132kV S/S 132 kV Busbar-2 is restored.
|  | 11:37 | Rampura 230/132kV S/S Auto Transformer - 02 HT is restored.
|  | 11:37 | Rampura 230/132kV S/S Auto Transformer - 02 LT is restored.
| 12:00 |  | Day Peak Gen. 13843 MW
| 12:33 | 16:01 | Bhaluka 132/33kV S/S BR Powergen Ckt- 01 Scheduled S/D Due to NLDC list End to End test
| 14:42 |  | TR-1 , New Transformer commission At Goalpara S/S .
| 16:00 | 16:30 | Muradnagar 132/33kV S/S 132KV Transformar-01 LT Forced S/D Due to due to kite obstruction | [7 empty] | 14.0MW load
|  |  | on 33 kv side | [7 empty] | interrup.
|  | 18:32 | Hasnabad 230/132kV S/S AUTO TR-2 LT is restored.
|  | 18:32 | Hasnabad 230/132kV S/S AUTO TR-2 HT is restored.
| 18:49 |  | Raozan 25 MW PP Synchronized
|  | 20:01 | Madunaghat 400/230kV S/S ATR-1 7006T LT is restored.
|  | 20:01 | Madunaghat 400/230kV S/S ATR-1 7006T HT is restored.
| 21:13 |  | Raozan 25 MW PP Shutdown
| 02:39 | 02:54 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T HT Tripped showing SIPROTECH 7UT86 | [7 empty] | 20.0MW load
|  |  | relays Due to Thunderstorm | [7 empty] | interrup.
| 06:39 |  | Goalpara 132/33kV S/S T1 HT Scheduled S/D Due to Earth wire installation | [7 empty] | 2.0MW load
interrup.
| 06:40 |  | Goalpara 132/33kV S/S T-5 LT Scheduled S/D Due to Earth wire installation | [7 empty] | 2.0MW load
interrup.
| 06:40 |  | Goalpara 132/33kV S/S T1 LT Scheduled S/D Due to Earth wire installation | [7 empty] | 2.0MW load
interrup.
| 06:42 |  | Goalpara 132/33kV S/S T-5 HT Scheduled S/D Due to Earth wire installation work | [7 empty] | 2.0MW load
interrup.
| 06:50 |  | Goalpara 132/33kV S/S T-6 LT Scheduled S/D Due to Earth wire installation | [7 empty] | 2.0MW load
interrup.
| 06:51 |  | Goalpara 132/33kV S/S T-6 HT Scheduled S/D Due to Earth wire installation | [7 empty] | 2.0MW load
interrup.
| 07:00 |  | Minimum Generation is 12584 MW
| 07:57 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is OFF with remarks:- Demand Full.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 23-06-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 325 | 8334000 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 8787000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 294 | 7171316 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 57889 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 7744522 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 11808 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 453600 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 147 | 2707680 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 462379 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 303823 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 25 | 546000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 481320 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 540960 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 30 | 101367 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 88 | 2057184 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1325760 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 51 | 589440 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 1389600 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 193156 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 1065960 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 500 | 10709090.91 | None
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 142 | 2109600 | -
Dhaka Area Total |  |  |  |  | 5939.724 | 2788 | 57143454.91
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 55530 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 109485 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 14 | 174240 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 172 | 4164760 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 216 | 5125614 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 46 | 705891 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 40 | 270624 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 487692 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1760640 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 12 | 406560 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21258 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 30 | 491782 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 15 | 90327 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2130240 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1127 | 24414543 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 23 | 394560 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 201 | 4894545.46 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4895.72 | 2169 | 45698291.46
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 213 | 5025000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 351 | 8632900 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 8148000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 28 | 448200 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 46 | 1113600 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 165 | 3746909 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1114538 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 50 | 1047127 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 44 | 1036016 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 180 | 3705600 | -
| Import (Tripura) |  | Import | 0 | 160 | 40 | 845760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 806208 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 387870 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2316480 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 337680 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1399680 | Fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 312382 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1836.2 | 40423950
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 48 | 1194240 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9650 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 175 | 3434400 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 102 | 1857600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 232880 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 2880 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 393480 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 342 | 7125130
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 37 | 828000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 680520 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 154 | 3554754 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 28 | 676992 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 58 | 1416000 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 166 | 3471250 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 184392 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7349500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 314 | 8743000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7698000 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1420 | 34602408
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 880 | 21296000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 258 | 6577632 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 34 | 219360 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 660960 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1028 | 20138190 | Coal Unloading problem due to bad weather
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2238 | 49804142
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 614 | 13498181.81 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 8 | 209835 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2858000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1100 | 23170909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5385500 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 225 | 4952000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3972 | -
Barishal Area Total |  |  |  |  | 2236 | 2287 | 50078397.9
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 38 | 260884 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 169 | 4273818 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 169 | 4479145 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Plant is in Standby as per NLDC request.
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 335 | 8791854 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 33 | 208784 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 79104 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 25800 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1410.45 | 28227273 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 292496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 665150 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2154.45 | 47304308
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 46 | 1103999 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 187 | 4590000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 1485657 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 33851.25 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2320784 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 162720 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1103760 | -
Rangpur Area Total |  |  |  |  | 950 | 446 | 10800771.25
Eastern Grid Total |  |  |  |  | 16705.895 | 8555.2 | 184993234.37
Western Grid Total |  |  |  |  | 10378.16 | 7125.45 | 157987619.15
National Grid Total |  |  |  |  | 27084.055 | 15680.65 | 342980853.52
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 23-06-2025
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10036.29 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4844.1 | MW
i) Dhaka area |  |  | 5404.43 |  | MW | i) Khulna area |  |  |  | 1851 | MW
ii) Chattogram area |  |  | 1412 |  | MW | ii) Barishal area |  |  |  | 473.5 | MW
iii) Cumilla area |  |  | 1398.86 |  | MW | iii) Rajshahi area |  |  |  | 1523.6 | MW
iv) Mymensingh area |  |  | 1236 |  | MW | iv) Rangpur area |  |  |  | 996 | MW
v) Sylhet area |  |  | 585 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14880.39 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 86 | 19:30 | 133 | Patuakhali | 86.5 | 22:00
2 | AKSML | 135 | 15:00 | 68 | Jaldhaka | 88 | 21:00 | 134 | Payra | 34 | 22:00
3 | Aftabnagar | 42 | 16:00 | 69 | Jamalpur | 132 | 22:00 | 135 | Postogola | 60 | 15:00
4 | Agargaon | 138 | 14:00 | 70 | Jashore | 152 | 21:00 | 136 | Purbachal | 22 | 01:00
5 | Agrabad | 94 | 18:30 | 71 | Jhenaidah | 133 | 22:00 | 137 | Purbasadipur | 152 | 21:00
6 | Amnura | 40 | 00:00 | 72 | Joydebpur | 154 | 18:30 | 138 | Rahanpur | 34 | 23:00
7 | Ashuganj | 99 | 23:00 | 73 | Joypurhat | 67 | 00:00 | 139 | Rahim | 43 | 16:00
8 | BSRM | 196 | 19:00 | 74 | Juldah | 13.5 | 00:00 | 140 | Rajbari | 86 | 20:00
9 | Bagerhat | 89 | 19:30 | 75 | KSRM | 21 | 03:00 | 141 | Rajendrapur | 138 | 00:00
10 | Bajitpur | 60 | 19:30 | 76 | Kabirpur | 258 | 17:00 | 142 | Rajshahi | 115 | 21:00
11 | Bakulia | 93 | 19:00 | 77 | Kachua | 94 | 20:00 | 143 | Rajshahi-230 | 86 | 10:00
12 | Banani | 37 | 13:00 | 78 | Kallyanpur | 105 | 00:00 | 144 | Ramganj | 116 | 21:00
13 | Bangabhaban | 18 | 13:00 | 79 | Kalurghat | 38 | 09:00 | 145 | Rampur | 41 | 23:00
14 | Barapukuria | 72 | 00:00 | 80 | Kamrangirchar | 68 | 19:00 | 146 | Rangamati | 17 | 19:30
15 | Barguna | 24 | 22:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 160 | 21:00
16 | Barishal | 116 | 13:00 | 82 | Kasba | 37 | 21:00 | 148 | Ruppur | 7.2 | 10:00
17 | Barishal-230 | 104 | 23:00 | 83 | Kazla | 93 | 14:00 | 149 | SSM | 12 | 05:00
18 | Baroaulia | 60 | 11:00 | 84 | Keranigonj | 87 | 00:00 | 150 | Saidpur | 115 | 22:00
19 | Baroirhat | 63 | 19:00 | 85 | Khagrachori | 32 | 21:00 | 151 | Satkhira | 138 | 22:00
20 | Bashundhara | 188 | 13:00 | 86 | Khulna | 81 | 13:00 | 152 | Satmasjid | 106 | 16:00
21 | BashundharaCement | 13 | 15:00 | 87 | Khulshi | 153 | 19:00 | 153 | Savar | 238 | 12:00
22 | Beanibazar | 84 | 00:00 | 88 | Kishoreganj | 152 | 20:00 | 154 | SevenRings | 14.1 | 00:00
23 | Benapole | 74 | 00:00 | 89 | Kodda | 313 | 14:00 | 155 | ShahCement | 32 | 00:00
24 | Bhaluka | 149 | 20:00 | 90 | Kulaura | 52 | 19:30 | 156 | Shahjadpur | 84 | 19:30
25 | Bhandaria | 57 | 22:00 | 91 | Kurigram | 74 | 20:00 | 157 | Shahjibazar | 136 | 22:00
26 | Bhangura | 41 | 19:30 | 92 | Kushtia | 162 | 19:30 | 158 | Shahmirpur | 67 | 00:00
27 | Bheramara(GK) | 69 | 21:00 | 93 | Lalbag | 66 | 00:00 | 159 | Shariatpur | 94 | 23:00
28 | Bhulta | 243 | 00:00 | 94 | Lalmonirhat | 67 | 21:00 | 160 | Sherpur | 156 | 19:30
29 | Bog-Sherpur | 70 | 21:00 | 95 | MI_Cement | 11 | 00:00 | 161 | Shikalbaha | 18 | 13:00
30 | Bogura | 169 | 19:30 | 96 | Madanganj | 38 | 00:00 | 162 | Shitalakhya | 87 | 16:00
31 | Borhanuddin | 92 | 00:00 | 97 | Madaripur | 123 | 22:00 | 163 | Sholosohor | 47 | 12:00
32 | Brahmanbaria | 142 | 00:00 | 98 | Madartek | 91.49 | 22:00 | 164 | Shyampur | 142 | 00:00
33 | Cantonment | 170 | 13:00 | 99 | Madunaghat | 55 | 19:30 | 165 | Siddhirganj | 118 | 15:00
34 | Chandina | 19.6 | 07:00 | 100 | Magura | 69 | 23:00 | 166 | Sirajganj | 104 | 22:00
35 | Chandpur | 84 | 21:00 | 101 | Mahasthangarh | 82 | 00:00 | 167 | Sonargaon | 112 | 16:00
36 | Chandraghona | 37 | 19:30 | 102 | Manikganj | 132 | 20:00 | 168 | Sreemongol | 86 | 22:00
37 | Chapai | 75 | 22:00 | 103 | Maniknagar | 84 | 14:00 | 169 | Sreepur | 104 | 19:30
38 | Charsaidpur | 49 | 00:00 | 104 | Matarbari | 53 | 20:00 | 170 | Srinagar | 50.96 | 22:00
39 | Chauddagram | 71 | 01:00 | 105 | Matuail | 64 | 00:00 | 171 | Sunamganj | 62 | 02:00
40 | Chhatak | 38 | 00:00 | 106 | Millgate | 95 | 10:00 | 172 | Sylhet | 50 | 00:00
41 | Chowmuhani | 201 | 20:00 | 107 | Mirpur | 127 | 13:00 | 173 | Sylhet-132 | 127 | 18:30
42 | Chuadanga | 122 | 00:00 | 108 | Mirsorai | 10 | 09:00 | 174 | TK | 22 | 00:00
43 | Coxsbazar | 132 | 14:00 | 109 | Mirzapur | 44 | 21:00 | 175 | Tangail | 190 | 21:00
44 | Cumilla(N) | 155 | 00:00 | 110 | Mithapukur | 70 | 00:00 | 176 | Thakurgaon | 111 | 20:00
45 | Cumilla(S) | 168 | 19:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 129 | 12:00
46 | Daudkandi | 159 | 21:00 | 112 | Mogbazar | 159.3 | 13:00 | 178 | Ullahpara | 40 | 21:00
47 | Dhaka | 62 | 13:00 | 113 | Mongla | 39 | 06:00 | 179 | Ullon | 49 | 00:00
48 | Dhamrai | 136 | 15:00 | 114 | Motijheel | 42 | 13:00 | 180 | Uttara | 86 | 16:00
49 | Dhanmondi | 153.6 | 13:00 | 115 | Muktagacha | 40 | 19:30 | 181 | UttaraNew | 63 | 00:00
50 | Dohazari | 106 | 00:00 | 116 | Munshiganj | 120 | 23:00 | 182 | Zigatola | 96 | 01:00
51 | Faridpur | 174 | 00:00 | 117 | Muradnagar | 33 | 00:00
52 | Fatullah | 100 | 15:00 | 118 | Mymensingh | 221 | 21:00
53 | Fenchuganj | 43 | 23:00 | 119 | Naogaon | 143 | 20:00
54 | Feni | 112 | 00:00 | 120 | Narail | 61 | 19:30
55 | GPH | 66 | 00:00 | 121 | Narinda | 98 | 16:00
56 | Ghatail | 76 | 20:00 | 122 | Narshingdi | 187 | 00:00
57 | Ghorashal | 15 | 00:00 | 123 | Natore | 154 | 22:00
58 | Ghorashal-230 | 89 | 00:00 | 124 | Nawabganj | 61.2 | 23:00
59 | Goalpara | 42 | 23:00 | 125 | Netrakona | 139 | 00:00
60 | Gollamari | 98 | 00:00 | 126 | New | 88.3 | 15:00
61 | Gopalganj | 116 | 20:00 | 127 | Niamatpur | 76 | 21:00
62 | Gulshan | 130 | 13:00 | 128 | Noapara | 48 | 00:00
63 | Halishahar | 80.5 | 13:00 | 129 | PHP | 8 | 03:00
64 | HaripurSBU | 178 | 17:00 | 130 | Pabna | 135 | 21:00
65 | Hasnabad | 79 | 23:00 | 131 | Palashbari | 120 | 19:30
66 | Hathazari | 84 | 21:00 | 132 | Panchagarh | 63 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 23-06-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15189.19 | 56 |  | 15247.71
1:00 | 15174.44 | 73 |  | 15250.44
2:00 | 14701.65 | 66 |  | 14770.65
3:00 | 14230.03 | 49 |  | 14281.03
4:00 | 13902.29 | 27 |  | 13930.29
5:00 | 13621.1 | 24 |  | 13646.1
6:00 | 12996.54 | 0 |  | 12996.54
7:00 | 12734.07 | 0 |  | 12734.07
8:00 | 12697.55 | 0 |  | 12697.55
9:00 | 13135.27 | 0 |  | 13135.27
10:00 | 13337.13 | 0 |  | 13337.13
11:00 | 13453.48 | 0 |  | 13453.48
12:00 | 13843.01 | 0 |  | 13843.01
13:00 | 14195.46 | 0 |  | 14195.46
14:00 | 14245.92 | 0 |  | 14245.92
15:00 | 14445.33 | 0 |  | 14445.33
16:00 | 14323.58 | 0 |  | 14323.58
17:00 | 13820.86 | 0 |  | 13820.86
18:00 | 13483.93 | 0 |  | 13483.93
19:00 | 14736.44 | 0 |  | 14736.44
19:30 | 15664.32 | 0 |  | 15664.32
20:00 | 15680.65 | 0 |  | 15680.65
21:00 | 15571.49 | 0 |  | 15571.49
22:00 | 15353.89 | 0 |  | 15353.89
23:00 | 15435.25 | 43 |  | 15480.25
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 23-06-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8080.7 | 7108.49 | 15189.19 | DAILY GENERATION CURVE
00:30 | 8117.45 | 7064.365 | 15181.815
01:00 | 8154.2 | 7020.24 | 15174.44 | 23-06-2025
01:30 | 8013.7 | 6924.345 | 14938.045
02:00 | 7873.2 | 6828.45 | 14701.65
02:30 | 7748.2 | 6717.64 | 14465.84
03:00 | 7623.2 | 6606.83 | 14230.03
03:30 | 7561.2 | 6504.96 | 14066.16
04:00 | 7499.2 | 6403.09 | 13902.29
04:30 | 7432.7 | 6328.995 | 13761.695
05:00 | 7366.2 | 6254.9 | 13621.1
05:30 | 7205.43 | 6103.39 | 13308.82
06:00 | 7044.66 | 5951.88 | 12996.54
06:30 | 7022.555 | 5842.75 | 12865.305
07:00 | 7000.45 | 5733.62 | 12734.07
07:30 | 6962.015 | 5753.795 | 12715.81
08:00 | 6923.58 | 5773.97 | 12697.55
08:30 | 7020.245 | 5896.165 | 12916.41
09:00 | 7116.91 | 6018.36 | 13135.27
09:30 | 7154.18 | 6082.02 | 13236.2
10:00 | 7191.45 | 6145.68 | 13337.13
10:30 | 7294.79 | 6100.515 | 13395.305
11:00 | 7398.13 | 6055.35 | 13453.48
11:30 | 7450.8 | 6197.445 | 13648.245
12:00 | 7503.47 | 6339.54 | 13843.01
12:30 | 7584.435 | 6434.8 | 14019.235
13:00 | 7665.4 | 6530.06 | 14195.46
13:30 | 7704.92 | 6515.77 | 14220.69
14:00 | 7744.44 | 6501.48 | 14245.92
14:30 | 7796.16 | 6549.465 | 14345.625
15:00 | 7847.88 | 6597.45 | 14445.33
15:30 | 7849.575 | 6534.88 | 14384.455
16:00 | 7851.27 | 6472.31 | 14323.58
16:30 | 7715.99 | 6356.23 | 14072.22
17:00 | 7580.71 | 6240.15 | 13820.86
17:30 | 7488.3 | 6164.095 | 13652.395
18:00 | 7395.89 | 6088.04 | 13483.93
18:30 | 7766.445 | 6343.74 | 14110.185
19:00 | 8137 | 6599.44 | 14736.44
19:30 | 8563.2 | 7101.12 | 15664.32
20:00 | 8555.2 | 7125.45 | 15680.65
20:30 | 8473.7 | 7152.37 | 15626.07 |  | Executive Engineer
21:00 | 8392.2 | 7179.29 | 15571.49 |  | Network Operation Division
21:30 | 8250.7 | 7211.99 | 15462.69
22:00 | 8109.2 | 7244.69 | 15353.89
22:30 | 8091.7 | 7302.87 | 15394.57
23:00 | 8074.2 | 7361.05 | 15435.25

## En-Curve
QF-LDC-12
Date | 23-06-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3910 | 2214.5 | 917 | 38 | 36 | 1404.49 | 172 | 4350 | 0 | 533 | 1613.2 | 0 | 0 | 1 | 56 | DAILY ENERGY CURVE
00:30 | 3932.5 | 2221.25 | 898.5 | 38 | 38 | 1409.365 | 172 | 4315 | 0 | 570 | 1584.7 | 0 | 0 | 2.5 | 64.5 | 23-06-2025
01:00 | 3955 | 2228 | 880 | 38 | 40 | 1414.24 | 172 | 4280 | 0 | 607 | 1556.2 | 0 | 0 | 4 | 73
01:30 | 3940 | 2227.5 | 880 | 38 | 37 | 1413.345 | 172 | 4256.5 | 0 | 507.5 | 1462.7 | 0 | 0 | 3.5 | 69.5 | Energy Generated | 342.9809 |  | MKWHr
02:00 | 3925 | 2227 | 880 | 38 | 34 | 1412.45 | 172 | 4233 | 0 | 408 | 1369.2 | 0 | 0 | 3 | 66 | Energy not Served | 0.338 |  | MKWHr
02:30 | 3914 | 2226 | 880 | 38 | 36 | 1357.14 | 172 | 4149 | 0 | 378.5 | 1297.7 | 0 | 0 | 17.5 | 57.5 | Total Energy Requirement | 343.3189 |  | MKWHr
03:00 | 3903 | 2225 | 880 | 38 | 38 | 1301.83 | 172 | 4065 | 0 | 349 | 1226.2 | 0 | 0 | 32 | 49
03:30 | 3914.5 | 2224.5 | 880 | 38 | 38 | 1205.46 | 172 | 4061.5 | 0 | 313.5 | 1198.2 | 0 | 0 | 20.5 | 38
04:00 | 3926 | 2224 | 880 | 38 | 38 | 1109.09 | 172 | 4058 | 0 | 278 | 1170.2 | 0 | 0 | 9 | 27
04:30 | 3929.5 | 2224.5 | 879.5 | 38 | 38 | 1113.495 | 172 | 3995.5 | 0 | 269.5 | 1091.7 | 0 | 0 | 10 | 25.5
05:00 | 3933 | 2225 | 879 | 38 | 38 | 1117.9 | 172 | 3933 | 0 | 261 | 1013.2 | 0 | 0 | 11 | 24
05:30 | 3894 | 2204.5 | 879.5 | 38 | 37 | 1041.15 | 172 | 3803.5 | 14.97 | 261 | 954.2 | 0 | 0 | 9 | 12
06:00 | 3855 | 2184 | 880 | 38 | 36 | 964.4 | 172 | 3674 | 29.94 | 261 | 895.2 | 0 | 0 | 7 | 0
06:30 | 3830.5 | 2149.5 | 880 | 38 | 34 | 911.04 | 172 | 3625.5 | 57.065 | 261 | 897.7 | 0 | 0 | 9 | 0
07:00 | 3806 | 2115 | 880 | 38 | 32 | 857.68 | 172 | 3577 | 84.19 | 261 | 900.2 | 0 | 0 | 11 | 0
07:30 | 3830.5 | 2102.5 | 879.5 | 38 | 29 | 867.04 | 172 | 3571 | 138.67 | 248 | 821.1 | 0 | 0 | 18.5 | 0
08:00 | 3855 | 2090 | 879 | 38 | 26 | 876.4 | 172 | 3565 | 193.15 | 235 | 742 | 0 | 0 | 26 | 0
08:30 | 3893 | 2128.25 | 879.5 | 38 | 25 | 881.61 | 172 | 3592.5 | 285.55 | 234.5 | 766.5 | 0 | 0 | 20 | 0
09:00 | 3931 | 2166.5 | 880 | 38 | 24 | 886.82 | 172 | 3620 | 377.95 | 234 | 791 | 0 | 0 | 14 | 0
09:30 | 3934 | 2191.25 | 880 | 38 | 25 | 880.66 | 172 | 3618 | 426.29 | 251.5 | 801 | 0 | 0 | 18.5 | 0
10:00 | 3937 | 2216 | 880 | 38 | 26 | 874.5 | 172 | 3616 | 474.63 | 269 | 811 | 0 | 0 | 23 | 0
10:30 | 3957.5 | 2230.3 | 880 | 38 | 29 | 876.69 | 172 | 3616.5 | 452.315 | 269 | 850.5 | 0 | 0 | 23.5 | 0
11:00 | 3978 | 2244.6 | 880 | 38 | 32 | 878.88 | 172 | 3617 | 430 | 269 | 890 | 0 | 0 | 24 | 0
11:30 | 4011 | 2248.2 | 879.5 | 38 | 31 | 977.64 | 172 | 3627 | 451.905 | 269 | 927.5 | 0 | 0 | 15.5 | 0
12:00 | 4044 | 2251.8 | 879 | 38 | 30 | 1076.4 | 172 | 3637 | 473.81 | 269 | 965 | 0 | 0 | 7 | 0
12:30 | 3990 | 2227.15 | 879 | 38 | 31 | 1149.295 | 172 | 3658 | 487.29 | 276.5 | 1101.5 | 0 | 0 | 9.5 | 0
13:00 | 3936 | 2202.5 | 879 | 38 | 32 | 1222.19 | 172 | 3679 | 500.77 | 284 | 1238 | 0 | 0 | 12 | 0
13:30 | 3905 | 2182.75 | 879.5 | 38 | 30 | 1218.945 | 172 | 3703.5 | 468.495 | 284 | 1323 | 0 | 0 | 15.5 | 0
14:00 | 3874 | 2163 | 880 | 38 | 28 | 1215.7 | 172 | 3728 | 436.22 | 284 | 1408 | 0 | 0 | 19 | 0
14:30 | 3904 | 2195.5 | 880 | 38 | 31 | 1221.57 | 172 | 3762.5 | 422.555 | 290.5 | 1404 | 0 | 0 | 24 | 0
15:00 | 3934 | 2228 | 880 | 38 | 34 | 1227.44 | 172 | 3797 | 408.89 | 297 | 1400 | 0 | 0 | 29 | 0
15:30 | 3920 | 2219 | 880 | 38 | 36 | 1221.24 | 172 | 3826.5 | 316.715 | 309.5 | 1421 | 0 | 0 | 24.5 | 0
16:00 | 3906 | 2210 | 880 | 38 | 38 | 1215.04 | 172 | 3856 | 224.54 | 322 | 1442 | 0 | 0 | 20 | 0
16:30 | 3861.5 | 2163.5 | 880 | 38 | 37 | 1163.48 | 172 | 3824.5 | 173.24 | 313 | 1427 | 0 | 0 | 19 | 0
17:00 | 3817 | 2117 | 880 | 38 | 36 | 1111.92 | 172 | 3793 | 121.94 | 304 | 1412 | 0 | 0 | 18 | 0
17:30 | 3722 | 2087.25 | 880 | 38 | 35 | 1111.93 | 172 | 3762 | 72.215 | 313 | 1438 | 0 | 0 | 21 | 0
18:00 | 3627 | 2057.5 | 880 | 38 | 34 | 1111.94 | 172 | 3731 | 22.49 | 322 | 1464 | 0 | 0 | 24 | 0
18:30 | 3735.5 | 2138.25 | 880 | 38 | 38 | 1196.69 | 172 | 3928 | 11.245 | 403 | 1544.5 | 0 | 0 | 25 | 0
19:00 | 3844 | 2219 | 880 | 38 | 42 | 1281.44 | 172 | 4125 | 0 | 484 | 1625 | 0 | 0 | 26 | 0
19:30 | 3815 | 2280 | 879 | 38 | 42 | 1406.12 | 172 | 4559 | 0 | 586 | 1876.2 | 0 | 0 | 11 | 0
20:00 | 3797 | 2286 | 880 | 38 | 40 | 1410.45 | 172 | 4528 | 0 | 622 | 1884.2 | 0 | 0 | 23 | 0
20:30 | 3818.5 | 2263.5 | 879.5 | 38 | 38 | 1408.87 | 172 | 4558 | 0 | 609.5 | 1820.7 | 0 | 0 | 19.5 | 0
21:00 | 3840 | 2241 | 879 | 38 | 36 | 1407.29 | 172 | 4588 | 0 | 597 | 1757.2 | 0 | 0 | 16 | 0
21:30 | 3836.5 | 2194.5 | 879.5 | 38 | 38 | 1416.49 | 172 | 4609.5 | 0 | 588.5 | 1674.7 | 0 | 0 | 15 | 0
22:00 | 3833 | 2148 | 880 | 38 | 40 | 1425.69 | 172 | 4631 | 0 | 580 | 1592.2 | 0 | 0 | 14 | 0
22:30 | 3859.5 | 2156 | 880 | 38 | 43 | 1424.37 | 172 | 4684 | 0 | 581 | 1538.2 | 0 | 0 | 18.5 | 21.5
23:00 | 3886 | 2164 | 880 | 38 | 46 | 1423.05 | 172 | 4737 | 0 | 582 | 1484.2 | 0 | 0 | 23 | 43
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 23-06-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 385 | 06:00 | 370 | 23:00 | Payra | 416 | 06:00 | 406 | 23:00
Ashuganj | 404 | 6:00 | 381 | 13:00 | Rahanpur | 400 | 07:00 | 382 | 23:00
Bhulta | 399 | 06:00 | 371 | 12:00 | Rampal | 401 | 06:00 | 389 | 00:00
Bibiana | 389 | 06:00 | 382 | 19:00
BIPTC | 399 | 09:00 | 388 | 22:00
Bogura | 388 | 07:00 | 368 | 02:00
Gopalganj | 398 | 07:00 | 380 | 23:00
Kaliakoir | 376 | 06:00 | 361 | 23:00
Madunaghat | 396 | 07:00 | 389 | 23:00
Meghnaghat | 388 | 06:00 | 376 | 23:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 225 | 06:00 | 215 | 12:00 | Keranigonj | 223 | 06:00 | 214 | 12:00
AKSML | 230 | 00:00 | 224 | 14:00 | Khulna(S) | 230 | 08:00 | 213 | 23:00
Aminbazar | 226 | 06:00 | 215 | 12:00 | Madunaghat | 231 | 18:00 | 227 | 15:00
Ashuganj | 234 | 06:00 | 222 | 23:00 | Madunaghat-400 | 232 | 07:00 | 228 | 10:00
Ashuganj-400 | 234 | 6:00 | 222 | 23:00 | Maniknagar | 220 | 04:00 | 212 | 12:00
Baghabari | 234 | 06:00 | 224 | 19:30 | Meghnaghat | 230 | 04:00 | 221 | 13:00
Barapukuria | 224 | 07:00 | 215 | 22:00 | Meghnaghat-400 | 224 | 06:00 | 217 | 12:00
Barapukuria-230 | 224 | 7:00 | 222 | 23:00 | Mirsorai | 227 | 07:00 | 220 | 19:00
Barishal | 235 | 06:00 | 223 | 23:00 | Rajshahi | 234 | 06:00 | 221 | 19:30
Bheramara | 233 | 07:00 | 221 | 19:30 | Rampal | 230 | 06:00 | 218 | 00:00
Bhulta | 231 | 06:00 | 213 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 227 | 06:00 | 222 | 22:00 | Rampura | 231 | 06:00 | 210 | 12:00
BIPTC | 236 | 06:00 | 221 | 23:00 | Shikalbaha | 229 | 04:00 | 225 | 10:00
Bogura | 234 | 06:00 | 222 | 19:30 | Shyampur | 223 | 06:00 | 215 | 12:00
Bogura-400 | 235 | 07:00 | 223 | 19:30 | Siddhirganj | 220 | 07:00 | 215 | 12:00
Borhanuddin | 240 | 07:00 | 231 | 23:00 | Sirajgonj | 238 | 07:00 | 231 | 23:00
BSRM | 229 | 07:00 | 220 | 19:00 | Sreepur | 230 | 06:00 | 220 | 19:30
Cumilla(N) | 223 | 06:00 | 214 | 23:00 | Tongi | 225 | 06:00 | 215 | 14:00
Faridpur | 233 | 06:00 | 225 | 03:00
Fenchuganj | 229 | 06:00 | 222 | 14:00
Ghorashal | 235 | 04:00 | 220 | 15:00
Ghorashal-230 | 231 | 06:00 | 214 | 12:00
Gopalganj | 234 | 06:00 | 222 | 23:00
GPH | 230 | 07:00 | 223 | 15:00
Haripur | 221 | 07:00 | 214 | 12:00
Hasnabad | 223 | 05:00 | 215 | 15:00
Hathazari | 231 | 05:00 | 226 | 19:00
Ishurdi | 236 | 06:00 | 224 | 19:30
Jhenaidah | 230 | 06:00 | 214 | 19:30
Kaliakoir | 232 | 06:00 | 220 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 00:00 | 121 | 12:00 | Madartek | 136 | 00:00 | 121 | 12:00
Agargaon | 132 | 06:00 | 124 | 12:00 | Madunaghat | 131 | 11:00 | 128 | 15:00
Agrabad | 132 | 07:00 | 128 | 10:00 | Magura | 133 | 06:00 | 120 | 21:00
AKS | 131 | 05:00 | 126 | 10:00 | Mahasthangarh | 135 | 10:00 | 125 | 19:30
Aminbazar | 133 | 06:00 | 126 | 12:00 | Manikganj | 130 | 07:00 | 120 | 00:00
Amnura | 136 | 07:00 | 124 | 00:00 | Maniknagar | 131 | 07:00 | 124 | 12:00
Ashuganj | 137 | 06:00 | 132 | 15:00 | Matarbari | 121 | 08:00 | 113 | 00:00
Bagerhat | 132 | 08:00 | 116 | 23:00 | Matuail | 128 | 18:30 | 123 | 12:00
Bajitpur | 131 | 06:00 | 123 | 19:00 | Millgate | 133 | 07:00 | 122 | 12:00
Bakulia | 133 | 06:00 | 129 | 11:00 | Mirpur | 131 | 05:00 | 125 | 11:00
Banani | 135 | 06:00 | 122 | 12:00 | Mirzapur | 130 | 08:00 | 123 | 22:00
Bangabhaban | 131 | 07:00 | 124 | 12:00 | Mithapukur | 130 | 08:00 | 118 | 00:00
Barapukuria | 137 | 06:00 | 128 | 00:00 | MI_Cement | 127 | 06:00 | 122 | 12:00
Barguna | 134 | 09:00 | 128 | 23:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 136 | 05:00 | 127 | 23:00 | Mogbazar | 125 | 13:00 | 121 | 12:00
Barishal-230 | 137 | 07:00 | 128 | 23:00 | Mongla | 132 | 07:00 | 118 | 23:00
Baroaulia | 133 | 21:00 | 129 | 10:00 | Motijheel | 131 | 07:00 | 124 | 12:00
Baroirhat | 125 | 18:00 | 119 | 00:00 | Muktagacha | 135 | 10:00 | 128 | 19:00
Bashundhara | 133 | 05:00 | 119 | 12:00 | Munshiganj | 127 | 18:30 | 122 | 00:00
BashundharaCement | 126 | 05:00 | 122 | 00:00 | Muradnagar | 126 | 07:00 | 119 | 00:00
Beanibazar | 127 | 08:00 | 122 | 23:00 | Mymensingh | 136 | 10:00 | 114 | 19:00
Benapole | 131 | 07:00 | 115 | 23:00 | Naogaon | 133 | 07:00 | 122 | 19:30
Bhaluka | 130 | 06:00 | 123 | 15:00 | Narail | 132 | 07:00 | 117 | 21:00
Bhandaria | 131 | 18:00 | 120 | 21:00 | Narinda | 131 | 7:00 | 124 | 12:00
Bhangura | 133 | 09:00 | 127 | 00:00 | Narshingdi | 132 | 00:00 | 117 | 12:00
Bheramara | 137 | 07:00 | 131 | 19:30 | Natore | 137 | 19:30 | 126 | 23:00
Bheramara(GK) | 137 | 06:00 | 131 | 19:30 | Nawabganj | 133 | 06:00 | 125 | 23:00
Bhulta | 124 | 18:30 | 118 | 02:00 | Netrakona | 124 | 18:30 | 112 | 20:00
Bog-Sherpur | 135 | 06:00 | 127 | 19:30 | New | 134 | 04:00 | 123 | 12:00
Bogura | 137 | 06:00 | 129 | 01:00 | Niamatpur | 136 | 09:00 | 128 | 23:00
Bogura-230 | 138 | 07:00 | 129 | 19:30 | Noapara | 134 | 07:00 | 120 | 23:00
Brahmanbaria | 133 | 05:00 | 123 | 23:00 | Pabna | 134 | 06:00 | 127 | 19:30
Cantonment | 131 | 05:00 | 124 | 12:00 | Palashbari | 130 | 10:00 | 117 | 01:00
Chandina | 128 | 07:00 | 121 | 01:00 | Panchagarh | 139 | 06:00 | 121 | 19:30
Chandpur | 126 | 07:00 | 115 | 01:00 | Patuakhali | 134 | 07:00 | 130 | 00:00
Chandraghona | 132 | 18:00 | 129 | 10:00 | Payra | 136 | 06:00 | 132 | 23:00
Chapai | 131 | 08:00 | 124 | 23:00 | PHP | 124 | 07:00 | 116 | 01:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 127 | 07:00 | 122 | 12:00 | Postogola | 129 | 07:00 | 125 | 02:00
Chauddagram | 124 | 18:00 | 116 | 01:00 | Purbachal | 135 | 06:00 | 121 | 12:00
Chhatak | 127 | 08:00 | 120 | 22:00 | Purbasadipur | 134 | 06:00 | 122 | 12:00
Chowmuhani | 119 | 18:00 | 109 | 19:00 | Rahanpur | 136 | 05:00 | 129 | 21:00
Chuadanga | 132 | 10:00 | 115 | 23:00 | Rahanpur-400 | 137 | 07:00 | 130 | 22:00
Coxsbazar | 121 | 17:00 | 113 | 00:00 | Rahim | 128 | 05:00 | 123 | 13:00
Cumilla(N) | 128 | 07:00 | 120 | 23:00 | Rajbari | 136 | 06:00 | 126 | 23:00
Cumilla(S) | 132 | 04:00 | 119 | 15:00 | Rajendrapur | 134 | 00:00 | 122 | 15:00
Daudkandi | 124 | 06:00 | 117 | 00:00 | Rajshahi | 135 | 07:00 | 127 | 21:00
Dhaka | 137 | 00:00 | 121 | 12:00 | Rajshahi-230 | 135 | 06:00 | 118 | 22:00
Dhamrai | 129 | 04:00 | 122 | 15:00 | Ramganj | 122 | 07:00 | 115 | 04:00
Dhanmondi | 134 | 06:00 | 122 | 12:00 | Rampur | 131 | 01:00 | 128 | 11:00
Dohazari | 130 | 08:00 | 125 | 10:00 | Rampura | 135 | 00:00 | 121 | 12:00
Faridpur | 137 | 07:00 | 130 | 00:00 | Rangamati | 130 | 02:00 | 128 | 10:00
Fatullah | 128 | 06:00 | 123 | 12:00 | Rangpur | 133 | 11:00 | 124 | 00:00
Fenchuganj | 134 | 06:00 | 131 | 02:00 | Ruppur | 137 | 03:00 | 131 | 19:30
Feni | 123 | 07:00 | 115 | 01:00 | Saidpur | 132 | 06:00 | 119 | 20:00
Ghatail | 130 | 05:00 | 123 | 21:00 | Satkhira | 133 | 07:00 | 116 | 23:00
Ghorashal | 137 | 04:00 | 128 | 12:00 | Satmasjid | 138 | 18:00 | 124 | 12:00
Goalpara | 137 | 09:00 | 123 | 23:00 | Savar | 131 | 20:00 | 125 | 02:00
Gollamari | 137 | 08:00 | 124 | 23:00 | SevenRings | 137 | 06:00 | 128 | 12:00
Gopalganj | 135 | 07:00 | 124 | 23:00 | ShahCement | 127 | 07:00 | 122 | 12:00
Gopalganj-400 | 137 | 06:00 | 130 | 23:00 | Shahjadpur | 136 | 04:00 | 130 | 21:00
Gulshan | 135 | 03:00 | 121 | 12:00 | Shahjibazar | 130 | 06:00 | 122 | 23:00
Halishahar | 134 | 21:00 | 128 | 10:00 | Shahmirpur | 134 | 20:00 | 131 | 00:00
Haripur | 128 | 07:00 | 124 | 12:00 | Shariatpur | 135 | 06:00 | 125 | 23:00
HaripurSBU | 128 | 18:30 | 120 | 03:00 | Sherpur | 137 | 05:00 | 130 | 02:00
Hasnabad | 128 | 04:00 | 124 | 15:00 | Shikalbaha | 123 | 05:00 | 119 | 08:00
Hathazari | 135 | 06:00 | 130 | 19:00 | Shikalbaha-230 | 134 | 07:00 | 131 | 11:00
Ishurdi | 138 | 06:00 | 131 | 21:00 | Shitalakhya | 127 | 06:00 | 122 | 12:00
Jaldhaka | 131 | 06:00 | 118 | 19:30 | Sholosohor | 133 | 07:00 | 127 | 11:00
Jamalpur | 140 | 05:00 | 133 | 00:00 | Shyampur | 127 | 08:00 | 122 | 12:00
Jashore | 134 | 06:00 | 119 | 19:30 | Shyampur-230 | 127 | 06:00 | 122 | 12:00
Jhenaidah | 136 | 07:00 | 120 | 22:00 | Siddhirganj | 128 | 02:00 | 124 | 12:00
Jhenaidah-230 | 136 | 06:00 | 124 | 21:00 | Sirajganj | 133 | 09:00 | 125 | 23:00
Joydebpur | 134 | 00:00 | 123 | 14:00 | Sonargaon | 127 | 18:00 | 121 | 12:00
Joypurhat | 131 | 06:00 | 120 | 00:00 | Sreemongol | 130 | 07:00 | 123 | 23:00
Juldah | 134 | 20:00 | 130 | 11:00 | Sreepur | 133 | 06:00 | 126 | 19:30
Kabirpur | 133 | 07:00 | 121 | 12:00 | Srinagar | 133 | 06:00 | 126 | 12:00
Kachua | 125 | 06:00 | 115 | 01:00 | SSM | 136 | 03:00 | 132 | 15:00
Kaliakoir | 134 | 06:00 | 126 | 12:00 | Sunamganj | 124 | 07:00 | 118 | 01:00
Kallyanpur | 131 | 01:00 | 126 | 12:00 | Sylhet | 130 | 07:00 | 124 | 23:00
Kalurghat | 131 | 07:00 | 128 | 09:00 | Sylhet-132 | 129 | 03:00 | 125 | 22:00
Kamrangirchar | 134 | 06:00 | 120 | 11:00 | Tangail | 129 | 06:00 | 121 | 22:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 137 | 06:00 | 120 | 19:30
Kasba | 125 | 06:00 | 118 | 01:00 | TK | 131 | 06:00 | 129 | 00:00
Kazla | 130 | 06:00 | 124 | 13:00 | Tongi | 134 | 05:00 | 126 | 12:00
Keranigonj | 134 | 06:00 | 127 | 12:00 | Ullahpara | 134 | 06:00 | 124 | 20:00
Khagrachori | 130 | 06:00 | 127 | 12:00 | Ullon | 135 | 00:00 | 121 | 12:00
Khulna | 135 | 09:00 | 121 | 23:00 | Uttara | 131 | 06:00 | 124 | 12:00
Khulna(S) | 137 | 08:00 | 124 | 23:00 | UttaraNew | 131 | 06:00 | 125 | 12:00
Khulshi | 131 | 06:00 | 127 | 11:00 | Zigatola | 133 | 06:00 | 126 | 13:00
Kishoreganj | 128 | 05:00 | 120 | 19:30
Kodda | 133 | 00:00 | 122 | 12:00
KSRM | 134 | 21:00 | 128 | 02:00
Kulaura | 133 | 06:00 | 129 | 22:00
Kurigram | 132 | 11:00 | 120 | 00:00
Kushtia | 133 | 06:00 | 125 | 22:00
Lalbag | 133 | 06:00 | 127 | 00:00
Lalmonirhat | 130 | 10:00 | 120 | 16:00
Madanganj | 126 | 05:00 | 122 | 10:00
Madaripur | 136 | 05:00 | 130 | 19:30
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division