## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 25-06-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-06-2025 | during | 25-06-2025 | during | 25-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 391 | 325 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 300 | 450 | 450 | 450 | 450 | Allocation limit by Titas, instructed by DS(Gen)
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 299 | 278 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 40 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 325 | 280 | 335 | 335 | 270 | 270 | Allocation limit by Titas, instructed by DS(Gen)
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 98 | 8 | 102 | 32 | 32 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 96 | 143 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20.5 | 19 | 4.4 | 4.4 | 4.4 | 4.4 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 75 | 210 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 70 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 88 | 105 | 105 | 88 | 88 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 16 | 68 | 104 | 104 | 50 | 50 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 90 | 108 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 26 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 350 | 350 | 584 | 584 | 300 | 300 | None
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 142 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2427.5 | 2823 | 5093.8 | 5159.8 | 3165.48 | 3137.48
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 14 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 8 | 0 | 17 | 0 | 17 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 13 | 32 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 172 | 172 | 172 | 172 | 172 | 172 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 215 | 215 | 215 | 210 | 210 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 18 | 57 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 71 | 64 | 80 | 72 | 72 | Machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 64 | 65 | 65 | 65 | 65 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 86 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 4 | 2 | 2 | 25 | 4 | 15 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0 | 0 | 3.9 | 0 | 3.9 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 150 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 9 | 15 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 21 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 5 | 160 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1100 | 1100 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 43 | 27 | 52 | 42 | 52 | 42 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 202 | 202 | 575 | 575 | 200 | 200 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1990 | 2502 | 3618.62 | 3626.72 | 3218.62 | 3198.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 194 | 186 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 336 | 347 | 353.35 | 353.35 | 320 | 320 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 340 | 340 | 340 | 340 | 340 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 26 | 26 | 46.7 | 46.7 | 23 | 23 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 44 | 10 | 55 | 55 | 48 | 48 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 0 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 56 | 139 | 150 | 150 | 145 | 145 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 43 | 47 | 47 | 47 | 47 | Machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 143 | 160 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 36 | 44 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 20.83 | 24.5 | 16 | 16 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 95 | 97 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 28 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 48 | 115 | 115 | 115 | 115 | 115 | Fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 23 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1480.2 | 1657.2 | 2447.08 | 2400.75 | 2090.2 | 2040.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-06-2025 | during | 25-06-2025 | during | 25-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 28 | 11 | 157.5 | 157.5 | 27 | 27 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 141 | 163 | 200 | 200 | 160 | 160 | Fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 70 | 102 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 52.27 | 0 | 39 | 0 | 39 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 11 | 11 | 22 | 22 | 22 | 22
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 320.27 | 304 | 590.1 | 549 | 419.6 | 378.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 35 | 0 | 35 | 35 | 33 | 33 | Machine Problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 152 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 27 | 25 | 30 | 30 | 30 | 30 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 37 | 64 | 64 | 0 | 0 | Under Maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 165 | 164 | 160 | 160 | 160 | 160 | Machine Problem
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 7 | 7 | Machine problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 295 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 372 | 300 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | Machine Problem
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1403 | 1301 | 1541 | 1541 | 1361 | 1361
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 879 | 450 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 14 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 14 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 221 | 162 | 410 | 410 | 182 | 182 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 51 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 80 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 62 | 0 | 45 | 0 | 45 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 806 | 1146 | 1234.2 | 1234.2 | 1204 | 1204 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2006 | 1955 | 3599.2 | 3554.2 | 3341 | 3296
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 617 | 617 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 32 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 6 | 10 | 10 | 10 | 6 | 6 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 895 | 1060 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 30 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 173 | 245 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.15 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 2031.15 | 2334 | 2172 | 2171 | 2106 | 2105
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 47 | 47 | 44 | 44 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 5 | 32 | 32 | 30 | 30 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 26 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 181 | 140 | 214 | 214 | 140 | 140 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 182 | 140 | 220 | 220 | 141 | 141 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is in Standby as per NLDC request.
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 405 | 396 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 | 30 | 30 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 45 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 113 | 113 | 28 | 28 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.66 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1232.46 | 1380 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 54.88 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 86 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 2146 | 2350 | 3192.47 | 3025.87 | 2687.68 | 2521.08
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 48 | 47 | 47 | 47 | 47 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 159 | 189 | 150 | 150 | 150 | 150 | Machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 98 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.7 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 100 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 18 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 123 | 0 | 77.38 | 0 | 77.38 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 352.7 | 435 | 556.98 | 445 | 556.98 | 445
System Total |  |  |  |  | 28565.2 | 27084.055 | 14156.82 | 15661.2 | 22811.25 | 22473.34 | 18946.56 | 18482.98
Forecast Scenario (25-06-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15440 |  | 0 |  | 15440
|  |  |  | 1:00 | 15450 |  | 0 |  | 15450
|  |  |  | 2:00 | 14970 |  | 0 |  | 14970
|  |  |  | 3:00 | 14480 |  | 0 |  | 14480
|  |  |  | 4:00 | 14130 |  | 0 |  | 14130
|  |  |  | 5:00 | 13840 |  | 0 |  | 13840
|  |  |  | 6:00 | 13190 |  | 0 |  | 13190
|  |  |  | 7:00 | 12930 |  | 0 |  | 12930
|  |  |  | 8:00 | 12890 |  | 0 |  | 12890
|  |  |  | 9:00 | 13330 |  | 0 |  | 13330
|  |  |  | 10:00 | 13530 |  | 0 |  | 13530
|  |  |  | 11:00 | 13650 |  | 0 |  | 13650
|  |  |  | 12:00 | 14040 |  | 0 |  | 14040
|  |  |  | 13:00 | 14390 |  | 0 |  | 14390
|  |  |  | 14:00 | 14440 |  | 0 |  | 14440
|  |  |  | 15:00 | 14640 |  | 0 |  | 14640
|  |  |  | 16:00 | 14520 |  | 0 |  | 14520
|  |  |  | 17:00 | 14020 |  | 0 |  | 14020
|  |  |  | 18:00 | 13680 |  | 0 |  | 13680
|  |  |  | 18:30 | 14300 |  | 0 |  | 14300
|  |  |  | 19:00 | 14930 |  | 0 |  | 14930
|  |  |  | 19:30 | 15860 |  | 0 |  | 15860
|  |  |  | 20:00 | 15880 |  | 0 |  | 15880
|  |  |  | 21:00 | 15770 |  | 0 |  | 15770
|  |  |  | 22:00 | 15550 |  | 0 |  | 15550
|  |  |  | 23:00 | 15680 |  | 0 |  | 15680
Probable Maximum Temperature: |  |  | 31.60°C
Probable Maximum Demand at Day Peak: |  |  | 14040.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 15880.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15880.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 345.37 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:20 hrs on 25-06-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 24-06-2025 | [28 empty] | Date: | 24-06-2025 | [28 empty] | Date: | 24-06-2025 | [28 empty] | Date: | 24-06-2025 | [28 empty] | Date: | 24-06-2025 | [12 empty] | Date: | 24-06-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [12 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 55 | 105 | 146 | 0 | 0 | 0 | 89 | 51 | 350 | 295 | 0 | 0 | 35 | 280 | 0 | 0 | 0 | 125 | 26 | 21 | 0 | 500 | 0 | 15 | 0 | 0 | 14 | 66 | 48 | 0 | 88 | 100 | 0 | 172 | 3 | 22 | 202 | 0 | 0 | 19 | 0 | 5 | 220 | 0 | 0 | 0 | 1171 | 0 | 51 | 50 | 86 | 0 | 349 | 340 | 48 | 184 | 28 | 47 | 0 | 156 | 11 | 19 | 114 | 48 | 52.2 | 0 | 46 | 300 | 320 | 357 | 36 | 30 | 159 | 7 | 0 | 59 | 28 | 0 | 0 | 168 | 17 | 112 | 164 | 48 | 0 | 0 | 0 | 8067.2 | 880 | 258 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1220 | 35 | 1413.99 | 0 | 38 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 181 | 0 | 0 | 0 | 414 | 0 | 0 | 189 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 10 | 120 | 220 | 0 | 617 | 1110 | 0 | 7449.99 | 15517.19 | 98.68
01:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 55 | 105 | 146 | 0 | 0 | 0 | 86 | 51 | 350 | 290 | 0 | 0 | 35 | 280 | 0 | 0 | 0 | 125 | 26.7 | 21 | 0 | 500 | 0 | 15 | 0 | 0 | 18 | 66 | 48 | 0 | 88 | 100 | 0 | 172 | 15 | 23 | 201 | 0 | 0 | 19 | 0 | 16 | 220 | 0 | 0 | 0 | 1165 | 0 | 51 | 50 | 86 | 0 | 350 | 340 | 48 | 184 | 28 | 34 | 0 | 162 | 9 | 19 | 114 | 46 | 52.2 | 0 | 46 | 305 | 320 | 337 | 36 | 30 | 158 | 7 | 0 | 59 | 30 | 0 | 0 | 168 | 17 | 112 | 164 | 49 | 0 | 0 | 0 | 8045.9 | 880 | 258 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 850 | 34 | 1405.11 | 0 | 38 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 181 | 0 | 0 | 0 | 414 | 0 | 0 | 191 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 261 | 10 | 120 | 220 | 0 | 617 | 1107 | 0 | 7095.11 | 15141.01 | 98.68
02:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 14 | 101 | 145 | 0 | 0 | 0 | 25 | 51 | 350 | 286 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 125 | 26.7 | 21 | 0 | 500 | 0 | 15 | 0 | 0 | 22 | 33 | 24 | 0 | 88 | 100 | 0 | 172 | 15 | 23 | 201 | 0 | 0 | 19 | 0 | 15 | 221 | 0 | 0 | 0 | 1110 | 0 | 51 | 50 | 86 | 0 | 354 | 340 | 48 | 179 | 28 | 34 | 0 | 162 | 9 | 20 | 114 | 44 | 52.2 | 0 | 46 | 295 | 320 | 311 | 36 | 30 | 152 | 7 | 0 | 59 | 30 | 0 | 0 | 168 | 17 | 112 | 153 | 49 | 0 | 0 | 0 | 7724.9 | 880 | 259 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 727 | 17 | 1403.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 181 | 0 | 0 | 0 | 335 | 0 | 0 | 190 | 49 | 115 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 251 | 11 | 120 | 220 | 0 | 617 | 1097 | 0 | 6764.97 | 14489.87 | 98.68
03:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 25 | 74 | 145 | 0 | 0 | 0 | 15 | 32 | 350 | 302 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 90 | 26.8 | 21 | 0 | 500 | 0 | 0 | 0 | 0 | 37 | 7 | 0 | 0 | 60 | 75 | 0 | 172 | 0 | 24 | 204 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1104 | 0 | 51 | 0 | 86 | 0 | 351 | 340 | 48 | 180 | 28 | 34 | 0 | 162 | 9 | 19 | 114 | 42 | 52.2 | 0 | 44 | 300 | 320 | 357 | 36 | 30 | 143 | 7 | 0 | 59 | 30 | 0 | 0 | 168 | 17 | 104 | 163 | 49 | 0 | 0 | 0 | 7503 | 880 | 259 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 17 | 1317.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 181 | 0 | 0 | 0 | 364 | 0 | 0 | 192 | 49 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 259 | 10 | 120 | 220 | 0 | 617 | 1050 | 0 | 6601.09 | 14104.09 | 98.68
04:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 17 | 70 | 146 | 0 | 0 | 0 | 0 | 0 | 350 | 304 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 70 | 26.8 | 21 | 0 | 500 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 36 | 48 | 0 | 172 | 0 | 24 | 201 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1057 | 0 | 51 | 0 | 86 | 0 | 349 | 340 | 48 | 180 | 28 | 34 | 0 | 161 | 9 | 17 | 114 | 42 | 52.2 | 0 | 23 | 305 | 320 | 345 | 36 | 30 | 142 | 7 | 0 | 59 | 30 | 0 | 0 | 168 | 17 | 65 | 163 | 49 | 0 | 0 | 11 | 7255 | 880 | 260 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 903 | 0 | 1166.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 181 | 0 | 0 | 0 | 377 | 0 | 0 | 192 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 10 | 120 | 220 | 0 | 617 | 1000 | 0 | 6387.9 | 13642.9 | 98.68
05:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 17 | 70 | 145 | 0 | 0 | 0 | 0 | 0 | 350 | 293 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 70 | 26.8 | 21 | 0 | 500 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 24 | 201 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 935 | 0 | 51 | 0 | 35 | 0 | 353 | 340 | 48 | 195 | 28 | 36 | 0 | 158 | 9 | 17 | 114 | 40 | 52.2 | 0 | 23 | 300 | 320 | 335 | 36 | 30 | 139 | 7 | 0 | 59 | 30 | 0 | 0 | 168 | 17 | 65 | 151 | 49 | 0 | 0 | 12 | 6974 | 879 | 260 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1054 | 0 | 1111.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 181 | 0 | 0 | 0 | 347 | 0 | 0 | 193 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 10 | 120 | 220 | 0 | 617 | 930 | 0 | 6350.5 | 13324.5 | 98.68
06:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 17 | 70 | 112 | 0 | 0 | 0 | 0 | 0 | 350 | 300 | 0 | 0 | 0 | 280 | 0 | 0 | 2 | 52 | 26.8 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 34 | 201 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 859 | 1 | 51 | 0 | 16 | 0 | 354 | 280 | 48 | 214 | 28 | 35 | 0 | 144 | 9 | 19 | 85 | 32 | 25 | 5 | 0 | 295 | 320 | 343 | 36 | 30 | 132 | 7 | 0 | 59 | 30 | 0 | 0 | 168 | 17 | 65 | 151 | 50 | 0 | 4.68 | 12 | 6698.48 | 879 | 265 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9 | 980 | 0 | 910.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 2.57 | 175 | 0 | 181 | 0 | 0 | 0 | 345 | 0 | 0.23 | 194 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0 | 174 | 9 | 120 | 220 | 0 | 617 | 830 | 0 | 6002.22 | 12700.7 | 98.68
07:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 17 | 70 | 96 | 0 | 0 | 0 | 0 | 0 | 350 | 303 | 0 | 0 | 0 | 280 | 0 | 0 | 7 | 52 | 26.8 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 1 | 172 | 0 | 20 | 201 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 856 | 3 | 51 | 0 | 16 | 0 | 346 | 280 | 48 | 212 | 28 | 34 | 0 | 144 | 9 | 19 | 84 | 36 | 25 | 14 | 0 | 300 | 320 | 348 | 36 | 30 | 142 | 7 | 0 | 59 | 30 | 0 | 0 | 168 | 17 | 65 | 132 | 49 | 0 | 18.23 | 12 | 6745.03 | 879 | 265 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 21 | 820 | 0 | 861.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 8.47 | 182 | 0 | 181 | 0 | 0 | 0 | 381 | 0 | 0.79 | 192 | 48 | 0 | 0 | 0 | 0 | 0 | 0.2 | 4 | 0.15 | 0 | 173 | 7 | 120 | 220 | 0 | 617 | 800 | 0 | 5841.78 | 12586.81 | 98.68
08:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 19 | 70 | 96 | 0 | 0 | 0 | 0 | 0 | 350 | 301 | 0 | 0 | 0 | 280 | 0 | 0 | 7 | 52 | 24 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 3 | 172 | 0 | 4 | 200 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 875 | 5 | 51 | 0 | 16 | 0 | 340 | 340 | 48 | 209 | 28 | 34 | 0 | 144 | 9 | 19 | 82 | 34 | 25 | 28 | 0 | 300 | 320 | 358 | 36 | 30 | 154 | 7 | 0 | 59 | 30 | 0 | 0 | 168 | 17 | 65 | 132 | 49 | 1 | 21.3 | 12 | 6838.3 | 879 | 265 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 50 | 816 | 0 | 873.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 14.09 | 189 | 0 | 182 | 0 | 0 | 0 | 414 | 0 | 1.46 | 191 | 49 | 0 | 1 | 0 | 0 | 0 | 1.1 | 16 | 0.15 | 0 | 177 | 7 | 120 | 220 | 0 | 616 | 795 | 0 | 5952.84 | 12791.14 | 98.68
09:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 28 | 70 | 96 | 0 | 0 | 17 | 0 | 0 | 400 | 299 | 0 | 0 | 0 | 329 | 0 | 0 | 28 | 52 | 24 | 14 | 0 | 370 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 2 | 172 | 0 | 2 | 202 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1050 | 15 | 51 | 0 | 40 | 0 | 340 | 340 | 47 | 206 | 23 | 34 | 0 | 144 | 9 | 19 | 80 | 32 | 25 | 55 | 0 | 295 | 320 | 348 | 35 | 30 | 157 | 8 | 0 | 0 | 30 | 0 | 0 | 168 | 17 | 65 | 123 | 44 | 1 | 28.51 | 12 | 7005.51 | 878 | 252 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 69 | 828 | 0 | 930.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 26.87 | 186 | 0 | 182 | 0 | 0 | 0 | 414 | 0 | 1.75 | 194 | 49 | 0 | 2 | 0 | 0 | 0 | 0.5 | 31 | 0.62 | 0 | 176 | 6 | 120 | 220 | 0 | 616 | 815 | 0 | 6080.99 | 13086.5 | 98.68
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 29 | 70 | 96 | 0 | 0 | 17 | 17 | 0 | 450 | 297 | 0 | 0 | 0 | 326 | 0 | 0 | 29 | 52 | 23 | 14 | 0 | 350 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 12 | 12 | 3 | 172 | 0 | 2 | 201 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 1055 | 8 | 43 | 0 | 45 | 0 | 336 | 335 | 44 | 208 | 27 | 51 | 0 | 143 | 9 | 19 | 80 | 34 | 25 | 60 | 0 | 290 | 320 | 349 | 35 | 30 | 157 | 8 | 0 | 0 | 28 | 0 | 0 | 168 | 17 | 65 | 142 | 33 | 1 | 43.76 | 12 | 7105.76 | 879 | 244 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 78 | 829 | 0 | 1071.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 32.72 | 186 | 0 | 182 | 0 | 0 | 0 | 414 | 0 | 3.25 | 191 | 49 | 0 | 8 | 0 | 0 | 0 | 0.4 | 61 | 0.71 | 0 | 172 | 7 | 120 | 220 | 0 | 616 | 885 | 0 | 6355.83 | 13461.59 | 98.68
11:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 17 | 29 | 70 | 96 | 0 | 0 | 35 | 73 | 0 | 450 | 297 | 0 | 0 | 0 | 325 | 0 | 0 | 22 | 52 | 18 | 14 | 0 | 350 | 0 | 5 | 0 | 0 | 46 | 0 | 0 | 0 | 36 | 48 | 3 | 172 | 0 | 2 | 204 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1105 | 11 | 43 | 12 | 72 | 0 | 335 | 335 | 43 | 206 | 27 | 51 | 0 | 144 | 9 | 19 | 86 | 34 | 25 | 33 | 0 | 295 | 320 | 364 | 35 | 30 | 158 | 8 | 0 | 0 | 27 | 0 | 0 | 166 | 17 | 65 | 142 | 31 | 2 | 33.97 | 11 | 7335.97 | 878 | 234 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 65 | 803 | 0 | 1054.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 46.05 | 183 | 0 | 186 | 0 | 0 | 0 | 414 | 0 | 3.94 | 194 | 49 | 0 | 9 | 0 | 0 | 0 | 0.5 | 114 | 0.86 | 0 | 173 | 7 | 120 | 220 | 0 | 622 | 891 | 0 | 6404.06 | 13740.03 | 98.68
12:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 0 | 17 | 0 | 70 | 96 | 75 | 0 | 35 | 90 | 16 | 450 | 299 | 0 | 0 | 17 | 325 | 0 | 0 | 26 | 52 | 20.5 | 21 | 0 | 350 | 0 | 15 | 0 | 0 | 43 | 0 | 0 | 0 | 86 | 100 | 0 | 172 | 9 | 4 | 202 | 5 | 0 | 13 | 0 | 18 | 215 | 0 | 0 | 0 | 1100 | 8 | 51 | 56 | 8 | 0 | 336 | 340 | 44 | 194 | 26 | 48 | 0 | 143 | 9 | 19 | 95 | 36 | 52.2 | 23 | 0 | 290 | 320 | 372 | 35 | 30 | 156 | 8 | 0 | 0 | 27 | 0 | 0 | 165 | 17 | 70 | 141 | 28 | 1 | 52.27 | 11 | 7620.97 | 879 | 221 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 62 | 806 | 0 | 1232.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 54.88 | 181 | 0 | 182 | 0 | 0 | 0 | 405 | 0 | 4.66 | 159 | 50 | 0 | 18 | 0 | 0 | 0 | 2.7 | 123 | 0.15 | 0 | 173 | 6 | 120 | 220 | 0 | 617 | 895 | 0 | 6535.85 | 14156.82 | 98.68
13:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 0 | 17 | 0 | 92 | 110 | 224 | 15 | 35 | 90 | 28 | 370 | 292 | 0 | 0 | 17 | 325 | 0 | 0 | 32 | 142 | 20 | 21 | 0 | 180 | 0 | 65 | 0 | 0 | 41 | 0 | 40 | 0 | 88 | 100 | 3 | 172 | 16 | 6 | 201 | 17 | 0 | 20 | 0 | 45 | 215 | 0 | 0 | 0 | 1060 | 8 | 51 | 93 | 8 | 0 | 338 | 340 | 39 | 165 | 26 | 51 | 0 | 142 | 11 | 17 | 97 | 38 | 52.2 | 30 | 29 | 290 | 320 | 359 | 33 | 0 | 154 | 8 | 0 | 0 | 27 | 0 | 0 | 165 | 17 | 93 | 145 | 28 | 2 | 20.79 | 11 | 7777.99 | 879 | 214 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 60 | 777 | 0 | 1454.23 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 23.4 | 140 | 0 | 140 | 0 | 0 | 0 | 390 | 0 | 2.09 | 189 | 50 | 0 | 9 | 0 | 0 | 0 | 7 | 116 | 0.16 | 0 | 165 | 4 | 120 | 220 | 0 | 618 | 895 | 0 | 6599.88 | 14377.87 | 98.68
14:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 17 | 1 | 148 | 110 | 278 | 55 | 35 | 90 | 33 | 370 | 289 | 0 | 0 | 17 | 322 | 0 | 0 | 31 | 142 | 20 | 21 | 0 | 100 | 0 | 65 | 0 | 0 | 41 | 0 | 40 | 0 | 88 | 100 | 3 | 172 | 16 | 2 | 201 | 17 | 0 | 30 | 0 | 45 | 213 | 0 | 0 | 0 | 1100 | 2 | 51 | 112 | 0 | 0 | 336 | 340 | 24 | 164 | 27 | 60 | 0 | 142 | 15 | 17 | 103 | 40 | 52.2 | 47 | 41 | 295 | 320 | 363 | 33 | 0 | 135 | 8 | 0 | 0 | 27 | 0 | 0 | 165 | 17 | 94 | 148 | 28 | 1 | 21.8 | 11 | 7929 | 760 | 207 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 99 | 752 | 0 | 1461 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 44.34 | 140 | 0 | 140 | 0 | 0 | 0 | 360 | 0 | 3.68 | 191 | 50 | 20 | 11 | 2 | 0 | 0 | 4.7 | 78 | 0.07 | 0 | 171 | 5 | 120 | 220 | 0 | 616 | 915 | 0 | 6491.79 | 14420.79 | 98.68
15:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 17 | 52 | 149 | 109 | 278 | 55 | 35 | 90 | 42 | 420 | 295 | 0 | 0 | 17 | 326 | 0 | 0 | 15 | 142 | 19.5 | 21 | 0 | 60 | 0 | 65 | 0 | 0 | 60 | 6 | 40 | 0 | 88 | 100 | 3 | 172 | 15 | 2 | 202 | 17 | 0 | 32 | 0 | 51 | 212 | 0 | 0 | 0 | 1165 | 15 | 51 | 112 | 0 | 0 | 333 | 340 | 10 | 178 | 25 | 69 | 0 | 144 | 9 | 19 | 110 | 40 | 52.2 | 54 | 41 | 295 | 320 | 380 | 33 | 0 | 152 | 8 | 0 | 0 | 25 | 0 | 0 | 166 | 17 | 103 | 147 | 27 | 1 | 45.08 | 11 | 8181.78 | 465 | 195 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 34 | 895 | 0 | 1453 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 23.01 | 140 | 0 | 140 | 0 | 0 | 0 | 400 | 0 | 1.99 | 186 | 47 | 35 | 4 | 34 | 0 | 0 | 6.8 | 64 | 0.21 | 0 | 178 | 6 | 120 | 220 | 0 | 616 | 1016 | 0 | 6454.01 | 14635.79 | 98.68
16:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 17 | 55 | 149 | 109 | 195 | 55 | 35 | 90 | 50 | 300 | 282 | 0 | 0 | 17 | 280 | 0 | 0 | 14 | 125 | 19.3 | 21 | 0 | 300 | 0 | 65 | 0 | 0 | 43 | 64 | 43 | 0 | 100 | 100 | 3 | 172 | 15 | 2 | 203 | 90 | 0 | 32 | 0 | 47 | 212 | 0 | 0 | 0 | 1150 | 2 | 51 | 103 | 0 | 0 | 317 | 340 | 10 | 178 | 25 | 69 | 0 | 127 | 9 | 19 | 98 | 32 | 52.2 | 21 | 35 | 295 | 320 | 321 | 33 | 0 | 146 | 8 | 0 | 0 | 25 | 0 | 0 | 164 | 17 | 93 | 147 | 27 | 1 | 24 | 11 | 8041.5 | 451 | 182 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 65 | 952 | 0 | 1409 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 14.7 | 140 | 0 | 140 | 0 | 0 | 0 | 335 | 0 | 1.34 | 177 | 48 | 55 | 5 | 83 | 0 | 0 | 5 | 67 | 0.09 | 0 | 167 | 6 | 104 | 180 | 0 | 617 | 1050 | 0 | 6408.13 | 14449.63 | 98.68
17:00 | 24 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 54 | 20 | 149 | 98 | 145 | 55 | 35 | 90 | 48 | 300 | 284 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 125 | 18.3 | 21 | 0 | 300 | 0 | 15 | 0 | 0 | 55 | 54 | 64 | 0 | 48 | 100 | 1 | 172 | 15 | 2 | 202 | 90 | 0 | 32 | 0 | 17 | 213 | 0 | 0 | 0 | 1020 | 1 | 51 | 110 | 0 | 0 | 283 | 340 | 10 | 208 | 25 | 69 | 0 | 127 | 9 | 19 | 96 | 38 | 52.2 | 15 | 41 | 300 | 320 | 315 | 33 | 0 | 133 | 8 | 0 | 0 | 25 | 0 | 0 | 164 | 17 | 93 | 147 | 25 | 1 | 11.43 | 11 | 7692.93 | 452 | 175 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 30 | 887 | 0 | 1245 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 10.95 | 140 | 0 | 140 | 0 | 0 | 0 | 335 | 0 | 0.91 | 200 | 47 | 70 | 6 | 98 | 0 | 0 | 3.1 | 61 | 0.04 | 0 | 168 | 6 | 104 | 180 | 0 | 617 | 947 | 0 | 6089 | 13781.93 | 98.68
18:00 | 48 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 54 | 55 | 149 | 143 | 95 | 55 | 35 | 108 | 60 | 300 | 289 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 125 | 18.3 | 21 | 0 | 350 | 0 | 15 | 0 | 0 | 48 | 64 | 68 | 0 | 48 | 100 | 0 | 172 | 15 | 2 | 201 | 54 | 0 | 32 | 0 | 31 | 214 | 0 | 0 | 0 | 905 | 0 | 51 | 120 | 0 | 0 | 283 | 305 | 10 | 195 | 25 | 69 | 0 | 164 | 10 | 19 | 96 | 34 | 52.2 | 4 | 42 | 300 | 320 | 315 | 0 | 0 | 130 | 8 | 0 | 5 | 28 | 0 | 0 | 164 | 17 | 93 | 163 | 11 | 0 | 0.75 | 11 | 7653.25 | 451 | 172 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7 | 872 | 0 | 1109 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 4 | 0 | 6 | 0 | 1.18 | 140 | 0 | 140 | 0 | 0 | 0 | 346 | 0 | 0.1 | 190 | 47 | 35 | 4 | 60 | 0 | 0 | 1.4 | 12 | 0.03 | 0 | 173 | 7 | 106 | 180 | 0 | 617 | 800 | 0 | 5568.71 | 13221.96 | 98.67
19:00 | 92 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 54 | 55 | 149 | 143 | 97 | 40 | 35 | 108 | 66 | 300 | 296 | 0 | 0 | 35 | 280 | 0 | 0 | 0 | 142 | 19.5 | 21 | 0 | 350 | 2 | 30 | 0 | 0 | 33 | 64 | 70 | 0 | 48 | 100 | 0 | 172 | 15 | 2 | 201 | 70 | 0 | 32 | 1 | 39 | 214 | 0 | 0 | 0 | 1148 | 0 | 51 | 135 | 0 | 0 | 317 | 320 | 10 | 208 | 26 | 74 | 0 | 168 | 27 | 19 | 98 | 44 | 52.2 | 0 | 42 | 295 | 320 | 369 | 0 | 0 | 141 | 8 | 0 | 35 | 28 | 0 | 0 | 164 | 17 | 102 | 163 | 11 | 0 | 0 | 11 | 8216.7 | 451 | 166 | 0 | 5 | 7 | 38 | 0 | 0 | 0 | 0 | 22 | 0 | 956 | 20 | 1230 | 0 | 0 | 0 | 50 | 5 | 25 | 20 | 19 | 8 | 0 | 30 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0 | 187 | 48 | 70 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 16 | 186 | 10 | 120 | 220 | 0 | 617 | 823 | 10 | 6138 | 14354.7 | 98.67
19:30 | 98 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 54 | 55 | 149 | 143 | 210 | 40 | 35 | 108 | 68 | 300 | 278 | 0 | 0 | 35 | 280 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 350 | 21 | 150 | 0 | 0 | 27 | 64 | 71 | 0 | 100 | 100 | 0 | 172 | 15 | 2 | 202 | 160 | 0 | 32 | 14 | 57 | 215 | 0 | 0 | 0 | 1100 | 0 | 51 | 139 | 0 | 0 | 347 | 340 | 10 | 186 | 26 | 115 | 0 | 160 | 28 | 19 | 97 | 44 | 52.2 | 0 | 43 | 295 | 320 | 300 | 0 | 0 | 152 | 8 | 0 | 37 | 25 | 0 | 0 | 164 | 17 | 102 | 163 | 11 | 0 | 0 | 11 | 8587.2 | 450 | 162 | 0 | 14 | 14 | 38 | 0 | 0 | 0 | 0 | 80 | 0 | 1146 | 51 | 1380 | 0 | 43 | 0 | 70 | 5 | 45 | 50 | 26 | 25 | 0 | 30 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 396 | 0 | 0 | 189 | 48 | 100 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 32 | 245 | 10 | 120 | 220 | 0 | 617 | 1060 | 30 | 7074 | 15661.2
20:00 | 98 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 54 | 55 | 149 | 143 | 195 | 40 | 55 | 108 | 69 | 300 | 275 | 0 | 0 | 35 | 280 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 320 | 42 | 50 | 1 | 0 | 43 | 64 | 71 | 0 | 100 | 100 | 0 | 172 | 27 | 3 | 201 | 90 | 0 | 32 | 21 | 62 | 216 | 0 | 0 | 0 | 1150 | 0 | 51 | 138 | 0 | 0 | 300 | 285 | 10 | 208 | 26 | 115 | 0 | 159 | 27 | 19 | 100 | 44 | 52.2 | 0 | 43 | 295 | 320 | 300 | 0 | 0 | 151 | 8 | 0 | 37 | 25 | 0 | 0 | 164 | 17 | 102 | 163 | 11 | 0 | 0 | 11 | 8421.2 | 451 | 158 | 0 | 30 | 24 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 1147 | 48 | 1437 | 0 | 35 | 0 | 85 | 6 | 95 | 70 | 30 | 34 | 0 | 30 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 280 | 0 | 0 | 188 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 16 | 256 | 10 | 110 | 180 | 0 | 617 | 1110 | 17 | 7148 | 15569.2 | 98.67
21:00 | 32 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 35 | 55 | 149 | 143 | 145 | 15 | 55 | 108 | 68 | 300 | 289 | 0 | 0 | 35 | 280 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 320 | 15 | 50 | 11 | 0 | 33 | 64 | 71 | 0 | 100 | 100 | 0 | 172 | 17 | 3 | 201 | 35 | 0 | 32 | 25.5 | 17 | 216 | 0 | 0 | 0 | 1124 | 0 | 51 | 137 | 0 | 0 | 348 | 335 | 10 | 169 | 27 | 115 | 0 | 161 | 29 | 19 | 105 | 42 | 52.2 | 0 | 44 | 295 | 320 | 317 | 0 | 0 | 155 | 8 | 0 | 37 | 25 | 0 | 0 | 166 | 17 | 112 | 165 | 11 | 0 | 0 | 11 | 8206.7 | 451 | 153 | 0 | 38 | 37 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 1226 | 48 | 1438.03 | 0 | 46 | 0 | 50 | 25 | 96 | 35 | 30 | 8 | 0 | 30 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 350 | 0 | 0 | 190 | 47 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 16 | 272 | 8 | 110 | 220 | 0 | 616 | 1118 | 14 | 7253.03 | 15459.73 | 98.67
22:00 | 32 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 35 | 55 | 149 | 144 | 145 | 15 | 0 | 90 | 68 | 300 | 302 | 0 | 0 | 35 | 330 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 220 | 16 | 50 | 11 | 0 | 18 | 63 | 71 | 0 | 100 | 100 | 0 | 172 | 17 | 2 | 202 | 35 | 0 | 0 | 25.5 | 16 | 217 | 0 | 0 | 0 | 1150 | 0 | 51 | 142 | 0 | 0 | 300 | 340 | 6 | 183 | 10 | 110 | 0 | 167 | 28 | 19 | 106 | 42 | 52.2 | 0 | 44 | 290 | 320 | 347 | 0 | 0 | 146 | 8 | 0 | 37 | 25 | 0 | 0 | 166 | 17 | 112 | 165 | 11 | 0 | 0 | 11 | 8061.7 | 451 | 139 | 0 | 30 | 25 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 1186 | 54 | 1460.05 | 0 | 38 | 0 | 50 | 25 | 97 | 35 | 30 | 8 | 0 | 30 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0 | 191 | 47 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 16 | 282 | 11 | 110 | 220 | 0 | 618 | 1115 | 16 | 7279.05 | 15340.75 | 98.66
23:00 | 32 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 35 | 55 | 149 | 144 | 145 | 15 | 0 | 54 | 68 | 380 | 298 | 0 | 0 | 35 | 330 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 180 | 16 | 65 | 12 | 0 | 18 | 66 | 70 | 0 | 100 | 100 | 0 | 172 | 16 | 13 | 202 | 53 | 0 | 18 | 25.5 | 20 | 218 | 0 | 0 | 0 | 1195 | 0 | 51 | 145 | 0 | 0 | 340 | 340 | 5 | 170 | 10 | 79 | 0 | 180 | 28 | 19 | 111 | 46 | 52.2 | 0 | 44 | 295 | 320 | 370 | 0 | 0 | 147 | 8 | 0 | 37 | 22 | 0 | 0 | 166 | 17 | 112 | 164 | 11 | 0 | 0 | 11 | 8213.7 | 406 | 123 | 0 | 29 | 26 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 1210 | 68 | 1465.63 | 0 | 37 | 0 | 72 | 25 | 97 | 50 | 30 | 8 | 0 | 30 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0 | 185 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 10 | 122 | 220 | 0 | 618 | 1218 | 17 | 7415.63 | 15629.33 | 98.66
Total KWH | 352368 | 1284480 | 547680 | 0 | 0 | 0 | 0 | 0 | 8748000 | 0 | 0 | 453600 | 815400 | 2665008 | 2958720 | 1994727 | 453826 | 462420 | 1378080 | 813120 | 8600500 | 7111098 | 0 | 0 | 401222 | 7234340 | 0 | 0 | 208177 | 2521200 | 517800 | 448200 | 0 | 8562272.73 | 127964 | 737673 | 50880 | 0 | 927840 | 681406 | 742140 | 0 | 1418880 | 1662720 | 27684 | 4161240 | 299414 | 240000 | 4887272.73 | 587127 | 0 | 420960 | 122427 | 536109 | 5130130 | 0 | 0 | 0 | 25592725 | 80865 | 1141884 | 1702836 | 652364 | 0 | 8300500 | 8018000 | 717600 | 4637000 | 601560 | 1392960 | 0 | 3682560 | 332640 | 426930 | 2445300 | 949440 | 1111262 | 362564 | 668784 | 7171500 | 7652300 | 8678000 | 615000 | 365040 | 3535936 | 179112 | 0 | 712320 | 648288 | 0 | 0 | 4450500 | 426960 | 2157600 | 3600000 | 694080 | 10450 | 314660 | 246960 | 185570585.46 | 16936727 | 5165856 | 0 | 121920 | 116224 | 912000 | 0 | 0 | 0 | 0 | 297648 | 648720 | 22196370 | 392160 | 30010909 | 0 | 235413 | 0 | 951168 | 91292 | 428824 | 277152 | 131322 | 59890 | 618210 | 147597 | 317256 | 3960181 | 0 | 4109936 | 0 | 0 | 0 | 9153163 | 0 | 27420 | 4637000 | 1114036 | 1140290 | 74953 | 1111507 | 0 | 0 | 31765.56 | 717120 | 2548.5 | 100704 | 5019000 | 194345 | 2818000 | 5324520 | 0 | 14820336 | 24154181.82 | 106800 | 158674464.88 | 344245050.34

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 24-06-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14156.82 | MW | 12:00 Hr. | Energy Generated |  |  | 344.2451 |  | MKWHr.
| Day Peak Demand |  |  | 14193.82 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.608 |  | MKWHr.
| Evening Peak Generation |  |  | 15661.2 | MW | 19:30 Hr. | Energy Demand |  |  | 344.8531 |  | MKWHr.
| Evening Peak Demand |  |  | 15690.46 | MW | 19:30 Hr. | Maximum Temperature |  |  | 31.1 |  | °C
| Minimum Generation of the Day |  |  | 12586.81 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 934.41 |  | MMCFD
| Maximum Generation of the Day |  |  | 15661.2 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.6855 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 41.2222 | 0 | 17.1019 | 0 | 0 | 0.20818 | 0 | 0 | 58.5322 | Gas | 136.5163 | Gas | 478895812.6741
| Chattogram Zone |  |  | 5.3701 | 30.48 | 7.3877 | 0 | 4.1612 | 0.10855 | 0 | 0.92784 | 48.4355 | Coal | 102.4209 | Coal | 596129328.586
| Cumilla Zone |  |  | 24.4958 | 0 | 11.3363 | 0 | 0 | 0.36256 | 0.94944 | 0 | 37.1442 | HFO | 47.9673 | HFO | 904986116.64
| Mymensingh Zone |  |  | 0.69408 | 0 | 6.4315 | 0 | 0 | 0.32511 | 0 | 0 | 7.4507 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 34.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.008 | Hydro | 4.1612 | Hydro | 416124
| Khulna Zone |  |  | 5.1659 | 22.1964 | 0.92795 | 0 | 0 | 0.64872 | 17.8487 | 0 | 46.7876 | Solar | 3.4424 | Solar | 55391755.2866
| Barishal Zone |  |  | 8.3369 | 43.9935 | 0.2075 | 0 | 0 | 0.0025485 | 0 | 0 | 52.5404 | Import | 48.8091 | Import | 252061998.99
| Rajshahi Zone |  |  | 17.2233 | 0 | 2.3227 | 0 | 0 | 0.96289 | 30.0109 | 0 | 50.5197 | Wind | 0.92784 | Wind | 13583577.6
| Rangpur Zone |  |  | 0 | 5.751 | 2.2518 | 0 | 0 | 0.82384 | 0 | 0 | 8.8267
| Total |  |  | 136.5163 | 102.4209 | 47.9673 | 0 | 4.1612 | 3.4424 | 48.8091 | 0.92784 | 344.2451
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 478895812.6741 |  | Hydro | 416124
|  |  |  | Coal | 596129328.586 |  | Solar | 55391755.2866
|  |  |  | HFO | 904986116.64 |  | Import | 252061998.99
|  |  |  | HSD | 0 |  | Wind | 13583577.6
[5 empty] | Total: | 230,14,64,713 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 16.9367 | Peak Hr Flow | 450.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 47742709.16 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 30.0109 | Peak Hr Flow | 1380.00 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 586 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.94944 | Peak Hr Flow | 44.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 916 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 47.8971 | Peak Hr Flow | 1874.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5700
|  |  |  | Chattogram |  | 0 |  | 1486
|  |  |  | Cumilla |  | 0 |  | 1398
|  |  |  | Mymensingh |  | 28 |  | 1241
|  |  |  | Sylhet |  | 0 |  | 661
|  |  |  | Khulna |  | 0 |  | 1817
|  |  |  | Barishal |  | 0 |  | 478
|  |  |  | Rajshahi |  | 0 |  | 1416
|  |  |  | Rangpur |  | 0 |  | 1009
|  |  |  | Total |  | 28 |  | 15206
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[7 empty] | 5 | Meghnaghat CCPP(Summit) GT-2 |  |  | 110
[5 empty] | Total | 300 |  |  |  | Total | 586
|  |  |  | Total Unavailable Capacity |  |  |  | 886
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:48 | Goalpara 132/33kV S/S T-5 HT is restored.
|  | 08:49 | Goalpara 132/33kV S/S T-5 LT is restored.
| 08:50 | 16:55 | Shahjibazar 132/33kV S/S SPCL 86 MW Scheduled S/D Due to 86 mw maintenance work
|  | 08:52 | Goalpara 132/33kV S/S T-6 HT is restored.
|  | 08:53 | Goalpara 132/33kV S/S T-6 LT is restored.
| 09:03 |  | Ishurdi - DSEPL 132KV CKT-2 S/D.
| 09:08 |  | Unique Meghnaghat Power 584 MW CCPP ST was forced shutdown due to hotspot maintenance
| 09:22 | 16:07 | Ishurdi 230/132kV S/S 230/132 kV T-02 LT Scheduled S/D Due to for bus -1 Shut down
| 09:22 | 16:07 | Ishurdi 132/33kV S/S 132 kV Bus-1 Scheduled S/D | [7 empty] | 2.0MW load interrup.
| 11:20 | 14:31 | Khulna (C) S/S TR-1 425T LT Forced S/D Due to Due to Khulna PBS work
| 11:21 | 14:30 | Khulna (C) S/S TR-1 425T HT Forced S/D Due to Due to Khulna PBS work
| 12:00 |  | Day Peak Generation: 14153 MW.
|  | 13:24 | Goalpara 132/33kV S/S T1 HT is restored.
|  | 13:25 | Goalpara 132/33kV S/S T1 LT is restored.
| 13:46 |  | Rangpur- Taraganj 132kV ckt-1 and Saidpur- Taraganj 132kV ckt-1 charged (from Rangpur and
Saidpur end) for the first time at 13:29 hrs. and 13:46 hrs. respectively.
|  | 13:46 | Rangpur-Saidpur 132kV Ckt-1 is restored.
| 15:16 |  | Unique Meghnaghat Power 584 MW CCPP ST was syn.
| 15:16 |  | Unique Meghnaghat Power Limited (UMPL) ST Synchronized with remarks:- None
| 15:16 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized with remarks:- ST
|  | 15:23 | Bashundhara-Rampura 132 kV Ckt-2 is restored.
| 15:51 | 17:11 | Natore-Rajshahi 132kV Ckt-1 Forced S/D from Natore 132/33kV end.
| 16:16 | 17:45 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T LT Scheduled S/D Due to Emergency | [7 empty] | 35.0MW load
|  |  | maintenance 33KV bus | [7 empty] | interrup.
| 16:19 | 17:41 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T HT Scheduled S/D Due to Emergency | [7 empty] | 35.0MW load
|  |  | maintenance of 33 KV Bus | [7 empty] | interrup.
| 16:21 | 18:08 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) HT Scheduled S/D
| 16:21 | 18:09 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) LT Scheduled S/D
| 16:23 |  | Ishurdi - DSEPL 132KV CKT-2 syn.
| 18:49 |  | Raozan 25 MW PP Synchronized
| 19:30 |  | Evening Peak Gen. 15661 MW
| 21:10 |  | Kurigram 132/33kV S/S Capacitor Bank Forced S/D Due to red hot at R phase cell.
| 21:13 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized with remarks:- ST tripped-21:13 on 24.6.25
| 21:13 |  | Unique Meghnaghat Power 584 MW CCPP ST tripped.
| 21:13 |  | Unique Meghnaghat Power Limited (UMPL) Tripped with remarks:- ST
| 00:00 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized with remarks:- ST
| 00:09 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized with remarks:- ST
| 00:51 |  | Meghnaghat CCPP(Summit) Shutdown with remarks:- GT2
| 00:51 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- GT2 sd-00:51 on 25.6.25
| 02:34 |  | Raozan 25 MW PP Shutdown
| 02:39 |  | Meghnaghat CCPP(Summit) GT-2 Forced Shutdown with remarks:- GT-2 Shutdown given at 00:51
hours for HRSG-2 leakage rectification work.
| 05:49 |  | Rangpur-Saidpur 132kV Ckt-2 Scheduled S/D from Saidpur 132/33kV end Due to LILO work on Taragong grid.
| 05:51 | 06:14 | Sholosohor 132/33kV S/S TRAFO-01 LT Tripped showing Restricted E/F, Non-Directional IDMT, | [7 empty] | 29.0MW load interrup.
Standby E/F, 86.2, 86.1 relays Due to 11kV BPDB feeder fault. (11kV sholoshahar 07no feeder)
| 05:51 | 06:13 | Sholosohor 132/33kV S/S TRAFO-01 HT Tripped showing Restricted E/F, Non-Dir IDMT, Standby | [7 empty] | 29.0MW load
|  |  | E/F, 86.2, 86.1 relay Operated. relays Due to Both side trip due to 11kV BPDB feeder | [7 empty] | interrup.
fault. (11kv Sholoshahar -07 no feeder from bpdb control room)
| 06:02 |  | Rangpur-Saidpur 132kV Ckt-2 Project Work S/D from Rangpur 132/33kV end Due to For
Taragonj Grid LILO connection.
| 06:57 |  | Moghbazar-Rampura 132kV Ckt-1 Scheduled S/D from Rampura 230/132kV end Due to Shutdown from NLDC.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 24-06-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 325 | 8748000 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 8600500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 278 | 7111098 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 40 | 453826 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 7234340 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 98 | 352368 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 453600 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 143 | 2958720 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 462420 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 401222 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 517800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 448200 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 547680 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 210 | 1994727 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2665008 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1284480 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 68 | 813120 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 1378080 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 208177 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 815400 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 350 | 8562272.73 | None
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 142 | 2521200 | -
Dhaka Area Total |  |  |  |  | 5939.724 | 2823 | 58532238.73
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 14 | 122427 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 80865 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 32 | 420960 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 172 | 4161240 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 215 | 5130130 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 57 | 536109 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 71 | 742140 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 64 | 681406 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1418880 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 2 | 240000 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 50880 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 27684 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 150 | 737673 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 15 | 299414 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1662720 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 21 | 127964 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 160 | 587127 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1100 | 25592725 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 27 | 927840 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 202 | 4887272.73 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4895.72 | 2502 | 48435456.73
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 186 | 4637000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 347 | 8300500 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 8018000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 26 | 601560 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 10 | 717600 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 652364 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1141884 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 139 | 1702836 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 43 | 668784 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 160 | 3682560 | -
| Import (Tripura) |  | Import | 0 | 160 | 44 | 949440 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 1111262 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 426930 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 97 | 2445300 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 332640 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1392960 | Fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 362564 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1657.2 | 37144184
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 11 | 694080 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 163 | 3600000 | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 102 | 2157600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 314660 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 11 | 246960 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 426960 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 304 | 7450710
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 615000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 365040 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3535936 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 25 | 648288 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 37 | 712320 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 164 | 4450500 | Machine Problem
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 179112 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7171500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 300 | 8678000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7652300 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1301 | 34007996
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 450 | 16936727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 14 | 121920 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 14 | 116224 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 162 | 5165856 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 51 | 392160 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 80 | 297648 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 648720 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1146 | 22196370 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1955 | 46787625
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 617 | 14820336 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 32 | 100704 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 10 | 194345 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2818000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1060 | 24154181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5324520 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 30 | 106800 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 245 | 5019000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2548.5 | -
Barishal Area Total |  |  |  |  | 2236 | 2334 | 52540435.32
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 235413 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 5 | 91292 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 131322 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 140 | 3960181 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 140 | 4109936 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Plant is in Standby as per NLDC request.
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 396 | 9153163 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 147597 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 25 | 59890 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 45 | 428824 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 951168 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 50 | 277152 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 27420 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1380 | 30010909 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 317256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 618210 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2350 | 50519733
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 48 | 1114036 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 189 | 4637000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 1111507 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 31765.56 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 100 | 1140290 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 74953 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 717120 | -
Rangpur Area Total |  |  |  |  | 950 | 435 | 8826671.56
Eastern Grid Total |  |  |  |  | 16705.895 | 8587.2 | 185570585.46
Western Grid Total |  |  |  |  | 10378.16 | 7074 | 158674464.88
National Grid Total |  |  |  |  | 27084.055 | 15661.2 | 344245050.34
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 24-06-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10457.68 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4720.6 | MW
i) Dhaka area |  |  | 5699.61 |  | MW | i) Khulna area |  |  |  | 1817.1 | MW
ii) Chattogram area |  |  | 1486 |  | MW | ii) Barishal area |  |  |  | 478.5 | MW
iii) Cumilla area |  |  | 1398.07 |  | MW | iii) Rajshahi area |  |  |  | 1416 | MW
iv) Mymensingh area |  |  | 1213 |  | MW | iv) Rangpur area |  |  |  | 1009 | MW
v) Sylhet area |  |  | 661 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15178.28 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 86 | 20:00 | 133 | Patuakhali | 83.5 | 22:00
2 | AKSML | 137 | 06:00 | 68 | Jaldhaka | 82 | 19:00 | 134 | Payra | 34 | 00:00
3 | Aftabnagar | 42 | 13:00 | 69 | Jamalpur | 135 | 00:00 | 135 | Postogola | 63 | 13:00
4 | Agargaon | 141 | 15:00 | 70 | Jashore | 151 | 21:00 | 136 | Purbachal | 23 | 21:00
5 | Agrabad | 100 | 19:00 | 71 | Jhenaidah | 131 | 00:00 | 137 | Purbasadipur | 142 | 19:30
6 | Amnura | 40 | 00:00 | 72 | Joydebpur | 143 | 12:00 | 138 | Rahanpur | 34 | 00:00
7 | Ashuganj | 96 | 21:00 | 73 | Joypurhat | 65 | 21:00 | 139 | Rahim | 50 | 12:00
8 | BSRM | 203 | 17:00 | 74 | Juldah | 17 | 18:00 | 140 | Rajbari | 83 | 21:00
9 | Bagerhat | 89 | 21:00 | 75 | KSRM | 23 | 11:00 | 141 | Rajendrapur | 138 | 19:30
10 | Bajitpur | 58 | 01:00 | 76 | Kabirpur | 263 | 15:00 | 142 | Rajshahi | 117 | 23:00
11 | Bakulia | 98 | 16:00 | 77 | Kachua | 94 | 23:00 | 143 | Rajshahi-230 | 89 | 13:00
12 | Banani | 33 | 12:00 | 78 | Kallyanpur | 108 | 23:00 | 144 | Ramganj | 112 | 21:00
13 | Bangabhaban | 19 | 10:00 | 79 | Kalurghat | 40 | 12:00 | 145 | Rampur | 43 | 23:00
14 | Barapukuria | 71 | 21:00 | 80 | Kamrangirchar | 67 | 17:00 | 146 | Rangamati | 18 | 19:30
15 | Barguna | 24 | 22:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 151 | 00:00
16 | Barishal | 113 | 19:30 | 82 | Kasba | 40 | 22:00 | 148 | Ruppur | 7.4 | 15:00
17 | Barishal-230 | 104 | 00:00 | 83 | Kazla | 100 | 13:00 | 149 | SSM | 13 | 01:00
18 | Baroaulia | 60 | 12:00 | 84 | Keranigonj | 96 | 13:00 | 150 | Saidpur | 114 | 00:00
19 | Baroirhat | 62 | 19:00 | 85 | Khagrachori | 36 | 19:30 | 151 | Satkhira | 136 | 00:00
20 | Bashundhara | 201 | 13:00 | 86 | Khulna | 80 | 20:00 | 152 | Satmasjid | 104 | 14:00
21 | BashundharaCement | 16 | 18:00 | 87 | Khulshi | 165 | 19:30 | 153 | Savar | 236 | 19:00
22 | Beanibazar | 88 | 21:00 | 88 | Kishoreganj | 150 | 00:00 | 154 | SevenRings | 4.54 | 13:00
23 | Benapole | 70 | 00:00 | 89 | Kodda | 306 | 18:30 | 155 | ShahCement | 32 | 00:00
24 | Bhaluka | 158 | 20:00 | 90 | Kulaura | 56 | 19:30 | 156 | Shahjadpur | 82 | 21:00
25 | Bhandaria | 56 | 23:00 | 91 | Kurigram | 70 | 00:00 | 157 | Shahjibazar | 133 | 23:00
26 | Bhangura | 40 | 00:00 | 92 | Kushtia | 164 | 19:30 | 158 | Shahmirpur | 61 | 00:00
27 | Bheramara(GK) | 71 | 21:00 | 93 | Lalbag | 56 | 17:00 | 159 | Shariatpur | 94 | 23:00
28 | Bhulta | 272 | 01:00 | 94 | Lalmonirhat | 70 | 19:30 | 160 | Sherpur | 148 | 03:00
29 | Bog-Sherpur | 72 | 00:00 | 95 | MI_Cement | 17.8 | 09:00 | 161 | Shikalbaha | 9 | 16:00
30 | Bogura | 170 | 23:00 | 96 | Madanganj | 40 | 13:00 | 162 | Shitalakhya | 87.7 | 15:00
31 | Borhanuddin | 93 | 22:00 | 97 | Madaripur | 121 | 00:00 | 163 | Sholosohor | 49 | 19:00
32 | Brahmanbaria | 138 | 00:00 | 98 | Madartek | 95.91 | 00:00 | 164 | Shyampur | 166 | 12:00
33 | Cantonment | 168 | 12:00 | 99 | Madunaghat | 58 | 19:00 | 165 | Siddhirganj | 137 | 13:00
34 | Chandina | 16.81 | 23:00 | 100 | Magura | 69 | 22:00 | 166 | Sirajganj | 114 | 21:00
35 | Chandpur | 82 | 00:00 | 101 | Mahasthangarh | 84 | 23:00 | 167 | Sonargaon | 112 | 00:00
36 | Chandraghona | 40 | 21:00 | 102 | Manikganj | 136 | 21:00 | 168 | Sreemongol | 88 | 19:30
37 | Chapai | 75 | 00:00 | 103 | Maniknagar | 90 | 13:00 | 169 | Sreepur | 105 | 19:30
38 | Charsaidpur | 44 | 11:00 | 104 | Matarbari | 59 | 23:00 | 170 | Srinagar | 51 | 22:00
39 | Chauddagram | 76 | 19:00 | 105 | Matuail | 67 | 15:00 | 171 | Sunamganj | 60 | 00:00
40 | Chhatak | 42 | 23:00 | 106 | Millgate | 99 | 15:00 | 172 | Sylhet | 53 | 21:00
41 | Chowmuhani | 194 | 21:00 | 107 | Mirpur | 129.5 | 15:00 | 173 | Sylhet-132 | 136 | 21:00
42 | Chuadanga | 121 | 01:00 | 108 | Mirsorai | 11 | 16:00 | 174 | TK | 35 | 21:00
43 | Coxsbazar | 136 | 19:00 | 109 | Mirzapur | 46 | 21:00 | 175 | Tangail | 186 | 00:00
44 | Cumilla(N) | 151 | 00:00 | 110 | Mithapukur | 74 | 22:00 | 176 | Thakurgaon | 109 | 00:00
45 | Cumilla(S) | 183 | 19:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 141 | 12:00
46 | Daudkandi | 157 | 19:00 | 112 | Mogbazar | 152.8 | 13:00 | 178 | Ullahpara | 37 | 00:00
47 | Dhaka | 66 | 13:00 | 113 | Mongla | 45 | 12:00 | 179 | Ullon | 43 | 21:00
48 | Dhamrai | 130 | 00:00 | 114 | Motijheel | 44 | 13:00 | 180 | Uttara | 89 | 13:00
49 | Dhanmondi | 145 | 13:00 | 115 | Muktagacha | 40 | 21:00 | 181 | UttaraNew | 64 | 23:00
50 | Dohazari | 110 | 15:00 | 116 | Munshiganj | 126 | 21:00 | 182 | Zigatola | 76 | 00:00
51 | Faridpur | 173 | 21:00 | 117 | Muradnagar | 31 | 23:00
52 | Fatullah | 104 | 16:00 | 118 | Mymensingh | 216 | 19:30
53 | Fenchuganj | 46 | 23:00 | 119 | Naogaon | 139 | 22:00
54 | Feni | 116 | 21:00 | 120 | Narail | 62.5 | 20:00
55 | GPH | 21 | 01:00 | 121 | Narinda | 91 | 13:00
56 | Ghatail | 76 | 21:00 | 122 | Narshingdi | 189 | 22:00
57 | Ghorashal | 16 | 13:00 | 123 | Natore | 151 | 00:00
58 | Ghorashal-230 | 103 | 21:00 | 124 | Nawabganj | 62.2 | 21:00
59 | Goalpara | 42 | 21:00 | 125 | Netrakona | 135 | 20:00
60 | Gollamari | 96 | 23:00 | 126 | New | 89.7 | 15:00
61 | Gopalganj | 115 | 21:00 | 127 | Niamatpur | 77 | 00:00
62 | Gulshan | 162 | 14:00 | 128 | Noapara | 48 | 20:00
63 | Halishahar | 79 | 15:00 | 129 | PHP | 5 | 00:00
64 | HaripurSBU | 180 | 12:00 | 130 | Pabna | 129 | 21:00
65 | Hasnabad | 79 | 00:00 | 131 | Palashbari | 126 | 20:00
66 | Hathazari | 83 | 00:00 | 132 | Panchagarh | 62 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 24-06-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15517.19 | 52 |  | 15571.53
1:00 | 15141.01 | 53 |  | 15196.01
2:00 | 14489.87 | 50 |  | 14541.87
3:00 | 14104.09 | 45 |  | 14151.09
4:00 | 13642.9 | 37 |  | 13681.9
5:00 | 13324.5 | 35 |  | 13361.5
6:00 | 12700.7 | 0 |  | 12700.7
7:00 | 12586.81 | 0 |  | 12586.81
8:00 | 12791.14 | 0 |  | 12791.14
9:00 | 13086.5 | 0 |  | 13086.5
10:00 | 13461.59 | 0 |  | 13461.59
11:00 | 13740.03 | 0 |  | 13740.03
12:00 | 14156.82 | 35 |  | 14193.82
13:00 | 14377.87 | 37 |  | 14416.87
14:00 | 14420.79 | 31 |  | 14453.19
15:00 | 14635.79 | 0 |  | 14635.79
16:00 | 14449.63 | 0 |  | 14449.63
17:00 | 13781.93 | 0 |  | 13781.93
18:00 | 13221.96 | 0 |  | 13221.96
19:00 | 14354.7 | 0 |  | 14354.7
19:30 | 15661.2 | 28 |  | 15690.46
20:00 | 15569.2 | 68 |  | 15640.2
21:00 | 15459.73 | 39 |  | 15500.49
22:00 | 15340.75 | 57 |  | 15400.75
23:00 | 15629.33 | 69 |  | 15701.33
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 24-06-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8067.2 | 7449.99 | 15517.19 | DAILY GENERATION CURVE
00:30 | 8056.55 | 7272.55 | 15329.1
01:00 | 8045.9 | 7095.11 | 15141.01 | 24-06-2025
01:30 | 7885.4 | 6930.04 | 14815.44
02:00 | 7724.9 | 6764.97 | 14489.87
02:30 | 7613.95 | 6683.03 | 14296.98
03:00 | 7503 | 6601.09 | 14104.09
03:30 | 7379 | 6494.495 | 13873.495
04:00 | 7255 | 6387.9 | 13642.9
04:30 | 7114.5 | 6369.2 | 13483.7
05:00 | 6974 | 6350.5 | 13324.5
05:30 | 6836.24 | 6176.36 | 13012.6
06:00 | 6698.48 | 6002.22 | 12700.7
06:30 | 6721.755 | 5922 | 12643.755
07:00 | 6745.03 | 5841.78 | 12586.81
07:30 | 6791.665 | 5897.31 | 12688.975
08:00 | 6838.3 | 5952.84 | 12791.14
08:30 | 6921.905 | 6016.915 | 12938.82
09:00 | 7005.51 | 6080.99 | 13086.5
09:30 | 7055.635 | 6218.41 | 13274.045
10:00 | 7105.76 | 6355.83 | 13461.59
10:30 | 7220.865 | 6379.945 | 13600.81
11:00 | 7335.97 | 6404.06 | 13740.03
11:30 | 7478.47 | 6469.955 | 13948.425
12:00 | 7620.97 | 6535.85 | 14156.82
12:30 | 7699.48 | 6567.865 | 14267.345
13:00 | 7777.99 | 6599.88 | 14377.87
13:30 | 7853.495 | 6545.835 | 14399.33
14:00 | 7929 | 6491.79 | 14420.79
14:30 | 8055.39 | 6472.9 | 14528.29
15:00 | 8181.78 | 6454.01 | 14635.79
15:30 | 8111.64 | 6431.07 | 14542.71
16:00 | 8041.5 | 6408.13 | 14449.63
16:30 | 7867.215 | 6248.565 | 14115.78
17:00 | 7692.93 | 6089 | 13781.93
17:30 | 7673.09 | 5828.855 | 13501.945
18:00 | 7653.25 | 5568.71 | 13221.96
18:30 | 7934.975 | 5853.355 | 13788.33
19:00 | 8216.7 | 6138 | 14354.7
19:30 | 8587.2 | 7074 | 15661.2
20:00 | 8421.2 | 7148 | 15569.2
20:30 | 8313.95 | 7200.515 | 15514.465 |  | Executive Engineer
21:00 | 8206.7 | 7253.03 | 15459.73 |  | Network Operation Division
21:30 | 8134.2 | 7266.04 | 15400.24
22:00 | 8061.7 | 7279.05 | 15340.75
22:30 | 8137.7 | 7347.34 | 15485.04
23:00 | 8213.7 | 7415.63 | 15629.33

## En-Curve
QF-LDC-12
Date | 24-06-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3885 | 2173 | 880 | 38 | 48 | 1413.99 | 172 | 4817 | 0 | 529 | 1547.2 | 0 | 0 | 14 | 52 | DAILY ENERGY CURVE
00:30 | 3875.5 | 2173.35 | 880 | 38 | 47 | 1409.55 | 172 | 4629 | 0 | 524.5 | 1564.2 | 0 | 0 | 16 | 52.5 | 24-06-2025
01:00 | 3866 | 2173.7 | 880 | 38 | 46 | 1405.11 | 172 | 4441 | 0 | 520 | 1581.2 | 0 | 0 | 18 | 53
01:30 | 3808 | 2164.7 | 880 | 38 | 45 | 1404.54 | 172 | 4341.5 | 0 | 472 | 1469.7 | 0 | 0 | 20 | 51.5 | Energy Generated | 344.2451 |  | MKWHr
02:00 | 3750 | 2155.7 | 880 | 38 | 44 | 1403.97 | 172 | 4242 | 0 | 424 | 1358.2 | 0 | 0 | 22 | 50 | Energy not Served | 0.608 |  | MKWHr
02:30 | 3791 | 2161.25 | 880 | 38 | 43 | 1360.53 | 172 | 4236 | 0 | 380.5 | 1205.2 | 0 | 0 | 29.5 | 47.5 | Total Energy Requirement | 344.8531 |  | MKWHr
03:00 | 3832 | 2166.8 | 880 | 38 | 42 | 1317.09 | 172 | 4230 | 0 | 337 | 1052.2 | 0 | 0 | 37 | 45
03:30 | 3830 | 2168.8 | 880 | 38 | 42 | 1241.995 | 172 | 4225 | 0 | 313.5 | 924.7 | 0 | 0 | 37.5 | 41
04:00 | 3828 | 2170.8 | 880 | 38 | 42 | 1166.9 | 172 | 4220 | 0 | 290 | 797.2 | 0 | 0 | 38 | 37
04:30 | 3817 | 2135.8 | 879.5 | 38 | 41 | 1139.2 | 172 | 4183 | 0 | 289.5 | 749.2 | 0 | 0 | 39.5 | 36
05:00 | 3806 | 2100.8 | 879 | 38 | 40 | 1111.5 | 172 | 4146 | 0 | 289 | 701.2 | 0 | 0 | 41 | 35
05:30 | 3785.5 | 2090.8 | 879 | 38 | 36 | 1010.94 | 172 | 4024.5 | 14.76 | 252 | 665.6 | 0 | 0 | 43.5 | 17.5
06:00 | 3765 | 2080.8 | 879 | 38 | 32 | 910.38 | 172 | 3903 | 29.52 | 215 | 630 | 0 | 0 | 46 | 0
06:30 | 3793.5 | 2081.8 | 879 | 38 | 34 | 885.775 | 172 | 3805 | 65.18 | 220 | 619.5 | 0 | 0 | 50 | 0
07:00 | 3822 | 2082.8 | 879 | 38 | 36 | 861.17 | 172 | 3707 | 100.84 | 225 | 609 | 0 | 0 | 54 | 0
07:30 | 3878 | 2078.4 | 879 | 38 | 35 | 867.105 | 172 | 3713 | 143.97 | 225 | 609 | 0 | 0 | 50.5 | 0
08:00 | 3934 | 2074 | 879 | 38 | 34 | 873.04 | 172 | 3719 | 187.1 | 225 | 609 | 0 | 0 | 47 | 0
08:30 | 3942.5 | 2013 | 878.5 | 38 | 33 | 901.645 | 172 | 3824.5 | 246.675 | 225 | 616.5 | 0 | 0 | 47.5 | 0
09:00 | 3951 | 1952 | 878 | 38 | 32 | 930.25 | 172 | 3930 | 306.25 | 225 | 624 | 0 | 0 | 48 | 0
09:30 | 3943 | 1960.5 | 878.5 | 38 | 33 | 1001 | 172 | 3964 | 351.545 | 225 | 662.5 | 0 | 0 | 45 | 0
10:00 | 3935 | 1969 | 879 | 38 | 34 | 1071.75 | 172 | 3998 | 396.84 | 225 | 701 | 0 | 0 | 42 | 0
10:30 | 3936.5 | 1982.5 | 878.5 | 38 | 34 | 1063.23 | 172 | 4019.5 | 419.58 | 225 | 788 | 0 | 0 | 44 | 0
11:00 | 3938 | 1996 | 878 | 38 | 34 | 1054.71 | 172 | 4041 | 442.32 | 225 | 875 | 0 | 0 | 46 | 0
11:30 | 3925.5 | 1971.25 | 878.5 | 38 | 35 | 1143.585 | 172 | 4021.5 | 451.99 | 225 | 1041.6 | 0 | 0 | 44.5 | 17.5
12:00 | 3913 | 1946.5 | 879 | 38 | 36 | 1232.46 | 172 | 4002 | 461.66 | 225 | 1208.2 | 0 | 0 | 43 | 35
12:30 | 3826 | 1813.25 | 879 | 38 | 37 | 1343.345 | 172 | 3978.5 | 431.55 | 311.5 | 1395.2 | 0 | 0 | 42 | 36
13:00 | 3739 | 1680 | 879 | 38 | 38 | 1454.23 | 172 | 3955 | 401.44 | 398 | 1582.2 | 0 | 0 | 41 | 37
13:30 | 3722 | 1618.5 | 819.5 | 38 | 39 | 1457.615 | 172 | 3975.5 | 398.015 | 404 | 1714.2 | 0 | 0 | 41 | 34
14:00 | 3705 | 1557 | 760 | 38 | 40 | 1461 | 172 | 3996 | 394.59 | 410 | 1846.2 | 0 | 0 | 41 | 31
14:30 | 3732.5 | 1567.75 | 612.5 | 38 | 40 | 1457 | 172 | 4150.5 | 366.34 | 412.5 | 1928.7 | 0 | 0 | 50.5 | 15.5
15:00 | 3760 | 1578.5 | 465 | 38 | 40 | 1453 | 172 | 4305 | 338.09 | 415 | 2011.2 | 0 | 0 | 60 | 0
15:30 | 3646.5 | 1608.9 | 458 | 38 | 36 | 1431 | 172 | 4334.5 | 296.11 | 434 | 2036.2 | 0 | 0 | 51.5 | 0
16:00 | 3533 | 1639.3 | 451 | 38 | 32 | 1409 | 172 | 4364 | 254.13 | 453 | 2061.2 | 0 | 0 | 43 | 0
16:30 | 3506.5 | 1635.8 | 451.5 | 38 | 35 | 1327 | 172 | 4226 | 206.78 | 456 | 2012.2 | 0 | 0 | 49 | 0
17:00 | 3480 | 1632.3 | 452 | 38 | 38 | 1245 | 172 | 4088 | 159.43 | 459 | 1963.2 | 0 | 0 | 55 | 0
17:30 | 3424 | 1661.3 | 451.5 | 38 | 36 | 1177 | 172 | 3946.5 | 97.945 | 509 | 1937.2 | 0 | 0 | 51.5 | 0
18:00 | 3368 | 1690.3 | 451 | 38 | 34 | 1109 | 172 | 3805 | 36.46 | 559 | 1911.2 | 0 | 0 | 48 | 0
18:30 | 3465 | 1733.9 | 451 | 38 | 39 | 1169.5 | 172 | 3985.5 | 18.23 | 623 | 2052.7 | 0 | 0 | 40.5 | 0
19:00 | 3562 | 1777.5 | 451 | 38 | 44 | 1230 | 172 | 4166 | 0 | 687 | 2194.2 | 0 | 0 | 33 | 0
19:30 | 3497 | 1772 | 450 | 38 | 44 | 1380 | 172 | 4607 | 0 | 833 | 2841.2 | 0 | 0 | 27 | 28
20:00 | 3287 | 1699 | 451 | 38 | 44 | 1437 | 172 | 4717 | 0 | 931 | 2750.2 | 0 | 0 | 43 | 68
20:30 | 3353.5 | 1727 | 451 | 38 | 43 | 1437.515 | 172 | 4755.5 | 0 | 930 | 2568.95 | 0 | 0 | 38 | 53.5
21:00 | 3420 | 1755 | 451 | 38 | 42 | 1438.03 | 172 | 4794 | 0 | 929 | 2387.7 | 0 | 0 | 33 | 39
21:30 | 3478 | 1703.5 | 451 | 38 | 42 | 1449.04 | 172 | 4792.5 | 0 | 906.5 | 2342.2 | 0 | 0 | 25.5 | 48
22:00 | 3536 | 1652 | 451 | 38 | 42 | 1460.05 | 172 | 4791 | 0 | 884 | 2296.7 | 0 | 0 | 18 | 57
22:30 | 3563.5 | 1677.5 | 428.5 | 38 | 44 | 1462.84 | 172 | 4878.5 | 0 | 875.5 | 2326.7 | 0 | 0 | 18 | 63
23:00 | 3591 | 1703 | 406 | 38 | 46 | 1465.63 | 172 | 4966 | 0 | 867 | 2356.7 | 0 | 0 | 18 | 69
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 24-06-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 384 | 18:30 | 368 | 23:00 | Payra | 413 | 05:00 | 405 | 23:00
Ashuganj | 401 | 5:00 | 373 | 11:00 | Rahanpur | 407 | 06:00 | 390 | 00:00
Bhulta | 394 | 05:00 | 368 | 12:00 | Rampal | 400 | 18:00 | 384 | 23:00
Bibiana | 387 | 06:00 | 380 | 22:00
BIPTC | 407 | 15:00 | 391 | 00:00
Bogura | 393 | 06:00 | 371 | 00:00
Gopalganj | 395 | 18:00 | 380 | 23:00
Kaliakoir | 375 | 18:00 | 361 | 12:00
Madunaghat | 395 | 19:00 | 386 | 11:00
Meghnaghat | 387 | 18:30 | 373 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 223 | 06:00 | 213 | 12:00 | Keranigonj | 222 | 18:30 | 211 | 12:00
AKSML | 235 | 19:30 | 230 | 18:00 | Khulna(S) | 229 | 08:00 | 216 | 22:00
Aminbazar | 228 | 08:00 | 214 | 11:00 | Madunaghat | 235 | 19:00 | 227 | 10:00
Ashuganj | 230 | 06:00 | 221 | 10:00 | Madunaghat-400 | 235 | 20:00 | 227 | 11:00
Ashuganj-400 | 230 | 18:00 | 221 | 10:00 | Maniknagar | 220 | 18:00 | 209 | 12:00
Baghabari | 234 | 05:00 | 225 | 00:00 | Meghnaghat | 230 | 18:30 | 220 | 11:00
Barapukuria | 228 | 17:00 | 216 | 19:30 | Meghnaghat-400 | 225 | 18:30 | 215 | 10:00
Barapukuria-230 | 227 | 7:00 | 216 | 19:30 | Mirsorai | 235 | 19:30 | 219 | 10:00
Barishal | 233 | 18:30 | 227 | 02:00 | Rajshahi | 235 | 06:00 | 221 | 00:00
Bheramara | 234 | 06:00 | 223 | 00:00 | Rampal | 229 | 18:00 | 218 | 00:00
Bhulta | 229 | 05:00 | 210 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 228 | 05:00 | 220 | 23:00 | Rampura | 228 | 05:00 | 211 | 12:00
BIPTC | 236 | 06:00 | 222 | 00:00 | Shikalbaha | 235 | 19:30 | 225 | 05:00
Bogura | 237 | 06:00 | 225 | 00:00 | Shyampur | 222 | 18:30 | 212 | 11:00
Bogura-400 | 238 | 17:00 | 225 | 00:00 | Siddhirganj | 223 | 18:30 | 212 | 12:00
Borhanuddin | 238 | 08:00 | 230 | 22:00 | Sirajgonj | 240 | 22:00 | 233 | 21:00
BSRM | 233 | 19:30 | 219 | 10:00 | Sreepur | 230 | 21:00 | 221 | 10:00
Cumilla(N) | 224 | 18:00 | 214 | 11:00 | Tongi | 226 | 04:00 | 214 | 12:00
Faridpur | 231 | 18:00 | 219 | 00:00
Fenchuganj | 229 | 07:00 | 221 | 22:00
Ghorashal | 228 | 08:00 | 220 | 09:00
Ghorashal-230 | 227 | 06:00 | 214 | 10:00
Gopalganj | 232 | 06:00 | 222 | 00:00
GPH | 233 | 19:30 | 222 | 10:00
Haripur | 222 | 18:30 | 211 | 12:00
Hasnabad | 223 | 18:00 | 211 | 12:00
Hathazari | 234 | 17:00 | 226 | 11:00
Ishurdi | 236 | 06:00 | 225 | 00:00
Jhenaidah | 231 | 08:00 | 215 | 00:00
Kaliakoir | 230 | 05:00 | 220 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 06:00 | 122 | 11:00 | Madartek | 133 | 05:00 | 122 | 12:00
Agargaon | 131 | 06:00 | 122 | 12:00 | Madunaghat | 135 | 19:00 | 129 | 07:00
Agrabad | 134 | 18:00 | 127 | 10:00 | Magura | 135 | 08:00 | 121 | 00:00
AKS | 132 | 18:00 | 126 | 09:00 | Mahasthangarh | 137 | 17:00 | 127 | 00:00
Aminbazar | 131 | 04:00 | 125 | 09:00 | Maijdee | N/A | N/A | N/A | N/A
Amnura | 137 | 20:00 | 126 | 00:00 | Manikganj | 130 | 05:00 | 119 | 23:00
Ashuganj | 135 | 01:00 | 132 | 12:00 | Maniknagar | 131 | 06:00 | 122 | 12:00
Bagerhat | 131 | 09:00 | 117 | 00:00 | Matarbari | 124 | 18:00 | 114 | 00:00
Bajitpur | 131 | 21:00 | 124 | 00:00 | Matuail | 130 | 18:00 | 121 | 12:00
Bakulia | 134 | 18:00 | 128 | 10:00 | Millgate | 133 | 05:00 | 127 | 20:00
Banani | 134 | 04:00 | 122 | 10:00 | Mirpur | 130 | 03:00 | 122 | 23:00
Bangabhaban | 130 | 05:00 | 122 | 12:00 | Mirzapur | 131 | 18:30 | 123 | 23:00
Barapukuria | 140 | 17:00 | 128 | 19:30 | Mithapukur | 133 | 18:30 | 120 | 00:00
Barguna | 134 | 13:00 | 129 | 00:00 | MI_Cement | 130 | 18:30 | 121 | 10:00
Barishal | 135 | 18:00 | 128 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal-230 | 136 | 18:00 | 128 | 00:00 | Mogbazar | 134 | 05:00 | 121 | 12:00
Baroaulia | 135 | 18:00 | 130 | 08:00 | Mongla | 131 | 18:30 | 118 | 00:00
Baroirhat | 127 | 18:00 | 119 | 00:00 | Motijheel | 130 | 05:00 | 122 | 12:00
Bashundhara | 134 | 05:00 | 122 | 12:00 | Muktagacha | 134 | 10:00 | 125 | 23:00
BashundharaCement | 129 | 18:30 | 120 | 11:00 | Munshiganj | 129 | 18:00 | 120 | 11:00
Beanibazar | 127 | 06:00 | 120 | 23:00 | Muradnagar | 127 | 18:00 | 118 | 11:00
Benapole | 130 | 18:00 | 116 | 00:00 | Mymensingh | 135 | 12:00 | 126 | 21:00
Bhaluka | 135 | 21:00 | 124 | 10:00 | Naogaon | 135 | 17:00 | 124 | 00:00
Bhandaria | 130 | 09:00 | 120 | 23:00 | Narail | 136 | 08:00 | 121 | 00:00
Bhangura | 134 | 06:00 | 127 | 00:00 | Narinda | 131 | 6:00 | 122 | 12:00
Bheramara | 138 | 09:00 | 130 | 23:00 | Narshingdi | 133 | 05:00 | 115 | 10:00
Bheramara(GK) | 138 | 08:00 | 129 | 23:00 | Natore | 136 | 17:00 | 127 | 00:00
Bhulta | 125 | 17:00 | 116 | 11:00 | Nawabganj | 133 | 06:00 | 124 | 12:00
Bog-Sherpur | 138 | 17:00 | 128 | 00:00 | Netrakona | 131 | 21:00 | 112 | 19:30
Bogura | 140 | 17:00 | 132 | 00:00 | New | 133 | 05:00 | 123 | 11:00
Bogura-230 | 140 | 17:00 | 131 | 00:00 | Niamatpur | 138 | 05:00 | 130 | 00:00
Brahmanbaria | 130 | 06:00 | 121 | 23:00 | Noapara | 133 | 09:00 | 121 | 00:00
Cantonment | 131 | 06:00 | 122 | 12:00 | Pabna | 135 | 09:00 | 127 | 23:00
Chandina | 128 | 18:00 | 121 | 00:00 | Palashbari | 132 | 17:00 | 119 | 00:00
Chandpur | 129 | 18:00 | 116 | 00:00 | Panchagarh | 138 | 02:00 | 124 | 12:00
Chandraghona | 134 | 18:00 | 129 | 10:00 | Patuakhali | 134 | 18:00 | 130 | 01:00
Chapai | 134 | 18:00 | 126 | 00:00 | Payra | 135 | 05:00 | 133 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 18:30 | 121 | 10:00 | PHP | 126 | 18:00 | 115 | 23:00
Chauddagram | 125 | 18:00 | 117 | 00:00 | Postogola | 131 | 18:30 | 123 | 11:00
Chhatak | 126 | 18:00 | 117 | 23:00 | Purbachal | 138 | 18:30 | 122 | 10:00
Chowmuhani | 121 | 18:00 | 110 | 23:00 | Purbasadipur | 135 | 06:00 | 121 | 13:00
Chuadanga | 136 | 18:30 | 119 | 23:00 | Rahanpur | 138 | 05:00 | 132 | 00:00
Coxsbazar | 124 | 18:00 | 115 | 00:00 | Rahanpur-400 | 139 | 06:00 | 132 | 00:00
Cumilla(N) | 128 | 18:00 | 121 | 00:00 | Rahim | 129 | 18:00 | 124 | 16:00
Cumilla(S) | 133 | 04:00 | 119 | 00:00 | Rajbari | 135 | 18:00 | 126 | 00:00
Daudkandi | 126 | 18:00 | 115 | 12:00 | Rajendrapur | 133 | 18:30 | 123 | 19:30
Dhaka | 133 | 05:00 | 122 | 11:00 | Rajshahi | 135 | 04:00 | 127 | 00:00
Dhamrai | 131 | 03:00 | 123 | 10:00 | Rajshahi-230 | 136 | 07:00 | 120 | 00:00
Dhanmondi | 135 | 06:00 | 123 | 12:00 | Ramganj | 124 | 18:00 | 109 | 00:00
Dohazari | 132 | 18:00 | 124 | 10:00 | Rampur | 134 | 18:00 | 127 | 10:00
Faridpur | 135 | 06:00 | 128 | 00:00 | Rampura | 134 | 05:00 | 122 | 12:00
Fatullah | 129 | 18:00 | 121 | 11:00 | Rangamati | 132 | 18:00 | 128 | 11:00
Fenchuganj | 134 | 06:00 | 129 | 23:00 | Rangpur | 137 | 03:00 | 124 | 13:00
Feni | 123 | 18:30 | 115 | 22:00 | Ruppur | 138 | 06:00 | 131 | 00:00
Ghatail | 130 | 06:00 | 122 | 00:00 | Saidpur | 135 | 06:00 | 124 | 00:00
Ghorashal | 135 | 07:00 | 129 | 09:00 | Satkhira | 133 | 09:00 | 116 | 00:00
Goalpara | 136 | 09:00 | 122 | 00:00 | Satmasjid | 130 | 06:00 | 122 | 11:00
Gollamari | 136 | 09:00 | 125 | 00:00 | Savar | 131 | 18:00 | 122 | 10:00
Gopalganj | 135 | 18:00 | 125 | 00:00 | SevenRings | 136 | 05:00 | 128 | 11:00
Gopalganj-400 | 137 | 18:00 | 130 | 00:00 | ShahCement | 130 | 18:30 | 121 | 10:00
Gulshan | 135 | 05:00 | 122 | 12:00 | Shahjadpur | 136 | 07:00 | 132 | 00:00
Halishahar | 136 | 18:00 | 127 | 10:00 | Shahjibazar | 130 | 06:00 | 121 | 23:00
Haripur | 130 | 18:30 | 122 | 10:00 | Shahmirpur | 136 | 18:00 | 129 | 10:00
HaripurSBU | 130 | 18:30 | 122 | 10:00 | Shariatpur | 135 | 18:00 | 125 | 00:00
Hasnabad | 130 | 18:00 | 123 | 13:00 | Sherpur | 138 | 18:00 | 127 | 19:30
Hathazari | 136 | 18:00 | 131 | 01:00 | Shikalbaha | 124 | 18:00 | 118 | 10:00
Ishurdi | 139 | 08:00 | 131 | 23:00 | Shikalbaha-230 | 136 | 17:00 | 131 | 07:00
Jaldhaka | 136 | 06:00 | 120 | 00:00 | Shitalakhya | 130 | 18:30 | 121 | 10:00
Jamalpur | 139 | 18:00 | 131 | 21:00 | Sholosohor | 134 | 18:00 | 127 | 10:00
Jashore | 135 | 09:00 | 119 | 06:00 | Shyampur | 128 | 18:00 | 119 | 12:00
Jhenaidah | 137 | 08:00 | 119 | 23:00 | Shyampur-230 | 128 | 18:30 | 120 | 12:00
Jhenaidah-230 | 138 | 09:00 | 125 | 00:00 | Siddhirganj | 130 | 18:30 | 122 | 11:00
Joydebpur | 133 | 02:00 | 122 | 12:00 | Sirajganj | 134 | 18:30 | 126 | 00:00
Joypurhat | 134 | 18:30 | 122 | 00:00 | Sonargaon | 129 | 18:30 | 119 | 10:00
Juldah | 136 | 18:30 | 130 | 05:00 | Sreemongol | 129 | 08:00 | 121 | 23:00
Kabirpur | 133 | 18:30 | 122 | 11:00 | Sreepur | 136 | 21:00 | 126 | 19:30
Kachua | 128 | 18:00 | 116 | 00:00 | Srinagar | 133 | 06:00 | 125 | 11:00
Kaliakoir | 135 | 18:00 | 126 | 10:00 | SSM | 139 | 19:30 | 132 | 01:00
Kallyanpur | 131 | 05:00 | 124 | 10:00 | Sunamganj | 126 | 18:00 | 117 | 01:00
Kalurghat | 131 | 16:00 | 127 | 10:00 | Sylhet | 128 | 06:00 | 122 | 23:00
Kamrangirchar | 133 | 06:00 | 124 | 11:00 | Sylhet-132 | 128 | 05:00 | 124 | 22:00
Kaptai | N/A | N/A | N/A | N/A | Tangail | 129 | 18:00 | 121 | 00:00
Kasba | 125 | 18:00 | 117 | 12:00 | Thakurgaon | 137 | 02:00 | 122 | 09:00
Kazla | 130 | 06:00 | 122 | 12:00 | TK | 133 | 18:00 | 128 | 09:00
Keranigonj | 133 | 06:00 | 125 | 12:00 | Tongi | 135 | 04:00 | 126 | 11:00
Khagrachori | 130 | 17:00 | 127 | 10:00 | Ullahpara | 135 | 06:00 | 128 | 00:00
Khulna | 134 | 09:00 | 124 | 01:00 | Ullon | 134 | 06:00 | 122 | 12:00
Khulna(S) | 136 | 08:00 | 128 | 00:00 | Uttara | 130 | 06:00 | 122 | 23:00
Khulshi | 133 | 18:00 | 126 | 10:00 | UttaraNew | 130 | 06:00 | 122 | 23:00
Kishoreganj | 130 | 21:00 | 121 | 19:30 | Zigatola | 133 | 06:00 | 125 | 12:00
Kodda | 133 | 18:00 | 124 | 12:00
KSRM | 135 | 18:00 | 128 | 02:00
Kulaura | 133 | 07:00 | 127 | 22:00
Kurigram | 133 | 13:00 | 120 | 19:30
Kushtia | 134 | 08:00 | 123 | 23:00
Lalbag | 133 | 06:00 | 124 | 12:00
Lalmonirhat | 131 | 03:00 | 121 | 19:30
Madanganj | 129 | 18:30 | 120 | 11:00
Madaripur | 135 | 17:00 | 129 | 23:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division