## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 26-06-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 25-06-2025 | during | 26-06-2025 | during | 26-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 402 | 400.75 | 400.75 | 400.75 | 400.75 | Allocation limit by Titas, instructed by DS(Gen)
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 350 | 450 | 450 | 450 | 450 | Allocation limit by Titas, instructed by DS(Gen)
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 149 | 148 | 150 | 150 | 133 | 133 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 8 | 30 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 326 | 332 | 335 | 335 | 333 | 333 | Allocation limit by Titas, instructed by DS(Gen)
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 24 | 8 | 102 | 32 | 32 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 95 | 125 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 17 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 18.5 | 21.6 | 33 | 33 | 26.8 | 26.8 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 34 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 145 | 285 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 110 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 88 | 105 | 105 | 88 | 88 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 16 | 51 | 104 | 104 | 50 | 50 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 108 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 5 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 53 | 35 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 400 | 500 | 584 | 584 | 500 | 500 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 108 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2450.5 | 2917.6 | 4939.4 | 5003.4 | 3312.07 | 3282.07
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 11 | 0 | 11 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 25 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 172 | 172 | 172 | 172 | 172 | 172 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 216 | 215 | 215 | 210 | 210 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 75 | 105 | 105 | 105 | 105 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 31 | 58 | 82 | 72 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 66 | 65 | 65 | 65 | 65 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 36 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 4 | 2 | 15 | 2 | 2 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 30 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3 | 0 | 1.53 | 0 | 1.53 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 150 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 17 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 17 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 48 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 15 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 54 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1100 | 1112 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 62 | 30 | 58 | 41 | 58 | 41 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 205 | 204 | 575 | 575 | 200 | 200 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1862 | 2435 | 3610.25 | 3617.72 | 3244.25 | 3214.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 207 | 190 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 330 | 345 | 353.35 | 353.35 | 353.35 | 353.35 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 300 | 340 | 340 | 340 | 340 | 340 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 10 | 20 | 46.7 | 46.7 | 23 | 23 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 20 | 43 | 55 | 55 | 48 | 48 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 61 | 129 | 150 | 150 | 145 | 145 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 42 | 43 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 167 | 180 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 36 | 42 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 16 | 13 | 24.5 | 24.5 | 10 | 10 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 92 | 95 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 28 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 115 | 115 | 115 | 115 | 115 | Fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 79 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1479 | 1668 | 2470.75 | 2400.75 | 1942.55 | 1872.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 25-06-2025 | during | 26-06-2025 | during | 26-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 11 | 19 | 157.5 | 157.5 | 10 | 10 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.6 | 0 | 1.6 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 147 | 164 | 200 | 200 | 160 | 160 | Fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 75 | 109 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 8.14 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 11 | 0 | 22 | 22 | 22 | 22 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0.72 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 253.86 | 309 | 598.6 | 549 | 411.1 | 361.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage instructed by DS(Gen)
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 30 | 30 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 152 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 25 | 25 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 61 | 59 | 64 | 64 | 40 | 40 | Under Maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 168 | 165 | 160 | 160 | 160 | 160 | Machine Problem
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 6 | 8 | 25 | 25 | 6 | 6 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 295 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 370 | 361 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 325 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1411 | 1390 | 1536 | 1536 | 1362 | 1362
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 448 | 451 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 39 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 98 | 106 | 410 | 410 | 90 | 90 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 51 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 50 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 84 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 967 | 970 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1635 | 1705 | 3634.2 | 3554.2 | 3314.2 | 3234.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 616 | 616 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 5 | 9 | 10 | 10 | 4 | 4 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 116 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 946 | 990 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 205 | 216 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.37 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 2112.37 | 2200 | 2172 | 2171 | 2104 | 2103
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 44 | 44 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 30 | 30 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 12 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 135 | 135 | 214 | 214 | 135 | 135 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 137 | 136 | 220 | 220 | 130 | 130 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 340 | 385 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 | 30 | 30 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 96 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 90 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 113 | 113 | 28 | 28 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0.83 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1424.21 | 1464.14 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 14.37 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 26 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 2077.41 | 2423.14 | 3192.47 | 3025.87 | 2671.68 | 2505.08
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 50 | 50 | 50 | 47 | 47 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 194 | 199 | 190 | 190 | 190 | 190 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 90 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.6 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 39 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 102 | 0 | 116.43 | 0 | 116.43 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 457.6 | 454 | 649.43 | 502 | 646.43 | 499
System Total |  |  |  |  | 28565.2 | 27084.055 | 13738.74 | 15501.74 | 22803.1 | 22359.94 | 19008.28 | 18434.12
Forecast Scenario (26-06-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15630 |  | 0 |  | 15630
|  |  |  | 1:00 | 15080 |  | 0 |  | 15080
|  |  |  | 2:00 | 14700 |  | 0 |  | 14700
|  |  |  | 3:00 | 14320 |  | 0 |  | 14320
|  |  |  | 4:00 | 14100 |  | 0 |  | 14100
|  |  |  | 5:00 | 13610 |  | 0 |  | 13610
|  |  |  | 6:00 | 13030 |  | 0 |  | 13030
|  |  |  | 7:00 | 12780 |  | 0 |  | 12780
|  |  |  | 8:00 | 12850 |  | 0 |  | 12850
|  |  |  | 9:00 | 13020 |  | 0 |  | 13020
|  |  |  | 10:00 | 13260 |  | 0 |  | 13260
|  |  |  | 11:00 | 13430 |  | 0 |  | 13430
|  |  |  | 12:00 | 13730 |  | 0 |  | 13730
|  |  |  | 13:00 | 14030 |  | 0 |  | 14030
|  |  |  | 14:00 | 13940 |  | 0 |  | 13940
|  |  |  | 15:00 | 14290 |  | 0 |  | 14290
|  |  |  | 16:00 | 14050 |  | 0 |  | 14050
|  |  |  | 17:00 | 13720 |  | 0 |  | 13720
|  |  |  | 18:00 | 13070 |  | 0 |  | 13070
|  |  |  | 18:30 | 13600 |  | 0 |  | 13600
|  |  |  | 19:00 | 14270 |  | 0 |  | 14270
|  |  |  | 19:30 | 15570 |  | 0 |  | 15570
|  |  |  | 20:00 | 15420 |  | 0 |  | 15420
|  |  |  | 21:00 | 15470 |  | 0 |  | 15470
|  |  |  | 22:00 | 15340 |  | 0 |  | 15340
|  |  |  | 23:00 | 15320 |  | 0 |  | 15320
Probable Maximum Temperature: |  |  | 31.50°C
Probable Maximum Demand at Day Peak: |  |  | 13730.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15570.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15570.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 338.46 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:04 hrs on 26-06-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 25-06-2025 | [28 empty] | Date: | 25-06-2025 | [28 empty] | Date: | 25-06-2025 | [28 empty] | Date: | 25-06-2025 | [28 empty] | Date: | 25-06-2025 | [12 empty] | Date: | 25-06-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [12 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 32 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 0 | 55 | 149 | 144 | 175 | 15 | 0 | 17 | 51 | 420 | 205 | 0 | 0 | 35 | 333 | 0 | 0 | 0 | 142 | 16 | 21 | 0 | 77 | 30 | 100 | 13 | 0 | 34 | 66 | 69 | 0 | 100 | 100 | 0 | 172 | 56 | 14 | 202 | 72 | 0 | 32 | 25.5 | 66 | 218 | 0 | 0 | 0 | 1190 | 0 | 43 | 143 | 0 | 0 | 347 | 320 | 5 | 158 | 10 | 43 | 0 | 180 | 13 | 19 | 114 | 48 | 52.2 | 0 | 44 | 295 | 320 | 333 | 0 | 0 | 145 | 8 | 0 | 40 | 22 | 0 | 0 | 167 | 17 | 102 | 163 | 17 | 0 | 0 | 11 | 8077.7 | 451 | 103 | 0 | 20 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 1160 | 68 | 1464.99 | 0 | 35 | 0 | 113 | 25 | 97 | 113 | 28 | 8 | 0 | 30 | 0 | 142 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0 | 184 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 16 | 279 | 11 | 120 | 220 | 0 | 616 | 1244 | 14 | 7464.99 | 15542.69 | 98.66
01:00 | 8 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 0 | 55 | 149 | 144 | 145 | 15 | 0 | 17 | 51 | 370 | 143 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 108 | 19.5 | 21 | 0 | 350 | 41 | 100 | 0 | 0 | 45 | 66 | 69 | 0 | 100 | 100 | 0 | 172 | 77 | 14 | 204 | 35 | 0 | 42 | 25.5 | 80 | 217 | 0 | 0 | 0 | 1126 | 0 | 51 | 143 | 0 | 0 | 330 | 300 | 5 | 186 | 10 | 33 | 0 | 180 | 8 | 17 | 114 | 48 | 52.2 | 0 | 44 | 290 | 320 | 331 | 0 | 0 | 152 | 8 | 0 | 40 | 30 | 0 | 0 | 167 | 17 | 102 | 153 | 19 | 0 | 0 | 11 | 8027.2 | 451 | 92 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 52 | 1450.34 | 0 | 34 | 0 | 70 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 143 | 0 | 0 | 0 | 340 | 0 | 0 | 187 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 11 | 116 | 220 | 0 | 617 | 1244 | 0 | 6968.34 | 14995.54 | 98.66
02:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 55 | 149 | 143 | 145 | 15 | 0 | 17 | 51 | 370 | 152 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 108 | 16 | 21 | 0 | 350 | 42 | 50 | 0 | 0 | 19 | 66 | 69 | 0 | 100 | 100 | 0 | 172 | 40 | 15 | 201 | 0 | 0 | 50 | 25.5 | 66 | 218 | 0 | 0 | 0 | 1143 | 0 | 51 | 90 | 0 | 0 | 330 | 300 | 5 | 204 | 10 | 34 | 0 | 180 | 9 | 17 | 114 | 44 | 52.2 | 0 | 44 | 295 | 320 | 332 | 0 | 0 | 150 | 0 | 0 | 40 | 30 | 0 | 0 | 167 | 17 | 94 | 153 | 30 | 0 | 0 | 12 | 7837.7 | 451 | 91 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1118 | 34 | 1450.63 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 144 | 0 | 0 | 0 | 340 | 0 | 0 | 186 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 11 | 120 | 220 | 0 | 617 | 1244 | 0 | 6768.63 | 14606.33 | 98.65
03:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 55 | 149 | 144 | 15 | 0 | 0 | 17 | 51 | 370 | 151 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 108 | 19.5 | 21 | 0 | 350 | 0 | 15 | 0 | 0 | 37 | 33 | 23.5 | 0 | 100 | 100 | 0 | 172 | 34 | 15 | 205 | 0 | 0 | 50 | 0 | 34 | 220 | 0 | 0 | 0 | 1132 | 0 | 51 | 70 | 0 | 0 | 330 | 300 | 5 | 211 | 10 | 34 | 0 | 180 | 9 | 17 | 114 | 44 | 52.2 | 0 | 43 | 290 | 320 | 335 | 0 | 0 | 153 | 0 | 0 | 40 | 30 | 0 | 0 | 168 | 17 | 94 | 153 | 30 | 0 | 0 | 12 | 7429.2 | 451 | 90 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1145 | 34 | 1462.71 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 144 | 0 | 0 | 0 | 340 | 0 | 0 | 190 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 10 | 120 | 220 | 0 | 620 | 1244 | 0 | 6815.71 | 14244.91 | 98.65
04:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 55 | 149 | 144 | 0 | 0 | 0 | 17 | 51 | 370 | 151 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 90 | 19.5 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 29 | 33 | 0 | 0 | 100 | 100 | 0 | 172 | 17 | 15 | 204 | 0 | 0 | 2 | 0 | 30 | 220 | 0 | 0 | 0 | 1157 | 0 | 51 | 60 | 0 | 0 | 330 | 300 | 5 | 214 | 10 | 34 | 0 | 181 | 9 | 15 | 114 | 44 | 52.2 | 0 | 43 | 295 | 320 | 345 | 0 | 0 | 153 | 0 | 0 | 40 | 30 | 0 | 0 | 169 | 17 | 94 | 148 | 30 | 0 | 0 | 12 | 7315.7 | 451 | 90 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1130 | 17 | 1440.66 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 144 | 0 | 0 | 0 | 340 | 0 | 0 | 190 | 48 | 70 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 10 | 120 | 220 | 0 | 619 | 1244 | 0 | 6717.66 | 14033.36 | 98.65
05:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 55 | 136 | 144 | 0 | 0 | 0 | 17 | 51 | 340 | 152 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 35 | 19.5 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 56 | 33 | 0 | 0 | 70 | 100 | 0 | 172 | 0 | 23 | 204 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1102 | 0 | 43 | 0 | 0 | 0 | 330 | 300 | 5 | 209 | 10 | 36 | 0 | 179 | 9 | 17 | 114 | 34 | 52.2 | 0 | 43 | 295 | 320 | 365 | 0 | 0 | 157 | 0 | 0 | 40 | 30 | 0 | 0 | 169 | 17 | 94 | 156 | 30 | 0 | 0 | 12 | 7070.7 | 451 | 90 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1070 | 0 | 1431.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 144 | 0 | 0 | 0 | 340 | 0 | 0 | 190 | 48 | 70 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 10 | 120 | 220 | 0 | 619 | 1180 | 0 | 6488.97 | 13559.67 | 98.65
06:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 55 | 113 | 144 | 0 | 0 | 0 | 17 | 16 | 340 | 146 | 0 | 0 | 0 | 300 | 0 | 0 | 1 | 35 | 20.5 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 70 | 75 | 0 | 172 | 0 | 25 | 204 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1085 | 1 | 51 | 0 | 0 | 0 | 330 | 300 | 5 | 193 | 10 | 34 | 0 | 180 | 9 | 17 | 114 | 28 | 52.2 | 4 | 44 | 300 | 320 | 325 | 0 | 0 | 158 | 0 | 0 | 40 | 30 | 0 | 0 | 169 | 17 | 95 | 148 | 32 | 0 | 0.79 | 12 | 6874.49 | 451 | 93 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 992 | 0 | 1309.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0.83 | 135 | 0 | 144 | 0 | 0 | 0 | 340 | 0 | 0.11 | 194 | 48 | 35 | 0 | 70 | 0 | 0 | 0.3 | 6 | 0.01 | 0 | 229 | 9 | 120 | 220 | 0 | 619 | 1050 | 0 | 6112.23 | 12986.72 | 98.64
07:00 | 0 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 2 | 55 | 104 | 127 | 0 | 0 | 0 | 17 | 16 | 340 | 147 | 0 | 0 | 0 | 300 | 0 | 0 | 6 | 17 | 20.5 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 36 | 36 | 1 | 172 | 0 | 10 | 203 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1053 | 2 | 51 | 0 | 0 | 0 | 330 | 300 | 5 | 202 | 10 | 34 | 0 | 180 | 9 | 17 | 114 | 40 | 8 | 10 | 43 | 295 | 320 | 345 | 0 | 0 | 155 | 0 | 0 | 40 | 30 | 0 | 0 | 169 | 17 | 94 | 139 | 27 | 1 | 2.15 | 3 | 6707.65 | 448 | 93 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14 | 1006 | 0 | 1260.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 5.51 | 135 | 0 | 144 | 0 | 0 | 0 | 340 | 0 | 1.11 | 196 | 48 | 35 | 5 | 34 | 0 | 0 | 0.5 | 35 | 0.1 | 0 | 230 | 7 | 120 | 220 | 0 | 619 | 1030 | 0 | 6076.12 | 12783.77 | 98.64
08:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 17 | 55 | 82 | 112 | 0 | 0 | 0 | 17 | 16 | 340 | 152 | 0 | 0 | 0 | 300 | 0 | 0 | 17 | 17 | 20 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 36 | 36 | 2 | 172 | 0 | 2 | 203 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 1053 | 8 | 51 | 0 | 0 | 0 | 330 | 300 | 8 | 201 | 10 | 34 | 0 | 180 | 9 | 14 | 100 | 36 | 8 | 19 | 43 | 295 | 320 | 345 | 0 | 0 | 157 | 0 | 0 | 40 | 30 | 0 | 0 | 170 | 17 | 75 | 139 | 27 | 1 | 8.25 | 10 | 6723.25 | 410 | 88 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 58 | 1002 | 0 | 1266.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 18.56 | 135 | 0 | 144 | 0 | 0 | 0 | 350 | 0 | 3.75 | 198 | 47 | 35 | 6 | 34 | 0 | 0 | 1.2 | 38 | 0.18 | 0 | 231 | 6 | 120 | 220 | 0 | 619 | 1031 | 0 | 6134.88 | 12858.13 | 98.64
09:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 17 | 55 | 80 | 112 | 0 | 0 | 17 | 17 | 16 | 340 | 151 | 0 | 0 | 0 | 300 | 0 | 0 | 18 | 17 | 19.5 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 36 | 36 | 4 | 172 | 0 | 2 | 202 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 1053 | 11 | 51 | 0 | 0 | 0 | 330 | 300 | 10 | 200 | 10 | 35 | 0 | 180 | 9 | 14 | 88 | 34 | 8 | 46 | 43 | 300 | 320 | 346 | 0 | 0 | 159 | 6 | 0 | 40 | 30 | 0 | 0 | 169 | 17 | 75 | 147 | 27 | 0 | 23.56 | 11 | 6801.06 | 448 | 83 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 59 | 1003 | 0 | 1271.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 25.45 | 135 | 0 | 144 | 0 | 0 | 0 | 340 | 0 | 1.12 | 195 | 47 | 35 | 19 | 34 | 0 | 0 | 1.5 | 49 | 0.14 | 0 | 232 | 6 | 120 | 220 | 0 | 618 | 1034 | 0 | 6205.74 | 13006.8 | 98.64
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 0 | 17 | 55 | 77 | 95 | 0 | 0 | 17 | 72 | 16 | 450 | 149 | 0 | 0 | 0 | 330 | 0 | 0 | 13 | 17 | 18.5 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 36 | 36 | 2 | 172 | 0 | 2 | 204 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1053 | 4 | 51 | 0 | 0 | 0 | 330 | 300 | 10 | 204 | 10 | 51 | 0 | 179 | 9 | 14 | 90 | 36 | 8 | 50 | 42 | 300 | 320 | 335 | 0 | 0 | 159 | 6 | 0 | 61 | 30 | 0 | 0 | 169 | 17 | 75 | 147 | 11 | 1 | 27.12 | 11 | 7057.62 | 448 | 78 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 40 | 974 | 0 | 1395.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 29.18 | 135 | 0 | 141 | 0 | 0 | 0 | 340 | 0 | 2.03 | 196 | 47 | 35 | 33 | 34 | 0 | 0 | 3.6 | 40 | 0.2 | 0 | 203 | 5 | 120 | 220 | 0 | 617 | 950 | 0 | 6186.97 | 13244.59 | 98.63
11:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 55 | 80 | 95 | 105 | 0 | 35 | 72 | 16 | 450 | 145 | 0 | 0 | 17 | 330 | 0 | 0 | 30 | 17 | 18.5 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 36 | 36 | 3 | 172 | 0 | 2 | 203 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 1050 | 11 | 51 | 2 | 0 | 0 | 330 | 300 | 14 | 192 | 10 | 51 | 0 | 165 | 9 | 16 | 91 | 36 | 8 | 70 | 42 | 305 | 320 | 340 | 0 | 0 | 156 | 6 | 0 | 61 | 30 | 0 | 0 | 169 | 0 | 75 | 147 | 11 | 1 | 33.79 | 11 | 7226.29 | 448 | 90 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 33 | 960 | 0 | 1408.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 32.42 | 135 | 0 | 139 | 0 | 0 | 0 | 340 | 0 | 2.74 | 194 | 48 | 35 | 16 | 34 | 0 | 0 | 2.8 | 74 | 0.44 | 0 | 199 | 6 | 120 | 220 | 0 | 615 | 947 | 0 | 6210.16 | 13436.45 | 98.63
12:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 53 | 110 | 95 | 145 | 8 | 35 | 72 | 16 | 450 | 149 | 0 | 0 | 35 | 326 | 0 | 0 | 5 | 17 | 18.5 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 36 | 48 | 3 | 172 | 0 | 2 | 205 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 1100 | 20 | 51 | 61 | 0 | 0 | 330 | 300 | 20 | 207 | 10 | 51 | 0 | 167 | 9 | 16 | 92 | 36 | 8 | 79 | 42 | 295 | 325 | 370 | 0 | 0 | 156 | 6 | 0 | 61 | 30 | 0 | 0 | 168 | 0.72 | 75 | 147 | 11 | 1 | 8.14 | 11 | 7456.36 | 448 | 98 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 84 | 967 | 0 | 1424.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 14.37 | 135 | 0 | 137 | 0 | 0 | 0 | 340 | 0 | 0.83 | 194 | 48 | 35 | 39 | 34 | 0 | 0 | 5.6 | 102 | 0.37 | 0 | 205 | 5 | 120 | 220 | 0 | 616 | 946 | 0 | 6282.38 | 13738.74 | 98.63
13:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 35 | 112 | 95 | 185 | 15 | 35 | 72 | 16 | 450 | 143 | 0 | 0 | 35 | 327 | 0 | 0 | 21 | 17 | 18.5 | 21 | 0 | 400 | 0 | 30 | 0 | 0 | 56 | 0 | 0 | 0 | 88 | 88 | 2 | 172 | 0 | 5 | 205 | 0 | 0 | 5 | 0 | 23 | 214 | 0 | 0 | 0 | 1045 | 3 | 51 | 108 | 0 | 0 | 330 | 300 | 20 | 195 | 23 | 51 | 0 | 161 | 9 | 16 | 99 | 40 | 8 | 38 | 42 | 290 | 320 | 334 | 0 | 0 | 157 | 8 | 0 | 59 | 30 | 0 | 0 | 168 | 17 | 75 | 147 | 10 | 1 | 10.84 | 11 | 7557.34 | 448 | 102 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 91 | 948 | 0 | 1447.03 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 34.93 | 135 | 0 | 135 | 0 | 0 | 0 | 340 | 0 | 3.11 | 194 | 47 | 35 | 14 | 65 | 0 | 0 | 7.8 | 183 | 0.29 | 0 | 201 | 5 | 120 | 220 | 0 | 618 | 945 | 0 | 6477.16 | 14034.5 | 98.63
14:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 17 | 35 | 112 | 95 | 278 | 15 | 35 | 72 | 16 | 450 | 149 | 0 | 0 | 35 | 280 | 0 | 0 | 0 | 17 | 19.3 | 21 | 0 | 350 | 0 | 30 | 0 | 0 | 62 | 0 | 0 | 0 | 100 | 88 | 5 | 172 | 0 | 2 | 204 | 0 | 0 | 18 | 0 | 46 | 213 | 0 | 0 | 0 | 1052 | 4 | 51 | 118 | 8 | 0 | 300 | 280 | 22 | 197 | 23 | 56 | 0 | 171 | 9 | 17 | 97 | 34 | 8 | 38 | 42 | 295 | 320 | 346 | 0 | 0 | 146 | 8 | 0 | 58 | 30 | 0 | 0 | 168 | 17 | 75 | 146 | 10 | 1 | 25.07 | 11 | 7584.37 | 447 | 103 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 85 | 921 | 0 | 1452.34 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 1.06 | 135 | 0 | 134 | 0 | 0 | 0 | 340 | 0 | 0.02 | 193 | 47 | 35 | 27 | 70 | 0 | 0 | 8 | 125 | 0.65 | 0 | 201 | 4 | 120 | 180 | 0 | 617 | 935 | 0 | 6364.07 | 13948.44 | 98.62
15:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 17 | 35 | 112 | 110 | 278 | 15 | 35 | 72 | 18 | 450 | 143 | 0 | 0 | 35 | 327 | 0 | 0 | 28 | 17 | 19 | 21 | 0 | 400 | 0 | 30 | 0 | 0 | 62 | 0 | 0 | 0 | 100 | 100 | 2 | 172 | 0 | 2 | 203 | 0 | 0 | 18 | 0 | 50 | 217 | 0 | 0 | 0 | 1038 | 1 | 51 | 118 | 8 | 0 | 337 | 340 | 30 | 194 | 23 | 69 | 0 | 176 | 9 | 17 | 95 | 44 | 8 | 32 | 42 | 295 | 320 | 378 | 0 | 0 | 142 | 8 | 0 | 0 | 25 | 0 | 0 | 168 | 17 | 75 | 155 | 10 | 1 | 7.9 | 11 | 7768.9 | 448 | 104 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 92 | 952 | 0 | 1445.23 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 119 | 0 | 6.54 | 135 | 0 | 131 | 0 | 0 | 0 | 380 | 0 | 0.64 | 192 | 49 | 35 | 14 | 70 | 0 | 0 | 5.6 | 160 | 0.71 | 0 | 171 | 4 | 120 | 180 | 0 | 616 | 941 | 0 | 6522.72 | 14291.62 | 98.62
16:00 | 0 | 52 | 32 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 35 | 35 | 83 | 110 | 281 | 15 | 35 | 72 | 40 | 450 | 148 | 0 | 0 | 35 | 325 | 0 | 0 | 19 | 35 | 19 | 21 | 0 | 450 | 0 | 15 | 0 | 0 | 51 | 0 | 0 | 0 | 100 | 100 | 1 | 172 | 0 | 2 | 202 | 0 | 0 | 19 | 0 | 17 | 215 | 0 | 0 | 0 | 1055 | 2 | 51 | 113 | 8 | 0 | 333 | 340 | 31 | 205 | 23 | 69 | 0 | 161 | 8 | 5 | 95 | 40 | 8 | 13 | 42 | 300 | 320 | 379 | 0 | 0 | 144 | 8 | 0 | 40 | 25 | 0 | 0 | 165 | 0 | 75 | 154 | 11 | 1 | 15.59 | 11 | 7793.59 | 448 | 104 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 52 | 884 | 0 | 1459.69 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 5.95 | 135 | 0 | 131 | 0 | 0 | 0 | 380 | 0 | 0.55 | 194 | 49 | 35 | 19 | 34 | 0 | 0 | 6.1 | 127 | 0.21 | 0 | 172 | 5 | 120 | 180 | 0 | 617 | 945 | 0 | 6257.5 | 14051.09 | 98.62
17:00 | 0 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 35 | 35 | 77 | 110 | 281 | 15 | 35 | 108 | 51 | 380 | 145 | 0 | 0 | 17 | 325 | 0 | 0 | 10 | 35 | 19 | 21 | 0 | 450 | 0 | 15 | 0 | 0 | 63 | 0 | 0 | 0 | 100 | 100 | 0 | 172 | 0 | 6 | 204 | 0 | 0 | 19 | 0 | 15 | 216 | 0 | 0 | 0 | 1050 | 2 | 51 | 118 | 0 | 0 | 300 | 280 | 40 | 197 | 20 | 69 | 0 | 162 | 8 | 14 | 95 | 40 | 8 | 13 | 42 | 300 | 320 | 383 | 0 | 0 | 143 | 8 | 0 | 58 | 30 | 0 | 0 | 165 | 13 | 75 | 154 | 11 | 1 | 6.11 | 11 | 7688.11 | 451 | 104 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 46 | 875 | 0 | 1450.13 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 2.6 | 135 | 0 | 130 | 0 | 0 | 0 | 280 | 0 | 0.2 | 194 | 49 | 35 | 6 | 34 | 0 | 0 | 2.8 | 61 | 0 | 0 | 171 | 6 | 120 | 220 | 0 | 617 | 942 | 0 | 6038.73 | 13726.84 | 98.62
18:00 | 8 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 35 | 35 | 106 | 110 | 285 | 15 | 35 | 108 | 51 | 320 | 149 | 0 | 0 | 17 | 280 | 0 | 0 | 1 | 35 | 19 | 21 | 0 | 400 | 10 | 15 | 7 | 0 | 56 | 0 | 0 | 12 | 100 | 100 | 0 | 172 | 10 | 2 | 201 | 17 | 0 | 19 | 1 | 15 | 215 | 0 | 0 | 0 | 960 | 2 | 51 | 123 | 0 | 0 | 300 | 280 | 43 | 204 | 20 | 69 | 0 | 173 | 20 | 19 | 100 | 34 | 8 | 3 | 42 | 295 | 320 | 388 | 0 | 0 | 135 | 8 | 0 | 59 | 30 | 0 | 0 | 165 | 17 | 75 | 152 | 11 | 0 | 2.88 | 11 | 7579.88 | 451 | 104 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 15 | 784 | 0 | 1226.08 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 8 | 7 | 0 | 1.7 | 135 | 0 | 130 | 0 | 0 | 0 | 280 | 0 | 0 | 194 | 49 | 35 | 3 | 34 | 0 | 0 | 0.7 | 16 | 0.09 | 0 | 172 | 6 | 120 | 220 | 0 | 616 | 800 | 0 | 5495.57 | 13075.45 | 98.61
19:00 | 8 | 88 | 34 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 54 | 35 | 149 | 110 | 281 | 15 | 35 | 108 | 51 | 380 | 148 | 0 | 0 | 17 | 327 | 0 | 0 | 0 | 75 | 21 | 21 | 0 | 450 | 16 | 30 | 25 | 0 | 22 | 62 | 16 | 17 | 100 | 100 | 0 | 172 | 17 | 14 | 203 | 25 | 0 | 19 | 7 | 20 | 216 | 0 | 0 | 0 | 1080 | 0 | 51 | 125 | 0 | 0 | 333 | 305 | 42 | 208 | 20 | 76 | 0 | 174 | 27 | 19 | 110 | 44 | 8 | 0 | 43 | 295 | 320 | 383 | 0 | 0 | 148 | 8 | 0 | 59 | 30 | 0 | 0 | 165 | 17 | 101 | 154 | 19 | 0 | 0 | 10 | 8242 | 451 | 104 | 0 | 30 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 845 | 20 | 1279.85 | 0 | 0 | 0 | 50 | 0 | 85 | 10 | 12 | 11 | 0 | 20 | 0 | 135 | 0 | 133 | 0 | 0 | 0 | 334 | 0 | 0 | 197 | 50 | 95 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 16 | 212 | 9 | 130 | 220 | 0 | 616 | 820 | 6 | 6031.85 | 14273.85 | 98.61
19:30 | 24 | 88 | 34 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 54 | 35 | 149 | 125 | 285 | 30 | 35 | 108 | 51 | 350 | 148 | 0 | 0 | 17 | 332 | 0 | 0 | 0 | 108 | 21.6 | 21 | 0 | 500 | 15 | 150 | 30 | 0 | 30 | 66 | 31 | 17 | 100 | 100 | 0 | 172 | 17 | 4 | 204 | 54 | 0 | 25 | 17 | 75 | 216 | 0 | 0 | 0 | 1112 | 0 | 51 | 129 | 0 | 0 | 345 | 340 | 43 | 190 | 20 | 115 | 0 | 180 | 28 | 13 | 95 | 42 | 34 | 0 | 43 | 295 | 320 | 361 | 0 | 0 | 152 | 8 | 0 | 59 | 30 | 0 | 0 | 165 | 17 | 109 | 164 | 19 | 0 | 0 | 0 | 8719.6 | 451 | 106 | 0 | 39 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 970 | 51 | 1464.14 | 0 | 0 | 0 | 90 | 0 | 96 | 50 | 12 | 25 | 0 | 30 | 0 | 135 | 0 | 136 | 0 | 0 | 0 | 385 | 0 | 0 | 199 | 50 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 16 | 216 | 9 | 116 | 220 | 0 | 616 | 990 | 17 | 6782.14 | 15501.74 | 98.61
20:00 | 24 | 88 | 34 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 35 | 148 | 130 | 195 | 40 | 55 | 108 | 51 | 350 | 152 | 0 | 0 | 17 | 333 | 0 | 0 | 0 | 108 | 21.5 | 21 | 0 | 500 | 13 | 150 | 31 | 0 | 27 | 66 | 34 | 17 | 100 | 100 | 0 | 172 | 15 | 8 | 204 | 54 | 0 | 29 | 25.5 | 67 | 216 | 0 | 0 | 0 | 1097 | 0 | 51 | 130 | 0 | 0 | 347 | 340 | 44 | 187 | 20 | 115 | 0 | 180 | 27 | 19 | 97 | 40 | 38 | 0 | 44 | 295 | 320 | 353 | 0 | 0 | 152 | 8 | 0 | 60 | 30 | 0 | 0 | 165 | 17 | 108 | 164 | 19 | 0 | 0 | 0 | 8661 | 451 | 106 | 0 | 35 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 954 | 52 | 1445.02 | 0 | 42 | 0 | 110 | 0 | 96 | 70 | 28 | 25 | 0 | 30 | 0 | 135 | 0 | 137 | 0 | 0 | 0 | 250 | 0 | 0 | 196 | 49 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 16 | 213 | 7 | 112 | 220 | 0 | 617 | 1027 | 17 | 6733.02 | 15394.02 | 98.61
21:00 | 0 | 88 | 34 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 54 | 35 | 132 | 143 | 45 | 15 | 55 | 108 | 50 | 350 | 150 | 0 | 0 | 17 | 333 | 0 | 0 | 0 | 35 | 21.5 | 21 | 0 | 500 | 15 | 100 | 0 | 0 | 54 | 66 | 79 | 17 | 100 | 100 | 0 | 172 | 15 | 12 | 204 | 0 | 0 | 33 | 25.5 | 51 | 216 | 0 | 0 | 0 | 1140 | 0 | 51 | 130 | 0 | 0 | 347 | 340 | 46 | 201 | 20 | 115 | 0 | 180 | 28 | 20 | 97 | 36 | 52.2 | 0 | 44 | 300 | 320 | 372 | 0 | 0 | 154 | 8 | 0 | 60 | 28 | 0 | 0 | 165 | 17 | 110 | 175 | 32 | 0 | 0 | 0 | 8436.2 | 451 | 114 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1100 | 34 | 1447.96 | 0 | 43 | 0 | 113 | 0 | 96 | 0 | 37 | 0 | 0 | 30 | 0 | 135 | 0 | 147 | 0 | 0 | 0 | 402 | 0 | 0 | 194 | 50 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 9 | 120 | 220 | 0 | 617 | 1090 | 17 | 7002.96 | 15439.16 | 98.6
22:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 35 | 35 | 149 | 142 | 45 | 15 | 17 | 108 | 50 | 350 | 153 | 0 | 0 | 17 | 333 | 0 | 0 | 0 | 70 | 21.5 | 21 | 0 | 500 | 13 | 100 | 0 | 0 | 25 | 66 | 79 | 17 | 100 | 100 | 0 | 172 | 15 | 17 | 205 | 0 | 0 | 33 | 25.5 | 49 | 218 | 0 | 0 | 0 | 1151 | 0 | 51 | 132 | 0 | 0 | 345 | 340 | 48 | 162 | 20 | 111 | 0 | 181 | 28 | 20 | 99 | 42 | 52.2 | 0 | 46 | 290 | 320 | 388 | 0 | 0 | 142 | 8 | 0 | 60 | 25 | 0 | 0 | 165 | 17 | 110 | 185 | 31 | 0 | 0 | 0 | 8362.2 | 419 | 119 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1155 | 40 | 1445 | 0 | 43 | 0 | 113 | 0 | 96 | 0 | 30 | 0 | 0 | 30 | 0 | 135 | 0 | 152 | 0 | 0 | 0 | 330 | 0 | 0 | 194 | 50 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 11 | 120 | 220 | 0 | 617 | 1106 | 17 | 6979 | 15341.2 | 98.6
23:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 35 | 149 | 142 | 145 | 15 | 0 | 72 | 50 | 350 | 152 | 0 | 0 | 17 | 333 | 0 | 0 | 0 | 90 | 21.5 | 21 | 0 | 450 | 15 | 100 | 0 | 0 | 35 | 66 | 77 | 17 | 100 | 100 | 0 | 172 | 16 | 20 | 205 | 0 | 0 | 33 | 25.5 | 51 | 218 | 0 | 0 | 0 | 1165 | 0 | 51 | 128 | 0 | 0 | 346 | 340 | 48 | 149 | 20 | 84 | 0 | 198 | 28 | 19 | 100 | 44 | 52.2 | 0 | 46 | 295 | 320 | 397 | 0 | 0 | 127 | 8 | 0 | 60 | 25 | 0 | 0 | 168 | 0 | 110 | 185 | 34 | 0 | 0 | 1 | 8321.2 | 348 | 125 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1196 | 69 | 1462 | 0 | 43 | 0 | 113 | 0 | 96 | 35 | 30 | 0 | 0 | 30 | 0 | 140 | 0 | 153 | 0 | 0 | 0 | 330 | 0 | 0 | 195 | 49 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 11 | 130 | 220 | 0 | 616 | 1202 | 17 | 7148 | 15469.2 | 98.59
Total KWH | 64080 | 1159680 | 584640 | 0 | 0 | 0 | 0 | 0 | 9273600 | 0 | 0 | 455400 | 1112040 | 2887632 | 2942400 | 3145145 | 288577 | 462804 | 1373760 | 848640 | 9159000 | 3585658 | 0 | 0 | 406650 | 7565749 | 0 | 0 | 157054 | 1220400 | 472800 | 488520 | 0 | 9770909.09 | 201982 | 938400 | 78720 | 0 | 1140000 | 616362 | 510768 | 123723 | 1984320 | 2026560 | 27742 | 4125280 | 332034 | 219360 | 4923636.36 | 195709 | 0 | 467040 | 194104.8 | 714255 | 5018691 | 0 | 0 | 0 | 26198179 | 56700 | 1157890 | 1985527 | 16727 | 0 | 8252000 | 7526000 | 530880 | 4773000 | 377712 | 1394880 | 0 | 4254720 | 330120 | 373760 | 2481780 | 939840 | 698510 | 436791 | 1029088 | 7144000 | 7680800 | 8910000 | 0 | 0 | 3592390 | 123552 | 0 | 1161600 | 683904 | 0 | 0 | 3465360 | 348120 | 2126400 | 3698400 | 456960 | 8000 | 185280 | 222960 | 183885655.25 | 10688727 | 2565504 | 0 | 76800 | 9984 | 912000 | 0 | 0 | 0 | 0 | 154512 | 603360 | 24327270 | 417120 | 32145481 | 0 | 211522 | 0 | 1400448 | 0 | 553632 | 328512 | 144970 | 47126 | 595974 | 158240 | 186744 | 3427000 | 0 | 3623973 | 0 | 0 | 0 | 8323490 | 0 | 16620 | 4712000 | 1093963 | 1658244 | 208439 | 1648406 | 0 | 0 | 46596.24 | 976320 | 3279 | 41856 | 5389000 | 194345 | 2879000 | 5378690 | 0 | 14814545.45 | 26036363.64 | 99600 | 156099656.33 | 339985311.58

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 25-06-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13738.74 | MW | 12:00 Hr. | Energy Generated |  |  | 339.9853 |  | MKWHr.
| Day Peak Demand |  |  | 13738.74 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.665 |  | MKWHr.
| Evening Peak Generation |  |  | 15501.74 | MW | 19:30 Hr. | Energy Demand |  |  | 340.6503 |  | MKWHr.
| Evening Peak Demand |  |  | 15570.74 | MW | 19:30 Hr. | Maximum Temperature |  |  | 34.4 |  | °C
| Minimum Generation of the Day |  |  | 12783.77 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 932.78 |  | MMCFD
| Maximum Generation of the Day |  |  | 15542.69 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.9335 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.3162 | 0 | 16.9518 | 0 | 0 | 0.15705 | 0 | 0 | 57.4251 | Gas | 128.1728 | Gas | 447692947.2353
| Chattogram Zone |  |  | 5.2381 | 31.1218 | 8.384 | 0 | 4.1253 | 0.084442 | 0 | 1.14 | 50.0936 | Coal | 107.495 | Coal | 631205125.552
| Cumilla Zone |  |  | 23.008 | 0 | 12.1746 | 0 | 0 | 0.43679 | 0.93984 | 0 | 36.5592 | HFO | 50.8573 | HFO | 954160607.636
| Mymensingh Zone |  |  | 0.45696 | 0 | 6.3959 | 0 | 0 | 0.19328 | 0 | 0 | 7.0461 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 32.7616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.7616 | Hydro | 4.1253 | Hydro | 412528
| Khulna Zone |  |  | 2.5655 | 24.3273 | 0.65842 | 0 | 0 | 0.60336 | 11.6007 | 0 | 39.7553 | Solar | 3.5089 | Solar | 56864188.2364
| Barishal Zone |  |  | 8.452 | 46.2399 | 0.14146 | 0 | 0 | 0.003279 | 0 | 0 | 54.8367 | Import | 44.686 | Import | 250254840.51
| Rajshahi Zone |  |  | 15.3745 | 0 | 2.8445 | 0 | 0 | 0.79934 | 32.1455 | 0 | 51.1637 | Wind | 1.14 | Wind | 16689600
| Rangpur Zone |  |  | 0 | 5.806 | 3.3066 | 0 | 0 | 1.2314 | 0 | 0 | 10.344
| Total |  |  | 128.1728 | 107.495 | 50.8573 | 0 | 4.1253 | 3.5089 | 44.686 | 1.14 | 339.9853
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 447692947.2353 |  | Hydro | 412528
|  |  |  | Coal | 631205125.552 |  | Solar | 56864188.2364
|  |  |  | HFO | 954160607.636 |  | Import | 250254840.51
|  |  |  | HSD | 0 |  | Wind | 16689600
[5 empty] | Total: | 235,72,79,837 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 10.6887 | Peak Hr Flow | 451.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 46394690.96 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 32.1455 | Peak Hr Flow | 1464.14 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 548 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.93984 | Peak Hr Flow | 42.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 884 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 43.774 | Peak Hr Flow | 1957.14 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5584
|  |  |  | Chattogram |  | 0 |  | 1440
|  |  |  | Cumilla |  | 0 |  | 1427
|  |  |  | Mymensingh |  | 30 |  | 1147
|  |  |  | Sylhet |  | 0 |  | 638
|  |  |  | Khulna |  | 0 |  | 1819
|  |  |  | Barishal |  | 0 |  | 467
|  |  |  | Rajshahi |  | 0 |  | 1508
|  |  |  | Rangpur |  | 36 |  | 1035
|  |  |  | Total |  | 66 |  | 15065
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[7 empty] | 5 | Meghnaghat CCPP(Summit) GT-2 |  |  | 110
[5 empty] | Total | 300 |  |  |  | Total | 586
|  |  |  | Total Unavailable Capacity |  |  |  | 886
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:52 |  | Ishwardi-Natore 132kV Ckt-1 Scheduled S/D from Ishurdi 132/33kV end. and from Natore
132/33kV end Due to CT Change
|  | 09:18 | Moghbazar-Rampura 132kV Ckt-1 is restored.
| 10:32 | 11:02 | Dohazari 132/33kV S/S Power Transformer -T-2 HT Scheduled S/D Due to Replacing the fuse | [7 empty] | 27.0MW load
|  |  | of station supply transformer. | [7 empty] | interrup.
| 10:32 | 11:02 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Scheduled S/D Due to Replacing the fuse | [7 empty] | 27.0MW load
|  |  | of station supply transformer. | [7 empty] | interrup.
| 11:03 | 16:51 | Haripur 230/132kV S/S 132KV Bhulta-2 Scheduled S/D Due to Red Hot Maintenance by other
end.
| 11:21 | 12:10 | Kurigram 132/33kV S/S Transformer T-2 (Tr-413T) LT Forced S/D
| 11:22 | 12:09 | Kurigram 132/33kV S/S Transformer T-2 (Tr-413T) HT Forced S/D
| 12:00 |  | Day Peak Generation: 13735 MW.
|  | 13:32 | Kishoreganj 132/33kV S/S Tr-2 (414T) HT is restored.
|  | 13:39 | Kishoreganj 132/33kV S/S Tr-2 (414T) LT is restored.
| 16:33 |  | Gopalganj 400/132kV S/S 400kV Rooppur Scheduled S/D
| 16:39 |  | Bogura 400/230kV S/S Bogura - Rooppur 400 KV Line-1 Scheduled S/D Due to CT, PT and
Energy Meter testing work at Rooppur 400kV GIS Substation.
| 17:32 | 18:10 | Gopalganj 132/33kV S/S Gopalganj 100 MW PS Tripped showing Main-2 DIST. Protection OPTD.
Z1/Z1B relays Due to L/A blast BPDB substation
| 18:01 |  | Raozan 25 MW PP Synchronized
|  | 18:17 | Kurigram 132/33kV S/S Capacitor Bank is restored.
| 19:30 |  | Evening peak Generation is 15501 MW
| 21:44 |  | Rangpur-Taraganj 132kV ckt.-2 and Taraganj-Saidpur 132kV ckt.-2 was switched on at
21:44hr. & 21:50hr. respectively for the first time.
|  | 21:47 | Rangpur-Saidpur 132kV Ckt-2 is restored.
| 21:50 |  | Feni-Cumilla north 230kV ckt.-1 was switched on at 21:50 hr. for the first time.
| 01:41 |  | Raozan 25 MW PP Shutdown
| 05:22 | 06:03 | Jhenaidah-Magura 132 kV Ckt-2 Tripped from Magura 132/33kV end showing Distance relay | [7 empty] | 102.0MW load
|  |  | relays Due to Over current | [7 empty] | interrup. Magura
132/33kV end
| 05:22 |  | Jhenaidah 132/33kV S/S Jhenaidah-Magura, 132kV Circuit-1(L7) Tripped showing Distance
relay,Z-2, Z-3 relays Due to Y- phase, PT brust , magura sub- Station.
| 05:29 |  | Jhenaidah-Magura 132 kV Ckt-1 Forced S/D from Magura 132/33kV end Due to PT Blast | [7 empty] | 102.0MW load
interrup. Magura
132/33kV end
| 06:09 | 07:46 | Mymensingh 132/33kV S/S Transformer-1 (404T) HT Scheduled S/D Due to 33kV bus loup
connection with Bus -T (R Ph) of 33kV Bhaluka-2 Feedet
| 06:09 | 07:47 | Mymensingh 132/33kV S/S Transformer-1 (404T) LT Scheduled S/D Due to 33kV bus loup
connection with Bus -T (R Ph) of 33kV Bhaluka-2 Feedet
| 06:14 |  | Haripur-Meghnaghat 230kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to Isolator
Replacement Work.
| 06:16 | 07:52 | Kodda 132/33kV S/S Tr-1 (406T) LT Scheduled S/D Due to Red hot maintenance
| 06:16 | 07:51 | Kodda 132/33kV S/S Tr-1 (406T) HT Scheduled S/D Due to Red hot maintenance | [7 empty] | 40.0MW load
interrup.
| 06:43 |  | Aminbazar-Kallyanpur 132kV Ckt-1 Scheduled S/D from Kallyanpur 132/33kV end Due to CT
Changing Work
| 06:52 | 07:01 | Sylhet 132/33kV S/S T1 LT Tripped showing OC relays Due to 33 kv Badaghat PBS feeder C | [7 empty] | 2.0MW load
|  |  | phase loop foult. | [7 empty] | interrup.
| 07:00 |  | Min. Gen. 12669 MW
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 25-06-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 402 | 9273600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 9159000 | Allocation limit by Titas, instructed by DS(Gen)
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 148 | 3585658 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 30 | 288577 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 332 | 7565749 | Allocation limit by Titas, instructed by DS(Gen)
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 24 | 64080 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 455400 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 125 | 2942400 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 462804 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 406650 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21.6 | 472800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 488520 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 34 | 584640 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 285 | 3145145 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2887632 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1159680 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 51 | 848640 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 1373760 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 157054 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 1112040 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 500 | 9770909.09 | None
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 1220400 | -
Dhaka Area Total |  |  |  |  | 5939.724 | 2917.6 | 57425138.09
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 194104.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 56700 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 25 | 467040 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 172 | 4125280 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 216 | 5018691 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 75 | 714255 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 31 | 510768 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 616362 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1984320 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 4 | 219360 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 30 | 78720 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 27742 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 150 | 938400 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 17 | 123723 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 332034 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2026560 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 15 | 201982 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 54 | 195709 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1112 | 26198179 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 30 | 1140000 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 204 | 4923636.36 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4895.72 | 2435 | 50093566.16
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 190 | 4773000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 345 | 8252000 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 7526000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 20 | 377712 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 43 | 530880 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 16727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1157890 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 129 | 1985527 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 43 | 1029088 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 180 | 4254720 | -
| Import (Tripura) |  | Import | 0 | 160 | 42 | 939840 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 34 | 698510 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 373760 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 95 | 2481780 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 330120 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1394880 | Fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 436791 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1668 | 36559225
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 19 | 456960 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 164 | 3698400 | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 109 | 2126400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 185280 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 222960 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 348120 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 309 | 7046120
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3592390 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 683904 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 59 | 1161600 | Under Maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 165 | 3465360 | Machine Problem
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 123552 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7144000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 361 | 8910000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7680800 | Machine Problem
Sylhet Area Total |  |  |  |  | 2325 | 1390 | 32761606
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 451 | 10688727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 39 | 76800 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 9984 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 106 | 2565504 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 51 | 417120 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 50 | 154512 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 603360 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 970 | 24327270 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1705 | 39755277
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 616 | 14814545.45 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 41856 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 9 | 194345 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 116 | 2879000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 990 | 26036363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5378690 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 99600 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 216 | 5389000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3279 | -
Barishal Area Total |  |  |  |  | 2236 | 2200 | 54836679.09
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 211522 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 12 | 144970 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 135 | 3427000 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 136 | 3623973 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Plant is in Standby as per NLDC request.
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 385 | 8323490 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 158240 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 25 | 47126 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 553632 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 90 | 1400448 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 50 | 328512 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 16620 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1464.14 | 32145481 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 186744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 595974 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2423.14 | 51163732
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1093963 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 199 | 4712000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 90 | 1648406 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 46596.24 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1658244 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 208439 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 976320 | -
Rangpur Area Total |  |  |  |  | 950 | 454 | 10343968.24
Eastern Grid Total |  |  |  |  | 16705.895 | 8719.6 | 183885655.25
Western Grid Total |  |  |  |  | 10378.16 | 6782.14 | 156099656.33
National Grid Total |  |  |  |  | 27084.055 | 15501.74 | 339985311.58
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 25-06-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10205.09 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4792.4 | MW
i) Dhaka area |  |  | 5584.06 |  | MW | i) Khulna area |  |  |  | 1818.8 | MW
ii) Chattogram area |  |  | 1439.5 |  | MW | ii) Barishal area |  |  |  | 467 | MW
iii) Cumilla area |  |  | 1426.53 |  | MW | iii) Rajshahi area |  |  |  | 1507.6 | MW
iv) Mymensingh area |  |  | 1117 |  | MW | iv) Rangpur area |  |  |  | 999 | MW
v) Sylhet area |  |  | 638 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14997.49 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 83 | 19:30 | 133 | Patuakhali | 83 | 00:00
2 | AKSML | 127 | 13:00 | 68 | Jaldhaka | 92 | 20:00 | 134 | Payra | 32 | 00:00
3 | Aftabnagar | 42 | 13:00 | 69 | Jamalpur | 120 | 20:00 | 135 | Postogola | 61 | 13:00
4 | Agargaon | 144 | 13:00 | 70 | Jashore | 144 | 20:00 | 136 | Purbachal | 23 | 00:00
5 | Agrabad | 96 | 18:30 | 71 | Jhenaidah | 125 | 22:00 | 137 | Purbasadipur | 141 | 23:00
6 | Amnura | 40 | 00:00 | 72 | Joydebpur | 152 | 19:00 | 138 | Rahanpur | 34 | 01:00
7 | Ashuganj | 102 | 21:00 | 73 | Joypurhat | 65 | 22:00 | 139 | Rahim | 52 | 03:00
8 | BSRM | 203 | 00:00 | 74 | Juldah | 18 | 15:00 | 140 | Rajbari | 83 | 19:30
9 | Bagerhat | 89 | 00:00 | 75 | KSRM | 25 | 18:30 | 141 | Rajendrapur | 138 | 20:00
10 | Bajitpur | 56 | 00:00 | 76 | Kabirpur | 266 | 10:00 | 142 | Rajshahi | 118 | 23:00
11 | Bakulia | 98 | 15:00 | 77 | Kachua | 94 | 22:00 | 143 | Rajshahi-230 | 87 | 21:00
12 | Banani | 27 | 13:00 | 78 | Kallyanpur | 108 | 00:00 | 144 | Ramganj | 112 | 22:00
13 | Bangabhaban | 18 | 10:00 | 79 | Kalurghat | 42 | 12:00 | 145 | Rampur | 55 | 14:00
14 | Barapukuria | 71 | 22:00 | 80 | Kamrangirchar | 67 | 12:00 | 146 | Rangamati | 18 | 19:00
15 | Barguna | 22 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 136 | 00:00
16 | Barishal | 115 | 19:30 | 82 | Kasba | 39 | 22:00 | 148 | Ruppur | 7.8 | 11:00
17 | Barishal-230 | 100 | 21:00 | 83 | Kazla | 98 | 16:00 | 149 | SSM | 14 | 03:00
18 | Baroaulia | 75 | 13:00 | 84 | Keranigonj | 92 | 00:00 | 150 | Saidpur | 122 | 19:30
19 | Baroirhat | 64 | 19:00 | 85 | Khagrachori | 32 | 19:00 | 151 | Satkhira | 135 | 20:00
20 | Bashundhara | 188 | 15:00 | 86 | Khulna | 74 | 13:00 | 152 | Satmasjid | 106 | 19:30
21 | BashundharaCement | 8 | 00:00 | 87 | Khulshi | 144 | 00:00 | 153 | Savar | 236 | 16:00
22 | Beanibazar | 86 | 00:00 | 88 | Kishoreganj | 146 | 21:00 | 154 | SevenRings | 35.38 | 19:00
23 | Benapole | 73 | 21:00 | 89 | Kodda | 317 | 08:00 | 155 | ShahCement | 30 | 00:00
24 | Bhaluka | 162 | 03:00 | 90 | Kulaura | 54 | 00:00 | 156 | Shahjadpur | 81 | 21:00
25 | Bhandaria | 55 | 22:00 | 91 | Kurigram | 90 | 12:00 | 157 | Shahjibazar | 135 | 21:00
26 | Bhangura | 40 | 19:30 | 92 | Kushtia | 156 | 00:00 | 158 | Shahmirpur | 67 | 00:00
27 | Bheramara(GK) | 69 | 20:00 | 93 | Lalbag | 56 | 12:00 | 159 | Shariatpur | 92 | 00:00
28 | Bhulta | 260 | 23:00 | 94 | Lalmonirhat | 66 | 19:30 | 160 | Sherpur | 154 | 21:00
29 | Bog-Sherpur | 68 | 01:00 | 95 | MI_Cement | 17.9 | 16:00 | 161 | Shikalbaha | 15 | 11:00
30 | Bogura | 167 | 22:00 | 96 | Madanganj | 40 | 00:00 | 162 | Shitalakhya | 87.3 | 16:00
31 | Borhanuddin | 92 | 00:00 | 97 | Madaripur | 116 | 00:00 | 163 | Sholosohor | 48 | 15:00
32 | Brahmanbaria | 141 | 00:00 | 98 | Madartek | 97.66 | 00:00 | 164 | Shyampur | 174 | 12:00
33 | Cantonment | 164 | 13:00 | 99 | Madunaghat | 57 | 00:00 | 165 | Siddhirganj | 122 | 16:00
34 | Chandina | 20.53 | 19:30 | 100 | Magura | 68 | 19:30 | 166 | Sirajganj | 107 | 20:00
35 | Chandpur | 80 | 23:00 | 101 | Mahasthangarh | 82 | 00:00 | 167 | Sonargaon | 116 | 00:00
36 | Chandraghona | 38 | 20:00 | 102 | Manikganj | 124 | 23:00 | 168 | Sreemongol | 94 | 23:00
37 | Chapai | 74 | 00:00 | 103 | Maniknagar | 86 | 13:00 | 169 | Sreepur | 103 | 19:00
38 | Charsaidpur | 47 | 23:00 | 104 | Matarbari | 52 | 00:00 | 170 | Srinagar | 49.04 | 22:00
39 | Chauddagram | 74 | 00:00 | 105 | Matuail | 64 | 00:00 | 171 | Sunamganj | 64 | 22:00
40 | Chhatak | 42 | 00:00 | 106 | Millgate | 99 | 12:00 | 172 | Sylhet | 55 | 22:00
41 | Chowmuhani | 196 | 21:00 | 107 | Mirpur | 128 | 15:00 | 173 | Sylhet-132 | 131 | 19:00
42 | Chuadanga | 116 | 00:00 | 108 | Mirsorai | 10 | 00:00 | 174 | TK | 34.4 | 01:00
43 | Coxsbazar | 134 | 19:30 | 109 | Mirzapur | 46 | 21:00 | 175 | Tangail | 188 | 21:00
44 | Cumilla(N) | 157 | 22:00 | 110 | Mithapukur | 74 | 19:30 | 176 | Thakurgaon | 114 | 23:00
45 | Cumilla(S) | 175 | 00:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 136 | 12:00
46 | Daudkandi | 160 | 19:30 | 112 | Mogbazar | 167.9 | 15:00 | 178 | Ullahpara | 38 | 21:00
47 | Dhaka | 62 | 12:00 | 113 | Mongla | 41 | 16:00 | 179 | Ullon | 42 | 00:00
48 | Dhamrai | 134 | 19:00 | 114 | Motijheel | 44 | 13:00 | 180 | Uttara | 86 | 16:00
49 | Dhanmondi | 168 | 13:00 | 115 | Muktagacha | 40 | 00:00 | 181 | UttaraNew | 63 | 00:00
50 | Dohazari | 105 | 22:00 | 116 | Munshiganj | 120 | 00:00 | 182 | Zigatola | 78 | 13:00
51 | Faridpur | 170 | 21:00 | 117 | Muradnagar | 30 | 00:00
52 | Fatullah | 103 | 12:00 | 118 | Mymensingh | 212 | 19:30
53 | Fenchuganj | 45 | 00:00 | 119 | Naogaon | 142 | 00:00
54 | Feni | 115 | 19:30 | 120 | Narail | 60.5 | 00:00
55 | GPH | 20 | 13:00 | 121 | Narinda | 92 | 13:00
56 | Ghatail | 78 | 19:30 | 122 | Narshingdi | 200 | 23:00
57 | Ghorashal | 16 | 10:00 | 123 | Natore | 154 | 19:30
58 | Ghorashal-230 | 99 | 00:00 | 124 | Nawabganj | 60 | 00:00
59 | Goalpara | 42 | 00:00 | 125 | Netrakona | 135 | 20:00
60 | Gollamari | 100 | 00:00 | 126 | New | 92 | 15:00
61 | Gopalganj | 112 | 00:00 | 127 | Niamatpur | 74 | 23:00
62 | Gulshan | 162 | 13:00 | 128 | Noapara | 47 | 22:00
63 | Halishahar | 78 | 10:00 | 129 | PHP | 5 | 08:00
64 | HaripurSBU | 166 | 00:00 | 130 | Pabna | 128 | 19:30
65 | Hasnabad | 65 | 00:00 | 131 | Palashbari | 124 | 20:00
66 | Hathazari | 85 | 00:00 | 132 | Panchagarh | 65 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 25-06-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15542.69 | 89 |  | 15635.7
1:00 | 14995.54 | 82 |  | 15081.54
2:00 | 14606.33 | 91 |  | 14701.33
3:00 | 14244.91 | 74 |  | 14321.91
4:00 | 14033.36 | 65 |  | 14101.36
5:00 | 13559.67 | 50 |  | 13611.67
6:00 | 12986.72 | 45 |  | 13033.72
7:00 | 12783.77 | 0 |  | 12783.77
8:00 | 12858.13 | 0 |  | 12858.13
9:00 | 13006.8 | 15 |  | 13022.48
10:00 | 13244.59 | 22 |  | 13267.58
11:00 | 13436.45 | 0 |  | 13436.45
12:00 | 13738.74 | 0 |  | 13738.74
13:00 | 14034.5 | 0 |  | 14034.5
14:00 | 13948.44 | 0 |  | 13948.44
15:00 | 14291.62 | 0 |  | 14291.62
16:00 | 14051.09 | 0 |  | 14051.09
17:00 | 13726.84 | 0 |  | 13726.84
18:00 | 13075.45 | 0 |  | 13075.45
19:00 | 14273.85 | 0 |  | 14273.85
19:30 | 15501.74 | 66 |  | 15570.74
20:00 | 15394.02 | 31 |  | 15426.02
21:00 | 15439.16 | 32 |  | 15472.16
22:00 | 15341.2 | 29 |  | 15371.2
23:00 | 15469.2 | 40 |  | 15511.2
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 25-06-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8077.7 | 7464.99 | 15542.69 | DAILY GENERATION CURVE
00:30 | 8052.45 | 7216.665 | 15269.115
01:00 | 8027.2 | 6968.34 | 14995.54 | 25-06-2025
01:30 | 7932.45 | 6868.485 | 14800.935
02:00 | 7837.7 | 6768.63 | 14606.33
02:30 | 7633.45 | 6792.17 | 14425.62
03:00 | 7429.2 | 6815.71 | 14244.91
03:30 | 7372.45 | 6766.685 | 14139.135
04:00 | 7315.7 | 6717.66 | 14033.36
04:30 | 7193.2 | 6603.315 | 13796.515
05:00 | 7070.7 | 6488.97 | 13559.67
05:30 | 6972.595 | 6300.6 | 13273.195
06:00 | 6874.49 | 6112.23 | 12986.72
06:30 | 6791.07 | 6094.175 | 12885.245
07:00 | 6707.65 | 6076.12 | 12783.77
07:30 | 6715.45 | 6105.5 | 12820.95
08:00 | 6723.25 | 6134.88 | 12858.13
08:30 | 6762.155 | 6170.31 | 12932.465
09:00 | 6801.06 | 6205.74 | 13006.8
09:30 | 6929.34 | 6196.355 | 13125.695
10:00 | 7057.62 | 6186.97 | 13244.59
10:30 | 7141.955 | 6198.565 | 13340.52
11:00 | 7226.29 | 6210.16 | 13436.45
11:30 | 7341.325 | 6246.27 | 13587.595
12:00 | 7456.36 | 6282.38 | 13738.74
12:30 | 7506.85 | 6379.77 | 13886.62
13:00 | 7557.34 | 6477.16 | 14034.5
13:30 | 7570.855 | 6420.615 | 13991.47
14:00 | 7584.37 | 6364.07 | 13948.44
14:30 | 7676.635 | 6443.395 | 14120.03
15:00 | 7768.9 | 6522.72 | 14291.62
15:30 | 7781.245 | 6390.11 | 14171.355
16:00 | 7793.59 | 6257.5 | 14051.09
16:30 | 7740.85 | 6148.115 | 13888.965
17:00 | 7688.11 | 6038.73 | 13726.84
17:30 | 7633.995 | 5767.15 | 13401.145
18:00 | 7579.88 | 5495.57 | 13075.45
18:30 | 7910.94 | 5763.71 | 13674.65
19:00 | 8242 | 6031.85 | 14273.85
19:30 | 8719.6 | 6782.14 | 15501.74
20:00 | 8661 | 6733.02 | 15394.02
20:30 | 8548.6 | 6867.99 | 15416.59 |  | Executive Engineer
21:00 | 8436.2 | 7002.96 | 15439.16 |  | Network Operation Division
21:30 | 8399.2 | 6990.98 | 15390.18
22:00 | 8362.2 | 6979 | 15341.2
22:30 | 8341.7 | 7063.5 | 15405.2
23:00 | 8321.2 | 7148 | 15469.2

## En-Curve
QF-LDC-12
Date | 25-06-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3556 | 1539 | 451 | 38 | 48 | 1464.99 | 172 | 4923 | 0 | 810 | 2506.7 | 0 | 0 | 34 | 89 | DAILY ENERGY CURVE
00:30 | 3490.5 | 1625.25 | 451 | 38 | 48 | 1457.665 | 172 | 4893 | 0 | 654 | 2400.2 | 0 | 0 | 39.5 | 85.5 | 25-06-2025
01:00 | 3425 | 1711.5 | 451 | 38 | 48 | 1450.34 | 172 | 4863 | 0 | 498 | 2293.7 | 0 | 0 | 45 | 82
01:30 | 3436.5 | 1712.25 | 451 | 38 | 46 | 1450.485 | 172 | 4846.5 | 0 | 480.5 | 2135.7 | 0 | 0 | 32 | 86.5 | Energy Generated | 339.9853 |  | MKWHr
02:00 | 3448 | 1713 | 451 | 38 | 44 | 1450.63 | 172 | 4830 | 0 | 463 | 1977.7 | 0 | 0 | 19 | 91 | Energy not Served | 0.665 |  | MKWHr
02:30 | 3447 | 1712.75 | 451 | 38 | 44 | 1456.67 | 172 | 4845 | 0 | 423.75 | 1807.45 | 0 | 0 | 28 | 82.5 | Total Energy Requirement | 340.6503 |  | MKWHr
03:00 | 3446 | 1712.5 | 451 | 38 | 44 | 1462.71 | 172 | 4860 | 0 | 384.5 | 1637.2 | 0 | 0 | 37 | 74
03:30 | 3457 | 1714 | 451 | 38 | 44 | 1451.685 | 172 | 4865 | 0 | 363.75 | 1549.7 | 0 | 0 | 33 | 69.5
04:00 | 3468 | 1715.5 | 451 | 38 | 44 | 1440.66 | 172 | 4870 | 0 | 343 | 1462.2 | 0 | 0 | 29 | 65
04:30 | 3475.5 | 1704 | 451 | 38 | 39 | 1436.315 | 172 | 4758.5 | 0 | 315.5 | 1364.2 | 0 | 0 | 42.5 | 57.5
05:00 | 3483 | 1692.5 | 451 | 38 | 34 | 1431.97 | 172 | 4647 | 0 | 288 | 1266.2 | 0 | 0 | 56 | 50
05:30 | 3457.5 | 1697.5 | 451 | 38 | 31 | 1370.975 | 172 | 4534 | 11.02 | 272 | 1189.2 | 0 | 0 | 49 | 47.5
06:00 | 3432 | 1702.5 | 451 | 38 | 28 | 1309.98 | 172 | 4421 | 22.04 | 256 | 1112.2 | 0 | 0 | 42 | 45
06:30 | 3443.5 | 1690.5 | 449.5 | 38 | 34 | 1285.44 | 172 | 4403 | 58.205 | 246.5 | 1022.6 | 0 | 0 | 42 | 22.5
07:00 | 3455 | 1678.5 | 448 | 38 | 40 | 1260.9 | 172 | 4385 | 94.37 | 237 | 933 | 0 | 0 | 42 | 0
07:30 | 3456 | 1677.25 | 429 | 38 | 38 | 1263.545 | 172 | 4384.5 | 155.155 | 243 | 916.5 | 0 | 0 | 48 | 0
08:00 | 3457 | 1676 | 410 | 38 | 36 | 1266.19 | 172 | 4384 | 215.94 | 249 | 900 | 0 | 0 | 54 | 0
08:30 | 3448.5 | 1682.75 | 429 | 38 | 35 | 1268.86 | 172 | 4384 | 260.355 | 249 | 906.5 | 0 | 0 | 58.5 | 7.5
09:00 | 3440 | 1689.5 | 448 | 38 | 34 | 1271.53 | 172 | 4384 | 304.77 | 249 | 913 | 0 | 0 | 63 | 15
09:30 | 3450.5 | 1778 | 448 | 38 | 35 | 1333.745 | 172 | 4314 | 305.95 | 240 | 947.5 | 0 | 0 | 63 | 18.5
10:00 | 3461 | 1866.5 | 448 | 38 | 36 | 1395.96 | 172 | 4244 | 307.13 | 231 | 982 | 0 | 0 | 63 | 22
10:30 | 3467 | 1869 | 448 | 38 | 36 | 1402.36 | 172 | 4230 | 344.66 | 231 | 1039.5 | 0 | 0 | 63 | 11
11:00 | 3473 | 1871.5 | 448 | 38 | 36 | 1408.76 | 172 | 4216 | 382.19 | 231 | 1097 | 0 | 0 | 63 | 0
11:30 | 3497.5 | 1871 | 448 | 38 | 36 | 1416.485 | 172 | 4248.5 | 385.25 | 231 | 1181.36 | 0 | 0 | 62.5 | 0
12:00 | 3522 | 1870.5 | 448 | 38 | 36 | 1424.21 | 172 | 4281 | 388.31 | 231 | 1265.72 | 0 | 0 | 62 | 0
12:30 | 3503 | 1867 | 448 | 38 | 38 | 1435.62 | 172 | 4242 | 421.14 | 231 | 1431.86 | 0 | 0 | 59 | 0
13:00 | 3484 | 1863.5 | 448 | 38 | 40 | 1447.03 | 172 | 4203 | 453.97 | 231 | 1598 | 0 | 0 | 56 | 0
13:30 | 3436 | 1821.9 | 447.5 | 38 | 37 | 1449.685 | 172 | 4186.5 | 406.885 | 230.5 | 1706.5 | 0 | 0 | 59 | 0
14:00 | 3388 | 1780.3 | 447 | 38 | 34 | 1452.34 | 172 | 4170 | 359.8 | 230 | 1815 | 0 | 0 | 62 | 0
14:30 | 3478.5 | 1775.15 | 447.5 | 38 | 39 | 1448.785 | 172 | 4166 | 415.095 | 237.5 | 1840.5 | 0 | 0 | 62 | 0
15:00 | 3569 | 1770 | 448 | 38 | 44 | 1445.23 | 172 | 4162 | 470.39 | 245 | 1866 | 0 | 0 | 62 | 0
15:30 | 3568.5 | 1816 | 448 | 38 | 42 | 1452.46 | 172 | 4140 | 399.395 | 258 | 1780.5 | 0 | 0 | 56.5 | 0
16:00 | 3568 | 1862 | 448 | 38 | 40 | 1459.69 | 172 | 4118 | 328.4 | 271 | 1695 | 0 | 0 | 51 | 0
16:30 | 3470.5 | 1861.5 | 449.5 | 38 | 40 | 1454.91 | 172 | 4110 | 249.055 | 271.5 | 1715 | 0 | 0 | 57 | 0
17:00 | 3373 | 1861 | 451 | 38 | 40 | 1450.13 | 172 | 4102 | 169.71 | 272 | 1735 | 0 | 0 | 63 | 0
17:30 | 3356 | 1804 | 451 | 38 | 37 | 1338.105 | 172 | 3939 | 111.04 | 290 | 1805.5 | 0 | 0 | 59.5 | 0
18:00 | 3339 | 1747 | 451 | 38 | 34 | 1226.08 | 172 | 3776 | 52.37 | 308 | 1876 | 0 | 0 | 56 | 0
18:30 | 3440.5 | 1816 | 451 | 38 | 39 | 1252.965 | 172 | 3899.5 | 26.185 | 449 | 2051.5 | 0 | 0 | 39 | 0
19:00 | 3542 | 1885 | 451 | 38 | 44 | 1279.85 | 172 | 4023 | 0 | 590 | 2227 | 0 | 0 | 22 | 0
19:30 | 3618 | 1894.6 | 451 | 38 | 42 | 1464.14 | 172 | 4357 | 0 | 722 | 2713 | 0 | 0 | 30 | 66
20:00 | 3471 | 1908.5 | 451 | 38 | 40 | 1445.02 | 172 | 4357 | 0 | 785 | 2699.5 | 0 | 0 | 27 | 31
20:30 | 3582.5 | 1915.5 | 451 | 38 | 38 | 1446.49 | 172 | 4515 | 0 | 747.5 | 2470.1 | 0 | 0 | 40.5 | 31.5
21:00 | 3694 | 1922.5 | 451 | 38 | 36 | 1447.96 | 172 | 4673 | 0 | 710 | 2240.7 | 0 | 0 | 54 | 32
21:30 | 3649.5 | 1917.5 | 435 | 38 | 39 | 1446.48 | 172 | 4715 | 0 | 711 | 2227.2 | 0 | 0 | 39.5 | 30.5
22:00 | 3605 | 1912.5 | 419 | 38 | 42 | 1445 | 172 | 4757 | 0 | 712 | 2213.7 | 0 | 0 | 25 | 29
22:30 | 3618 | 1883 | 383.5 | 38 | 43 | 1453.5 | 172 | 4832.5 | 0 | 712 | 2239.7 | 0 | 0 | 30 | 34.5
23:00 | 3631 | 1853.5 | 348 | 38 | 44 | 1462 | 172 | 4908 | 0 | 712 | 2265.7 | 0 | 0 | 35 | 40
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 25-06-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 379 | 06:00 | 365 | 22:00 | Payra | 412 | 18:00 | 404 | 23:00
Ashuganj | 398 | 18:00 | 377 | 10:00 | Rahanpur | 401 | 08:00 | 389 | 21:00
Bhulta | 393 | 18:30 | 376 | 09:00 | Rampal | 398 | 15:00 | 381 | 23:00
Bibiana | 386 | 18:00 | 379 | 22:00
BIPTC | 408 | 06:00 | 397 | 19:30
Bogura | 388 | 05:00 | 370 | 22:00
Gopalganj | 393 | 18:30 | 375 | 23:00
Kaliakoir | 378 | 18:30 | 360 | 22:00
Madunaghat | 395 | 19:00 | 389 | 05:00
Meghnaghat | 382 | 06:00 | 372 | 23:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 222 | 06:00 | 213 | 23:00 | Keranigonj | 219 | 07:00 | 211 | 23:00
AKSML | 236 | 19:30 | 225 | 04:00 | Khulna(S) | 229 | 18:00 | 213 | 23:00
Aminbazar | 222 | 06:00 | 213 | 23:00 | Madunaghat | 235 | 18:00 | 228 | 12:00
Ashuganj | 231 | 18:30 | 222 | 11:00 | Madunaghat-400 | 235 | 20:00 | 229 | 12:00
Ashuganj-400 | 231 | 18:30 | 222 | 11:00 | Maniknagar | 219 | 05:00 | 211 | 12:00
Baghabari | 233 | 06:00 | 224 | 21:00 | Meghnaghat | 227 | 18:30 | 220 | 00:00
Barapukuria | 224 | 18:30 | 216 | 21:00 | Meghnaghat-400 | 221 | 06:00 | 214 | 23:00
Barapukuria-230 | 224 | 18:30 | 216 | 21:00 | Mirsorai | 232 | 18:00 | 222 | 03:00
Barishal | 231 | 18:00 | 221 | 23:00 | Rajshahi | 234 | 06:00 | 221 | 21:00
Bheramara | 235 | 18:00 | 222 | 00:00 | Rampal | 228 | 18:00 | 213 | 23:00
Bhulta | 228 | 06:00 | 211 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 228 | 06:00 | 220 | 21:00 | Rampura | 227 | 06:00 | 214 | 10:00
BIPTC | 235 | 06:00 | 220 | 00:00 | Shikalbaha | 234 | 19:00 | 225 | 12:00
Bogura | 234 | 18:00 | 224 | 22:00 | Shyampur | 220 | 06:00 | 213 | 00:00
Bogura-400 | 234 | 18:00 | 225 | 21:00 | Siddhirganj | 219 | 07:00 | 214 | 00:00
Borhanuddin | 237 | 18:00 | 228 | 22:00 | Sirajgonj | 239 | 18:30 | 232 | 21:00
BSRM | 230 | 18:00 | 221 | 23:00 | Sreepur | 228 | 18:00 | 219 | 21:00
Cumilla(N) | 222 | 18:30 | 214 | 00:00 | Tongi | 225 | 17:00 | 216 | 11:00
Faridpur | 229 | 18:00 | 215 | 23:00
Fenchuganj | 228 | 06:00 | 220 | 23:00
Ghorashal | 230 | 00:00 | 225 | 08:00
Ghorashal-230 | 226 | 06:00 | 215 | 10:00
Gopalganj | 231 | 18:00 | 220 | 23:00
GPH | 232 | 18:00 | 225 | 04:00
Haripur | 219 | 06:00 | 212 | 23:00
Hasnabad | 219 | 04:00 | 212 | 23:00
Hathazari | 236 | 18:30 | 226 | 10:00
Ishurdi | 236 | 18:00 | 220 | 00:00
Jhenaidah | 231 | 18:00 | 214 | 21:00
Kaliakoir | 232 | 18:30 | 221 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 23:00 | 124 | 12:00 | Madartek | 134 | 06:00 | 123 | 12:00
Agargaon | 130 | 06:00 | 123 | 12:00 | Madunaghat | 134 | 00:00 | 129 | 09:00
Agrabad | 134 | 01:00 | 129 | 10:00 | Magura | 136 | 18:00 | 122 | 00:00
AKS | 131 | 00:00 | 127 | 12:00 | Mahasthangarh | 135 | 13:00 | 126 | 22:00
Aminbazar | 130 | 04:00 | 124 | 23:00 | Maijdee | N/A | N/A | N/A | N/A
Amnura | 137 | 19:00 | 125 | 22:00 | Manikganj | 129 | 06:00 | 119 | 23:00
Ashuganj | 135 | 01:00 | 133 | 15:00 | Maniknagar | 129 | 05:00 | 123 | 13:00
Bagerhat | 129 | 08:00 | 118 | 21:00 | Matarbari | 126 | 14:00 | 116 | 00:00
Bajitpur | 130 | 14:00 | 125 | 00:00 | Matuail | 127 | 02:00 | 123 | 12:00
Bakulia | 135 | 18:00 | 130 | 10:00 | Millgate | 132 | 05:00 | 123 | 10:00
Banani | 133 | 06:00 | 124 | 15:00 | Mirpur | 129 | 04:00 | 123 | 00:00
Bangabhaban | 129 | 06:00 | 123 | 12:00 | Mirzapur | 130 | 18:00 | 123 | 20:00
Barapukuria | 137 | 18:30 | 128 | 00:00 | Mithapukur | 131 | 10:00 | 119 | 22:00
Barguna | 134 | 18:30 | 128 | 01:00 | MI_Cement | 127 | 18:30 | 122 | 12:00
Barishal | 134 | 08:00 | 127 | 23:00 | Modern | N/A | N/A | N/A | N/A
Barishal-230 | 135 | 18:00 | 127 | 23:00 | Mogbazar | 135 | 05:00 | 125 | 09:00
Baroaulia | 134 | 17:00 | 130 | 12:00 | Mongla | 130 | 08:00 | 119 | 21:00
Baroirhat | 124 | 18:30 | 118 | 01:00 | Motijheel | 129 | 06:00 | 123 | 12:00
Bashundhara | 133 | 05:00 | 123 | 11:00 | Muktagacha | 134 | 18:00 | 124 | 20:00
BashundharaCement | 132 | 10:00 | 120 | 16:00 | Munshiganj | 126 | 18:00 | 121 | 23:00
Beanibazar | 128 | 06:00 | 120 | 00:00 | Muradnagar | 125 | 18:00 | 118 | 23:00
Benapole | 130 | 18:00 | 116 | 21:00 | Mymensingh | 134 | 04:00 | 116 | 21:00
Bhaluka | 131 | 20:00 | 122 | 21:00 | Naogaon | 134 | 18:30 | 124 | 02:00
Bhandaria | 130 | 08:00 | 117 | 00:00 | Narail | 136 | 18:30 | 121 | 21:00
Bhangura | 133 | 06:00 | 127 | 21:00 | Narinda | 0 | 00:00 | N/A | N/A
Bheramara | 137 | 18:00 | 129 | 00:00 | Narshingdi | 134 | 18:00 | 116 | 23:00
Bheramara(GK) | 136 | 06:00 | 128 | 00:00 | Natore | 135 | 03:00 | 126 | 22:00
Bhulta | 124 | 05:00 | 116 | 23:00 | Nawabganj | 131 | 05:00 | 125 | 00:00
Bog-Sherpur | 135 | 06:00 | 129 | 02:00 | Netrakona | 126 | 07:00 | 112 | 22:00
Bogura | 138 | 14:00 | 132 | 22:00 | New | 132 | 18:00 | 124 | 10:00
Bogura-230 | 138 | 13:00 | 131 | 22:00 | Niamatpur | 135 | 05:00 | 130 | 23:00
Brahmanbaria | 128 | 06:00 | 122 | 22:00 | Noapara | 134 | 07:00 | 120 | 23:00
Cantonment | 129 | 04:00 | 122 | 12:00 | Pabna | 135 | 06:00 | 127 | 00:00
Chandina | 127 | 18:00 | 120 | 23:00 | Palashbari | 131 | 09:00 | 118 | 22:00
Chandpur | 129 | 18:00 | 116 | 00:00 | Panchagarh | 135 | 19:00 | 120 | 23:00
Chandraghona | 134 | 20:00 | 130 | 10:00 | Patuakhali | 134 | 18:30 | 130 | 01:00
Chapai | 131 | 06:00 | 120 | 00:00 | Payra | 135 | 06:00 | 133 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 127 | 18:00 | 122 | 10:00 | PHP | 125 | 18:00 | 116 | 00:00
Chauddagram | 125 | 18:00 | 115 | 15:00 | Postogola | 128 | 06:00 | 124 | 12:00
Chhatak | 128 | 02:00 | 118 | 00:00 | Purbachal | 134 | 06:00 | 122 | 10:00
Chowmuhani | 121 | 18:00 | 108 | 01:00 | Purbasadipur | 131 | 18:30 | 123 | 00:00
Chuadanga | 132 | 06:00 | 118 | 21:00 | Rahanpur | 136 | 04:00 | 132 | 00:00
Coxsbazar | 124 | 10:00 | 116 | 22:00 | Rahanpur-400 | 137 | 08:00 | 132 | 22:00
Cumilla(N) | 128 | 18:30 | 120 | 02:00 | Rahim | 127 | 05:00 | 123 | 13:00
Cumilla(S) | 132 | 04:00 | 119 | 00:00 | Rajbari | 134 | 18:00 | 125 | 22:00
Daudkandi | 124 | 07:00 | 117 | 23:00 | Rajendrapur | 135 | 19:00 | 122 | 22:00
Dhaka | 133 | 04:00 | 125 | 12:00 | Rajshahi | 135 | 18:00 | 127 | 22:00
Dhamrai | 129 | 03:00 | 123 | 10:00 | Rajshahi-230 | 135 | 06:00 | 119 | 22:00
Dhanmondi | 134.5 | 06:00 | 125 | 11:00 | Ramganj | 124 | 18:30 | 109 | 00:00
Dohazari | 132 | 14:00 | 127 | 07:00 | Rampur | 134 | 18:00 | 128 | 09:00
Faridpur | 135 | 18:00 | 127 | 22:00 | Rampura | 134 | 06:00 | 124 | 15:00
Fatullah | 127 | 18:00 | 122 | 12:00 | Rangamati | 133 | 20:00 | 128 | 12:00
Fenchuganj | 135 | 06:00 | 128 | 23:00 | Rangpur | 132 | 14:00 | 124 | 00:00
Feni | 124 | 18:00 | 115 | 00:00 | Ruppur | 137 | 06:00 | 129 | 23:00
Ghatail | 130 | 06:00 | 120 | 20:00 | Saidpur | 131 | 18:30 | 123 | 00:00
Ghorashal | 135 | 06:00 | 130 | 07:00 | Satkhira | 131 | 18:00 | 115 | 23:00
Goalpara | 134 | 08:00 | 123 | 21:00 | Satmasjid | 129 | 06:00 | 123 | 12:00
Gollamari | 135 | 18:00 | 124 | 23:00 | Savar | 130 | 18:00 | 121 | 23:00
Gopalganj | 134 | 18:30 | 124 | 23:00 | SevenRings | 137 | 17:00 | 128 | 10:00
Gopalganj-400 | 135 | 06:00 | 129 | 22:00 | ShahCement | 127 | 18:00 | 122 | 10:00
Gulshan | 133 | 06:00 | 125 | 11:00 | Shahjadpur | 136 | 18:00 | 131 | 00:00
Halishahar | 136 | 18:00 | 128 | 12:00 | Shahjibazar | 129 | 06:00 | 122 | 00:00
Haripur | 127 | 06:00 | 123 | 23:00 | Shahmirpur | 136 | 01:00 | 130 | 10:00
HaripurSBU | 127 | 06:00 | 117 | 08:00 | Shariatpur | 134 | 18:00 | 124 | 23:00
Hasnabad | 128 | 03:00 | 124 | 23:00 | Sherpur | 137 | 16:00 | 126 | 20:00
Hathazari | 136 | 18:30 | 131 | 07:00 | Shikalbaha | 125 | 19:00 | 119 | 10:00
Ishurdi | 138 | 06:00 | 130 | 00:00 | Shikalbaha-230 | 137 | 20:00 | 131 | 12:00
Jaldhaka | 131 | 19:00 | 120 | 00:00 | Shitalakhya | 127 | 18:30 | 122 | 12:00
Jamalpur | 139 | 05:00 | 128 | 19:00 | Sholosohor | 135 | 18:00 | 128 | 10:00
Jashore | 135 | 15:00 | 120 | 00:00 | Shyampur | 125 | 01:00 | 121 | 12:00
Jhenaidah | 136 | 08:00 | 118 | 00:00 | Shyampur-230 | 126 | 18:00 | 121 | 12:00
Jhenaidah-230 | 139 | 09:00 | 125 | 21:00 | Siddhirganj | 128 | 18:30 | 123 | 10:00
Joydebpur | 134 | 03:00 | 124 | 16:00 | Sirajganj | 133 | 08:00 | 126 | 22:00
Joypurhat | 132 | 08:00 | 122 | 01:00 | Sonargaon | 128 | 18:30 | 122 | 00:00
Juldah | 136 | 18:00 | 131 | 09:00 | Sreemongol | 129 | 06:00 | 122 | 22:00
Kabirpur | 131 | 18:30 | 122 | 10:00 | Sreepur | 132 | 18:00 | 125 | 21:00
Kachua | 127 | 18:00 | 115 | 00:00 | Srinagar | 131 | 06:00 | 125 | 00:00
Kaliakoir | 135 | 18:30 | 126 | 10:00 | SSM | 139 | 18:30 | 132 | 07:00
Kallyanpur | 131 | 18:00 | 124 | 23:00 | Sunamganj | 127 | 02:00 | 116 | 22:00
Kalurghat | 133 | 19:30 | 128 | 12:00 | Sylhet | 130 | 02:00 | 122 | 00:00
Kamrangirchar | 130 | 06:00 | 125 | 01:00 | Sylhet-132 | 129 | 02:00 | 124 | 23:00
Kaptai | 135 | 1:00 | 132 | 12:00 | Tangail | 129 | 18:30 | 118 | 20:00
Kasba | 124 | 06:00 | 117 | 00:00 | Thakurgaon | 134 | 19:00 | 123 | 00:00
Kazla | 129 | 07:00 | 123 | 13:00 | TK | 132 | 01:00 | 129 | 07:00
Keranigonj | 132 | 06:00 | 125 | 23:00 | Tongi | 132 | 05:00 | 128 | 09:00
Khagrachori | 132 | 20:00 | 127 | 10:00 | Ullahpara | 134 | 06:00 | 128 | 21:00
Khulna | 133 | 10:00 | 122 | 23:00 | Ullon | 133 | 06:00 | 124 | 12:00
Khulna(S) | 136 | 18:30 | 125 | 23:00 | Uttara | 129 | 06:00 | 122 | 23:00
Khulshi | 133 | 01:00 | 128 | 09:00 | UttaraNew | 129 | 06:00 | 122 | 23:00
Kishoreganj | 130 | 18:00 | 122 | 21:00 | Zigatola | 131 | 07:00 | 125 | 13:00
Kodda | 135 | 18:30 | 123 | 16:00
KSRM | 135 | 00:00 | 129 | 12:00
Kulaura | 133 | 07:00 | 127 | 00:00
Kurigram | 130 | 19:00 | 118 | 00:00
Kushtia | 133 | 09:00 | 123 | 00:00
Lalbag | 130 | 18:30 | 125 | 00:00
Lalmonirhat | 129 | 19:00 | 119 | 00:00
Madanganj | 127 | 18:30 | 121 | 13:00
Madaripur | 135 | 18:00 | 128 | 22:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division