## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID BANGLADESH PLC
SYSTEM OPERATION DATA
Month: April 2025
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2025-04-02 |  | 2025-03-01 |  | 2024-04-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 16365.8 | 2025-04-24 | 15336.92 | 2025-03-15 | 16477 | 2024-04-30 | 16477 | 2024-04-30
|  |  | 19:30 Hr. |  | 21:00 Hr. |  | 21:00 |  | 21:00
2 | Minimum Generation (MW) | 9058.19 | 2025-04-29 | 8360.79 | 2025-03-08 | 8472 | 2024-04-11 | - | -
|  |  | 05:00 Hr. |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 16365.8 | 2025-04-24 | 11385.54 | 2025-01-31 | 16477 | 2024-04-30 | 16477 | 2024-04-30
|  |  | 19:30 Hr. |  | 19:00 Hr. |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 14594.67 | 2025-04-24 | 13926.95 | 2025-03-27 | 14301 | 2024-04-30 | 14594.67 | 2025-04-24
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 16510.8 | 2025-04-24 | 14658 | 2025-03-15 | 17200 | 2024-04-29 | 17200 | 2024-04-29
|  |  | 19:30 Hr. |  | 21:00 Hr. |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 14342.7523 |  | 13455.0287 |  | 14226.8667 |  | - | -
7 | Average Generation (MW) at Day Peak | 12823.5187 |  | 12259.0329 |  | 12460.6333 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 924 | 2025-04-28 | 936 | 2025-03-01 | 938 | 2024-04-14 | 970 | 2024-07-06
|  |  | 12:00 |  | 2:00 |  | 12:30 |  | 14:30
9 | Maximum Power Import from Tripura, India (MW) | 106 | 2025-04-20 | 173 | 2025-03-19 | 164 | 2024-04-04 | 194 | 12/06/19
|  |  | 22:00 |  | 21:00 |  | 9:30 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 1491 | 2025-04-26 | 113 | 2025-03-16 | 1533 | 2024-04-29 | 4395 | 04/10/2022
|  |  | 21:00 |  | 19:00 |  | 21:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 14440.43 | 2025-04-26 | 14425 | 2025-03-16 | 15595 | 45411 | 14965 | 2024-05-16
|  |  | 21:00 |  | 19:00 | - | 0.875 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2025-04-01 | 0 | 2025-03-03 | 0 | 45394 | - | -
|  |  | 20:00 |  | 19:00 |  | 21:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 12576 | 2025-04-01 | 12195 | 2025-03-03 | 11762 | 2024-04-12 | - | -
|  |  | 20:00 |  | 19:00 |  | 21:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 196 | 2025-04-12 | 175 | 2025-03-20 | 2640 | 45411 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 13140 | 2025-04-12 | 12899 | 2025-03-20 | 13036 | 45411 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2025-04-01 | 0 | 2025-03-01 | 0 | 45394 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 10576.14 | 2025-04-01 | 11795 | 2025-03-03 | 9637 | 45394 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 16 |  | 4 |  | 26 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 17 |  | 13 |  | 25 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 1417.8481 |  | 1723.1429 |  | 2294.259 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 50.0825 |  | 135.2017 |  | 206.7694 |  | - | -
22 | Net Generation of BPDB (MKWH) | 1367.7656 |  | 1587.9412 |  | 2087.4896 |  | - | -
23 | Net Generation of IPP (MKWH) | 3367.4554 |  | 2881.8044 |  | 3422.9317 |  | - | -
23b | Net Generation by Generation Companies | 2738.0106 |  | 2640.4845 |  | 2587.4548
24 | Net Generation of REB (MKWH) | 116.0982 |  | 154.781 |  | 104.2242 |  | - | -
24 | Net Generation of Rental Power Plant (MKWH) | 225.7863 |  | 239.0099 |  | 150.1603 |  | - | -
25 | Total Net Generation (MKHWh) (Excluding Import) | 7815.1161 |  | 7504.021 |  | 8352.2606 |  | - | -
26 | Energy Generation by Gas (MKWH) | 4009.324 |  | 4228.5203 |  | 4724.5177 |  | - | -
27 | Energy Generation by Diesel (MKWH) | 219.8468 |  | 432.8368 |  | 30.5077 |  | - | -
28 | Energy Generation by Furnace Oil (MKWH) | 1171.3858 |  | 708.9829 |  | 983.8623 |  | - | -
29 | Energy Generation by Hydro (MKWH) | 0.70868 |  | 0.74082 |  | 22.8768 |  | - | -
30 | Energy Generation by Solar (MKWH) | 149.0391 |  | 142.698 |  | 95.9778 |  | - | -
30b | Energy Generation by Wind (MKWH) | 0.1 |  | 0 |  | 8.2392 |  | - | -
31 | Energy Generation by Coal (MKWH) | 2314.7942 |  | 2125.4439 |  | 2693.0479 |  | - | -
32 | Enegry Import from India (MKWH) | 1413.5762 |  | 1468.4092 |  | 676.71 |  | - | -
33 | Monthly Load Factor (%) | 78.7446 |  | 79.8168 |  | 73.8657 |  | - | -

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: April 2025
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 16365.8 | 2025-04-24 | 19:30 Hr.
Generation Period
| Dhaka | MW | 5822.04
| Chattogram | MW | 1522.2
| Cumilla | MW | 1396
| Mymensingh | MW | 1185
| Sylhet | MW | 578
a) | Total supply in East zone | MW | 10503.24
| Khulna | MW | 1924
| Barisal | MW | 477.5
| Rajshahi | MW | 1729.2
| Rangpur | MW | 1011
b) | Total supply in West zone | MW | 5141.7
c) | Total supply in both zone ( a+b) | MW | 15644.94
Ref: | 27.21.0000.603.16.087.20.913 | Date: 15/05/2025
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:April 2025
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 192 | 2025-04-05 | 19:30
| b) Ishurdi end | MW | 364 | 2025-04-10 | 23:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 890 | 2025-04-13 | 6:00
| b) Ishurdi end | MW | 72 | 2025-04-05 | 19:30
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 0.28969
| b) Ishurdi end | MKWH | 114.7959
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 111.3521
| b) Ishurdi end | MKWH | 0.28126
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 340 | 2025-04-12 | 7:00
| b)Serajganj end | MW | 800 | 2025-04-13 | 5:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 420 | 2025-04-13 | 8:00
| b)Sirajganj end | MW | 20 | 2025-04-12 | 19:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end(Sreepur) | MKWH | 324.1244
| b)Sirajganj end | MKWH | 0
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end(Sreepur) | MKWH | 0
| b)Sirajganj end | MKWH | 334.566
30 | Transmission loss of EWI /NO-2 | % | 3.12%
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 2348 | 2025-04-10 | 21:00
|  | MW | 1582
| b) Aminbazar end | AMPS | -
|  | MW | -
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | -
|  | MW | -
| b) Aminbazar end | AMPS | 2318 | 2025-04-10 | 21:00
|  | MW | 1581
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 32853 | 2025-04-12 | N/A
| a) Aminbazar end | MWh | -
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | - | - | N/A
| a) Aminbazar end | MWh | 32755 | 2025-04-12
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MKWH | 721.304
| b) Aminbazar end (ckt-1 ) | MWh | -
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | -
| b) Aminbazar end (ckt-2 ) | MKWH | 731.202
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 1.372%
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: April 2025
| Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bhaluka 132/33kV | Transformer- 02 LT | 2025-04-09 12:10 | 2025-04-09 12:16 | 0.0041667 | T | df/dt NA | 70 | 7 | Power interruption
Bhaluka 132/33kV | Transformer- 01 LT | 2025-04-09 12:10 | 2025-04-09 12:16 | 0.0041667 | T | BR Powergen 1 & 2 trip from BR Powergen side and load 0 MW from 160 MW. GCB Open by NLDC For TR2 df/dt NA | 70 | 7 | Power interruption
Bhaluka 132/33kV | Transformer- 02 HT | 2025-04-13 06:13 | 2025-04-13 08:03 | 0.076389 | E/O | 33 kv bushing temperature minimize | 30 | 55 | Power interruption
Bhaluka 132/33kV | Transformer-03 LT | 2025-04-13 08:09 | 2025-04-13 09:04 | 0.038194 | E/O | 33 kv bushing clamps temperature minimize | 5 | 4.5833 | Power interruption
Bhaluka 132/33kV | Transformer- 01 HT | 2025-04-14 06:12 | 2025-04-14 07:37 | 0.059028 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Bhaluka 132/33kV | Transformer- 02 LT | 2025-04-25 07:12 | 2025-04-25 09:26 | 0.093056 | E/O | T2 33 kv bushing temperature minimize | 10 | 22.3333 | Power interruption
Dhamrai 132/33kV | Transformer-1 LT | 2025-04-03 06:43 | 2025-04-03 06:58 | 0.010417 | T | Over current and earth fault. 86 relay operate. | 30 | 7.5 | Power interruption
Dhamrai 132/33kV | Transformer-2 LT | 2025-04-03 06:43 | 2025-04-03 06:58 | 0.010417 | T | Over current and earth fault. 86 relay Operate. | 30 | 7.5 | Power interruption
Joydebpur 132/33kV | GT-4 HT | 2025-04-24 15:10 | 2025-04-24 15:17 | 0.0048611 | T | Trip Lock out Realy | 39 | 4.55 | Power interruption
Kabirpur 132/33kV | XFR, T-3 LT | 2025-04-05 17:32 | 2025-04-05 21:26 | 0.1625 | T | Directional over current relay trip. | 0 | 0 | No interruption
Kabirpur 132/33kV | XFR, T-3 LT | 2025-04-13 10:42 | 2025-04-13 11:02 | 0.013889 | T | DIR E/F Trip. | 60 | 20 | Power interruption
Kabirpur 132/33kV | XFR, T-3 LT | 2025-04-16 15:58 | 2025-04-16 16:13 | 0.010417 | T | Trip Micom-127 | 40 | 10 | Power interruption
Kabirpur 132/33kV | XFR, T-3 LT | 2025-04-29 19:00 | 2025-04-29 23:06 | 0.17083 | T | 33 kv EPZ feeder fault. Protection relay | 80 | 328 | Power interruption
Kishoreganj 132/33kV | Tr-1 (404T) LT | 2025-04-22 18:20 | 2025-04-22 19:30 | 0.048611 | T | Due to PBD 33kv Feeder fault. Micom | 0 | 0 | No interruption
Kishoreganj 132/33kV | Tr-2 (414T) LT | 2025-04-22 18:20 | 2025-04-22 19:32 | 0.05 | T | Due to PBD 33kv feeder fault. Micom | 0 | 0 | No interruption
Muktagacha 132/33kV | T-2(414T) LT | 2025-04-17 11:02 | 2025-04-17 11:25 | 0.015972 | E/O |  | 0 | 0 | No interruption
Muktagacha 132/33kV | T-2(414T) HT | 2025-04-17 11:03 | 2025-04-17 11:25 | 0.015278 | E/O |  | 0 | 0 | No interruption
Muktagacha 132/33kV | T-2(414T) HT | 2025-04-22 16:17 | 2025-04-26 12:48 | 1900-01-02 20:31 | T | Differential,ph-A,B | 0 | 0 | No interruption
Muktagacha 132/33kV | T-2(414T) LT | 2025-04-22 16:17 | 2025-04-26 12:53 | 1900-01-02 20:36 | T | Differential,ph-A,B | 0 | 0 | No interruption
Savar 132/33kV | T-3 LT | 2025-04-15 03:53 | 2025-04-15 04:15 | 0.015278 | T | dpbs-3 33kv feeder-L- 45 ( রাজাশন) ফিডার ফল্টের কারনে Over current | 0 | 0 | No interruption
Savar 132/33kV | T-4 LT | 2025-04-15 03:53 | 2025-04-15 03:58 | 0.0034722 | T | dpbs-3 33kv feeder-L- 45 ( রাজাশন) ফিডার ফল্টের কারনে Over current | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 01 LT | 2025-04-11 07:30 | 2025-04-11 09:10 | 0.069444 | E/O | Emargency incoming Bus DS change in 33 KV Dubaura Feeder . | 10 | 16.6667 | Power interruption
Sherpur 132/33kV | Transformer- 01 LT | 2025-04-11 12:33 | 2025-04-11 12:56 | 0.015972 | T | SPBS - Bay -03 , 33 Kv feeder Cross arm Brocken. O/C & E/F. | 70 | 26.8333 | Power interruption
Sherpur 132/33kV | Transformer- 02 LT | 2025-04-11 12:33 | 2025-04-11 12:55 | 0.015278 | T | SPBS - Bay -03 , 33 Kv feeder Cross arm Brocken. O/C & E/F. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 02 LT | 2025-04-20 10:13 | 2025-04-20 10:52 | 0.027083 | E/O | TR-02 33 Kv Bus PT Oil leakage. | 12 | 7.8 | Power interruption
Sherpur 132/33kV | Transformer- 03 HT | 2025-04-30 21:13 | 2025-04-30 23:01 | 0.075 | E/O | Red hot remove | 25 | 45 | Power interruption
Sreepur 230/132/33kV | Auxiliary Transformer - 2 LT | 2025-04-29 10:35 | 2025-04-29 11:41 | 0.045833 | E/O |  | 0 | 0 | No interruption
Tangail 132/33kV | Tr-1 HT | 2025-04-24 05:50 | 2025-04-24 06:27 | 0.025694 | T | 33 KV kachuadanga feeder B phase out. K-50 | 60 | 37 | Power interruption
Tangail 132/33kV | Tr-2 HT | 2025-04-24 05:50 | 2025-04-24 08:37 | 0.11597 | T | 33 Kv kachuadanga fedder B phase out K-50 | 0 | 0 | No interruption
|  |  | Total : | 1900-01-07 21:51 |  | Unserved Energy: |  | 606.7667
Dhaka (South) Grid Circle :
Gulshan 132/33kV | MT-2 HT | 2025-04-06 23:44 | 2025-04-07 08:55 | 0.38264 | T | Trip REC 316*4 | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 414 T-2 LT | 2025-04-16 15:12 | 2025-04-16 15:47 | 0.024306 | T | 33kv Zinzira-2 relay operated but CB not tripped. Over current relay operated | 25 | 14.5833 | Power interruption
Keranigonj 230/132/33kV | 33kV Bus Section-1 | 2025-04-23 11:29 | 2025-04-23 11:33 | 0.0027778 | T | 51 Non directional overcurrent | 0 | 0 | No interruption
Madanganj 132/33kV | GT-2 HT | 2025-04-16 18:56 | 2025-04-16 20:56 | 0.083333 | T | Earth fault in 33kv side Back up relay | 3 | 6 | Power interruption
Narshingdi 132/33kV | T-4 LT | 2025-04-26 17:03 | 2025-04-26 17:50 | 0.032639 | T | N/A dF/dt, Lockout Relay | 7 | 5.4833 | Power interruption
Narshingdi 132/33kV | T-4 LT | 2025-04-28 10:28 | 2025-04-28 10:28 | 0 | T | 33 kV Hasnabad and Shibpur feeeder earth fault triped. dF/dt | 11 | 0 | Power interruption
Nawabganj 132/33kV | TR-2 LT | 2025-04-05 18:54 | 2025-04-05 19:05 | 0.0076389 | T | For 33 kv agla feeder. Lock out relay 1, Lock out relay -2 | 0 | 0 | No interruption
Nawabganj 132/33kV | TR-2 LT | 2025-04-17 11:30 | 2025-04-17 11:36 | 0.0041667 | T | Overcurrent relay | 0 | 0 | No interruption
Shyampur 230/132kV | Auto TR-1 LT | 2025-04-20 22:36 | 2025-04-21 11:04 | 0.51944 | T | The CB insulator has crackdown of Y-phase at 33 KV Side. 230KV side- 86.1/86.2 relay optd. 132KV side- 86.1/86.2 relay optd. 33 KV side - Buchloz Alarm, SEF PROTN, Trip | 0 | 0 | No interruption
Shyampur 230/132kV | Aux TR-1 HT | 2025-04-20 22:36 | 2025-04-21 11:04 | 0.51944 | T | The CB insulator has crackdown of Y-phase at 33 KV Side. 230KV side- 86.1/86.2 relay optd. 132KV side- 86.1/86.2 relay optd. 33 KV side - Buchloz Alarm, SEF PROTN, Trip | 10 | 124.6667 | Power interruption
Siddhirganj 132/33kV | T-1 LT | 2025-04-16 15:45 | 2025-04-16 17:25 | 0.069444 | E/O | Due to the fire at DPDC 33kv Sub-station | 66 | 110 | Power interruption
Siddhirganj 132/33kV | T-2 LT | 2025-04-16 15:45 | 2025-04-16 17:25 | 0.069444 | E/O | Due to the fier at DPDC 33kv Sub-station | 66 | 110 | Power interruption
Sonargaon 132/33kV | Tr-1 LT | 2025-04-07 00:25 | 2025-04-07 00:51 | 0.018056 | T | 33 kv side feeder fault Astha feed feeder Auxiliary Transformer -01 drop out fuse R,Y phase burn DIR O/C & E/F relay | 20 | 8.6667 | Power interruption
Sonargaon 132/33kV | Tr-1 LT | 2025-04-07 14:33 | 2025-04-07 15:45 | 0.05 | E/O | Due to 33kV PBS Astafeed feeder E/F, R&B phase Fuse barrel bursts at Auxiliary Transformer-1. | 35 | 42 | Power interruption
Sonargaon 132/33kV | Tr-1 HT | 2025-04-16 15:35 | 2025-04-16 18:05 | 0.10417 | T | Due to bad weather. TRAFO.DIFF.RALAY | 3 | 7.5 | Power interruption
Sonargaon 132/33kV | Tr-2 HT | 2025-04-22 16:30 | 2025-04-22 17:52 | 0.056944 | E/O | For jumper ing Borpa 33kv feeder load side | 40 | 54.6667 | Power interruption
|  |  | Total : | 1899-12-31 22:40 |  | Unserved Energy: |  | 483.5667
Chattogram Grid Circle :
Dohazari 132/33kV | Power Transformer -T-1 HT | 2025-04-11 16:53 | 2025-04-11 17:57 | 0.044444 | E/O | 33kv bus shutdown for Bashkhali Feeder Isolator Problem. | 6 | 6.4 | Power interruption
Dohazari 132/33kV | Power Transformer -T-1 HT | 2025-04-12 16:33 | 2025-04-12 17:48 | 0.052083 | E/O | Bashkhali 33kv Isolator pin change | 2 | 2.5 | Power interruption
Halishahar 132/33kV | 405T(TR-1) HT | 2025-04-29 04:37 | 2025-04-29 06:04 | 0.060417 | T | Due to 33kV feeder fault. O/C relay | 0 | 0 | No interruption
Hathazari 230/132/33kV | T-01 HT | 2025-04-22 00:15 | 2025-04-22 01:20 | 0.045139 | E/O | 33 kV XLPE cable fault | 0 | 0 | No interruption
Hathazari 230/132/33kV | T-01 LT | 2025-04-29 04:16 | 2025-04-29 08:34 | 0.17917 | T | 33 Kv cable puncture R Phase Simens Siprotec | 0 | 0 | No interruption
Hathazari 230/132/33kV | T-01 HT | 2025-04-29 07:55 | 2025-04-29 08:33 | 0.026389 | E/O | 33 Kv XLPE Cable R phase faulty | 0 | 0 | No interruption
Khulshi 132/33kV | 405T (T1) LT | 2025-04-15 08:46 | 2025-04-15 09:33 | 0.032639 | T | O/C DMT MVAJM25 | 0 | 0 | No interruption
|  |  | Total : | 0.44028 |  | Unserved Energy: |  | 8.9
Cumilla Grid Circle :
Beanibazar 132/33kV | 132 KV Transformer TR-01 LT | 2025-04-24 08:35 | 2025-04-24 10:00 | 0.059028 | E/O | For red hot in 33KV Beanibazar and Golapgonj feeder | 20 | 28.3333 | Power interruption
Chhatak 132/33kV | Bus A | 2025-04-23 15:05 | 2025-04-23 15:05 | 0 | E/O | Y phase PT loop out | 0 | 0 | No interruption
Cumilla(S) 132/33kV | TR-2 LT | 2025-04-18 16:37 | 2025-04-18 16:52 | 0.010417 | T | 33KV Laksam REB Feeder Fault REF815 | 17 | 4.25 | Power interruption
Shahjibazar 132/33kV | TR-02 LT | 2025-04-13 10:27 | 2025-04-13 10:36 | 0.00625 | T | PDB 33/0.4 kv Auxilary Transformer loop flashing OC/EF-50 | 6 | 0.9 | Power interruption
Shahjibazar 132/33kV | TR-02 HT | 2025-04-20 21:47 | 2025-04-20 21:47 | 0 | T | Stormy Weather PRD, Bucholz Relay Lockout Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 HT | 2025-04-20 21:47 | 2025-04-20 22:26 | 0.027083 | T | Stormy Weather O/C, Lockout Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 HT | 2025-04-20 21:47 | 2025-04-20 22:25 | 0.026389 | T | Stormy Weather O/C,E/F Lockout Relay | 0 | 0 | No interruption
|  |  | Total : | 0.12917 |  | Unserved Energy: |  | 33.4833
Khulna Grid Circle :
Barishal 132/33kV | T-2 (415T) LT | 2025-04-11 07:17 | 2025-04-11 08:04 | 0.032639 | T | Unknown Ins. O/C, Def. O/C, lockout relay. | 29 | 22.7167 | Power interruption
Barishal 132/33kV | T-2 (415T) LT | 2025-04-11 10:41 | 2025-04-11 10:48 | 0.0048611 | T | 33 kV Nolcity feeder fault. Ins.O/C, Lookout. | 29 | 3.3833 | Power interruption
Barishal 132/33kV | T-1 (405T) LT | 2025-04-14 15:26 | 2025-04-14 15:43 | 0.011806 | T | Dopdopia 33kV feeder fault. Def. O/c, E/F | 15 | 4.25 | Power interruption
Barishal 132/33kV | T-1 (405T) LT | 2025-04-26 12:12 | 2025-04-26 12:24 | 0.0083333 | T | WZPDCL 33 kV Dopdopia feeder 2 line side loop disconnect Instt.O/C, Instt. E/F | 40 | 8 | Power interruption
Barishal 230/132kV | T-4 LT | 2025-04-13 11:16 | 2025-04-13 11:42 | 0.018056 | T | Due to 33 kV feeder fault | 31 | 13.4333 | Power interruption
Benapole 132/33kV | Transformer-1(406T) LT | 2025-04-08 02:19 | 2025-04-08 02:34 | 0.010417 | T | Benapole Feeder & Sharsha Feeder Fault Simultaniously . REF630 | 40 | 10 | Power interruption
Benapole 132/33kV | Transformer-1(406T) LT | 2025-04-10 23:46 | 2025-04-11 00:04 | 0.0125 | T | sharsha feeder fault REF630 | 0 | 0 | No interruption
Benapole 132/33kV | Transformer-1(406T) LT | 2025-04-17 14:20 | 2025-04-17 14:58 | 0.026389 | T | Heavy Storm ( Benapole,Sharsha) feeder fault simultaneously. REF630 | 35 | 22.1667 | Power interruption
Benapole 132/33kV | Transformer-1(406T) LT | 2025-04-26 17:46 | 2025-04-26 19:03 | 0.053472 | T | Under Frequency REF 630 | 30 | 38.5 | Power interruption
Benapole 132/33kV | Transformer-2(416T) LT | 2025-04-26 17:46 | 2025-04-26 19:02 | 0.052778 | T | Under Frequency REF630 | 24 | 30.4 | Power interruption
Bhandaria 132/33kV | Transformer-1 HT | 2025-04-17 19:36 | 2025-04-17 21:04 | 0.061111 | E/O | 33 kv bus section (extension) y-phase female contact burn out . | 0 | 0 | No interruption
Bhandaria 132/33kV | Transformer-1 HT | 2025-04-18 14:45 | 2025-04-18 17:11 | 0.10139 | E/O | Due to emeergency maint.work of 33 kV feeder fault | 0 | 0 | No interruption
Goalpara 132/33kV | T-5 LT | 2025-04-17 17:04 | 2025-04-17 17:20 | 0.011111 | T | ৩৩ কেভি সেনেরবাজার ফিডার ফল্ট O/C | 3 | 0.8 | Power interruption
Goalpara 132/33kV | T-6 LT | 2025-04-17 17:04 | 2025-04-17 17:20 | 0.011111 | T | ৩৩ কেভি সেনেরবাজার ফিডার ফল্ট O/C | 3 | 0.8 | Power interruption
Goalpara 132/33kV | T-5 LT | 2025-04-28 19:53 | 2025-04-28 20:05 | 0.0083333 | T | Trip due to PBS 33KV feeder fault Dir OC, EG | 10 | 2 | Power interruption
Goalpara 132/33kV | T-6 LT | 2025-04-28 19:53 | 2025-04-28 20:05 | 0.0083333 | T | Trip due to PBS 33KV feeder fault Dir OC,EF | 10 | 2 | Power interruption
Goalpara 132/33kV | T-5 LT | 2025-04-29 00:05 | 2025-04-29 00:11 | 0.0041667 | T | Trip due to WZPDCL 33KV Chandnimohal feeder fault E/F | 10 | 1 | Power interruption
Goalpara 132/33kV | T-6 LT | 2025-04-29 00:05 | 2025-04-29 00:11 | 0.0041667 | T | Trip due to WZPDCL 33KV Chandnimohal feeder fault E/F | 10 | 1 | Power interruption
Gopalganj 132/33kV | T1 LT | 2025-04-26 18:28 | 2025-04-26 18:56 | 0.019444 | T | O/V relay | 0 | 0 | No interruption
Gopalganj 132/33kV | T2 HT | 2025-04-26 18:28 | 2025-04-26 18:34 | 0.0041667 | T | O/v relay | 0 | 0 | No interruption
Gopalganj 132/33kV | T2 LT | 2025-04-26 18:28 | 2025-04-26 18:34 | 0.0041667 | T | O/v relay | 0 | 0 | No interruption
Gopalganj 132/33kV | T2 LT | 2025-04-29 10:35 | 2025-04-29 10:48 | 0.0090278 | T | Reb-8 Fault Insist O/C | 28 | 6.0667 | Power interruption
Khulna (C) | TR-1 425T LT | 2025-04-09 04:10 | 2025-04-09 04:49 | 0.027083 | T | 33 Kv BUS Touch by Bagdasha . O/C & E/F | 36 | 23.4 | Power interruption
Khulna (C) | Tr-2 415 T LT | 2025-04-09 04:10 | 2025-04-09 04:50 | 0.027778 | T | 33 KV BUS Touch by Bagdasha Inst E/F | 17 | 11.3333 | Power interruption
Khulna (C) | TR-1 425T HT | 2025-04-13 09:10 | 2025-04-13 16:02 | 0.28611 | E/O | Maintenance of 132kv main bus section-2 loop clamp. | 0 | 0 | No interruption
Khulna (C) | TR-1 425T LT | 2025-04-13 09:10 | 2025-04-13 16:03 | 0.28681 | E/O | Maintenance of 132kv main bus section-2 loop clamp | 0 | 0 | No interruption
Khulna (C) | TR-1 425T HT | 2025-04-21 13:34 | 2025-04-23 14:31 | 1900-01-01 00:57 | T | 33kv cable fault.B - phase 86T lockout Realy | 0 | 0 | No interruption
Madaripur 132/33kV | T3-426T HT | 2025-04-17 14:18 | 2025-04-17 18:39 | 0.18125 | T | 33kv west zone bus section fault Earth fault B phase | 0 | 0 | No interruption
Rajbari 132/33kV | Transformer-2 HT | 2025-04-09 13:20 | 2025-04-09 14:07 | 0.032639 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Satkhira 132/33kV | Transformer-2 (T-2) HT | 2025-04-05 08:19 | 2025-04-05 09:13 | 0.0375 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 09:31 |  | Unserved Energy: |  | 201.25
HVDC Grid Circle :
Bhangura 132/33kV | Tr-1(403T) HT | 2025-04-07 21:38 | 2025-04-07 22:19 | 0.028472 | E/O | Red Hot Removing | 15 | 10.25 | Power interruption
Ishurdi 132/33kV | 132/33 kV T-1 HT | 2025-04-25 08:18 | 2025-04-25 09:26 | 0.047222 | E/O | Due to emergency maint.work | 25 | 28.3333 | Power interruption
Ishurdi 230/132kV | 230/132 kV T-03 LT | 2025-04-06 19:15 | 2025-04-07 06:33 | 0.47083 | E/O | 230/132 kV T03 Transformer DS 803M red hot. | 0 | 0 | No interruption
Ishurdi 230/132kV | 230/132 kV T-03 HT | 2025-04-06 21:10 | 2025-04-07 06:32 | 0.39028 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Jashore 132/33kV | T-3 HT | 2025-04-07 09:40 | 2025-04-07 13:13 | 0.14792 | E/O | T3 Tx Abnormal Sound Remove | 0 | 0 | No interruption
Jashore 132/33kV | T-1 HT | 2025-04-11 06:11 | 2025-04-11 08:50 | 0.11042 | E/O | Red hot maintenance | 0 | 0 | No interruption
Kushtia 132/33kV | T-3 HT | 2025-04-05 11:18 | 2025-04-05 12:24 | 0.045833 | E/O | Kumarkhali Feeder Red Hot Maintenance by PBS | 46 | 50.6 | Power interruption
Kushtia 132/33kV | T-3 LT | 2025-04-10 22:01 | 2025-04-10 23:27 | 0.059722 | E/O | 11.4 kV PBS auxiliary transformer for sparking. | 0 | 0 | No interruption
Shahjadpur 132/33kV | T-4(435T) HT | 2025-04-19 09:50 | 2025-04-19 11:04 | 0.051389 | E/O | Redhot Remove | 0 | 0 | No interruption
Shahjadpur 132/33kV | T-2(415T) HT | 2025-04-23 15:55 | 2025-04-23 15:55 | 0 | E/O | 33 kV bus PT work by energy Audit and PBS | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 08:27 |  | Unserved Energy: |  | 89.1833
Bogura Grid Circle:
Amnura 132/33kV | T-1 (406T) LT | 2025-04-16 10:54 | 2025-04-16 14:51 | 0.16458 | T | 33kv side NONE | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 230/132 KV T-01, 703T LT | 2025-04-17 04:02 | 2025-04-17 04:42 | 0.027778 | T | Earth Fault RET-521 | 108 | 72 | Power interruption
Barapukuria 230/132/33kV | 230/132 KV T-01, 703T LT | 2025-04-17 05:17 | 2025-04-17 05:32 | 0.010417 | T | Earth Fault RET 521 | 58 | 14.5 | Power interruption
Barapukuria 230/132/33kV | 132/33 KV T-5, 424T LT | 2025-04-27 12:23 | 2025-04-27 17:26 | 0.21042 | E/O | Emergency Maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132/33 KV T-5, 424T HT | 2025-04-28 10:40 | 2025-04-28 21:35 | 0.45486 | E/O | Emergency Maintenance work by NESCO. | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132/33 KV T-5, 424T LT | 2025-04-28 10:41 | 2025-04-28 21:42 | 0.45903 | E/O | Emergency Maintenance work by NESCO. | 0 | 0 | No interruption
Bogura 230/132kV | T-03 HT | 2025-04-10 23:43 | 2025-04-11 11:28 | 0.48958 | T | PRD trip | 0 | 0 | No interruption
Bogura 230/132kV | T-03 LT | 2025-04-10 23:43 | 2025-04-11 11:29 | 0.49028 | T | Rain & Storming No Relay Show | 0 | 0 | No interruption
Bogura 230/132kV | T-03 LT | 2025-04-11 07:55 | 2025-04-11 11:29 | 0.14861 | E/O | Maintenance Work | 0 | 0 | No interruption
Chapai 132/33kV | T-2 (415T) LT | 2025-04-13 03:55 | 2025-04-13 04:23 | 0.019444 | T | 33 kv feeder trip, strom, thundering. O/C, Def, Phase R | 0 | 0 | No interruption
Jaldhaka 132/33kV | 406T-1 HT | 2025-04-26 12:07 | 2025-04-26 16:30 | 0.18264 | E/O | Emergency Maintenance Work of 33 kV side. | 15 | 65.75 | Power interruption
Jaldhaka 132/33kV | 416T-2 HT | 2025-04-26 16:51 | 2025-04-26 18:35 | 0.072222 | E/O | Emergency maintenance work | 35 | 60.6667 | Power interruption
Kurigram 132/33kV | Transformer T-1 (Tr-403T) HT | 2025-04-17 05:16 | 2025-04-17 05:48 | 0.022222 | T | Over voltage>> Overcurrent Protection P132 | 30 | 16 | Power interruption
Kurigram 132/33kV | Transformer T-2 (Tr-413T) HT | 2025-04-17 05:16 | 2025-04-17 05:48 | 0.022222 | T | Overvoltage>> Overcurrent Protection P132 | 0 | 0 | No interruption
Kurigram 132/33kV | Transformer T-1 (Tr-403T) HT | 2025-04-26 22:54 | 2025-04-26 23:44 | 0.034722 | T | Overcurrent protection | 0 | 0 | No interruption
Kurigram 132/33kV | Transformer T-2 (Tr-413T) HT | 2025-04-26 22:54 | 2025-04-26 23:44 | 0.034722 | T | overcurrent protection. | 0 | 0 | No interruption
Lalmonirhat 132/33kV | T-1 (425T) LT | 2025-04-26 22:52 | 2025-04-26 23:42 | 0.034722 | E/O | 132 KV Rangpur - Lalmonirhat Line Trip( From Rangpur Side) | 22 | 18.3333 | Power interruption
Lalmonirhat 132/33kV | T-2 (415T) LT | 2025-04-26 22:52 | 2025-04-26 23:42 | 0.034722 | E/O | 132 KV Rangpur - Lalmonirhat Line Trip(From Rangpur Side) | 22 | 18.3333 | Power interruption
Mahasthangarh 132/33kV | 406T MTR1 LT | 2025-04-23 09:24 | 2025-04-23 09:52 | 0.019444 | T | 33 kv incomer T1 CB trip of Over Current / Earth Fault for 33 kv Amtoli feeder (BPBS-1) trip. Over Current protection (Micom P-142) | 0 | 0 | No interruption
Mahasthangarh 132/33kV | 416T MTR 2 HT | 2025-04-24 16:35 | 2025-04-24 18:41 | 0.0875 | E/O | 33 kv Bus conductor and Amtoli feeder 33kv bus loop Maintenance of PBS. | 35 | 73.5 | Power interruption
Naogaon 132/33kV | T-1 LT | 2025-04-10 22:01 | 2025-04-10 23:40 | 0.06875 | T | Heavy thundering and raining. MCGG | 29 | 47.85 | Power interruption
Naogaon 132/33kV | T-2 LT | 2025-04-10 22:01 | 2025-04-10 22:26 | 0.017361 | T | Heavy thundering and raining. MCGG | 29 | 12.0833 | Power interruption
Niamatpur 132/33kV | Transformer-2 (417T) LT | 2025-04-13 04:10 | 2025-04-13 10:23 | 0.25903 | T | Thunder storm Protection panel: General trip | 0 | 0 | No interruption
Niamatpur 132/33kV | Transformer-3(426T) LT | 2025-04-30 08:55 | 2025-04-30 09:05 | 0.0069444 | T | Rajshahi-2 33 kV feeder fault. OC/EF &33 KV Lockout OPTD | 12 | 2 | Power interruption
Palashbari 132/33kV | TR1-414T LT | 2025-04-21 21:45 | 2025-04-21 22:23 | 0.026389 | E/O | Red hot for T1 transformer 33KV CT P1 Connector | 25 | 15.8333 | Power interruption
Purbasadipur 132/33kV | T-1 Transformer (403T) LT | 2025-04-13 01:57 | 2025-04-13 10:45 | 0.36667 | T | Alstom MCGG | 0 | 0 | No interruption
Purbasadipur 132/33kV | T-3 Transformer (423T) LT | 2025-04-13 01:57 | 2025-04-13 03:32 | 0.065972 | T | Thunder and rain Siprotec Siemens | 30 | 47.5 | Power interruption
Purbasadipur 132/33kV | T-1 Transformer (403T) HT | 2025-04-13 07:00 | 2025-04-13 10:42 | 0.15417 | E/O | ৩৩কেভি সাইডে কাজের স্বার্থে বন্ধ করা হলো। | 0 | 0 | No interruption
Rahanpur 132/33kV | TR-1 404T HT | 2025-04-13 06:03 | 2025-04-13 06:49 | 0.031944 | T | Over Voltage STG-1 OP Simens 7UT85 | 6 | 4.6 | Power interruption
Rahanpur 132/33kV | TR-2 (414T) HT | 2025-04-13 06:03 | 2025-04-13 06:49 | 0.031944 | T | Over Voltage STG-1 OP Differential Relay (Simens 7UT85) | 0 | 0 | No interruption
Rangpur 132/33kV | 132KV Bus A | 2025-04-11 09:05 | 2025-04-11 15:13 | 0.25556 | E/O | TEMPARATURE HIGH | 0 | 0 | No interruption
Thakurgaon 132/33kV | T-1(422T) LT | 2025-04-13 02:22 | 2025-04-13 03:25 | 0.04375 | T | Thundering Micom P142 | 28 | 29.4 | Power interruption
Thakurgaon 132/33kV | T-2(412T) LT | 2025-04-13 02:22 | 2025-04-13 03:19 | 0.039583 | T | Thundering SIEMENS | 28 | 26.6 | Power interruption
|  |  | Total : | 1900-01-03 09:19 |  | Unserved Energy: |  | 524.95
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 1900-01-19 13:28 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: April 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved2 | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | Gopalganj-1 | 2025-04-26 17:45 | 2025-04-26 18:19 | 0.023611 | T | Unknown | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Gopalganj-2 | 2025-04-26 17:45 | 2025-04-26 18:25 | 0.027778 | T | Unknown | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-01 | 2025-04-21 04:50 | 2025-04-21 05:21 | 0.021528 | T | Fault | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-1 | 2025-04-06 23:38 | 2025-04-15 23:24 | 1900-01-07 23:46 | T | Grid Fail | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-2 | 2025-04-07 00:52 | 2025-04-07 21:17 | 0.85069 | T | Tripped | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-1 | 2025-04-07 16:19 | 2025-04-15 23:24 | 1900-01-07 07:05 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-2 | 2025-04-07 16:25 | 2025-04-07 21:17 | 0.20278 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Kodda ckt-1 | 2025-04-07 21:14 | 2025-04-08 17:56 | 0.8625 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Kodda ckt-2 | 2025-04-07 21:17 | 2025-04-08 17:51 | 0.85694 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Kabirpur 132/33kV | Manikganj-1 | 2025-04-05 17:42 | 2025-04-05 17:59 | 0.011806 | T | Tripped | 0 | 0 | No interruption
Kabirpur 132/33kV | Tongi-2 | 2025-04-05 18:02 | 2025-04-05 18:46 | 0.030556 | T | Tripped | 0 | 0 | No interruption
Kabirpur 132/33kV | Tongi-2 | 2025-04-05 18:54 | 2025-04-05 20:09 | 0.052083 | T | Tripped | 0 | 0 | No interruption
Kabirpur 132/33kV | Tongi-1 | 2025-04-05 20:12 | 2025-04-05 22:38 | 0.10139 | T | Tripped | 0 | 0 | No interruption
Kabirpur 132/33kV | Tongi-2 | 2025-04-06 23:19 | 2025-04-07 00:24 | 0.045139 | T | Earth fault | 0 | 0 | No interruption
Kabirpur 132/33kV | Manikganj-1 | 2025-04-10 10:13 | 2025-04-10 12:42 | 0.10347 | E/O | Instruction of NLDC | 0 | 0 | No interruption
Kabirpur 132/33kV | Tongi-2 | 2025-04-21 13:37 | 2025-04-21 15:44 | 0.088194 | E/O | Emergency maintenance work | 0 | 0 | No interruption
Kishoreganj 132/33kV | Mymensingh Ckt-2 | 2025-04-02 17:28 | 2025-04-02 17:49 | 0.014583 | E/O | due to dry tree branches falling on the structure above the line | 0 | 0 | No interruption
Muktagacha 132/33kV | RPCL-2 | 2025-04-21 09:22 | 2025-04-21 10:01 | 0.027083 | E/O | Due to RPCL Plant emergency maintenance work. | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Jamalpur Ckt-1 | 2025-04-21 04:49 | 2025-04-21 05:21 | 0.022222 | T | Triped | 0 | 0 | No interruption
Rajendrapur 132/33kV | Kodda-1 | 2025-04-08 17:46 | 2025-04-10 15:11 | 1899-12-31 21:25 | E/O | Order By NLDC | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2025-04-05 18:05 | 2025-04-05 18:48 | 0.029861 | T | Bad whether | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2025-04-05 18:56 | 2025-04-05 20:08 | 0.05 | T | Bad weather | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2025-04-05 19:58 | 2025-04-05 20:07 | 0.00625 | T | Bad weather | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2025-04-05 20:12 | 2025-04-05 22:38 | 0.10139 | T | Bad weather | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2025-04-06 23:19 | 2025-04-07 00:23 | 0.044444 | T | Bad weather | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2025-04-08 18:56 | 2025-04-08 19:13 | 0.011806 | T | Tripped | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Ghorashal Ckt-1 | 2025-04-16 12:03 | 2025-04-16 13:30 | 0.060417 | T | Tripped | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Basundhara Ckt-1 | 2025-04-16 15:26 | 2025-04-16 16:00 | 0.023611 | T | Tripped | 0 | 0 | No interruption
|  |  | Total : | 1900-01-21 20:21 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Fatullah 132/33kV | 132 kV Madanganj | 2025-04-14 15:49 | 2025-04-14 21:10 | 0.22292 | T | Tripped | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi Circuit-2 | 2025-04-05 20:08 | 2025-04-05 23:00 | 0.11944 | T | Tripped | 0 | 0 | No interruption
Haripur 230/132kV | Meghnaghat-2 | 2025-04-17 03:40 | 2025-04-17 09:12 | 0.23056 | T | Unknown. | 0 | 0 | No interruption
Haripur 230/132kV | Ullon (Maniknagar-2) | 2025-04-23 19:06 | 2025-04-23 20:10 | 0.044444 | E/O | from other end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Kamrangirchar Ckt, | 2025-04-05 18:51 | 2025-04-05 18:55 | 0.0027778 | T | heavy wind blowing weather. | 75 | 5 | Power interruption
Madanganj 132/33kV | Madanganj-Fatullah 132KV Ckt | 2025-04-14 15:51 | 2025-04-14 21:11 | 0.22222 | T | Heavy stormy rain | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Shitalakhya 132 kv Ckt | 2025-04-17 12:13 | 2025-04-17 13:36 | 0.057639 | E/O | Due to Load Management by NLDC | 0 | 0 | No interruption
Meghnaghat 230/132kV | Meghnaghat-Haripur-02 | 2025-04-17 03:40 | 2025-04-17 09:10 | 0.22917 | T | Y-Phase LA BLust | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-2 | 2025-04-10 08:26 | 2025-04-10 16:09 | 0.32153 | E/O | requested by LDC | 0 | 0 | No interruption
Munshiganj 132/33kV | Sinha Peoples Energy Limited (SPEL) 52.5 MW IPP | 2025-04-22 11:50 | 2025-04-22 13:55 | 0.086806 | E/O | Emergency Shutdown For Tree Trimming | 0 | 0 | No interruption
Narshingdi 132/33kV | Haripur | 2025-04-11 12:59 | 2025-04-11 13:39 | 0.027778 | T | Trip from Bhulta side | 55 | 36.6667 | Power interruption
Rampura 230/132kV | Basundhara-01 | 2025-04-06 23:40 | 2025-04-06 23:49 | 0.00625 | T | Heavy Thunderstorm. | 0 | 0 | No interruption
Rampura 230/132kV | Basundhara-02 | 2025-04-06 23:40 | 2025-04-06 23:59 | 0.013194 | T | Heavy Thunderstorm. | 0 | 0 | No interruption
Rampura 230/132kV | Basundhara-01 | 2025-04-10 14:08 | 2025-04-10 16:28 | 0.097222 | E/O | redhot | 0 | 0 | No interruption
Rampura 230/132kV | Ullon-02 | 2025-04-16 16:18 | 2025-04-16 16:51 | 0.022917 | T | At Moghbazar substation and GT 3 LA brust. ( Moghbazar 2 overhead line shutdown Because of xlpe cable commissioning & relay setting. Now Moghbazar 2 connected via Ullon substation) | 0 | 0 | No interruption
Rampura 230/132kV | Basundhara-01 | 2025-04-29 11:22 | 2025-04-29 11:34 | 0.0083333 | T | N/A | 0 | 0 | No interruption
Siddhirganj 132/33kV | 120MW EGCB GT2 | 2025-04-19 12:35 | 2025-04-19 12:54 | 0.013194 | E/O | Tap change problem work EGCB ends | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 17:26 |  | Unserved Energy: |  | 41.6667
Chattogram Grid Circle :
AKS 132/33kV | Bar Aulia | 2025-04-14 10:24 | 2025-04-14 11:50 | 0.059722 | E/O | AKSPL to Baraulia 132 KV Line Shutdown due to forced shutdown. | 0 | 0 | No interruption
Bakulia 132/33kV | Bakalia-Modern Ckt | 2025-04-18 18:48 | 2025-04-18 19:22 | 0.023611 | T | Tripped | 0 | 0 | No interruption
Baroaulia 132/33kV | AKSPL | 2025-04-14 10:25 | 2025-04-14 11:49 | 0.058333 | E/O | CT OIL LEAKAGE | 58 | 81.2 | Power interruption
Baroirhat 132/33kV | Feni-1 | 2025-04-15 07:55 | 2025-04-15 09:28 | 0.064583 | T | Distance trip | 0 | 0 | No interruption
BSRM 230/33kV | GPH Ispat Ckt. -01 | 2025-04-23 12:46 | 2025-04-23 17:00 | 0.17639 | E/O | Kite is hanged in span of conductor 230kV GPH-BSRM Ckt-01. | 0 | 0 | No interruption
GPH 230/33kV | BSRM CKT-1 | 2025-04-14 08:19 | 2025-04-14 09:35 | 0.052778 | E/O | Emergency Works | 0 | 0 | No interruption
GPH 230/33kV | BSRM CKT-1 | 2025-04-21 06:15 | 2025-04-21 06:53 | 0.026389 | T | Tripped | 0 | 0 | No interruption
GPH 230/33kV | BSRM CKT-2 | 2025-04-22 08:05 | 2025-04-22 08:38 | 0.022917 | T | Tripped | 0 | 0 | No interruption
GPH 230/33kV | BSRM CKT-1 | 2025-04-23 12:48 | 2025-04-23 17:00 | 0.175 | E/O | Emergency shutdown | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2025-04-12 05:33 | 2025-04-12 05:50 | 0.011806 | T | Showing Z1 | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2025-04-12 09:24 | 2025-04-12 11:48 | 0.1 | T | Showing Z1 Fault. | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Sikalbaha | 2025-04-22 15:10 | 2025-04-22 17:54 | 0.11389 | E/O | Tripped | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2025-04-29 17:55 | 2025-04-29 18:24 | 0.020139 | T | no u/f | 0 | 0 | No interruption
Khagrachori 132/33kV | RANGAMATI-2 | 2025-04-15 05:49 | 2025-04-15 06:19 | 0.020833 | T | For thundering | 0 | 0 | No interruption
Khagrachori 132/33kV | RANGAMATI-1 | 2025-04-17 11:53 | 2025-04-17 12:10 | 0.011806 | E/O | Emergency maintenance at Rangamati SS | 0 | 0 | No interruption
Khagrachori 132/33kV | RANGAMATI-2 | 2025-04-18 13:20 | 2025-04-18 13:31 | 0.0076389 | T | Tripped | 0 | 0 | No interruption
Rangamati 132/33kV | Khagrachari Ckt-01 | 2025-04-17 11:53 | 2025-04-17 12:09 | 0.011111 | E/O | Destroyed nest | 0 | 0 | No interruption
Rangamati 132/33kV | Khagrachari Ckt-01 | 2025-04-27 18:09 | 2025-04-27 19:23 | 0.051389 | E/O | Rangamati-Khagrachari Ckt-01 taken emergency shutdown due to remove straw from Y-phase. | 0 | 0 | No interruption
Shikalbaha 230/132kV | Interconnection-2 | 2025-04-29 04:37 | 2025-04-29 04:37 | 0 | T | Tripped | 0 | 0 | No interruption
Shikalbaha 230/132kV | Interconnection-1 | 2025-04-29 04:37 | 2025-04-29 06:48 | 0.090972 | T | Tripped | 21 | 45.85 | Power interruption
Shikalbaha 230/132kV | Modunaghat Ckt-2(T.K Chemical) | 2025-04-29 13:39 | 2025-04-29 15:46 | 0.088194 | E/O | Emergency shutdown | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 04:30 |  | Unserved Energy: |  | 127.05
Cumilla Grid Circle :
Ashuganj 230/132/33kV | B.Baria 132 kV Ckt-2 | 2025-04-08 10:20 | 2025-04-08 11:47 | 0.060417 | E/O | As per demand of APSCL substation | 0 | 0 | No interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-2 | 2025-04-28 07:46 | 2025-04-28 08:28 | 0.029167 | T | Heavy Rain. | 4 | 2.8 | Power interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-1 | 2025-04-28 07:46 | 2025-04-28 08:28 | 0.029167 | T | HEAVY RAIN | 4 | 2.8 | Power interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-1 | 2025-04-28 09:53 | 2025-04-28 11:00 | 0.046528 | T | HEAVY RAIN | 0 | 0 | No interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-2 | 2025-04-28 09:53 | 2025-04-28 11:00 | 0.046528 | T | HEAVY RAIN | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-2 | 2025-04-07 10:36 | 2025-04-07 15:21 | 0.19792 | E/O | Shutdown taken by NLDC | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-2 | 2025-04-08 10:17 | 2025-04-08 11:49 | 0.063889 | E/O | maintenance ashugonj end. | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-1 | 2025-04-16 13:20 | 2025-04-16 13:50 | 0.020833 | T | Distance Relay Trip | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-2 | 2025-04-16 13:20 | 2025-04-16 14:10 | 0.034722 | T | Distance Relay Trip | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-1 | 2025-04-17 11:25 | 2025-04-17 11:46 | 0.014583 | E/O | tree trimming by maintenance team | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-2 | 2025-04-17 11:46 | 2025-04-17 12:31 | 0.03125 | E/O | tree trimming by maintenance team | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-2 | 2025-04-17 12:13 | 2025-04-17 12:25 | 0.0083333 | T | Tripped | 0 | 0 | No interruption
Chandpur 132/33kV | 115MW CPGL Power Plant Incomer (L5) | 2025-04-10 10:24 | 2025-04-14 13:19 | 1900-01-03 02:55 | E/O | Maintenance work by CPGL at power station end. | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Kachua Ckt-2 | 2025-04-18 14:40 | 2025-04-18 14:49 | 0.00625 | T | Kachua end CB not trip | 0 | 0 | No interruption
Chowmuhani 132/33kV | Feni line-01 | 2025-04-07 12:04 | 2025-04-07 16:21 | 0.17847 | T | Distance Relay Zone-1, B & C Phase. | 51 | 218.45 | Power interruption
Chowmuhani 132/33kV | Feni line-01 | 2025-04-07 12:28 | 2025-04-07 16:21 | 0.16181 | E/O | Maintenance Work (SOTF shown by Feni S/S) | 0 | 0 | No interruption
Chowmuhani 132/33kV | Ramganj line-01 | 2025-04-07 12:43 | 2025-04-07 14:41 | 0.081944 | E/O | 789BP Flashing shown | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Ashuganj Ckt-1 | 2025-04-13 11:52 | 2025-04-13 12:48 | 0.038889 | T | Tripped | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Ashuganj Ckt-1 | 2025-04-28 10:14 | 2025-04-28 10:48 | 0.023611 | T | Tripped | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sreemongal-2 | 2025-04-23 02:58 | 2025-04-23 03:05 | 0.0048611 | T | Bad Weather | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sreemongal-2 | 2025-04-23 03:06 | 2025-04-23 03:32 | 0.018056 | E/O | After tripped | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sylhet-2 | 2025-04-28 07:45 | 2025-04-28 07:50 | 0.0034722 | T | Bad weather | 34 | 2.8333 | Power interruption
Fenchuganj 230/132/33kV | Sylhet-2 | 2025-04-28 07:51 | 2025-04-28 08:28 | 0.025694 | E/O | After trip | 34 | 20.9667 | Power interruption
Fenchuganj 230/132/33kV | Sylhet-2 | 2025-04-28 09:54 | 2025-04-28 09:59 | 0.0034722 | T | Bad weather | 18 | 1.5 | Power interruption
Fenchuganj 230/132/33kV | Sylhet-2 | 2025-04-28 10:00 | 2025-04-28 10:59 | 0.040972 | E/O | After Trip | 18 | 17.7 | Power interruption
Ramganj 132/33kV | Ramgonj-Chowmuhani Ckt-02 | 2025-04-07 12:04 | 2025-04-07 12:28 | 0.016667 | T | Distance Trip, Zone-2 Phase A B C | 0 | 0 | No interruption | 0.040972
Ramganj 132/33kV | Ramgonj-Chowmuhani Ckt-01 | 2025-04-07 12:04 | 2025-04-07 12:49 | 0.03125 | T | Overcurrent A B C Trip | 42 | 31.5 | Power interruption | 0.058333
Ramganj 132/33kV | Ramgonj-Chowmuhani Ckt-01 | 2025-04-07 12:50 | 2025-04-07 14:41 | 0.077083 | E/O | Line Fault | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-Ashuganj Ckt-03 | 2025-04-11 18:22 | 2025-04-11 18:52 | 0.020833 | T | Bad weather | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-02 | 2025-04-17 12:13 | 2025-04-17 12:26 | 0.0090278 | T | Heavy Rain & Wind flow | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-Ashuganj Ckt-03 | 2025-04-21 01:05 | 2025-04-21 01:18 | 0.0090278 | T | Stormy Weather | 0 | 0 | No interruption
Shahjibazar 132/33kV | SPCL 86 MW | 2025-04-23 16:30 | 2025-04-23 16:34 | 0.0027778 | T | O/C Trip | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal-Fenchugonj circuit-1 | 2025-04-10 22:40 | 2025-04-10 22:46 | 0.0041667 | T | Fault | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal-Fenchugonj circuit-2 | 2025-04-23 02:58 | 2025-04-23 03:32 | 0.023611 | T | Tripped | 0 | 0 | No interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-1 | 2025-04-28 07:44 | 2025-04-28 08:30 | 0.031944 | T | HEAVY RAIN FALL. | 1 | 0.76667 | Power interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-2 | 2025-04-28 07:44 | 2025-04-28 08:30 | 0.031944 | T | heavy rain fall | 1 | 0.76667 | Power interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-1 | 2025-04-28 09:53 | 2025-04-28 11:01 | 0.047222 | T | thundering | 0 | 0 | No interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-2 | 2025-04-28 09:53 | 2025-04-28 11:01 | 0.047222 | T | THUNDERING | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2025-04-17 06:19 | 2025-04-17 06:25 | 0.0041667 | T | Distance Protection | 0 | 0 | No interruption
|  |  | Total : | 1900-01-04 15:35 |  | Unserved Energy: |  | 300.0833
Khulna Grid Circle :
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2025-04-14 15:01 | 2025-04-14 16:17 | 0.052778 | T | kalbayashi storms take place in the barisal zone. | 0 | 0 | No interruption
Barishal 132/33kV | 132kv Bhandaria ckt | 2025-04-18 13:57 | 2025-04-18 14:18 | 0.014583 | T | Unknown | 3 | 1.05 | Power interruption
Barishal 132/33kV | 132 kV Capacitor Bank | 2025-04-26 17:49 | 2025-04-26 20:18 | 0.10347 | T | O/V | 0 | 0 | No interruption
Barishal 132/33kV | 132 kV Barishal north ckt-2 | 2025-04-26 18:10 | 2025-04-26 19:36 | 0.059722 | T | O/V , | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Khulna Central-1 | 2025-04-12 21:12 | 2025-04-13 09:02 | 0.49306 | E/O | Order by ALDC Khulna | 0 | 0 | No interruption
Gollamari 132/33kV | E01 Gollamari-Gopalgonj Line - 1 | 2025-04-26 18:28 | 2025-04-26 18:31 | 0.0020833 | T | Over Voltage | 0 | 0 | No interruption
Gollamari 132/33kV | E07 Gollamari-Gopalgonj Line - 2 | 2025-04-26 18:28 | 2025-04-26 19:15 | 0.032639 | T | Over Voltage | 0 | 0 | No interruption
Gopalganj 132/33kV | Gopalganj North-1 | 2025-04-26 18:15 | 2025-04-26 19:39 | 0.058333 | T | None | 0 | 0 | No interruption
Gopalganj 132/33kV | Gopalganj North-2 | 2025-04-26 18:15 | 2025-04-26 19:39 | 0.058333 | T | 0 | 0 | 0 | No interruption
Gopalganj 132/33kV | Gallamari-1 | 2025-04-26 18:15 | 2025-04-26 18:39 | 0.016667 | T | None | 0 | 0 | No interruption
Gopalganj 132/33kV | Gopalganj 100 MW PS | 2025-04-26 18:28 | 2025-04-26 18:48 | 0.013889 | T | 0 | 0 | 0 | No interruption
Gopalganj 132/33kV | Gallamari-2 | 2025-04-26 18:28 | 2025-04-26 19:48 | 0.055556 | T | 0 | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-1 | 2025-04-05 10:09 | 2025-04-05 12:11 | 0.084722 | E/O | 0 | 0 | 0 | No interruption
Khulna (C) | North- West Ckt-2 | 2025-04-13 09:14 | 2025-04-13 16:00 | 0.28194 | E/O | Maintenance of 132kv main bus section-2 loop clamp | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- South -1 | 2025-04-13 09:15 | 2025-04-13 15:54 | 0.27708 | E/O | Maintenance of 132kv main bus section-2 loop clamp | 0 | 0 | No interruption
Khulna (C) | North-WestCkt-1 | 2025-04-13 09:18 | 2025-04-13 15:59 | 0.27847 | E/O | Maintenance of 132kv main bus section-2 loop clamp | 0 | 0 | No interruption
Khulna (C) | 132kV Central-Goalpara-2 | 2025-04-26 18:55 | 2025-04-28 17:15 | 1899-12-31 22:20 | T | Goal para End fault | 0 | 0 | No interruption
Madaripur 132/33kV | Gopaganj North CKT-04 | 2025-04-26 17:47 | 2025-04-26 18:27 | 0.027778 | T | Tripped | 80 | 0 | No interruption
Madaripur 132/33kV | Gopaganj North CKT-01 | 2025-04-26 18:12 | 2025-04-26 18:26 | 0.0097222 | T | Tripped | 0 | 0 | No interruption
Madaripur 132/33kV | Gopaganj North CKT-02 | 2025-04-26 18:12 | 2025-04-26 18:26 | 0.0097222 | T | None | 0 | 0 | No interruption
Madaripur 132/33kV | Gopaganj North CKT-03 | 2025-04-26 18:12 | 2025-04-26 18:27 | 0.010417 | T | Tripped | 0 | 0 | No interruption
Madaripur 132/33kV | Gopaganj North CKT-04 | 2025-04-26 18:40 | 2025-04-26 19:02 | 0.015278 | T | Tripped | 0 | 0 | No interruption
Patuakhali 132/33kV | Barishal-Pautakhali 132kV Line | 2025-04-18 13:54 | 2025-04-18 14:13 | 0.013194 | T | Tripped | 0 | 0 | No interruption
Rajbari 132/33kV | Faridpur - 2 | 2025-04-16 17:04 | 2025-04-16 17:22 | 0.0125 | T | Thundering faridpur grid end | 0 | 0 | No interruption
Rajbari 132/33kV | Faridpur -1 | 2025-04-26 18:06 | 2025-04-26 18:50 | 0.030556 | E/O | Grid fail so ordered by NLDC SD | 0 | 0 | No interruption
Rajbari 132/33kV | Faridpur - 2 | 2025-04-26 18:06 | 2025-04-26 18:49 | 0.029861 | E/O | Ordered by NLDC SD for Grid fail | 68 | 0 | No interruption
Rampal 400/230kV | Gopalganj Line-2 Reactor | 2025-04-12 18:42 | 2025-04-12 18:42 | 0 | E/O | Due to low voltage. | 0 | 0 | No interruption
Rampal 400/230kV | Gopalganj Line-1 Reactor | 2025-04-12 18:43 | 2025-04-12 18:43 | 0 | E/O | Due to low voltage. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 23:21 |  | Unserved Energy: |  | 1.05
HVDC Grid Circle :
BIPTC | 20DF24 | 2025-04-09 09:13 | 2025-04-09 09:13 | 0 | E/O | Shutdown is taken for DCRM test of CB | 0 | 0 | No interruption
BIPTC | 20DF11 | 2025-04-09 11:13 | 2025-04-09 13:30 | 0.095139 | E/O | Shutdown is taken for BCU and Relay checking. | 0 | 0 | No interruption
BIPTC | 20DF11 | 2025-04-12 10:53 | 2025-04-12 15:52 | 0.20764 | E/O | Corrective Maintenance. | 0 | 0 | No interruption
BIPTC | 20DF11 | 2025-04-17 11:16 | 2025-04-17 15:34 | 0.17917 | E/O | Shutdown is taken by Abdullah Al Farabi, AE Troubleshooting. | 0 | 0 | No interruption
BIPTC | 10CF14 | 2025-04-27 12:58 | 2025-04-27 16:22 | 0.14167 | T | C1 unbalance 60/61 instant L2 tripped | 0 | 0 | No interruption
BIPTC | 10CF14 | 2025-04-27 15:51 | 2025-04-27 16:22 | 0.021528 | E/O | Due to tripped by showing unbalance 60/61 instant trip. | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kv Natore-1 | 2025-04-09 09:32 | 2025-04-09 11:48 | 0.094444 | E/O | red hot maintenance | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 2 | 2025-04-05 20:08 | 2025-04-05 22:59 | 0.11875 | T | Tripped | 0 | 0 | No interruption
Jashore 132/33kV | JH-1(L2) | 2025-04-26 17:45 | 2025-04-26 18:17 | 0.022222 | T | Tripped | 107 | 0 | No interruption
Jashore 132/33kV | JH-2(L1) | 2025-04-26 17:45 | 2025-04-26 18:17 | 0.022222 | T | Tripped | 0 | 0 | No interruption
Jashore 132/33kV | Cap. Bank-1 | 2025-04-26 17:46 | 2025-04-26 19:07 | 0.05625 | T | Tripped | 0 | 0 | No interruption
Ullahpara 132/33kV | Shahjadpur Ckt | 2025-04-20 18:55 | 2025-04-26 11:26 | 1900-01-04 16:31 | E/O | Instruction By NLDC Dhaka. | 0 | 0 | No interruption
Ullahpara 132/33kV | 132 KV Sirajgonj Ckt-1 | 2025-04-26 11:26 | 2025-04-26 13:32 | 0.0875 | E/O | Instruction by ALDC Bogura | 0 | 0 | No interruption
Ullahpara 132/33kV | 132 KV Sirajgonj Ckt-2 | 2025-04-26 11:27 | 2025-04-26 13:32 | 0.086806 | E/O | Instruction by ALDC Bogura | 0 | 0 | No interruption
Ullahpara 132/33kV | Shahjadpur Ckt | 2025-04-26 13:33 | 2025-04-27 17:11 | 1899-12-31 03:38 | E/O | Instruction By ALDC Bogra. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-06 23:21 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Barapukuria 230/132/33kV | Rangpur 132 KV Ckt2 | 2025-04-13 04:51 | 2025-04-13 05:40 | 0.034028 | T | Thunderstorm | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Rangpur 132 KV Ckt1 | 2025-04-26 22:52 | 2025-04-26 23:13 | 0.014583 | T | Thunder storm of Rangpur end | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Rangpur 132 KV Ckt2 | 2025-04-26 22:52 | 2025-04-26 23:13 | 0.014583 | T | Thunder storm of Rangpur end | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Rangpur 132 KV Ckt2 | 2025-04-28 05:31 | 2025-04-28 07:08 | 0.067361 | E/O | Over voltage | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Saidpur 132 KV Ckt2 | 2025-04-28 05:32 | 2025-04-28 06:40 | 0.047222 | E/O | Over voltage | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Sherpur-Bogura Ckt-2 | 2025-04-26 11:34 | 2025-04-26 12:39 | 0.045139 | E/O | Emergency maint.work | 0 | 0 | No interruption
Bogura 132/33kV | New Bogura-2 | 2025-04-02 09:57 | 2025-04-02 11:40 | 0.071528 | E/O | Red Hot maintenance work. | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-2 | 2025-04-10 23:15 | 2025-04-10 23:15 | 0 | T | Rain and Storming. | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-2 | 2025-04-11 07:05 | 2025-04-11 07:05 | 0 | E/O | Emergency maint.work | 0 | 0 | No interruption
Bogura 230/132kV | Sherpur 132 KV Line-2 | 2025-04-26 11:33 | 2025-04-26 12:39 | 0.045833 | E/O | Red Hot Maintenance | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2025-04-06 08:39 | 2025-04-07 14:30 | 1899-12-31 05:51 | T | Line Fault | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2025-04-06 08:39 | 2025-04-07 14:30 | 1899-12-31 05:51 | T | TIE | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Rooppur 400 KV Line-1 | 2025-04-10 15:07 | 2025-04-10 15:07 | 0 | T | Earth Fault (R-Phase) | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2025-04-10 23:10 | 2025-04-11 15:29 | 0.67986 | T | Differential Fault | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2025-04-11 15:55 | 2025-04-23 16:51 | 1900-01-11 00:56 | T | Directional Earth Fault IDMT | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2025-04-13 06:22 | 2025-04-23 16:51 | 1900-01-09 10:29 | T | Directional Earth Fault IDMT (67N) pickup | 0 | 0 | No interruption
Bogura 400/230kV | 400 KV Reactor (125 MVAR) | 2025-04-21 00:54 | 2025-04-27 13:01 | 1900-01-05 12:07 | E/O | As per NLDC's instruction | 0 | 0 | No interruption
Kurigram 132/33kV | Capacitor Bank | 2025-04-12 10:35 | 2025-04-12 11:30 | 0.038194 | E/O | Due to Redhot | 0 | 0 | No interruption
Naogaon 132/33kV | Nao-Bog Ckt-2 | 2025-04-10 23:15 | 2025-04-11 10:33 | 0.47083 | T | Heavy thundering and raining. | 0 | 0 | No interruption
Palashbari 132/33kV | Mithapukur-02 | 2025-04-13 05:01 | 2025-04-13 06:21 | 0.055556 | T | Bad Weather | 0 | 0 | No interruption
Purbasadipur 132/33kV | Saidpur Line-2 | 2025-04-20 07:40 | 2025-04-20 08:25 | 0.03125 | T | Tripped | 90 | 67.5 | Power interruption
Purbasadipur 132/33kV | Thakurgaon Line-1 | 2025-04-20 07:40 | 2025-04-20 08:27 | 0.032639 | T | Tripped | 55 | 43.0833 | Power interruption
Purbasadipur 132/33kV | Saidpur Line-2 | 2025-04-28 03:50 | 2025-04-28 06:32 | 0.1125 | T | Tripped | 10 | 27 | Power interruption
Purbasadipur 132/33kV | Saidpur Line-1 | 2025-04-28 03:50 | 2025-04-28 04:15 | 0.017361 | T | Tripped | 10 | 4.1667 | Power interruption
Purbasadipur 132/33kV | Thakurgaon Line-1 | 2025-04-28 04:10 | 2025-04-28 06:32 | 0.098611 | E/O | high Voltage problem | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Barapukuria-1 | 2025-04-11 09:05 | 2025-04-11 15:03 | 0.24861 | E/O | TEMPARATURE HIGH | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Saidpur-1 | 2025-04-17 04:03 | 2025-04-17 04:26 | 0.015972 | T | Grid power Field | 20 | 7.6667 | Power interruption
Rangpur 132/33kV | Rangpur-Saidpur-2 | 2025-04-20 17:00 | 2025-04-23 20:20 | 1900-01-02 03:20 | E/O | 132 kv CB Maintenance | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Saidpur-2 | 2025-04-27 08:00 | 2025-04-27 08:00 | 0 | E/O | Emergency maint.work | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Saidpur-1 | 2025-04-27 08:02 | 2025-04-27 08:02 | 0 | E/O | Emergency maint.work | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Rangpur CKT-02 | 2025-04-15 10:38 | 2025-04-15 19:14 | 0.35833 | E/O | As the instruction of NLDC, Dhaka (299727) | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Rangpur CKT-02 | 2025-04-17 04:03 | 2025-04-19 21:19 | 1900-01-01 17:16 | T | Rain and thanderstrom. | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Rangpur CKT-01 | 2025-04-17 04:03 | 2025-04-17 05:15 | 0.05 | T | Rain and Thanderstron | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Purbosadipur CKT-01 | 2025-04-20 07:43 | 2025-04-20 08:01 | 0.0125 | T | Tripped | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Rangpur CKT-02 | 2025-04-26 22:32 | 2025-04-26 22:32 | 0 | T | Due to Rain and lightning | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Rangpur CKT-01 | 2025-04-26 22:44 | 2025-04-26 22:44 | 0 | T | Tripped | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Baropukuria CKT-02 | 2025-04-28 03:23 | 2025-04-28 04:06 | 0.029861 | T | None | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Purbosadipur CKT-02 | 2025-04-28 03:50 | 2025-04-28 06:34 | 0.11389 | T | Tripped | 0 | 0 | No interruption
Thakurgaon 132/33kV | Thakurgaon-EPV Ckt-2 | 2025-04-28 04:20 | 2025-04-28 06:36 | 0.094444 | E/O | For high voltage | 0 | 0 | No interruption
|  |  | Total : | 1900-02-08 03:03 |  | Unserved Energy: |  | 149.4167
Others :Nil
|  | (Estimated) | Total : | 0 | (Estimated) | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 1900-03-23 11:37 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
| Ashuganj-2 | 2024-11-13 12:06 | 2024-11-13 12:18
Formulas:
Duration = [Finish]-[Start]
Duration = SUM(E9:[Duration, row above])

## QF-LDC-25
QF-LDC-25
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: April 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | Bus-2 (400kV) | 2025-04-26 09:14 | 2025-04-26 21:37 | 12:23 | S/O | Development work | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Bus-1 (400kV) | 2025-04-27 07:22 | 2025-04-27 21:46 | 14:24 | S/O | Project Development work | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Bus-2 (400kV) | 2025-04-28 10:14 | 2025-04-30 21:40 | 59:26 | S/O | Project Development Work | 0 | 0 | No interruption
Bhaluka 132/33kV | Transformer- 01 LT | 2025-04-29 11:39 | 2025-04-29 12:47 | 1:08 | S/O | Metering purpose | 20 | 22.6667 | Power interruption
Bhaluka 132/33kV | Transformer- 02 | 2025-04-29 12:50 | 2025-04-29 13:37 | 0:47 | S/O | Metering purpose | 20 | 15.6667 | Power interruption
Bhaluka 132/33kV | Transformer-03 | 2025-04-29 14:09 | 2025-04-29 14:51 | 0:42 | S/O | Metering purpose | 18 | 12.6 | Power interruption
Dhamrai 132/33kV | Transformer-1 HT | 2025-04-05 07:21 | 2025-04-05 11:41 | 4:20 | S/O | Aux Tx-1 fuse and LA change | 0 | 0 | No interruption
Dhamrai 132/33kV | Transformer-2 HT | 2025-04-19 07:19 | 2025-04-19 12:50 | 5:31 | S/O | Redhot maintenance by PBS. | 0 | 0 | No interruption
Jamalpur 132/33kV | T-2 | 2025-04-09 11:15 | 2025-04-09 12:25 | 1:10 | S/O | CT Connector temperature high. | 0 | 0 | No interruption
Joydebpur 132/33kV | GT-3 | 2025-04-16 11:25 | 2025-04-16 12:50 | 1:25 | S/O | Installation Of Multifunctional Meter. | 0 | 0 | No interruption
Kabirpur 132/33kV | Aux. X-former-1 HT | 2025-04-19 06:27 | 2025-04-19 07:43 | 1:16 | S/O |  | 0 | 0 | No interruption
Kabirpur 132/33kV | XFR, T-I | 2025-04-19 06:30 | 2025-04-19 07:45 | 1:15 | S/O | High temoerature maintenance by DPBS-1 | 50 | 62.5 | Power interruption
Kabirpur 132/33kV | XFR, T-3 | 2025-04-22 23:25 | 2025-04-23 02:07 | 2:42 | S/O | High Temperature maintenance | 75 | 202.5 | Power interruption
Kabirpur 132/33kV | XFR, T-3 | 2025-04-23 13:10 | 2025-04-23 19:25 | 6:15 | S/O | High temperature maintenance | 85 | 531.25 | Power interruption
Kabirpur 132/33kV | XFR, T-3 | 2025-04-24 11:35 | 2025-04-24 14:42 | 3:07 | S/O | Shutdown taken by Dhaka PBS -1 due to High temperature maintenance work at 33KV BUS | 80 | 249.3333 | Power interruption
Kabirpur 132/33kV | XFR, T-3 | 2025-04-29 20:59 | 2025-04-29 23:05 | 2:06 | S/O | S/ D is taken by Dhaka Pbs-1 for 33 kv EPZ feeder underground cable maintenance. | 80 | 168 | Power interruption
Kaliakoir 400/230/132kV | 400/132kV TR1 LT | 2025-04-05 06:48 | 2025-04-05 10:03 | 3:15 | S/O | maintenance works | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400/132kV TR1 HT | 2025-04-07 06:36 | 2025-04-07 08:21 | 1:45 | S/O | Maintenance for high temperature issue at B phase of bushing | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400/132kV TR1 HT | 2025-04-12 06:29 | 2025-04-12 08:07 | 1:38 | S/O | Maintenance for temperature rising on B-ph bushing | 50 | 81.6667 | Power interruption
Kaliakoir 400/230/132kV | 400kV Bus 2 | 2025-04-12 09:54 | 2025-04-12 17:44 | 7:50 | S/O | Project works. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 1 | 2025-04-13 11:05 | 2025-04-13 17:52 | 6:47 | S/O | Busbar protection works. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 1 | 2025-04-17 09:57 | 2025-04-17 17:43 | 7:46 | S/O | Dismantle the D/S near the BUS -1 | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400/230kV TR2 HT | 2025-04-18 07:31 | 2025-04-18 17:34 | 10:03 | S/O | Project Work Shutdown | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400/230kV TR2 HT | 2025-04-19 07:19 | 2025-04-19 18:18 | 10:59 | S/O | Maint.work | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400/230kV TR2 LT | 2025-04-20 08:31 | 2025-04-20 15:44 | 7:13 | S/O | PROJECT WORKS | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 1 | 2025-04-22 08:07 | 2025-04-22 18:12 | 10:05 | S/O | Due to IDRNPP project work. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 1 | 2025-04-23 08:49 | 2025-04-23 17:25 | 8:36 | S/O | Project Work | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 1 | 2025-04-24 08:31 | 2025-04-24 18:27 | 9:56 | S/O | Maint.work | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 1 | 2025-04-27 07:29 | 2025-04-27 22:05 | 14:36 | S/O | Project Work | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 2 | 2025-04-28 10:26 | 2025-04-28 20:45 | 10:19 | S/O | IDRNPP project work. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 1 | 2025-04-29 10:12 | 2025-04-29 12:37 | 2:25 | S/O | IDRNPP Project work. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 2 | 2025-04-30 10:31 | 2025-04-30 12:33 | 2:02 | S/O | Project Work | 0 | 0 | No interruption
Kodda 132/33kV | Tr-3 (426T) | 2025-04-16 13:13 | 2025-04-16 14:26 | 1:13 | S/O | Red hot maintenance | 0 | 0 | No interruption
Kodda 132/33kV | Bus-2 | 2025-04-25 07:32 | 2025-04-25 12:06 | 4:34 | S/O | 132 kv summit 149 MW BDS-2 Alinement eork | 20 | 91.3333 | Power interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-3 (50/75 MVA) | 2025-04-17 13:50 | 2025-04-17 14:50 | 1:00 | S/O | Redhot removal work at 33kV side | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-2(35/50 MVA) | 2025-04-19 10:47 | 2025-04-19 12:48 | 2:01 | S/O | 33kV side CT to CB Redhot remove, 132 kV GT-2 X-former Main tank Oil filling. | 0 | 0 | No interruption
Mirpur 132/33kV | Reserve Bus | 2025-04-18 15:46 | 2025-04-18 16:51 | 1:05 | S/O | Maint.work | 0 | 0 | No interruption
New Tongi | T1(403T) HT | 2025-04-27 11:40 | 2025-04-27 12:58 | 1:18 | S/O | Multification meter connection | 0 | 0 | No interruption
Savar 132/33kV | Main Bus-I | 2025-04-07 07:48 | 2025-04-07 10:50 | 3:02 | S/O | Corrective maintenance work | 0 | 0 | No interruption
Savar 132/33kV | T-4 HT | 2025-04-07 10:48 | 2025-04-07 14:05 | 3:17 | S/O | Corrective maintenance work | 0 | 0 | No interruption
Savar 132/33kV | Main Bus-II | 2025-04-07 11:35 | 2025-04-07 13:59 | 2:24 | S/O | Corrective maintenance work | 0 | 0 | No interruption
Savar 132/33kV | T-1 HT | 2025-04-09 15:30 | 2025-04-09 15:45 | 0:15 | S/O | For the purpose of removing bird nests | 0 | 0 | No interruption
Savar 132/33kV | T-1 LT | 2025-04-18 15:36 | 2025-04-18 17:09 | 1:33 | S/O | OLTC Oil refilling | 0 | 0 | No interruption
Savar 132/33kV | T-3 LT | 2025-04-19 09:49 | 2025-04-19 14:50 | 5:01 | S/O | DS maintenance | 0 | 0 | No interruption
Savar 132/33kV | Main Bus-II | 2025-04-19 09:55 | 2025-04-19 14:50 | 4:55 | S/O | DS MAINTENANCE | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 03 HT | 2025-04-07 08:14 | 2025-04-07 18:05 | 9:51 | S/O | Blast wall Construction | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 03 HT | 2025-04-08 08:23 | 2025-04-08 17:16 | 8:53 | S/O | Blast Wall Works | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 02 HT | 2025-04-09 08:13 | 2025-04-09 17:22 | 9:09 | S/O | Maint.work | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 02 HT | 2025-04-10 08:36 | 2025-04-10 16:11 | 7:35 | S/O | Blast wall construction | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 04 LT | 2025-04-11 09:26 | 2025-04-11 17:20 | 7:54 | S/O | Fire Wall Construction Work. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 04 HT | 2025-04-12 08:23 | 2025-04-12 15:18 | 6:55 | S/O | Maint.work | 20 | 138.3333 | Power interruption
Sherpur 132/33kV | Transformer- 04 LT | 2025-04-13 10:46 | 2025-04-13 11:36 | 0:50 | S/O | Blast Wall Construction Work. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 03 LT | 2025-04-13 10:50 | 2025-04-13 12:41 | 1:51 | S/O | Blast Wall Construction Work. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 02 LT | 2025-04-13 11:38 | 2025-04-13 12:44 | 1:06 | S/O | Blast Wall Construction Work. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 02 HT | 2025-04-30 11:58 | 2025-04-30 16:48 | 4:50 | S/O | Blast wall painting | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132/33 kV T-2 HT | 2025-04-16 10:10 | 2025-04-16 14:00 | 3:50 | S/O | Maintenance of 33 kV jack bus | 50 | 191.6667 | Power interruption
Tongi 230/132/33kV | 132 kV Bus-2 | 2025-04-13 12:30 | 2025-04-13 13:42 | 1:12 | S/O | Maintenance work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-12 16:46 |  | Unserved Energy: |  | 1767.5167
Dhaka (South) Grid Circle :
Bashundhara 132/33kV | Tr-2 HT | 2025-04-09 06:41 | 2025-04-09 06:41 | 0:00 | S/O | Energy Meter Change | 0 | 0 | No interruption
Bhulta 132/33kV | GT2 HT | 2025-04-07 06:33 | 2025-04-07 07:58 | 1:25 | S/O | Red hot maintenace | 0 | 0 | No interruption
Bhulta 132/33kV | GT2 HT | 2025-04-10 21:07 | 2025-04-10 22:21 | 1:14 | S/O | Red hot maintenance | 40 | 49.3333 | Power interruption
Bhulta 400/230kV | 230kV Bus-02 | 2025-04-24 09:48 | 2025-04-24 16:46 | 6:58 | S/O | maint.work | 0 | 0 | No interruption
Cantonment 132/33kV | Auxiliary Transformer, AT-1 LT | 2025-04-04 07:07 | 2025-04-04 17:56 | 10:49 | S/O | Painting work. | 0 | 0 | No interruption
Cantonment 132/33kV | Transformer-1 (T-1) HT | 2025-04-04 07:14 | 2025-04-04 17:53 | 10:39 | S/O | Painting work. | 0 | 0 | No interruption
Cantonment 132/33kV | Auxiliary Transformer, AT-1 HT | 2025-04-04 07:21 | 2025-04-04 17:46 | 10:25 | S/O | Painting work. | 0 | 0 | No interruption
Cantonment 132/33kV | Auxiliary Transformer, AT-1 LT | 2025-04-05 07:09 | 2025-04-05 18:50 | 11:41 | S/O | Painting work. | 0 | 0 | No interruption
Cantonment 132/33kV | Transformer-1 (T-1) LT | 2025-04-05 07:10 | 2025-04-06 20:01 | 36:51 | S/O | Painting work. | 0 | 0 | No interruption
Cantonment 132/33kV | Transformer-1 (T-1) HT | 2025-04-05 07:12 | 2025-04-05 18:44 | 11:32 | S/O | Painting work. | 0 | 0 | No interruption
Cantonment 132/33kV | Auxiliary Transformer, AT-1 HT | 2025-04-05 07:20 | 2025-04-05 18:36 | 11:16 | S/O | Painting work. | 0 | 0 | No interruption
Cantonment 132/33kV | Auxiliary Transformer, AT-1 HT | 2025-04-06 07:16 | 2025-04-06 19:43 | 12:27 | S/O | Painting work. | 0 | 0 | No interruption
Cantonment 132/33kV | Transformer-1 (T-1) HT | 2025-04-06 07:22 | 2025-04-06 19:50 | 12:28 | S/O | Painting work. | 0 | 0 | No interruption
Cantonment 132/33kV | Transformer-2 (T-2) LT | 2025-04-07 07:13 | 2025-04-09 08:35 | 49:22 | S/O | Painting Work. | 0 | 0 | No interruption
Cantonment 132/33kV | Transformer-2 (T-2) HT | 2025-04-07 07:14 | 2025-04-07 18:39 | 11:25 | S/O | Painting Work. | 0 | 0 | No interruption
Cantonment 132/33kV | Auxiliary Transformer, AT-2 HT | 2025-04-07 07:17 | 2025-04-07 18:35 | 11:18 | S/O | Painting Work. | 0 | 0 | No interruption
Cantonment 132/33kV | Transformer-2 (T-2) HT | 2025-04-08 07:12 | 2025-04-08 18:35 | 11:23 | S/O | Painting Work. | 0 | 0 | No interruption
Cantonment 132/33kV | Auxiliary Transformer, AT-2 HT | 2025-04-08 07:18 | 2025-04-08 18:29 | 11:11 | S/O | Painting Work. | 0 | 0 | No interruption
Cantonment 132/33kV | Transformer-2 (T-2) HT | 2025-04-09 07:15 | 2025-04-09 19:01 | 11:46 | S/O | 132/33 KV Tr-2 Painting work | 0 | 0 | No interruption
Cantonment 132/33kV | Auxiliary Transformer, AT-2 HT | 2025-04-09 07:21 | 2025-04-09 18:57 | 11:36 | S/O | 132/33 KV Tr-2 Painting work | 0 | 0 | No interruption
Gulshan 132/33kV | MT-2 LT | 2025-04-22 07:00 | 2025-04-22 07:57 | 0:57 | S/O | Maintenance Work | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 404 T-1 HT | 2025-04-08 16:06 | 2025-04-08 16:26 | 0:20 | S/O | Bird nest cleaning | 0 | 0 | No interruption
Hasnabad 132/33kV | 33kv Main Bus | 2025-04-19 10:40 | 2025-04-19 14:13 | 3:33 | S/O | maint.work | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 424 T-5 HT | 2025-04-19 10:42 | 2025-04-19 15:53 | 5:11 | S/O | maint.work | 0 | 0 | No interruption
Hasnabad 132/33kV | 33kv Reserve Bus | 2025-04-19 14:13 | 2025-04-19 15:30 | 1:17 | S/O | maint.work | 0 | 0 | No interruption
Hasnabad 132/33kV | 33kv Reserve Bus | 2025-04-28 10:26 | 2025-04-28 13:18 | 2:52 | S/O | Dohar feeder Bus isolator problem | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-1 HT | 2025-04-05 09:03 | 2025-04-05 11:41 | 2:38 | S/O | Over temperature. | 0 | 0 | No interruption
Madanganj 132/33kV | Main Bus | 2025-04-19 10:34 | 2025-04-19 18:20 | 7:46 | S/O | maint.work | 0 | 0 | No interruption
Narshingdi 132/33kV | 132 kV Main Bus-2 | 2025-04-25 14:43 | 2025-04-25 18:00 | 3:17 | S/O | T-4 bus DS-2 maintenance work. | 0 | 0 | No interruption
Narshingdi 132/33kV | T-4 HT | 2025-04-25 14:44 | 2025-04-25 18:28 | 3:44 | S/O | T-4 bus DS-2 maintenance work. | 0 | 0 | No interruption
Nawabganj 132/33kV | TR-1 HT | 2025-04-21 13:31 | 2025-04-21 18:34 | 5:03 | S/O | 33 kV incomer-01 R-Phase CT change | 0 | 0 | No interruption
Rampura 230/132kV | 230kV Busbar-1 | 2025-04-25 07:03 | 2025-04-25 12:06 | 5:03 | S/O | Connect of Auto tx-2 to jackbus | 0 | 0 | No interruption
Rampura 230/132kV | 230kV Busbar-2 | 2025-04-25 14:45 | 2025-04-25 18:31 | 3:46 | S/O | maint.work | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-2 HT | 2025-04-29 14:16 | 2025-04-29 17:25 | 3:09 | S/O | 33 kv side , 33 KV Bus to DS loop change | 25 | 78.75 | Power interruption
|  |  | Total : | 1900-01-11 16:22 |  | Unserved Energy: |  | 128.0833
Chattogram Grid Circle :
Bakulia 132/33kV | Aux Tr-1 HT | 2025-04-16 07:08 | 2025-04-16 08:09 | 1:01 | S/O | New Aux Tr-2 loop connection and turn on. It is done from the edge of the bakalia S&D BPDB. | 0 | 0 | No interruption
Bakulia 132/33kV | T-1 (402T) LT | 2025-04-16 07:47 | 2025-04-16 08:09 | 0:22 | S/O | New Aux Tr-2 loop connection and turn on. It is done from the edge of the bakalia S&D BPDB. | 14 | 5.1333 | Power interruption
Bakulia 132/33kV | T-2 (412T) LT | 2025-04-16 07:47 | 2025-04-16 08:10 | 0:23 | S/O | New Aux Tr-2 loop connection and turn on. It is done from the edge of the bakalia S&D BPDB. | 14 | 5.3667 | Power interruption
BSRM 230/33kV | 230/33 kV Transformer-1 (125/140 MVA) HT | 2025-04-19 10:06 | 2025-04-30 11:06 | 265:00 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV | TR-01(406T) LT | 2025-04-24 07:32 | 2025-04-24 09:35 | 2:03 | S/O | Maint.work | 18 | 36.9 | Power interruption
Coxsbazar 132/33kV | T3 HT | 2025-04-11 06:10 | 2025-04-11 08:33 | 2:23 | S/O | Old auxiliary transformer energized. | 62 | 147.7667 | Power interruption
Hathazari 230/132/33kV | T-01 HT | 2025-04-23 07:32 | 2025-04-23 08:20 | 0:48 | S/O | Maint.work | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-03 LT | 2025-04-09 08:27 | 2025-04-09 16:50 | 8:23 | S/O | cleaning purpose | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-01 HT | 2025-04-09 08:29 | 2025-04-09 16:41 | 8:12 | S/O | cleaning purpose | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-02 LT | 2025-04-09 08:32 | 2025-04-09 16:51 | 8:19 | S/O | cleaning purpose | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-01 HT | 2025-04-29 08:42 | 2025-04-29 16:51 | 8:09 | S/O | 33 KV side Isolator Maintenance | 0 | 0 | No interruption
Sholosohor 132/33kV | TRAFO-01 HT | 2025-04-12 07:25 | 2025-04-12 12:11 | 4:46 | S/O | for bird nest removing and to prevent further nesting. | 0 | 0 | No interruption
Sholosohor 132/33kV | TRAFO-02 LT | 2025-04-12 07:25 | 2025-04-12 12:16 | 4:51 | S/O | for bird nest removing and to prevent further nesting. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-12 02:40 |  |  |  | 195.1667
Cumilla Grid Circle :
Ashuganj 230/132/33kV | TR-OAT-11 HT | 2025-04-08 05:57 | 2025-04-08 07:43 | 1:46 | S/O | 132kv CB hand isolator lower clamp(transformer side) B-phase temperature 230 C @1040 amp. | 0 | 0 | No interruption
Bibiana 400/230kV | ICT-02 LT | 2025-04-16 09:27 | 2025-04-16 11:16 | 1:49 | S/O | EM | 0 | 0 | No interruption
Brahmanbaria 132/33kV | 402T LT | 2025-04-10 13:30 | 2025-04-10 14:35 | 1:05 | S/O | Project Work | 0 | 0 | No interruption
Chandina 132/33kV | TR-3 HT | 2025-04-23 10:33 | 2025-04-23 17:46 | 7:13 | S/O | Project Work | 0 | 0 | No interruption
Chandina 132/33kV | TR-2 HT | 2025-04-23 10:34 | 2025-04-23 17:41 | 7:07 | S/O | Project Work | 0 | 0 | No interruption
Chandina 132/33kV | TR-2 HT | 2025-04-29 11:30 | 2025-04-29 15:16 | 3:46 | S/O | Project Work | 0 | 0 | No interruption
Chandina 132/33kV | TR-2 HT | 2025-04-30 10:34 | 2025-04-30 16:19 | 5:45 | S/O | Project Work | 0 | 0 | No interruption
Chauddagram 132/33kV | 132 kv T-2 HT | 2025-04-06 08:33 | 2025-04-06 11:21 | 2:48 | S/O | Cumilla PBS-2 Taken S/D due to loop connection Red-hot maintenance. | 23 | 64.4 | Power interruption
Chauddagram 132/33kV | 132 kv T-1 HT | 2025-04-09 08:18 | 2025-04-09 11:50 | 3:32 | S/O | CUmillaPBS-2 taken S/D for Red hot maintenance. | 20 | 70.6667 | Power interruption
Chauddagram 132/33kV | 132 kv T-2 HT | 2025-04-23 07:11 | 2025-04-23 12:05 | 4:54 | S/O | Maint.work | 0 | 0 | No interruption
Chauddagram 132/33kV | 132 kv T-1 LT | 2025-04-24 07:50 | 2025-04-24 10:22 | 2:32 | S/O | Red hot maintenance | 0 | 0 | No interruption
Chowmuhani 132/33kV | TR3-435T HT | 2025-04-26 08:52 | 2025-04-26 16:20 | 7:28 | S/O | 33KV Bus section of T-03 shutdown taken by BPDB and LPBS & NPBS. | 20 | 149.3333 | Power interruption
Cumilla(N) 230/132/33kV | 230KV ATR-03 HT | 2025-04-19 06:42 | 2025-04-19 11:00 | 4:18 | S/O | Maint.work | 0 | 0 | No interruption
Cumilla(S) 132/33kV | TR-2 HT | 2025-04-11 16:07 | 2025-04-12 14:10 | 22:03 | S/O | Energypac commissioning work. | 0 | 0 | No interruption
Cumilla(S) 132/33kV | TR-3 HT | 2025-04-17 21:57 | 2025-04-17 21:58 | 0:01 | S/O | Maint.work | 0 | 0 | No interruption
Feni 132/33kV | T-1(405T) LT | 2025-04-17 13:44 | 2025-04-17 18:18 | 4:34 | S/O | For Ten Delta Test By RTS | 0 | 0 | No interruption
Kasba 132/33kV | TR-1 HT | 2025-04-26 13:14 | 2025-04-26 15:12 | 1:58 | S/O | Shutdown taken by PBS for Redhot Maintanace. | 0 | 0 | No interruption
Kasba 132/33kV | TR-2 HT | 2025-04-26 15:33 | 2025-04-26 16:37 | 1:04 | S/O | Shutdown taken by redhot maintenance | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 HT | 2025-04-07 08:00 | 2025-04-07 09:33 | 1:33 | S/O | REB-2 feeder Red Hot maintenance | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 HT | 2025-04-16 07:20 | 2025-04-16 17:53 | 10:33 | S/O | TR-3 Development work | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 LT | 2025-04-17 14:00 | 2025-04-17 21:06 | 7:06 | S/O | TR-3 Relay testing | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 HT | 2025-04-17 14:01 | 2025-04-17 21:05 | 7:04 | S/O | TR-3 Relay testing | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 LT | 2025-04-20 13:53 | 2025-04-20 16:06 | 2:13 | S/O | for Tr- 01 (B) DS maintenance | 0 | 0 | No interruption
Ramganj 132/33kV | Transformer -02 LT | 2025-04-30 06:31 | 2025-04-30 07:46 | 1:15 | S/O | Red hot maintenance of 33 kv PBS feeder | 35 | 43.75 | Power interruption
Shahjibazar 132/33kV | TR-04 HT | 2025-04-13 08:49 | 2025-04-13 12:25 | 3:36 | S/O | Shutdown taken by PDB | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 LT | 2025-04-13 08:59 | 2025-04-13 12:26 | 3:27 | S/O | Shutdown Taken by PDB | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 HT | 2025-04-24 06:48 | 2025-04-24 09:46 | 2:58 | S/O | Shutdown taken by PBS | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 HT | 2025-04-24 07:05 | 2025-04-24 09:40 | 2:35 | S/O | Shutdown taken by PBS | 0 | 0 | No interruption
|  |  | Total : | 1900-01-04 06:03 |  |  |  | 328.15
Khulna Grid Circle :
Bagerhat 132/33kV | 132 kV BUS | 2025-04-21 17:10 | 2025-04-21 18:33 | 1:23 | S/O | 132 Tr2 bus side red hot maintenance work | 65 | 89.9167 | Power interruption
Bagerhat 132/33kV | Transformer-3 ( 423 T) HT | 2025-04-27 16:32 | 2025-04-27 17:56 | 1:24 | S/O | 33 kv Fakirhat-2 feeder red hot maintenance work. | 20 | 28 | Power interruption
Barguna 132/33kV | Transformer-1 HT | 2025-04-16 09:53 | 2025-04-16 11:12 | 1:19 | S/O | Emergency Maintenance for BREB-2(Betagi) Feeder | 4 | 5.2667 | Power interruption
Barishal 132/33kV | T-1 (405T) HT | 2025-04-04 07:28 | 2025-04-04 08:47 | 1:19 | S/O | Red hot remove at 33 kV busber (Padma bowing) under 132 kV T1 Transformer. | 50 | 65.8333 | Power interruption
Barishal 132/33kV | T-1 (405T) HT | 2025-04-28 23:11 | 2025-04-29 00:30 | 1:19 | S/O | To remove red hot problem | 30 | 39.5 | Power interruption
Barishal 132/33kV | T-2 (415T) HT | 2025-04-29 06:10 | 2025-04-29 07:38 | 1:28 | S/O | To remove red hot problem. | 0 | 0 | No interruption
Barishal 230/132kV | ATR-2 HT | 2025-04-07 09:47 | 2025-04-07 13:03 | 3:16 | S/O | oil leakage repair oltc | 0 | 0 | No interruption
Barishal 230/132kV | T-4 HT | 2025-04-12 07:22 | 2025-04-12 10:49 | 3:27 | S/O | Red Hot Repair at 33 Bus | 21 | 72.45 | Power interruption
Barishal 230/132kV | T-5 HT | 2025-04-12 07:22 | 2025-04-12 13:03 | 5:41 | S/O | Red Hot Repair | 21 | 119.35 | Power interruption
Barishal 230/132kV | T-5 HT | 2025-04-13 11:21 | 2025-04-13 15:28 | 4:07 | S/O | CB spring charged problem. | 0 | 0 | No interruption
Barishal 230/132kV | T-5 LT | 2025-04-13 16:51 | 2025-04-13 18:54 | 2:03 | S/O | Barisal PBS_2 take shutdown for DS maintenance | 33 | 67.65 | Power interruption
Barishal 230/132kV | T-5 HT | 2025-04-14 06:10 | 2025-04-14 07:30 | 1:20 | S/O | Banaripara 33 kV feeder bus DS maintenance work | 41 | 54.6667 | Power interruption
Barishal 230/132kV | T-4 HT | 2025-04-19 08:54 | 2025-04-19 13:10 | 4:16 | S/O | BCIC 33kv fedder bus DS maintenance work. | 8 | 34.1333 | Power interruption
Bhandaria 132/33kV | Transformer-1 HT | 2025-04-26 06:13 | 2025-04-26 13:05 | 6:52 | S/O | EEGBPSB Project work. | 35 | 240.3333 | Power interruption
Bhandaria 132/33kV | Transformer-2 HT | 2025-04-26 06:14 | 2025-04-26 13:09 | 6:55 | S/O | EEGBPSB Project work. | 35 | 242.0833 | Power interruption
Faridpur 132/33kV | ATR-2 HT | 2025-04-30 09:42 | 2025-04-30 09:42 | 0:00 | S/O | ATR-2 WTI Checking | 0 | 0 | No interruption
Goalpara 132/33kV | T-6 HT | 2025-04-12 09:44 | 2025-04-12 12:42 | 2:58 | S/O | Shutdown taken by wzpdcl | 5 | 14.8333 | Power interruption
Goalpara 132/33kV | T-5 HT | 2025-04-12 09:44 | 2025-04-12 12:42 | 2:58 | S/O | Shutdown taken by wzpdcl | 5 | 14.8333 | Power interruption
Goalpara 132/33kV | T-5 HT | 2025-04-20 07:41 | 2025-04-20 09:15 | 1:34 | S/O | PBS taken SD | 3 | 4.7 | Power interruption
Goalpara 132/33kV | T-6 HT | 2025-04-20 07:46 | 2025-04-20 09:10 | 1:24 | S/O | PBS taken SD | 3 | 4.2 | Power interruption
Gopalganj 400/132kV | 400kV Bus-01 | 2025-04-14 10:50 | 2025-04-14 13:29 | 2:39 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Bus-01 | 2025-04-19 10:52 | 2025-04-19 15:38 | 4:46 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Bus-01 | 2025-04-20 07:19 | 2025-04-20 21:34 | 14:15 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Bus-01 | 2025-04-21 07:20 | 2025-04-21 19:50 | 12:30 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Bus-01 | 2025-04-22 07:39 | 2025-04-22 18:19 | 10:40 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Bus-02 | 2025-04-23 07:35 | 2025-04-23 21:21 | 13:46 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Bus-02 | 2025-04-24 07:30 | 2025-04-24 19:54 | 12:24 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Bus-02 | 2025-04-25 07:47 | 2025-04-25 19:39 | 11:52 | S/O | Maint.work | 0 | 0 | No interruption
Khulna (C) | Tr-2 415 T HT | 2025-04-12 10:26 | 2025-04-12 12:26 | 2:00 | S/O | 33kv newly installed feeder's Bus loop( Riser) connection purpose. | 0 | 0 | No interruption
Narail 132/33kV | TR2 (413-T) HT | 2025-04-11 07:22 | 2025-04-11 10:00 | 2:38 | S/O | 33kV N5 and N8 Feeder Red hot Maintenance | 25 | 65.8333 | Power interruption
Narail 132/33kV | TR1 (403-T) LT | 2025-04-26 09:00 | 2025-04-26 09:00 | 0:00 | S/O | 33 kv bay extension work. | 0 | 0 | No interruption
Noapara 132/33kV | BUS A | 2025-04-12 10:28 | 2025-04-12 12:04 | 1:36 | S/O | Maint.work | 0 | 0 | No interruption
Payra 400/132/33kV | 400/132/33 kV Auto Transformer-02 HT | 2025-04-10 06:05 | 2025-04-10 06:55 | 0:50 | S/O | High temperature point | 0 | 0 | No interruption
Rajbari 132/33kV | Transformer-1 LT | 2025-04-09 12:28 | 2025-04-09 13:15 | 0:47 | S/O | OLTC Oil Samples collection... | 0 | 0 | No interruption
Rajbari 132/33kV | Transformer-3 HT | 2025-04-24 15:18 | 2025-04-27 16:50 | 73:32 | S/O | SAS Integration works. | 0 | 0 | No interruption
Rajbari 132/33kV | 132 kV Bus-I | 2025-04-25 15:49 | 2025-04-27 16:36 | 48:47 | S/O | T-3 SAS Work. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-10 04:05 |  | Unserved Energy : |  | 1163.5833
HVDC Grid Circle
Bhangura 132/33kV | Tr-2(413T) LT | 2025-04-18 03:37 | 2025-04-18 12:46 | 9:09 | S/O | Project development work | 10 | 91.5 | Power interruption
Bhangura 132/33kV | Tr-1(403T) LT | 2025-04-18 04:35 | 2025-04-18 12:45 | 8:10 | S/O | Project development work | 10 | 81.6667 | Power interruption
Bhangura 132/33kV | 132KV Single Bus | 2025-04-18 04:40 | 2025-04-18 12:43 | 8:03 | S/O | Project development work | 10 | 80.5 | Power interruption
Bheramara 230/132kV | Bus-A (132) | 2025-04-23 08:34 | 2025-04-24 16:43 | 32:09 | S/O | ishurdi ckt 1&2 Reconducting | 0 | 0 | No interruption
BIPTC | 20D09C 20MVA HT | 2025-04-18 07:51 | 2025-04-18 13:10 | 5:19 | S/O | 20D09C 20MVA Auxiliary Trafo-1 tripped by 87T (Differential Relay) Over Current Stage-2 Operated | 0 | 0 | No interruption
BIPTC | 20DF11 | 2025-04-07 11:40 | 2025-04-07 16:32 | 4:52 | S/O | Due to maint.work | 0 | 0 | No interruption
Jhenaidah 132/33kV | Transformer T-2 HT | 2025-04-08 07:30 | 2025-04-08 09:28 | 1:58 | S/O | 33kV WZPDCL Bus Section 1&2 B Phase Red Hot Maintenance Work. | 30 | 59 | Power interruption
Kushtia 132/33kV | T-1 HT | 2025-04-11 07:02 | 2025-04-11 09:23 | 2:21 | S/O | T-1 33kv bushing B-phase red hot maintenance | 0 | 0 | No interruption
Magura 132/33kV | T-3 (425T) HT | 2025-04-26 06:36 | 2025-04-26 15:49 | 9:13 | S/O | 33kv Bay extension of PBS | 12 | 110.6 | Power interruption
Pabna 132/33kV | T-3 HT | 2025-04-26 09:30 | 2025-04-26 16:15 | 6:45 | S/O | Oil Leakage Maintenance | 8 | 54 | Power interruption
Ullahpara 132/33kV | Power Transformer -1 LT | 2025-04-15 13:46 | 2025-04-15 14:03 | 0:17 | S/O | Energy Meter Changing work of 33kV Incomer-1 by Energy Audit Unit, Bogura. | 0 | 0 | No interruption
Ullahpara 132/33kV | Power Transformer -1 HT | 2025-04-15 13:48 | 2025-04-15 13:56 | 0:08 | S/O | Energy Meter Changing work of 33kV Incomer-1 by Energy Audit Unit, Bogura. | 0 | 0 | No interruption
Ullahpara 132/33kV | Power Transformer-2 LT | 2025-04-15 14:05 | 2025-04-15 14:15 | 0:10 | S/O | Energy Meter Changing work of 33kV Incomer-2 by Energy Audit Unit, Bogura. | 0 | 0 | No interruption
Ullahpara 132/33kV | Power Transformer-2 HT | 2025-04-15 14:06 | 2025-04-15 14:14 | 0:08 | S/O | Energy Meter Changing work of 33kV Incomer-2 by Energy Audit Unit, Bogura. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 16:42 |  | Unserved Energy : |  | 477.2667
Bogura Grid Circle:
Barapukuria 230/132/33kV | 132/33 KV T-3, 404T HT | 2025-04-19 11:12 | 2025-04-19 13:18 | 2:06 | S/O | Maintenance work. | 15 | 31.5 | Power interruption
Barapukuria 230/132/33kV | 132/33 KV T-5, 424T HT | 2025-04-26 09:12 | 2025-04-26 21:00 | 11:48 | S/O | Maintenance work. | 0 | 0 | No interruption
Bogura 230/132kV | T-04 HT | 2025-04-02 09:34 | 2025-04-02 11:44 | 2:10 | S/O | Bogura132 kv ckt-02, Q2 DS Finger Change, | 0 | 0 | No interruption
Bogura 400/230kV | ATR-02 HT | 2025-04-10 11:07 | 2025-04-10 14:36 | 3:29 | S/O | ATR-02 Punch list Problem Resolving. | 0 | 0 | No interruption
Kurigram 132/33kV | Transformer T-1 (Tr-403T) LT | 2025-04-16 07:38 | 2025-04-16 09:25 | 1:47 | S/O | Equipment loop connection tightening. | 0 | 0 | No interruption
Naogaon 132/33kV | T-1 HT | 2025-04-16 07:05 | 2025-04-16 08:40 | 1:35 | S/O | 33 KV T-1 Bus PT Y-Phase Oil leakage maintenance. | 35 | 55.4167 | Power interruption
Naogaon 132/33kV | T-3 HT | 2025-04-19 07:13 | 2025-04-19 09:23 | 2:10 | S/O | Baludanga 33 KV feeder (NESCO) Bus DS Emergency maintenance under Transformer-3 (425T). | 0 | 0 | No interruption
Naogaon 132/33kV | T-3 33kV BUS | 2025-04-19 07:18 | 2025-04-19 09:24 | 2:06 | S/O | Baludanga 33 KV feeder (NESCO) Bus DS Emergency maintenance under Transformer-3 (425T). | 0 | 0 | No interruption
Naogaon 132/33kV | T-1 HT | 2025-04-25 08:26 | 2025-04-25 09:54 | 1:28 | S/O | 33KV busbar PT maintenance work by Nesco. | 0 | 0 | No interruption
Natore 132/33kV | TR-1 (405 T) HT | 2025-04-25 06:30 | 2025-04-25 09:24 | 2:54 | S/O | Red hot maintenance and CT to CB conductor change. | 0 | 0 | No interruption
Panchagarh 132/33kV | T-3(A+B)(427T) HT | 2025-04-30 07:35 | 2025-04-30 11:43 | 4:08 | S/O | 33 kv Bus Section-03 Maintenance work (Nesco CB junction point Redhot) | 3 | 12.4 | Power interruption
Purbasadipur 132/33kV | T-1 Transformer (403T) HT | 2025-04-26 07:42 | 2025-04-26 10:10 | 2:28 | S/O | Maintenance work. | 25 | 61.6667 | Power interruption
Saidpur 132/33kV | TR-01 HT | 2025-04-15 08:54 | 2025-04-15 19:38 | 10:44 | S/O | QF- GMD- 39 and as the instruction of ALDC, Bogura (499264) | 0 | 0 | No interruption
Saidpur 132/33kV | BUS A | 2025-04-15 09:20 | 2025-04-15 19:02 | 9:42 | S/O | QF- GMD- 39 and as the instruction of ALDC, Bogura (499264) | 0 | 0 | No interruption
Saidpur 132/33kV | TR-01 HT | 2025-04-16 08:46 | 2025-04-16 13:21 | 4:35 | S/O | QF- GMD- 39 and as the instruction of ALDC, Bogura (499264) | 0 | 0 | No interruption
Saidpur 132/33kV | BUS A | 2025-04-16 09:15 | 2025-04-16 12:25 | 3:10 | S/O | QF- GMD- 39 and as the instruction of ALDC, Bogura (499264) | 0 | 0 | No interruption
Saidpur 132/33kV | BUS B | 2025-04-16 12:50 | 2025-04-16 17:55 | 5:05 | S/O | QF- GMD- 39 and as the instruction of ALDC, Bogura (499264) | 0 | 0 | No interruption
Thakurgaon 132/33kV | T-3(432T) HT | 2025-04-06 09:04 | 2025-04-06 12:05 | 3:01 | S/O | Maintenance work. | 0 | 0 | No interruption
Thakurgaon 132/33kV | T-1(422T) LT | 2025-04-23 13:40 | 2025-04-23 14:27 | 0:47 | S/O | Red hot at Incoming CT Clamp | 14 | 10.9667 | Power interruption
|  |  | Total : | 1900-01-02 03:13 |  | Unserved Energy : |  | 171.95
Others :Nil
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1505:51 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:April 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | Meghnaghat-01 | 2025-04-09 08:41 | 2025-04-09 17:11 | 8:30 | S/O | Disc changing Work | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Meghnaghat-02 | 2025-04-10 08:27 | 2025-04-10 16:08 | 7:41 | S/O | Disk cleaning Works | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Meghnaghat-01 | 2025-04-20 10:10 | 2025-04-20 18:16 | 8:06 | S/O | Disc cleaning | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Meghnaghat-01 | 2025-04-21 10:38 | 2025-04-21 18:19 | 7:41 | S/O | Disc cleaning | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Meghnaghat-01 | 2025-04-22 10:34 | 2025-04-22 16:51 | 6:17 | S/O | Disc cleaning work | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Meghnaghat-02 | 2025-04-23 10:01 | 2025-04-23 18:01 | 8:00 | S/O | Disc cleaning works. | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Meghnaghat-02 | 2025-04-24 10:43 | 2025-04-24 17:05 | 6:22 | S/O | Disc cleaning work | 0 | 0 | No interruption
Bhaluka 132/33kV | BR Powergen Ckt- 01 | 2025-04-21 14:28 | 2025-04-21 15:28 | 1:00 | S/O | N to N test | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-02 | 2025-04-16 09:28 | 2025-04-16 12:42 | 3:14 | S/O | Maint.work | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-01 | 2025-04-22 06:59 | 2025-04-22 13:41 | 6:42 | S/O | Work on mymensingh grid substation | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-02 | 2025-04-22 13:45 | 2025-04-22 19:15 | 5:30 | S/O | G2G work purpose. | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-01 | 2025-04-26 09:41 | 2025-04-26 14:14 | 4:33 | S/O | G2g | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Kodda ckt-1 | 2025-04-18 06:45 | 2025-04-18 21:36 | 14:51 | S/O | Maint.work | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Kodda ckt-2 | 2025-04-18 06:45 | 2025-04-18 21:32 | 14:47 | S/O | Maint.work | 0 | 0 | No interruption
Kabirpur 132/33kV | Tongi-1 | 2025-04-06 12:24 | 2025-04-06 13:56 | 1:32 | S/O | Conductor armaring. | 30 | 46 | Power interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Aminbazar Ckt-01 | 2025-04-10 07:23 | 2025-04-10 13:09 | 5:46 | S/O | Maint.work | 0 | 0 | No interruption
Kodda 132/33kV | Rajendrapur Ckt-1 | 2025-04-25 06:58 | 2025-04-25 14:36 | 7:38 | S/O | Bus 2 s/d | 0 | 0 | No interruption
Kodda 132/33kV | Summit 149 MW PS | 2025-04-25 07:17 | 2025-04-25 12:20 | 5:03 | S/O | BDS-2 alinement work | 0 | 0 | No interruption
Manikganj 132/33kV | Manikganj- Kabirpur CKT-2 | 2025-04-19 10:47 | 2025-04-19 12:45 | 1:58 | S/O | 33kV side CT to CB Redhot remove, 132 kV GT-2 X-former Main tank Oil filling. | 0 | 0 | No interruption
Mirpur 132/33kV | Aminbazar-2 | 2025-04-18 07:58 | 2025-04-18 18:20 | 10:22 | S/O | CVT, LA and Loop of DS Replacement work | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Jamalpur Ckt-2 | 2025-04-16 09:28 | 2025-04-16 11:20 | 1:52 | S/O | Tree trimming at Mymensingh end. | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Jamalpur Ckt-1 | 2025-04-22 06:59 | 2025-04-22 13:42 | 6:43 | S/O | LILO connection of ERS tower at Muktagachha end | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Netrakona Ckt-2 | 2025-04-22 07:10 | 2025-04-22 07:55 | 0:45 | S/O | At Net end | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Netrakona Ckt-1 | 2025-04-22 07:14 | 2025-04-22 07:46 | 0:32 | S/O | At Net end. | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Jamalpur Ckt-2 | 2025-04-22 13:44 | 2025-04-22 19:14 | 5:30 | S/O | Lilo connection of ERS Tower at Muktagasa ( Jamalpur-2 ckt) | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Jamalpur Ckt-1 | 2025-04-26 11:45 | 2025-04-26 14:13 | 2:28 | S/O | Maint.work | 0 | 0 | No interruption
Rajendrapur 132/33kV | Kodda-1 | 2025-04-25 06:42 | 2025-04-25 14:42 | 8:00 | S/O | Kodda end bus shutdown purpose. | 0 | 0 | No interruption
Savar 132/33kV | 132kV Manikganj PS-Savar Ckt-1 | 2025-04-07 07:52 | 2025-04-07 09:01 | 1:09 | S/O | Corrective maintenance work. | 0 | 0 | No interruption
Savar 132/33kV | 132kV Manikganj PS-Savar Ckt-2 | 2025-04-07 09:02 | 2025-04-07 09:47 | 0:45 | S/O | Corrective maintenance work. | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Summit PS(Kodda) | 2025-04-11 06:29 | 2025-04-11 16:08 | 9:39 | S/O | Shutdown taken by NLDC | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Summit PS(Kodda) | 2025-04-14 05:34 | 2025-04-14 15:08 | 9:34 | S/O | Shutdown taken by NLDC | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2025-04-17 07:09 | 2025-04-17 08:23 | 1:14 | S/O | Shutdown taken by NLDC | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2025-04-17 07:09 | 2025-04-17 08:23 | 1:14 | S/O | Maint.work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-06 16:58 |  | Unserved Energy: |  | 46
Dhaka (South) Grid Circle :
Bhulta 132/33kV | Haripur | 2025-04-07 08:43 | 2025-04-07 10:26 | 1:43 | S/O | Red hot maintenace | 0 | 0 | No interruption
Fatullah 132/33kV | 132 kV Madanganj | 2025-04-19 10:15 | 2025-04-19 12:17 | 2:02 | S/O | Maintenance | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi circuit-1 | 2025-04-08 06:53 | 2025-04-08 17:50 | 10:57 | S/O | Manikganj 132/33 Kv Grid For ERS work at Ishwardi line-1 | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi circuit-1 | 2025-04-10 06:33 | 2025-04-10 11:35 | 5:02 | S/O | Ruppoor Transmission line project work | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi Circuit-2 | 2025-04-10 06:33 | 2025-04-10 11:40 | 5:07 | S/O | Ruppoor Transmission line project work | 0 | 0 | No interruption
Haripur 230/132kV | Madanganj-1 | 2025-04-22 13:27 | 2025-04-22 16:16 | 2:49 | S/O | Work on another side. | 0 | 0 | No interruption
Hasnabad 230/132kV | Shyampur-APR-Hasnabad Ckt-2 | 2025-04-28 07:03 | 2025-04-29 19:52 | 36:49 | S/O | OPGW Maintenance work. | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj-Fatullah 132KV Ckt | 2025-04-19 10:16 | 2025-04-19 12:18 | 2:02 | S/O | red hot maintenance | 0 | 0 | No interruption
Meghnaghat 230/132kV | Meghnaghat-Start Up(MPL) | 2025-04-20 13:05 | 2025-04-20 17:33 | 4:28 | S/O | as per request of NLDC | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-1 | 2025-04-09 08:46 | 2025-04-09 17:11 | 8:25 | S/O | Requested by NLDC | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-1 | 2025-04-20 10:28 | 2025-04-20 18:15 | 7:47 | S/O | Requested by Aminbazar | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-1 | 2025-04-21 11:00 | 2025-04-21 18:20 | 7:20 | S/O | Requested by Aminbazar | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-1 | 2025-04-22 10:45 | 2025-04-22 16:51 | 6:06 | S/O | Maintenance Purpose | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-2 | 2025-04-23 10:02 | 2025-04-23 18:02 | 8:00 | S/O | Requested by LDC | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-2 | 2025-04-24 11:14 | 2025-04-24 17:06 | 5:52 | S/O | Maintenance Purpose | 0 | 0 | No interruption
Rampura 230/132kV | Moghbazar-02 | 2025-04-03 09:40 | 2025-04-03 09:40 | 0:00 | S/O | Taken by DPDC | 0 | 0 | No interruption
Rampura 230/132kV | Ullon-02 | 2025-04-03 09:40 | 2025-04-03 16:43 | 7:03 | S/O | Taken by DPDC | 0 | 0 | No interruption
Rampura 230/132kV | Basundhara-02 | 2025-04-05 07:14 | 2025-04-05 12:59 | 5:45 | S/O | High-temperature maintenance work at the tower attached to Basundhara grid SS. | 0 | 0 | No interruption
Rampura 230/132kV | Dhaka University - 01 | 2025-04-15 08:35 | 2025-04-15 11:00 | 2:25 | S/O | GIS bay Maintenance Taken by DPDC | 0 | 0 | No interruption
Haripur 230/132kV | 132KV Bhulta-1 (Old Narsingdi) | 2025-04-13 10:49 | 2025-04-13 14:38 | 3:49 | S/O | Project work | 0 | 0 | No interruption
Haripur 230/132kV | 132KV Bhulta-2 | 2025-04-30 10:15 | 2025-04-30 10:15 | 0:00 | S/O | Maint.work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-04 13:31 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Baroaulia 132/33kV | KSRM | 2025-04-09 08:38 | 2025-04-09 15:50 | 7:12 | S/O | Maintenance work at ksrm end | 0 | 0 | No interruption
BSRM 230/33kV | Cumilla Ckt-2 | 2025-04-13 06:04 | 2025-04-13 19:49 | 13:45 | S/O | Feni 230kV LILO | 0 | 0 | No interruption
BSRM 230/33kV | GPH Ispat Ckt. -01 | 2025-04-14 08:17 | 2025-04-14 09:35 | 1:18 | S/O | Kite remove | 0 | 0 | No interruption
BSRM 230/33kV | Cumilla Ckt-2 | 2025-04-15 08:27 | 2025-04-15 14:05 | 5:38 | S/O | CONDUCTOR REPLACE | 0 | 0 | No interruption
BSRM 230/33kV | Cumilla Ckt-1 | 2025-04-16 06:10 | 2025-04-16 14:31 | 8:21 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-1 | 2025-04-16 08:36 | 2025-04-16 19:45 | 11:09 | S/O | For disk change. 27 MW interruption matarbari around 3Hour. | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-2 | 2025-04-19 10:08 | 2025-04-19 16:44 | 6:36 | S/O | disk cleaning | 0 | 0 | No interruption
KSRM 132/33kV | Baraulia Main | 2025-04-09 08:35 | 2025-04-09 16:54 | 8:19 | S/O | Trimming tree | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Sikalbaha ckt | 2025-04-12 10:53 | 2025-04-12 11:50 | 0:57 | S/O | Emergency Maintenance work | 0 | 0 | No interruption
Rampur 230/132/33 | Khulshi-1 | 2025-04-19 10:27 | 2025-04-19 13:56 | 3:29 | S/O | red ot maintenance | 0 | 0 | No interruption
Shikalbaha 230/132kV | Julda | 2025-04-22 15:08 | 2025-04-22 17:52 | 2:44 | S/O | Maint.work | 0 | 0 | No interruption
|  |  | Total : | 69:28 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Chandpur 132/33kV | Chandpur-Kachua Ckt-2 | 2025-04-21 13:25 | 2025-04-21 14:54 | 1:29 | S/O | Maintenance | 0 | 0 | No interruption
Chandpur 132/33kV | 115MW CPGL Power Plant Incomer (L5) | 2025-04-22 14:10 | 2025-04-22 16:26 | 2:16 | S/O | CPGL maintenance work | 0 | 0 | No interruption
Chowmuhani 132/33kV | Ramganj line-01 | 2025-04-30 09:11 | 2025-04-30 16:25 | 7:14 | S/O | Maggar and parameter test | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Meghnagat Ckt-2 | 2025-04-06 16:38 | 2025-04-07 01:05 | 8:27 | S/O | Isulator (Q3) T-Phase High temp. Maintenance works | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Meghnagat Ckt 1 | 2025-04-07 10:43 | 2025-04-07 16:15 | 5:32 | S/O | Maint.work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-BSRM Ckt-2 | 2025-04-13 06:05 | 2025-04-13 19:49 | 13:44 | S/O | Disk Cleaning & Feni Project Work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-BSRM Ckt-2 | 2025-04-15 08:29 | 2025-04-15 14:06 | 5:37 | S/O | Project work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-BSRM Ckt-1 | 2025-04-16 06:11 | 2025-04-16 14:32 | 8:21 | S/O | Line maintenance | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Meghnagat Ckt-2 | 2025-04-18 06:12 | 2025-04-18 14:46 | 8:34 | S/O | Maint.work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Bibiyana-1 | 2025-04-13 09:18 | 2025-04-13 17:18 | 8:00 | S/O | due to deadline checking | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Bibiyana-1 | 2025-04-15 08:59 | 2025-04-15 16:53 | 7:54 | S/O | Deadline checking. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Bibiyana-2 | 2025-04-16 08:52 | 2025-04-16 18:42 | 9:50 | S/O | Deadline checking. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Bibiyana-2 | 2025-04-17 08:37 | 2025-04-17 18:11 | 9:34 | S/O | Deadline checking | 0 | 0 | No interruption
Kachua 132/33kV | Chandpur CKT-2 | 2025-04-21 13:15 | 2025-04-21 14:52 | 1:37 | S/O | Emergency maintenance of Earth wire connection at tower no 61. | 0 | 0 | No interruption
Ramganj 132/33kV | Ramgonj-Chowmuhani Ckt-01 | 2025-04-30 09:12 | 2025-04-30 16:25 | 7:13 | S/O | order from NLDC | 0 | 0 | No interruption
|  |  | Total : | 1900-01-03 09:22 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2025-04-26 06:19 | 2025-04-26 12:57 | 6:38 | S/O | SD Taken from bhandaria end | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2025-04-29 07:23 | 2025-04-29 15:31 | 8:08 | S/O | Due to maint.work | 0 | 0 | No interruption
Barishal 132/33kV | 132 kV Barishal north ckt-2 | 2025-04-16 10:23 | 2025-04-18 14:50 | 52:27 | S/O | For new Relay install work. | 0 | 0 | No interruption
Barishal 230/132kV | Barishal ckt-02 | 2025-04-16 10:23 | 2025-04-18 14:40 | 52:17 | S/O | S/d taken by Barishal 132/33kv s.stn. | 0 | 0 | No interruption
Bhandaria 132/33kV | Barishal (L4) | 2025-04-26 06:14 | 2025-04-26 12:55 | 6:41 | S/O | EEGBPSB Project work. | 35 | 233.9167 | Power interruption
Bhandaria 132/33kV | Bagerhat (L3) | 2025-04-26 06:25 | 2025-04-26 13:10 | 6:45 | S/O | EEGBPSB Project work. | 35 | 236.25 | Power interruption
Bhandaria 132/33kV | Bagerhat (L3) | 2025-04-29 07:45 | 2025-04-29 15:27 | 7:42 | S/O | EEGBPSB project work. | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Khulna Central-2 | 2025-04-26 18:59 | 2025-04-28 17:17 | 46:18 | S/O | Due to maint.work | 0 | 0 | No interruption
Gollamari 132/33kV | E03 Gollamari-Khulna(S) Line-1 | 2025-04-09 09:01 | 2025-04-09 16:26 | 7:25 | S/O | Due to maint.work | 0 | 0 | No interruption
Gollamari 132/33kV | E03 Gollamari-Khulna(S) Line-1 | 2025-04-10 08:50 | 2025-04-10 16:33 | 7:43 | S/O | Control Building | 0 | 0 | No interruption
Gollamari 132/33kV | E05 Gollamari-Khulna(S) Line-2 | 2025-04-12 09:28 | 2025-04-12 17:01 | 7:33 | S/O | Control Building Painting Work | 0 | 0 | No interruption
Gollamari 132/33kV | E05 Gollamari-Khulna(S) Line-2 | 2025-04-13 08:48 | 2025-04-13 16:30 | 7:42 | S/O | Control Building Painting | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Faridpur Ckt-1 | 2025-04-19 09:27 | 2025-04-19 14:16 | 4:49 | S/O | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Faridpur Ckt-2 | 2025-04-19 09:36 | 2025-04-19 14:17 | 4:41 | S/O | Due to maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Gallamari Ckt-1 | 2025-04-09 08:59 | 2025-04-09 16:25 | 7:26 | S/O | Due to maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Gallamari Ckt-1 | 2025-04-10 08:50 | 2025-04-10 16:32 | 7:42 | S/O | Due to maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Gallamari Ckt-2 | 2025-04-12 09:20 | 2025-04-12 17:02 | 7:42 | S/O | Due to maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Gallamari Ckt-2 | 2025-04-13 08:49 | 2025-04-13 16:31 | 7:42 | S/O | Maintenance Work at Gallamari S/S end. | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-1 | 2025-04-13 09:16 | 2025-04-13 15:54 | 6:38 | S/O | Maintenance Work at Central S/S end. | 0 | 0 | No interruption
Noapara 132/33kV | Jashore-2 | 2025-04-12 07:41 | 2025-04-12 09:59 | 2:18 | S/O | High temperature maintenance | 0 | 0 | No interruption
Noapara 132/33kV | Jashore-1 | 2025-04-12 10:14 | 2025-04-12 12:18 | 2:04 | S/O | Due to maint.work | 0 | 0 | No interruption
Patuakhali 132/33kV | PAYRA-PATUAKHALI CKT-1 | 2025-04-10 08:02 | 2025-04-10 09:10 | 1:08 | S/O | Red hot maintenance by Payra Grid | 0 | 0 | No interruption
Payra 400/132/33kV | Payra Patuakhali Line-01 | 2025-04-10 08:03 | 2025-04-10 09:09 | 1:06 | S/O | High temperature point | 0 | 0 | No interruption
Rajbari 132/33kV | Bheramara-1 | 2025-04-25 16:53 | 2025-04-25 21:46 | 4:53 | S/O | SAS INTEGRATION WORK. | 0 | 0 | No interruption
Rajbari 132/33kV | Bheramara-1 | 2025-04-26 10:05 | 2025-04-26 19:28 | 9:23 | S/O | SAS INTEGRATION WORK. | 0 | 0 | No interruption
Shariatpur 132/33kV | Madaripur-Shariatpur CKT-02 | 2025-04-29 15:10 | 2025-04-29 17:37 | 2:27 | S/O | SF6 Refilled work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-10 23:18 |  | Unserved Energy: |  | 470.1667
HVDC Grid Circle :
Bhangura 132/33kV | Bhangura-Bhagabari ckt-1 | 2025-04-19 08:20 | 2025-04-19 17:29 | 9:09 | S/O | Piling work at Bhangura -Bhagabari ckt-2 bay | 25 | 228.75 | Power interruption
Bheramara 230/132kV | Rajbari 1 | 2025-04-09 06:48 | 2025-04-09 12:06 | 5:18 | S/O | Re- splicins joint box | 0 | 0 | No interruption
Bheramara 230/132kV | Rajbari 2 | 2025-04-09 07:49 | 2025-04-09 12:07 | 4:18 | S/O | Re- splicins joint box | 0 | 0 | No interruption
Bheramara 230/132kV | Ishurdi 1 | 2025-04-15 11:07 | 2025-04-15 11:07 | 0:00 | S/O | Reconducting | 0 | 0 | No interruption
Bheramara 230/132kV | Ishurdi 2 | 2025-04-15 11:07 | 2025-04-15 11:07 | 0:00 | S/O | Reconducting | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kv Natore-1 | 2025-04-07 12:31 | 2025-04-07 17:56 | 5:25 | S/O | Reconducting | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kv Natore-1 | 2025-04-08 08:29 | 2025-04-08 18:10 | 9:41 | S/O | Project work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Rupppur-1 | 2025-04-08 10:55 | 2025-04-08 13:39 | 2:44 | S/O | 0 | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Rupppur-2 | 2025-04-08 13:43 | 2025-04-08 15:41 | 1:58 | S/O | 0 | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Pabna | 2025-04-10 07:12 | 2025-04-10 12:05 | 4:53 | S/O | 0 | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kv Natore-2 | 2025-04-11 10:35 | 2025-04-11 10:35 | 0:00 | S/O | Reconductoring Work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Rupppur-1 | 2025-04-12 09:45 | 2025-04-12 12:11 | 2:26 | S/O | 0 | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Rupppur-2 | 2025-04-12 12:13 | 2025-04-12 15:00 | 2:47 | S/O | 0 | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Baghabari Line | 2025-04-14 07:46 | 2025-04-14 16:39 | 8:53 | S/O | 0 | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Bheramara -1 | 2025-04-15 11:11 | 2025-04-15 11:11 | 0:00 | S/O | reconductoring work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Bheramara -2 | 2025-04-15 11:11 | 2025-04-15 11:11 | 0:00 | S/O | reconductoring work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Rupppur-1 | 2025-04-21 10:14 | 2025-04-21 11:24 | 1:10 | S/O | caddle guard remove | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Rupppur-2 | 2025-04-21 11:57 | 2025-04-21 13:13 | 1:16 | S/O | Scaffolding remove | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2025-04-08 06:55 | 2025-04-08 17:50 | 10:55 | S/O | Manikganj for project work | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 2 | 2025-04-10 06:35 | 2025-04-10 11:34 | 4:59 | S/O | removal of Cradle guard in Rooppur Dhaka line. | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2025-04-10 06:35 | 2025-04-10 11:34 | 4:59 | S/O | removal of Cradle guard in Rooppur Dhaka line. | 0 | 0 | No interruption
Jashore 132/33kV | NOA-2(L4) | 2025-04-12 07:39 | 2025-04-12 10:02 | 2:23 | S/O | Shutdown For Noapara End | 0 | 0 | No interruption
Jashore 132/33kV | NOA-1(L3) | 2025-04-12 10:14 | 2025-04-12 12:18 | 2:04 | S/O | Shutdown For Noapara End | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-Khulna (South) Ckt-1 | 2025-04-26 06:04 | 2025-04-26 14:54 | 8:50 | S/O | line strining work | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-Khulna (South) Ckt-2 | 2025-04-26 06:06 | 2025-04-26 14:54 | 8:48 | S/O | Line strining work | 0 | 0 | No interruption
Pabna 132/33kV | Pabna-Ishwardi Line | 2025-04-10 07:11 | 2025-04-10 12:06 | 4:55 | S/O | S/D taken by Ishwardi grid S/S | 0 | 0 | No interruption
Ruppur 132/11kV | 132kv Ishurdi Line-1 | 2025-04-08 10:53 | 2025-04-08 13:40 | 2:47 | S/O | Project work Ishwardi 230/132 kv grid substations | 0 | 0 | No interruption
Ruppur 132/11kV | 132kv Ishurdi Line-2 | 2025-04-08 13:42 | 2025-04-08 15:30 | 1:48 | S/O | Project work Ishwardi 230/132 kv grid substations | 0 | 0 | No interruption
Ruppur 132/11kV | 132kv Ishurdi Line-1 | 2025-04-12 09:44 | 2025-04-12 11:56 | 2:12 | S/O | 0 | 0 | 0 | No interruption
Ruppur 132/11kV | 132kv Ishurdi Line-2 | 2025-04-12 12:12 | 2025-04-12 14:48 | 2:36 | S/O | 0 | 0 | 0 | No interruption
Ruppur 132/11kV | 132kv Ishurdi Line-1 | 2025-04-21 09:56 | 2025-04-21 11:26 | 1:30 | S/O | project work | 0 | 0 | No interruption
Ruppur 132/11kV | 132kv Ishurdi Line-2 | 2025-04-21 11:56 | 2025-04-21 13:15 | 1:19 | S/O | project work | 0 | 0 | No interruption
Ullahpara 132/33kV | Baghabari ckt | 2025-04-20 09:34 | 2025-04-26 20:06 | 154:32 | S/O | Erecting a new Tower of Shahjadpur grid. | 0 | 0 | No interruption
Ullahpara 132/33kV | 132 KV Sirajgonj Ckt-1 | 2025-04-20 16:33 | 2025-04-20 18:51 | 2:18 | S/O | Instruction By ALDC Bogra. | 0 | 0 | No interruption
Ullahpara 132/33kV | 132 KV Sirajgonj Ckt-2 | 2025-04-20 16:35 | 2025-04-20 22:46 | 6:11 | S/O | Instruction By ALDC Bogra. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-10 19:04 |  | Unserved Energy: |  | 228.75
Bogura Grid Circle :
Barapukuria 230/132/33kV | Rangpur 132 KV Ckt1 | 2025-04-11 09:05 | 2025-04-11 15:01 | 5:56 | S/O | Maint.work | 0 | 0 | No interruption
Bogura 230/132kV | 132KV Main 2 | 2025-04-02 09:37 | 2025-04-02 11:19 | 1:42 | S/O | Bogura132 kv ckt-02, Q2 DS Finger Change, | 0 | 0 | No interruption
Bogura 230/132kV | Bogra 132KV Line-2 | 2025-04-02 09:45 | 2025-04-02 11:30 | 1:45 | S/O | Bogura132 kv ckt-02, Q2 DS Finger Change, | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2025-04-07 14:30 | 2025-04-07 14:30 | 0:00 | S/O | Line checking | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2025-04-07 14:30 | 2025-04-07 14:30 | 0:00 | S/O | Line checking | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2025-04-07 14:30 | 2025-04-07 14:30 | 0:00 | S/O | Line checking | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2025-04-07 14:40 | 2025-04-08 16:03 | 25:23 | S/O | Line checking | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2025-04-07 14:40 | 2025-04-08 16:04 | 25:24 | S/O | Line checking | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Naogaon 230 kV Ckt-1 | 2025-04-10 12:41 | 2025-04-10 16:19 | 3:38 | S/O | Punch list Problem solving. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2025-04-18 09:43 | 2025-04-18 17:41 | 7:58 | S/O | Tree Trimming | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2025-04-18 09:44 | 2025-04-18 17:42 | 7:58 | S/O | Tree Trimming | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2025-04-19 09:20 | 2025-04-19 17:38 | 8:18 | S/O | Tree Trimming work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2025-04-19 09:21 | 2025-04-19 17:37 | 8:16 | S/O | Tree Trimming work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2025-04-20 09:47 | 2025-04-20 18:31 | 8:44 | S/O | Project work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2025-04-20 09:48 | 2025-04-20 18:31 | 8:43 | S/O | Project work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2025-04-22 11:22 | 2025-04-22 20:27 | 9:05 | S/O | Tree cutting and aviation light setting on Parbatipur Ckt-01 | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2025-04-22 11:23 | 2025-04-22 20:28 | 9:05 | S/O | Tree cutting and aviation light setting on Parbatipur Ckt-02 | 0 | 0 | No interruption
Jaldhaka 132/33kV | Saidpur-Jaldhaka Ckt-01 | 2025-04-15 08:43 | 2025-04-15 19:34 | 10:51 | S/O | Saidpur 150MW SCPP Project ,BPDB has requested for a shutdown of Jaldhaka-Saidpur 132KV Ckt-01 at Saidpur Grid S/S due to power evacuation from plant side to Grid side. | 0 | 0 | No interruption
Jaldhaka 132/33kV | Saidpur-Jaldhaka Ckt-01 | 2025-04-16 08:40 | 2025-04-16 18:07 | 9:27 | S/O | Saidpur 150MW SCPP Project ,BPDB has requested for a shutdown of Jaldhaka-Saidpur 132KV Ckt-01 at Saidpur Grid S/S due to power evacuation from plant side to Grid side. | 0 | 0 | No interruption
Natore 132/33kV | Ishurdi-1 | 2025-04-09 09:32 | 2025-04-09 11:49 | 2:17 | S/O | Reconductoring Work | 0 | 0 | No interruption
Natore 132/33kV | Ishurdi-2 | 2025-04-11 10:35 | 2025-04-11 10:35 | 0:00 | S/O | Reconductoring work. | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Saidpur-1 | 2025-04-16 08:44 | 2025-04-16 18:05 | 9:21 | S/O | Work of OPGW | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Saidpur-2 | 2025-04-16 08:45 | 2025-04-16 15:54 | 7:09 | S/O | Work of OPGW | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Rangpur CKT-01 | 2025-04-15 08:41 | 2025-04-15 19:29 | 10:48 | S/O | QF- GMD- 39 and as the instruction of ALDC, Bogura (499264) | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Jaldhaka CKT-01 | 2025-04-15 08:44 | 2025-04-15 19:38 | 10:54 | S/O | QF- GMD- 39 and as the instruction of ALDC, Bogura (499264) | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Rangpur CKT-01 | 2025-04-16 08:40 | 2025-04-16 18:05 | 9:25 | S/O | QF- GMD- 39 and as the instruction of ALDC, Bogura (499264) | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Rangpur CKT-02 | 2025-04-16 08:41 | 2025-04-16 15:52 | 7:11 | S/O | QF- GMD- 39 and as the instruction of ALDC, Bogura (499264) | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Jaldhaka CKT-01 | 2025-04-16 08:42 | 2025-04-16 18:07 | 9:25 | S/O | QF- GMD- 39 and as the instruction of ALDC, Bogura (499264) | 0 | 0 | No interruption
|  |  | Total : | 1900-01-08 02:43 |  | Unserved Energy: |  | 0
Others :Nil
No interruption
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1900-02-21 06:35 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:April 2025
| Area | Previous Month (March' 2025) |  |  |  | Current Month (April '2025)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 9 | 20 | 98 | 127 | 38 | 19 | 90 | 147
2 | Dhaka (South) Grid Circle. | 14 | 7 | 39 | 60 | 23 | 10 | 55 | 88
3 | Chattogram Grid Circle. | 2 | 9 | 24 | 35 | 14 | 14 | 24 | 52
4 | Cumilla Grid Circle. | 22 | 11 | 62 | 95 | 32 | 14 | 43 | 89
5 | Khulna Grid Circle. | 9 | 6 | 40 | 55 | 43 | 15 | 62 | 120
6 | HVDC Grid Circle | 13 | 25 | 17 | 55 | 5 | 20 | 49 | 74
7 | Bogura Grid Circle. | 9 | 13 | 37 | 59 | 45 | 27 | 47 | 119
8 | Others
9 | Total | 78 | 91 | 317 | 486 | 200 | 119 | 370 | 689
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:April 2025
| Area | Previous Month (March' 2025) |  |  |  | Current Month (April '2025)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 215.82 | 230.26 | 714.1 | 1160.18 | 455.38 | 151.38 | 1813.52 | 2420.28
2 | Dhaka (South) Grid Circle. | 88.03 | 63.68 | 173.83 | 325.54 | 208.57 | 316.67 | 128.08 | 653.32
3 | Chattogram Grid Circle. | - | 69 | - | 69 | 45.85 | 90.01 | 195.17 | 331.03
4 | Cumilla Grid Circle. | 61.03 | 168.45 | 394.29 | 623.77 | 266.57 | 67 | 328.15 | 661.72
5 | Khulna Grid Circle. | 128.1 | - | 453.25 | 581.35 | 255.63 | 48.73 | 1633.75 | 1938.11
6 | HVDC Grid Circle | 30.4 | 438.62 | - | 469.02 | 57.07 | 89.18 | 706.02 | 852.27
7 | Bogura Grid Circle. | 61.27 | 206.77 | 334.53 | 602.57 | 421.95 | 252.42 | 171.95 | 846.32
8 | Others
9 | Total | 584.65 | 1176.78 | 2070 | 3831.43 | 1711.02 | 1015.39 | 4976.64 | 7703.05
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-29
QF-LDC-29
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:April 2025
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 17 | 12 | 29 | 7 | 6 | 16 | 2374.29
2 | Dhaka (South) | 5031.6 | 10 | 2 | 12 | 1 | 2 | 9 | 611.65
3 | Chattogram | 2042 | 2 | 4 | 6 | 2 | - | 4 | 204.06
4 | Khulna | 2434 | 18 | 17 | 35 | 12 | 4 | 19 | 1364.83
5 | HVDC | 5954.3 | 3 | 6 | 9 |  | 1 | 8 | 566.45
6 | Bogura | 3145.6 | 16 | 5 | 21 | 3 | 8 | 10 | 696.9
7 | Cumilla | 2981 | 2 | 4 | 6 | 1 | - | 5 | 361.63
8 | Others | - | - | - | - | - | - | - | -
| Total | 30390.1 | [6 empty] | 6179.81
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.97%
2 | Dhaka (South) | 99.97%
3 | Chattogram | 99.99%
4 | Khulna | 99.99%
5 | HVDC | 99.98%
6 | Bogura | 99.97%
7 | Cumilla | 99.99% | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:April 2025
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | - | 1 | 1 |  | - | 1 | 46
2 | Dhaka (South) | 990.29 | - | 2 | - | 2 | 1 | 1 | - | 41.67
3 | Chattogram | 917 | - | 2 | - | 2 | - | - | 2 | 127.05
4 | Khulna | 1238.4 | - | 3 | 2 | 5 | 1 | 2 | 2 | 573.28
5 | HVDC | 1325 | - | 1 | 1 | 2 |  | 1 | 1 | 285.82
6 | Bogura | 1803.3 | - | 5 | 1 | 1 | 2 | 2 | 1 | 149.4167
7 | Cumilla | 1648.16 | - | 10 | - | 10 | 2 | 7 | 1 | 300.0833
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 1523.32
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 100%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.99%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 99.99%
6 | Bogura | 99.99%
7 | Cumilla | 99.99% | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:April 2025
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2025-04-01 | 10 | - | 6 | 7hr 1 min | 3 | 3hr 00 min | - | - | 1 | 0hr 43 min | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-32
QF-LDC-32
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:April 2025
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Bhaluka 132/33kV | 5 | 5:11 | 95.92
Dhamrai 132/33kV | 2 | 0:30 | 15
Joydebpur 132/33kV | 1 | 0:07 | 4.55
Kabirpur 132/33kV | 3 | 4:41 | 358
Sherpur 132/33kV | 4 | 4:30 | 96.3
Tangail 132/33kV | 1 | 0:37 | 37
Bhaluka 132/33kV | 3 | 2:37 | 50.93
Kabirpur 132/33kV | 5 | 15:25 | 1213.58
Kaliakoir 400/230/132kV | 1 | 1:38 | 81.6667
Kodda 132/33kV | 1 | 4:34 | 91.3333
Sherpur 132/33kV | 1 | 6:55 | 138.3333
Sreepur 230/132/33kV | 1 | 3:50 | 191.6667
Kabirpur 132/33kV | 1 | 1:32 | 46
Hasnabad 132/33kV | 1 | 0:35 | 14.5833
Madanganj 132/33kV | 1 | 2:00 | 6
Narshingdi 132/33kV | 1 | 0:47 | 5.4833
Shyampur 230/132kV | 1 | 12:28 | 124.6667
Siddhirganj 132/33kV | 2 | 3:20 | 220
Sonargaon 132/33kV | 4 | 5:30 | 112.83
Keranigonj 230/132/33kV | 1 | 0:04 | 5
Narshingdi 132/33kV | 1 | 0:40 | 36.6667
Bhulta 132/33kV | 1 | 1:14 | 49.3333
Sonargaon 132/33kV | 1 | 3:09 | 78.75
Dohazari 132/33kV | 2 | 2:19 | 8.9
Baroaulia 132/33kV | 1 | 1:24 | 81.2
Shikalbaha 230/132kV | 1 | 2:11 | 45.85
Bakulia 132/33kV | 2 | 0:45 | 10.5
Chandraghona 132/33kV | 1 | 2:03 | 36.9
Coxsbazar 132/33kV | 1 | 2:23 | 147.7667
Beanibazar 132/33kV | 1 | 1:25 | 28.3333
Cumilla(S) 132/33kV | 1 | 0:15 | 4.25
Shahjibazar 132/33kV | 1 | 0:09 | 0.9
Beanibazar 132/33kV | 2 | 1:24 | 5.6
Chowmuhani 132/33kV | 1 | 4:17 | 218.45
Fenchuganj 230/132/33kV | 4 | 1:46 | 43
Ramganj 132/33kV | 1 | 0:45 | 31.5
Sylhet (South) | 2 | 1:32 | 1.53
Chauddagram 132/33kV | 2 | 6:20 | 135.03
Chowmuhani 132/33kV | 1 | 7:28 | 149.3333
Ramganj 132/33kV | 1 | 1:15 | 43.75
Barishal 132/33kV | 4 | 1:23 | 38.35
Barishal 230/132kV | 1 | 0:26 | 13.4333
Benapole 132/33kV | 4 | 3:26 | 101.07
Goalpara 132/33kV | 6 | 2:00 | 7.6
Gopalganj 132/33kV | 1 | 0:13 | 6.0667
Khulna (C) | 2 | 1:19 | 34.73
Barishal 132/33kV | 1 | 0:21 | 1.05
Madaripur 132/33kV | 1 | 0:40 | 53.3333
Rajbari 132/33kV | 1 | 0:43 | 48.7333
Bagerhat 132/33kV | 2 | 2:47 | 117.92
Barguna 132/33kV | 1 | 1:19 | 5.2667
Barishal 132/33kV | 2 | 2:38 | 105.33
Barishal 230/132kV | 5 | 16:47 | 348.25
Bhandaria 132/33kV | 2 | 3:47 | 482.42
Goalpara 132/33kV | 4 | 8:54 | 38.57
Narail 132/33kV | 1 | 2:38 | 65.8333
Bhandaria 132/33kV | 2 | 13:26 | 470.17
Bhangura 132/33kV | 1 | 0:41 | 10.25
Ishurdi 132/33kV | 1 | 1:08 | 28.3333
Kushtia 132/33kV | 1 | 1:06 | 50.6
Jashore 132/33kV | 1 | 0:32 | 57.0667
Bhangura 132/33kV | 3 | 25:22 | 253.67
Jhenaidah 132/33kV | 1 | 1:58 | 59
Magura 132/33kV | 1 | 9:13 | 110.6
Pabna 132/33kV | 1 | 6:45 | 54
Bhangura 132/33kV | 1 | 9:09 | 228.75
Barapukuria 230/132/33kV | 2 | 0:55 | 86.5
Jaldhaka 132/33kV | 2 | 6:07 | 126.42
Kurigram 132/33kV | 1 | 0:32 | 16
Lalmonirhat 132/33kV | 2 | 1:40 | 36.67
Mahasthangarh 132/33kV | 1 | 2:06 | 73.5
Naogaon 132/33kV | 2 | 2:04 | 59.93
Niamatpur 132/33kV | 1 | 0:10 | 2
Palashbari 132/33kV | 1 | 0:38 | 15.8333
Purbasadipur 132/33kV | 1 | 1:35 | 47.5
Rahanpur 132/33kV | 1 | 0:46 | 4.6
Thakurgaon 132/33kV | 2 | 2:00 | 56
Purbasadipur 132/33kV | 4 | 4:39 | 141.75
Rangpur 132/33kV | 1 | 0:23 | 7.6667
Barapukuria 230/132/33kV | 1 | 2:06 | 31.5
Naogaon 132/33kV | 1 | 1:35 | 55.4167
Panchagarh 132/33kV | 1 | 4:08 | 12.4
Purbasadipur 132/33kV | 1 | 2:28 | 61.6667
Thakurgaon 132/33kV | 1 | 0:47 | 10.9667
| 145 | 272:55 | 7703.1033
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: April 2025
Sl No. | Sub-station | Load (MW) | Date & Time
1 | AKS | 14 | 2025-04-01 18:00
2 | AKSML | 138 | 2025-04-16 01:00
3 | Aftabnagar | 42 | 2025-04-26 19:00
4 | Agargaon | 148 | 2025-04-27 16:00
5 | Agrabad | 100 | 2025-04-07 14:00
6 | Amnura | 60 | 2025-04-25 21:00
7 | Ashuganj | 130.5 | 2025-04-26 20:00
8 | BSRM | 208 | 2025-04-29 21:00
9 | Bagerhat | 95 | 2025-04-13 19:00
10 | Bajitpur | 61 | 2025-04-08 19:30
11 | Bakulia | 102 | 2025-04-13 19:30
12 | Banani | 69.2 | 2025-04-08 13:00
13 | Bangabhaban | 20 | 2025-04-06 10:00
14 | Barapukuria | 81 | 2025-04-08 21:00
15 | Barguna | 28 | 2025-04-21 22:00
16 | Barishal | 123 | 2025-04-26 21:00
17 | Barishal-230 | 114 | 2025-04-04 23:00
18 | Baroaulia | 72 | 2025-04-12 10:00
19 | Baroirhat | 74 | 2025-04-26 18:30
20 | Bashundhara | 223 | 2025-04-27 15:00
21 | BashundharaCement | 15 | 2025-04-23 12:00
22 | Beanibazar | 82 | 2025-04-26 23:00
23 | Benapole | 76 | 2025-04-01 22:00
24 | Bhaluka | 183 | 2025-04-23 19:00
25 | Bhandaria | 90 | 2025-04-27 01:00
26 | Bhangura | 70 | 2025-04-25 11:00
27 | Bheramara(GK) | 75 | 2025-04-24 20:00
28 | Bhulta | 255 | 2025-04-22 23:00
29 | Bog-Sherpur | 82 | 2025-04-27 00:00
30 | Bogura | 196 | 2025-04-08 19:30
31 | Borhanuddin | 95 | 2025-04-13 21:00
32 | Brahmanbaria | 148 | 2025-04-03 22:00
33 | Cantonment | 150 | 2025-04-24 13:00
34 | Chandina | 19.17 | 2025-04-29 22:00
35 | Chandpur | 83 | 2025-04-26 23:00
36 | Chandraghona | 39 | 2025-04-13 18:30
37 | Chapai | 91 | 2025-04-26 13:00
38 | Charsaidpur | 81 | 2025-04-24 01:00
39 | Chauddagram | 82 | 2025-04-06 18:30
40 | Chhatak | 40 | 2025-04-14 20:00
41 | Chowmuhani | 245 | 2025-04-14 19:00
42 | Chuadanga | 127 | 2025-04-24 22:00
43 | Coxsbazar | 140 | 2025-04-27 19:30
44 | Cumilla(N) | 192 | 2025-04-06 21:00
45 | Cumilla(S) | 187 | 2025-04-26 23:00
46 | Daudkandi | 162 | 2025-04-06 20:00
47 | Dhaka | 70 | 2025-04-23 13:00
48 | Dhamrai | 140 | 2025-04-27 18:30
49 | Dhanmondi | 176 | 2025-04-27 13:00
50 | Dohazari | 132 | 2025-04-08 19:30
51 | Faridpur | 187 | 2025-04-24 23:00
52 | Fatullah | 115 | 2025-04-27 15:00
53 | Fenchuganj | 42 | 2025-04-14 19:00
54 | Feni | 126 | 2025-04-12 20:00
55 | GPH | 100 | 2025-04-05 08:00
56 | Ghatail | 104 | 2025-04-25 19:00
57 | Ghorashal | 21 | 2025-04-13 13:00
58 | Ghorashal-230 | 102 | 2025-04-27 19:30
59 | Goalpara | 80 | 2025-04-26 18:30
60 | Gollamari | 104 | 2025-04-24 00:00
61 | Gopalganj | 122 | 2025-04-26 21:00
62 | Gulshan | 144 | 2025-04-24 15:00
63 | Halishahar | 85 | 2025-04-27 15:00
64 | HaripurSBU | 191 | 2025-04-21 19:00
65 | Hasnabad | 101 | 2025-04-23 22:00
66 | Hathazari | 92 | 2025-04-12 12:00
67 | Ishurdi | 91 | 2025-04-22 19:30
68 | Jaldhaka | 95 | 2025-04-25 19:30
69 | Jamalpur | 147 | 2025-04-01 19:30
70 | Jashore | 164 | 2025-04-07 19:00
71 | Jhenaidah | 157 | 2025-04-06 19:00
72 | Joydebpur | 165 | 2025-04-24 16:00
73 | Joypurhat | 86 | 2025-04-26 01:00
74 | Juldah | 22 | 2025-04-10 15:00
75 | KSRM | 20 | 2025-04-05 09:00
76 | Kabirpur | 282 | 2025-04-21 08:00
77 | Kachua | 96 | 2025-04-25 22:00
78 | Kallyanpur | 123 | 2025-04-23 18:00
79 | Kalurghat | 60 | 2025-04-27 11:00
80 | Kamrangirchar | 73.1 | 2025-04-23 13:00
81 | Kaptai | N/A | N/A
82 | Kasba | 44 | 2025-04-14 22:00
83 | Kazla | 132 | 2025-04-26 18:30
84 | Keranigonj | 85 | 2025-04-27 18:30
85 | Khagrachori | 36 | 2025-04-26 20:00
86 | Khulna | 97 | 2025-04-06 13:00
87 | Khulshi | 206 | 2025-04-30 12:00
88 | Kishoreganj | 156 | 2025-04-03 21:00
89 | Kodda | 309 | 2025-04-19 18:00
90 | Kulaura | 54 | 2025-04-09 19:00
91 | Kurigram | 76 | 2025-04-08 19:00
92 | Kushtia | 163 | 2025-04-26 19:30
93 | Lalbag | 72 | 2025-04-23 13:00
94 | Lalmonirhat | 74 | 2025-04-08 19:00
95 | MI_Cement | 18.5 | 2025-04-17 21:00
96 | Madanganj | 48 | 2025-04-23 18:30
97 | Madaripur | 124 | 2025-04-13 21:00
98 | Madartek | 99.25 | 2025-04-27 23:00
99 | Madunaghat | 57 | 2025-04-12 22:00
100 | Magura | 78 | 2025-04-06 19:00
101 | Mahasthangarh | 96 | 2025-04-24 22:00
102 | Manikganj | 152 | 2025-04-23 20:00
103 | Maniknagar | 92 | 2025-04-24 13:00
104 | Matarbari | 58 | 2025-04-16 20:00
105 | Matuail | 70 | 2025-04-27 15:00
106 | Millgate | 127 | 2025-04-27 15:00
107 | Mirpur | 160.5 | 2025-04-23 19:00
108 | Mirsorai | 19 | 2025-04-26 11:00
109 | Mirzapur | 53 | 2025-04-22 21:00
110 | Mithapukur | 76 | 2025-04-08 19:00
111 | Modern | N/A | N/A
112 | Mogbazar | 175.7 | 2025-04-27 15:00
113 | Mongla | 49 | 2025-04-27 15:00
114 | Motijheel | 46 | 2025-04-27 13:00
115 | Muktagacha | 42 | 2025-04-05 18:30
116 | Munshiganj | 131 | 2025-04-27 22:00
117 | Muradnagar | 32 | 2025-04-03 20:00
118 | Mymensingh | 228 | 2025-04-05 19:00
119 | Naogaon | 167 | 2025-04-26 19:30
120 | Narail | 70 | 2025-04-06 19:00
121 | Narinda | 85 | 2025-04-27 13:00
122 | Narshingdi | 195 | 2025-04-27 21:00
123 | Natore | 191 | 2025-04-26 20:00
124 | Nawabganj | 69.6 | 2025-04-26 23:00
125 | Netrakona | 144 | 2025-04-01 19:00
126 | New | 94.2 | 2025-04-22 15:00
127 | Niamatpur | 127 | 2025-04-08 19:00
128 | Noapara | 56 | 2025-04-26 20:00
129 | PHP | 10 | 2025-04-20 20:00
130 | Pabna | 132 | 2025-04-27 19:30
131 | Palashbari | 140 | 2025-04-09 19:30
132 | Panchagarh | 66 | 2025-04-25 19:30
133 | Patuakhali | 91 | 2025-04-26 22:00
134 | Payra | 36 | 2025-04-26 22:00
135 | Postogola | 61 | 2025-04-24 16:00
136 | Purbachal | 28 | 2025-04-05 13:00
137 | Purbasadipur | 145 | 2025-04-26 13:00
138 | Rahanpur | 38 | 2025-04-27 00:00
139 | Rahim | 57 | 2025-04-20 18:00
140 | Rajbari | 90 | 2025-04-23 19:00
141 | Rajendrapur | 152 | 2025-04-24 19:00
142 | Rajshahi | 169 | 2025-04-27 00:00
143 | Rajshahi-230 | 102 | 2025-04-24 00:00
144 | Ramganj | 126 | 2025-04-03 18:30
145 | Rampur | 45 | 2025-04-13 00:00
146 | Rangamati | 18 | 2025-04-02 19:00
147 | Rangpur | 165 | 2025-04-25 19:00
148 | Ruppur | 8.4 | 2025-04-23 16:00
149 | SSM | 18 | 2025-04-20 05:00
150 | Saidpur | 125 | 2025-04-26 20:00
151 | Satkhira | 146 | 2025-04-06 22:00
152 | Satmasjid | 123 | 2025-04-23 16:00
153 | Savar | 234 | 2025-04-27 18:30
154 | SevenRings | 22.65 | 2025-04-30 11:00
155 | ShahCement | 38 | 2025-04-27 02:00
156 | Shahjadpur | 103 | 2025-04-27 20:00
157 | Shahjibazar | 141 | 2025-04-14 22:00
158 | Shahmirpur | 69 | 2025-04-06 00:00
159 | Shariatpur | 97 | 2025-04-27 00:00
160 | Sherpur | 184 | 2025-04-06 19:00
161 | Shikalbaha | 32 | 2025-04-28 19:00
162 | Shitalakhya | 93.2 | 2025-04-24 16:00
163 | Sholosohor | 48 | 2025-04-24 16:00
164 | Shyampur | 182 | 2025-04-24 12:00
165 | Siddhirganj | 140 | 2025-04-16 12:00
166 | Sirajganj | 138 | 2025-04-26 21:00
167 | Sonargaon | 139 | 2025-04-28 00:00
168 | Sreemongol | 85 | 2025-04-27 21:00
169 | Sreepur | 115 | 2025-04-09 15:00
170 | Srinagar | 54.06 | 2025-04-26 23:00
171 | Sunamganj | 59 | 2025-04-25 20:00
172 | Sylhet | 50 | 2025-04-09 22:00
173 | Sylhet-132 | 135 | 2025-04-24 19:00
174 | TK | 37 | 2025-04-13 22:00
175 | Tangail | 212 | 2025-04-13 19:00
176 | Thakurgaon | 115 | 2025-04-26 19:30
177 | Tongi | 152 | 2025-04-24 18:30
178 | Ullahpara | 51 | 2025-04-26 23:00
179 | Ullon | 50 | 2025-04-22 19:30
180 | Uttara | 104 | 2025-04-24 16:00
181 | UttaraNew | 57 | 2025-04-27 00:00
182 | Zigatola | 86 | 2025-04-24 16:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID BANGLADESH PLC. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: April 2025
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 5941.46 | 2025-04-24 | 19:00
Chattogram | 1597.5 | 2025-04-27 | 19:30
Cumilla | 1504.5 | 2025-04-15 | 20:00
Mymensingh | 1357 | 2025-04-06 | 19:30
Sylhet | 646 | 2025-04-14 | 21:00
Khulna | 1929.2 | 2025-04-24 | 23:00
Barishal | 543 | 2025-04-27 | 1:00
Rajshahi | 1798.4 | 2025-04-25 | 22:00
Rangpur | 1085 | 2025-04-08 | 19:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: April 2025
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar | 400 | 408 | 2025-04-01 09:00 | 331 | 2025-04-11 05:00
2 | Ashuganj | 400 | N/A | N/A | N/A | N/A
3 | Bhulta | 400 | 414 | 2025-04-07 04:00 | 373 | 2025-04-27 10:00
4 | Bibiana | 400 | 398 | 2025-04-07 08:00 | 371 | 2025-04-01 23:00
5 | BIPTC | 400 | 406 | 2025-04-26 18:30 | 386 | 2025-04-25 15:00
6 | Bogura | 400 | 426 | 2025-04-13 06:00 | 369 | 2025-04-01 22:00
7 | Gopalganj | 400 | 414 | 2025-04-01 09:00 | 378 | 2025-04-27 13:00
8 | Kaliakoir | 400 | 397 | 2025-04-07 07:00 | 307 | 2025-04-25 04:00
9 | Madunaghat | 400 | 406 | 2025-04-07 05:00 | 325 | 2025-04-15 15:00
10 | Meghnaghat | 400 | 411 | 2025-04-01 10:00 | 306 | 2025-04-01 16:00
11 | Payra | 400 | 421 | 2025-04-01 10:00 | 400 | 2025-04-27 12:00
12 | Rahanpur | 400 | 423 | 2025-04-13 05:00 | 370 | 2025-04-12 01:00
13 | Rampal | 400 | 411 | 2025-04-01 09:00 | 376 | 2025-04-27 12:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon | 230 | 241 | 2025-04-01 09:00 | 213 | 2025-04-27 10:00
2 | AKSML | 230 | 240 | 2025-04-26 19:30 | 218 | 2025-04-25 15:00
3 | Aminbazar | 230 | 258 | 2025-04-12 09:00 | 213 | 2025-04-27 12:00
4 | Ashuganj | 230 | 241 | 2025-04-07 05:00 | 221 | 2025-04-27 10:00
5 | Ashuganj-400 | 230 | N/A | N/A | N/A | N/A
6 | Baghabari | 230 | 238 | 2025-04-10 23:00 | 222 | 2025-04-27 13:00
7 | Barapukuria | 230 | 235 | 2025-04-13 05:00 | 209 | 2025-04-20 19:30
8 | Barapukuria-230 | 230 | N/A | N/A | N/A | N/A
9 | Barishal | 230 | 241 | 2025-04-18 05:00 | 218 | 2025-04-24 23:00
10 | Bheramara | 230 | 240 | 2025-04-26 18:00 | 240 | 2025-04-26 18:00
11 | Bhulta | 230 | 238 | 2025-04-07 04:00 | 211 | 2025-04-27 10:00
12 | Bibiana | 230 | 231 | 2025-04-16 16:00 | 210 | 2025-04-05 23:00
13 | BIPTC | 230 | 240 | 2025-04-26 18:00 | 219 | 2025-04-27 14:00
14 | Bogura | 230 | 241 | 2025-04-10 14:00 | 214 | 2025-04-19 19:00
15 | Bogura-400 | 230 | 242 | 2025-04-10 14:00 | 214 | 2025-04-20 17:00
16 | Borhanuddin | 230 | 245 | 2025-04-29 05:00 | 218 | 2025-04-26 21:00
17 | BSRM | 230 | 238 | 2025-04-07 05:00 | 216 | 2025-04-27 10:00
18 | Cumilla(N) | 230 | 236 | 2025-04-07 05:00 | 213 | 2025-04-16 11:00
19 | Faridpur | 230 | 239 | 2025-04-29 06:00 | 239 | 2025-04-29 06:00
20 | Fenchuganj | 230 | 235 | 2025-04-07 04:00 | 217 | 2025-04-04 23:00
21 | Ghorashal | 230 | 240 | 2025-04-01 08:00 | 220 | 2025-04-21 13:00
22 | Ghorashal-230 | 230 | 237 | 2025-04-07 04:00 | 210 | 2025-04-01 22:00
23 | Gopalganj | 230 | 255 | 2025-04-08 22:00 | 216 | 2025-04-25 00:00
24 | GPH | 230 | 244 | 2025-04-22 15:00 | 220 | 2025-04-19 16:00
25 | Haripur | 230 | 238 | 2025-04-07 03:00 | 212 | 2025-04-27 10:00
26 | Hasnabad | 230 | 240 | 2025-04-01 10:00 | 212 | 2025-04-27 10:00
27 | Hathazari | 230 | 239 | 2025-04-07 05:00 | 221 | 2025-04-27 10:00
28 | Ishurdi | 230 | 241 | 2025-04-26 18:00 | 222 | 2025-04-27 14:00
29 | Jhenaidah | 230 | 237 | 2025-04-26 18:00 | 207 | 2025-04-09 19:00
30 | Kaliakoir | 230 | 239 | 2025-04-01 09:00 | 213 | 2025-04-27 10:00
31 | Keranigonj | 230 | 238 | 2025-04-01 09:00 | 212 | 2025-04-27 10:00
32 | Khulna(S) | 230 | 236 | 2025-04-01 09:00 | 212 | 2025-04-23 23:00
33 | Madunaghat | 230 | 266 | 2025-04-26 04:00 | 223 | 2025-04-16 12:00
34 | Madunaghat-400 | 230 | 240 | 2025-04-07 05:00 | 223 | 2025-04-25 15:00
35 | Maniknagar | 230 | 237 | 2025-04-07 06:00 | 210 | 2025-04-27 10:00
36 | Meghnaghat | 230 | 244 | 2025-04-07 04:00 | 220 | 2025-04-24 14:00
37 | Meghnaghat-400 | 230 | 239 | 2025-04-01 09:00 | 216 | 2025-04-15 12:00
38 | Mirsorai | 230 | 240 | 2025-04-12 19:30 | 216 | 2025-04-27 10:00
39 | Rajshahi | 230 | 240 | 2025-04-26 18:30 | 217 | 2025-04-01 19:30
40 | Rampal | 230 | 254 | 2025-04-01 11:00 | 212 | 2025-04-24 23:00
41 | Rampur | 230 | N/A | N/A | N/A | N/A
42 | Rampura | 230 | 238 | 2025-04-07 05:00 | 209 | 2025-04-27 10:00
43 | Shikalbaha | 230 | 240 | 2025-04-10 17:00 | 219 | 2025-04-25 12:00
44 | Shyampur | 230 | 239 | 2025-04-01 09:00 | 212 | 2025-04-27 10:00
45 | Siddhirganj | 230 | 259 | 2025-04-07 16:00 | 215 | 2025-04-15 11:00
46 | Sirajgonj | 230 | 243 | 2025-04-07 03:00 | 232 | 2025-04-19 19:00
47 | Sreepur | 230 | 239 | 2025-04-07 04:00 | 219 | 2025-04-20 17:00
48 | Tongi | 230 | 235 | 2025-04-01 07:00 | 210 | 2025-04-19 15:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar | 132 | 138 | 2025-04-07 00:00 | 119 | 2025-04-15 11:00
2 | Agargaon | 132 | 140 | 2025-04-16 16:00 | 122 | 2025-04-15 12:00
3 | Agrabad | 132 | 138 | 2025-04-11 07:00 | 124 | 2025-04-25 15:00
4 | AKS | 132 | 135 | 2025-04-29 04:00 | 124 | 2025-04-22 12:00
5 | Aminbazar | 132 | 138 | 2025-04-05 18:30 | 121 | 2025-04-23 10:00
6 | Amnura | 132 | 142 | 2025-04-13 05:00 | 120 | 2025-04-30 15:00
7 | Ashuganj | 132 | 142 | 2025-04-07 04:00 | 130 | 2025-04-19 17:00
8 | Bagerhat | 132 | 142 | 2025-04-17 16:00 | 116 | 2025-04-05 23:00
9 | Bajitpur | 132 | 140 | 2025-04-07 02:00 | 121 | 2025-04-01 23:00
10 | Bakulia | 132 | 140 | 2025-04-12 18:30 | 120 | 2025-04-19 16:00
11 | Banani | 132 | 138 | 2025-04-07 03:00 | 119 | 2025-04-15 11:00
12 | Bangabhaban | 132 | 138 | 2025-04-07 02:00 | 119 | 2025-04-15 11:00
13 | Barapukuria | 132 | 142 | 2025-04-10 10:00 | 124 | 2025-04-28 19:30
14 | Barguna | 132 | 138 | 2025-04-17 18:00 | 127 | 2025-04-25 23:00
15 | Barishal | 132 | 139 | 2025-04-26 19:00 | 119 | 2025-04-24 23:00
16 | Barishal-230 | 132 | 137 | 2025-04-29 04:00 | 119 | 2025-04-25 00:00
17 | Baroaulia | 132 | 140 | 2025-04-26 19:30 | 125 | 2025-04-22 10:00
18 | Baroirhat | 132 | 137 | 2025-04-17 13:00 | 117 | 2025-04-02 01:00
19 | Bashundhara | 132 | 140 | 2025-04-05 19:00 | 117 | 2025-04-27 10:00
20 | BashundharaCement | 132 | 139 | 2025-04-01 07:00 | 116 | 2025-04-23 08:00
21 | Beanibazar | 132 | 141 | 2025-04-07 03:00 | 117 | 2025-04-04 23:00
22 | Benapole | 132 | 141 | 2025-04-11 00:00 | 114 | 2025-04-01 23:00
23 | Bhaluka | 132 | 137 | 2025-04-13 08:00 | 117 | 2025-04-06 11:00
24 | Bhandaria | 132 | 135 | 2025-04-17 16:00 | 109 | 2025-04-24 23:00
25 | Bhangura | 132 | 137 | 2025-04-10 16:00 | 125 | 2025-04-01 22:00
26 | Bheramara | 132 | 138 | 2025-04-10 23:00 | 125 | 2025-04-02 22:00
27 | Bheramara(GK) | 132 | 156 | 2025-04-01 22:00 | 124 | 2025-04-27 23:00
28 | Bhulta | 132 | 135 | 2025-04-01 10:00 | 117 | 2025-04-27 10:00
29 | Bog-Sherpur | 132 | 140 | 2025-04-13 06:00 | 119 | 2025-04-20 16:00
30 | Bogura | 132 | 142 | 2025-04-13 06:00 | 123 | 2025-04-19 19:00
31 | Bogura-230 | 132 | 141 | 2025-04-13 06:00 | 122 | 2025-04-19 19:00
32 | Brahmanbaria | 132 | 140 | 2025-04-07 03:00 | 121 | 2025-04-23 23:00
33 | Cantonment | 132 | 140 | 2025-04-16 16:00 | 122 | 2025-04-15 11:00
34 | Chandina | 132 | 136 | 2025-04-16 16:00 | 120 | 2025-04-18 02:00
35 | Chandpur | 132 | 138 | 2025-04-17 13:00 | 113 | 2025-04-06 15:00
36 | Chandraghona | 132 | 138 | 2025-04-07 06:00 | 127 | 2025-04-16 12:00
37 | Chapai | 132 | 141 | 2025-04-13 04:00 | 122 | 2025-04-01 22:00
39 | Charsaidpur | 132 | 140 | 2025-04-01 08:00 | 122 | 2025-04-27 10:00
40 | Chauddagram | 132 | 136 | 2025-04-11 23:00 | 116 | 2025-04-01 23:00
41 | Chhatak | 132 | 141 | 2025-04-07 03:00 | 115 | 2025-04-04 23:00
42 | Chowmuhani | 132 | 136 | 2025-04-17 13:00 | 108 | 2025-04-02 01:00
43 | Chuadanga | 132 | 142 | 2025-04-10 23:00 | 113 | 2025-04-01 23:00
44 | Coxsbazar | 132 | 132 | 2025-04-11 07:00 | 103 | 2025-04-16 11:00
45 | Cumilla(N) | 132 | 139 | 2025-04-07 05:00 | 121 | 2025-04-16 11:00
46 | Cumilla(S) | 132 | 137 | 2025-04-07 05:00 | 136 | 2025-04-17 13:00
47 | Daudkandi | 132 | 137 | 2025-04-16 16:00 | 113 | 2025-04-09 23:00
48 | Dhaka | 132 | 139 | 2025-04-07 03:00 | 120 | 2025-04-15 11:00
49 | Dhamrai | 132 | 142 | 2025-04-19 07:00 | 120 | 2025-04-15 11:00
50 | Dhanmondi | 132 | 140 | 2025-04-01 08:00 | 122 | 2025-04-27 12:00
51 | Dohazari | 132 | 138 | 2025-04-26 19:00 | 122 | 2025-04-01 23:00
52 | Faridpur | 132 | 140 | 2025-04-16 16:00 | 125 | 2025-04-04 22:00
53 | Fatullah | 132 | 141 | 2025-04-01 09:00 | 123 | 2025-04-27 10:00
54 | Fenchuganj | 132 | 141 | 2025-04-07 03:00 | 126 | 2025-04-04 23:00
55 | Feni | 132 | 137 | 2025-04-07 06:00 | 110 | 2025-04-29
56 | Ghatail | 132 | 140 | 2025-04-15 02:00 | 112 | 2025-04-16 07:00
57 | Ghorashal | 132 | 144 | 2025-04-07 01:00 | 129 | 2025-04-19 14:00
58 | Goalpara | 132 | 142 | 2025-04-11 00:00 | 122 | 2025-04-01 22:00
59 | Gollamari | 132 | 141 | 2025-04-11 00:00 | 123 | 2025-04-20 19:00
60 | Gopalganj | 132 | 140 | 2025-04-11 00:00 | 123 | 2025-04-26 19:00
61 | Gopalganj-400 | 132 | 140 | 2025-04-01 09:00 | 120 | 2025-04-22 05:00
62 | Gulshan | 132 | 138 | 2025-04-07 05:00 | 120 | 2025-04-15 11:00
63 | Halishahar | 132 | 140 | 2025-04-17 15:00 | 125 | 2025-04-16 12:00
64 | Haripur | 132 | 140 | 2025-04-01 08:00 | 123 | 2025-04-27 10:00
65 | HaripurSBU | 132 | 140 | 2025-04-01 09:00 | 120 | 2025-04-09 15:00
66 | Hasnabad | 132 | 141 | 2025-04-01 09:00 | 124 | 2025-04-27 09:00
67 | Hathazari | 132 | 139 | 2025-04-26 19:30 | 127 | 2025-04-27 10:00
68 | Ishurdi | 132 | 141 | 2025-04-26 18:00 | 128 | 2025-04-01 19:30
69 | Jaldhaka | 132 | 141 | 2025-04-28 04:00 | 113 | 2025-04-19 19:00
70 | Jamalpur | 132 | 140 | 2025-04-15 02:00 | 116 | 2025-04-10 06:00
71 | Jashore | 132 | 141 | 2025-04-11 00:00 | 116 | 2025-04-01 23:00
72 | Jhenaidah | 132 | 143 | 2025-04-10 23:00 | 128 | 2025-04-30 11:00
73 | Jhenaidah-230 | 132 | 152 | 2025-04-13 23:00 | 120 | 2025-04-23 23:00
74 | Joydebpur | 132 | 145 | 2025-04-16 15:00 | 122 | 2025-04-27 10:00
75 | Joypurhat | 132 | 143 | 2025-04-13 06:00 | 111 | 2025-04-01 22:00
76 | Juldah | 132 | 141 | 2025-04-12 19:00 | 127 | 2025-04-24 07:00
77 | Kabirpur | 132 | 140 | 2025-04-07 04:00 | 115 | 2025-04-27 10:00
78 | Kachua | 132 | 136 | 2025-04-17 13:00 | 114 | 2025-04-06 14:00
79 | Kaliakoir | 132 | 143 | 2025-04-16 15:00 | 122 | 2025-04-28 05:00
80 | Kallyanpur | 132 | 138 | 2025-04-05 18:30 | 121 | 2025-04-15 12:00
81 | Kalurghat | 132 | 138 | 2025-04-12 18:30 | 127 | 2025-04-22 11:00
82 | Kamrangirchar | 132 | 140 | 2025-04-16 16:00 | 122 | 2025-04-15 13:00
83 | Kaptai | 132 | N/A | N/A | N/A | N/A
84 | Kasba | 132 | 138 | 2025-04-07 05:00 | 117 | 2025-04-09 23:00
85 | Kazla | 132 | 137 | 2025-04-01 10:00 | 120 | 2025-04-10 13:00
86 | Keranigonj | 132 | 140 | 2025-04-16 16:00 | 123 | 2025-04-15 12:00
87 | Khagrachori | 132 | 137 | 2025-04-07 05:00 | 124 | 2025-04-25 12:00
88 | Khulna | 132 | 151 | 2025-04-26 18:30 | 120 | 2025-04-20 19:00
89 | Khulna(S) | 132 | 144 | 2025-04-26 18:30 | 123 | 2025-04-09 19:00
90 | Khulshi | 132 | 137 | 2025-04-26 19:30 | 123 | 2025-04-06 10:00
91 | Kishoreganj | 132 | 138 | 2025-04-13 08:00 | 117 | 2025-04-03 18:30
92 | Kodda | 132 | 140 | 2025-04-08 18:00 | 117 | 2025-04-15 09:00
93 | KSRM | 132 | 137 | 2025-04-06 18:00 | 126 | 2025-04-16 12:00
94 | Kulaura | 132 | 141 | 2025-04-07 03:00 | 125 | 2025-04-04 23:00
95 | Kurigram | 132 | 142 | 2025-04-28 06:00 | 110 | 2025-04-19 19:00
96 | Kushtia | 132 | 141 | 2025-04-10 23:00 | 121 | 2025-04-23 23:00
97 | Lalbag | 132 | 160 | 2025-04-24 19:00 | 122 | 2025-04-15 12:00
98 | Lalmonirhat | 132 | 138 | 2025-04-27 01:00 | 111 | 2025-04-19 19:00
99 | Madanganj | 132 | 139 | 2025-04-01 07:00 | 113 | 2025-04-13 19:30
100 | Madaripur | 132 | 138 | 2025-04-01 09:00 | 125 | 2025-04-24 23:00
101 | Madartek | 132 | 139 | 2025-04-16 16:00 | 121 | 2025-04-10 11:00
102 | Madunaghat | 132 | 138 | 2025-04-12 19:00 | 127 | 2025-04-19 16:00
103 | Magura | 132 | 142 | 2025-04-10 23:00 | 117 | 2025-04-24 19:00
104 | Mahasthangarh | 132 | 140 | 2025-04-13 06:00 | 119 | 2025-04-19 19:00
105 | Manikganj | 132 | 136 | 2025-04-15 01:00 | 119 | 2025-04-13 10:00
106 | Maniknagar | 132 | 139 | 2025-04-16 16:00 | 120 | 2025-04-08 14:00
107 | Matarbari | 132 | 137 | 2025-04-29 05:00 | 100 | 2025-04-16 12:00
108 | Matuail | 132 | 140 | 2025-04-01 10:00 | 122 | 2025-04-27 10:00
109 | Millgate | 132 | 159 | 2025-04-26 22:00 | 118 | 2025-04-27 10:00
110 | Mirpur | 132 | 137 | 2025-04-01 09:00 | 120 | 2025-04-16 12:00
111 | Mirzapur | 132 | 138 | 2025-04-07 07:00 | 116 | 2025-04-27 10:00
112 | Mithapukur | 132 | 142 | 2025-04-13 05:00 | 117 | 2025-04-19 19:00
113 | MI_Cement | 132 | 140 | 2025-04-01 09:00 | 122 | 2025-04-27 10:00
114 | Modern | 132 | N/A | N/A | N/A | N/A
115 | Mogbazar | 132 | 141 | 2025-04-07 06:00 | 121 | 2025-04-15 11:00
116 | Mongla | 132 | 142 | 2025-04-17 16:00 | 118 | 2025-04-04 23:00
117 | Motijheel | 132 | 138 | 2025-04-07 02:00 | 119 | 2025-04-15 11:00
118 | Muktagacha | 132 | 159 | 2025-04-09 09:00 | 114 | 2025-04-10 10:00
119 | Munshiganj | 132 | 139 | 2025-04-01 09:00 | 121 | 2025-04-27 10:00
120 | Muradnagar | 132 | 138 | 2025-04-07 05:00 | 116 | 2025-04-27 23:00
121 | Mymensingh | 132 | 140 | 2025-04-15 02:00 | 114 | 2025-04-10 06:00
122 | Naogaon | 132 | 141 | 2025-04-13 06:00 | 115 | 2025-04-01 22:00
123 | Narail | 132 | 141 | 2025-04-10 23:00 | 116 | 2025-04-23 22:00
124 | Narinda | 132 | 0 | 2025-04-01 00:00 | N/A | N/A
125 | Narshingdi | 132 | 139 | 2025-04-07 03:00 | 114 | 2025-04-23 23:00
126 | Natore | 132 | 138 | 2025-04-10 23:00 | 122 | 2025-04-01 19:30
127 | Nawabganj | 132 | 140 | 2025-04-16 16:00 | 122 | 2025-04-15 12:00
128 | Netrakona | 132 | 136 | 2025-04-13 08:00 | 105 | 2025-04-09 19:30
129 | New | 132 | 141 | 2025-04-05 19:00 | 119 | 2025-04-27 09:00
130 | Niamatpur | 132 | 145 | 2025-04-13 05:00 | 126 | 2025-04-01 22:00
131 | Noapara | 132 | 141 | 2025-04-17 15:00 | 119 | 2025-04-20 19:00
132 | Pabna | 132 | 138 | 2025-04-10 23:00 | 117 | 2025-04-10 12:00
133 | Palashbari | 132 | 138 | 2025-04-13 05:00 | 115 | 2025-04-19 19:00
134 | Panchagarh | 132 | 142 | 2025-04-10 09:00 | 115 | 2025-04-20 09:00
135 | Patuakhali | 132 | 137 | 2025-04-27 02:00 | 129 | 2025-04-20 19:00
136 | Payra | 132 | 139 | 2025-04-07 00:00 | 131 | 2025-04-24 23:00
137 | PHP | 132 | 136 | 2025-04-17 13:00 | 114 | 2025-04-04 13:00
139 | Postogola | 132 | 142 | 2025-04-01 09:00 | 128 | 2025-04-10 12:00
140 | Purbachal | 132 | 140 | 2025-04-16 16:00 | 119 | 2025-04-15 11:00
141 | Purbasadipur | 132 | 144 | 2025-04-13 05:00 | 114 | 2025-04-26 11:00
142 | Rahanpur | 132 | 146 | 2025-04-13 06:00 | 126 | 2025-04-12 01:00
143 | Rahanpur-400 | 132 | 145 | 2025-04-13 05:00 | 126 | 2025-04-12 01:00
144 | Rahim | 132 | 139 | 2025-04-01 06:00 | 123 | 2025-04-12 23:00
145 | Rajbari | 132 | 140 | 2025-04-29 04:00 | 122 | 2025-04-03 23:00
146 | Rajendrapur | 132 | 159 | 2025-04-13 05:00 | 117 | 2025-04-10 16:00
147 | Rajshahi | 132 | 138 | 2025-04-10 23:00 | 124 | 2025-04-05 20:00
148 | Rajshahi-230 | 132 | 139 | 2025-04-05 12:00 | 114 | 2025-04-01 22:00
149 | Ramganj | 132 | 134 | 2025-04-17 13:00 | 107 | 2025-04-06 14:00
150 | Rampur | 132 | 138 | 2025-04-11 08:00 | 124 | 2025-04-22 11:00
151 | Rampura | 132 | 139 | 2025-04-16 16:00 | 120 | 2025-04-15 11:00
152 | Rangamati | 132 | 137 | 2025-04-07 06:00 | 120 | 2025-04-30 21:00
153 | Rangpur | 132 | 142 | 2025-04-28 06:00 | 113 | 2025-04-19 19:00
154 | Ruppur | 132 | 164 | 2025-04-05 08:00 | 120 | 2025-04-02 23:00
155 | Saidpur | 132 | 140 | 2025-04-13 04:00 | 114 | 2025-04-28 19:00
156 | Satkhira | 132 | 142 | 2025-04-17 16:00 | 115 | 2025-04-20 19:00
157 | Satmasjid | 132 | 140 | 2025-04-15 14:00 | 122 | 2025-04-15 11:00
158 | Savar | 132 | 156 | 2025-04-11 01:00 | 119 | 2025-04-27 10:00
159 | SevenRings | 132 | 144 | 2025-04-07 03:00 | 128 | 2025-04-16 11:00
160 | ShahCement | 132 | 140 | 2025-04-01 08:00 | 122 | 2025-04-27 10:00
161 | Shahjadpur | 132 | 141 | 2025-04-11 00:00 | 129 | 2025-04-19 19:00
162 | Shahjibazar | 132 | 139 | 2025-04-07 03:00 | 123 | 2025-04-03 23:00
163 | Shahmirpur | 132 | 141 | 2025-04-26 19:30 | 127 | 2025-04-25 11:00
164 | Shariatpur | 132 | 141 | 2025-04-30 11:00 | 123 | 2025-04-24 23:00
165 | Sherpur | 132 | 141 | 2025-04-28 07:00 | 112 | 2025-04-01 07:00
166 | Shikalbaha | 132 | 129 | 2025-04-11 07:00 | 117 | 2025-04-24 10:00
167 | Shikalbaha-230 | 132 | 141 | 2025-04-12 18:00 | 123 | 2025-04-22 17:00
168 | Shitalakhya | 132 | 140 | 2025-04-01 09:00 | 122 | 2025-04-27 10:00
169 | Sholosohor | 132 | 137 | 2025-04-07 05:00 | 126 | 2025-04-25 15:00
170 | Shyampur | 132 | 139 | 2025-04-01 00:00 | 122 | 2025-04-27 10:00
171 | Shyampur-230 | 132 | 140 | 2025-04-01 09:00 | 122 | 2025-04-27 10:00
172 | Siddhirganj | 132 | 140 | 2025-04-01 09:00 | 122 | 2025-04-27 10:00
173 | Sirajganj | 132 | 138 | 2025-04-11 00:00 | 112 | 2025-04-22 12:00
174 | Sonargaon | 132 | 139 | 2025-04-07 05:00 | 120 | 2025-04-27 10:00
175 | Sreemongol | 132 | 140 | 2025-04-07 03:00 | 122 | 2025-04-04 23:00
176 | Sreepur | 132 | 138 | 2025-04-21 09:00 | 122 | 2025-04-06 15:00
177 | Srinagar | 132 | 140 | 2025-04-16 16:00 | 123 | 2025-04-15 12:00
178 | SSM | 132 | 141 | 2025-04-26 19:30 | 118 | 2025-04-20 17:00
179 | Sunamganj | 132 | 139 | 2025-04-07 03:00 | 117 | 2025-04-04 23:00
180 | Sylhet | 132 | 139 | 2025-04-07 03:00 | 117 | 2025-04-04 23:00
181 | Sylhet-132 | 132 | 140 | 2025-04-07 03:00 | 120 | 2025-04-04 23:00
182 | Tangail | 132 | 139 | 2025-04-15 02:00 | 114 | 2025-04-15 18:30
183 | Thakurgaon | 132 | 144 | 2025-04-13 03:00 | 113 | 2025-04-06 08:00
184 | TK | 132 | 140 | 2025-04-26 19:30 | 127 | 2025-04-25 15:00
185 | Tongi | 132 | 142 | 2025-04-07 00:00 | 120 | 2025-04-08 09:00
186 | Ullahpara | 132 | 138 | 2025-04-14 01:00 | 110 | 2025-04-20 22:00
187 | Ullon | 132 | 139 | 2025-04-07 01:00 | 120 | 2025-04-10 13:00
188 | Uttara | 132 | 139 | 2025-04-05 19:00 | 120 | 2025-04-11 18:00
189 | UttaraNew | 132 | 138 | 2025-04-05 18:30 | 120 | 2025-04-13 12:00
190 | Zigatola | 132 | 139 | 2025-04-16 16:00 | 123 | 2025-04-10 13:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-36
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month: April 2025
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Aminbazar 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 12-04-2025 | 20:00 | 453 | 146 | 91.5282
Aminbazar 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 12-04-2025 | 20:00 | 443 | 135 | 89.0603
Aminbazar 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 520 | 12-04-2025 | 20:00 | 443 | 135 | 89.0603
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 325 | 01-04-2025 | 6:00 | 0 | 0 | 0
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 28-04-2025 | 10:00 | 199 | 78 | 41.1039
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 28-04-2025 | 10:00 | 199 | 78 | 41.1039
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | 520 | 16-04-2025 | 11:00 | 229 | 1 | 44.0389
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | 520 | 30-04-2025 | 23:00 | 195 | 15 | 37.6108
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 750 | 28-04-2025 | 18:30 | 434 | 13 | 57.8926
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 750 | 28-04-2025 | 18:30 | 434 | 13 | 57.8926
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 750 | 28-04-2025 | 18:30 | 434 | 13 | 57.8926
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | 325 | 24-04-2025 | 23:00 | 180 | 74 | 59.8823
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | 325 | 24-04-2025 | 23:00 | 180 | 74 | 59.8823
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | 325 | 24-04-2025 | 23:00 | 180 | 74 | 59.8823
Gopalganj 400/230kV Grid Sub-Station | ATR-04 | 400/230 | 750 | 27-04-2025 | 01:00 | 185 | 40 | 25.2367
Gopalganj 400/230kV Grid Sub-Station | ATR-05 | 400/230 | 750 | 27-04-2025 | 01:00 | 185 | 40 | 25.2367
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 520 | 23-04-2025 | 02:00 | 277 | 93 | 56.1914
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 520 | 18-04-2025 | 12:00 | 241 | 117 | 51.5191
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 325 | 09-04-2025 | 16:00 | 301 | 44 | 93.5997
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 325 | 09-04-2025 | 16:00 | 301 | 44 | 93.5997
Madunaghat 400/230kV Grid Sub-Station | ATR-1 7006T | 400/230 | 750 | 04-04-2025 | 23:00 | 435 | 189 | 63.238
Madunaghat 400/230kV Grid Sub-Station | ATR-2 7106T | 400/230 | 750 | 04-04-2025 | 23:00 | 435 | 189 | 63.238
Madunaghat 400/230kV Grid Sub-Station | ATR-3 7206T | 400/230 | 750 | 04-04-2025 | 23:00 | 435 | 189 | 63.238
Meghnaghat 400/230kV Grid Sub-Station | ATR-1 | 400/230 | 750 | 12-04-2025 | 18:30 | 542 | 86 | 73.1707
Meghnaghat 400/230kV Grid Sub-Station | ATR-2 | 400/230 | 750 | 12-04-2025 | 18:30 | 541 | 85 | 73.0182
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | 520 | 12-04-2025 | 19:30 | 437 | 70 | 85.1098
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | 520 | 12-04-2025 | 19:30 | 434 | 69 | 84.5098
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | 325 | 10-04-2025 | 07:00 | 79 | 17 | 24.8641
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | 325 | 05-04-2025 | 23:00 | 66 | 24 | 21.6087
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 520 | 26-04-2025 | 00:00 | 203 | 88 | 42.5487
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 520 | 26-04-2025 | 00:00 | 203 | 88 | 42.5487
Amtali 400/132kV Grid Sub-Station
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 300 | 27-04-2025 | 16:00 | 202 | 85 | 73.0517
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 300 | 27-04-2025 | 16:00 | 202 | 85 | 73.0517
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 225 | 27-04-2025 | 10:00 | 181 | 49 | 83.3401
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 225 | 27-04-2025 | 10:00 | 181 | 49 | 83.3401
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 225 | 27-04-2025 | 10:00 | 181 | 49 | 83.3401
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 300 | 02-04-2025 | 23:00 | 240 | 90 | 85.44
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 300 | 19-04-2025 | 19:30 | 240 | 60 | 82.4621
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 300 | 05-04-2025 | 20:00 | 177 | 67 | 63.0855
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 225 | 09-04-2025 | 05:00 | 144 | 31 | 65.4662
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 225 | 07-04-2025 | 19:00 | 190 | 50 | 87.3195
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 225 | 30-04-2025 | 19:30 | 191 | 55 | 88.3383
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 300 | 30-04-2025 | 19:00 | 249 | 42 | 84.1724
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 07-04-2025 | 13:00 | 154 | 14 | 51.545
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 27-04-2025 | 22:00 | 129 | 29 | 44.0732
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | 225 | 27-04-2025 | 19:00 | 148 | 42 | 68.3751
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | 225 | 13-04-2025 | 19:30 | 180 | 20 | 80.4923
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 225 | 22-04-2025 | 01:00 | 183 | 52 | 84.5531
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 225 | 22-04-2025 | 01:00 | 183 | 52 | 84.5531
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 300 | 22-04-2025 | 01:00 | 247 | 74 | 85.949
Bogura 230/132kV Grid Sub-Station | T-04 | 230/132 | 300 | 22-04-2025 | 01:00 | 247 | 74 | 85.949
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-01 | 230/132 | 225 | 05-04-2025 | 12:00 | 175 | 74 | 84.4456
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-02 | 230/132 | 225 | 12-04-2025 | 20:00 | 174 | 76 | 84.3883
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-03 | 230/132 | 225 | 05-04-2025 | 12:00 | 187 | 77 | 89.8811
Fenchuganj 230/132/33kV Grid Sub-Station | AT-01 | 230/132 | 300 | 05-04-2025 | 21:00 | 151 | 60 | 54.1613
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 300 | 05-04-2025 | 21:00 | 185 | 80 | 67.1855
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 125 | 05-04-2025 | 05:00 | 100 | 0 | 80
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 125 | 05-04-2025 | 05:00 | 100 | 0 | 80
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 225 | 23-04-2025 | 21:00 | 128 | 68 | 64.4184
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 225 | 23-04-2025 | 12:00 | 108 | 74 | 58.1866
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 225 | 23-04-2025 | 12:00 | 103 | 80 | 57.9638
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 225 | 23-04-2025 | 09:00 | 82 | 46 | 41.7872
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 225 | 23-04-2025 | 09:00 | 82 | 46 | 41.7872
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 225 | 23-04-2025 | 09:00 | 82 | 46 | 41.7872
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 150 | 05-04-2025 | 19:00 | 92 | 50 | 69.8061
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 150 | 05-04-2025 | 19:00 | 92 | 50 | 69.8061
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 150 | 05-04-2025 | 19:00 | 92 | 50 | 69.8061
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 150 | 05-04-2025 | 19:00 | 92 | 50 | 69.8061
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 225 | 08-04-2025 | 19:30 | 113 | 50 | 54.919
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 225 | 08-04-2025 | 19:30 | 113 | 50 | 54.919
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 225 | 08-04-2025 | 19:30 | 113 | 50 | 54.919
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | 300 | 09-04-2025 | 19:30 | 225 | 105 | 82.7647
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | 300 | 03-04-2025 | 19:00 | 286 | 73 | 98.3898
Kaliakoir 230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 300 | 05-04-2025 | 11:00 | 213 | 73 | 75.0541
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 23-04-2025 | 20:00 | 209 | 71 | 73.5769
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 23-04-2025 | 20:00 | 209 | 71 | 73.5769
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 300 | 01-04-2025 | 00:00 | 0 | 0 | 0
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | 225 | 01-04-2025 | 00:00 | 137 | 45 | 64.0894
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | 225 | 13-04-2025 | 19:00 | 157 | 57 | 74.2342
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | 300 | 04-04-2025 | 07:00 | 154 | 39 | 52.9539
Madunaghat 230/132/33kV Grid Sub-Station | ATR-1(705T) | 230/132 | 300 | 04-04-2025 | 04:00 | 133 | 233 | 89.4291
Madunaghat 230/132/33kV Grid Sub-Station | ATR-2(715T) | 230/132 | 300 | 04-04-2025 | 04:00 | 133 | 233 | 89.4291
Madunaghat 230/132/33kV Grid Sub-Station | ATR-3(725T) | 230/132 | 300 | 27-04-2025 | 04:01 | 133 | 233 | 89.4291
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 300 | 24-04-2025 | 13:00 | 176 | 81 | 64.5816
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 300 | 24-04-2025 | 13:00 | 176 | 81 | 64.5816
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | 300 | 25-04-2025 | 07:00 | 91 | 22 | 31.2072
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | 300 | 28-04-2025 | 01:00 | 289 | 8 | 96.3702
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 300 | 01-04-2025 | 00:00 | 1 | 0 | 0.33333
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 300 | 09-04-2025 | 03:00 | 1 | 0 | 0.33333
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 230/132 | 450 | 27-04-2025 | 18:30 | 249 | 40 | 56.0428
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 LT | 230/132 | 450 | 24-04-2025 | 13:00 | 395 | 67 | 89.0316
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 LT | 230/132 | 450 | 24-04-2025 | 13:00 | 395 | 67 | 89.0316
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 300 | 08-04-2025 | 14:00 | 222 | 160 | 91.2165
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 300 | 10-04-2025 | 19:30 | 231 | 141 | 90.2109
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 300 | 10-04-2025 | 19:30 | 209 | 60 | 72.4806
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 300 | 10-04-2025 | 19:30 | 209 | 60 | 72.4806
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 300 | 23-04-2025 | 00:00 | 114 | 16 | 38.3724
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 300 | 29-04-2025 | 17:00 | 174 | 1 | 58.001
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 300 | 10-04-2025 | 07:00 | 236 | 102 | 85.6997
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 300 | 10-04-2025 | 07:00 | 236 | 102 | 85.6997
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 225 | 08-04-2025 | 10:00 | 215 | 36 | 96.8858
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 225 | 12-04-2025 | 18:30 | 198 | 40 | 89.7778
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 225 | 24-04-2025 | 12:00 | 64 | 0 | 28.4444
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF_LDC_37
|  |  |  | POWER GRID BANGLADESH PLC. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID BANGLADESH PLC. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[5 empty] | Report on load shedding | [12 empty] | Report on load shedding
Month: April 2025 |  |  |  | (For Evening Peak) | [10 empty] | Month: April 2025 |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur
2025-04-01 | 12576 | 12576 | 0 | 20:00 Hr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-04-01 | 10576.14 | 10576.14 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-04-02 | 12903.03 | 12903.03 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-04-02 | 10923.86 | 10923.86 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-04-03 | 13118 | 13118 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-04-03 | 11323.29 | 11323.29 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-04-04 | 13033.5 | 13033.5 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-04-04 | 11482.48 | 11482.48 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-04-05 | 12893.92 | 12893.92 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-04-05 | 12607.04 | 12607.04 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-04-06 | 15046.06 | 15046.06 | 0 | 20:00 Hr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-04-06 | 13381.93 | 13381.93 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-04-07 | 14707.7 | 14800.7 | 89 | 19:00 Hr. | 29 | 0 | 10 | 50 | 0 | 0 | 0 | 0 | 0 | - | 2025-04-07 | 12601.94 | 12601.94 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-04-08 | 15400.79 | 15500.79 | 96 | 21:00 Hr. | 15 | 0 | 10 | 66 | 0 | 0 | 0 | 0 | 5 | - | 2025-04-08 | 13939.17 | 14103.17 | 157 | 12:00 Hr. | 137 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | -
2025-04-09 | 15819.4 | 15881.4 | 59 | 21:00 Hr. | 10 | 0 | 10 | 39 | 0 | 0 | 0 | 0 | 0 | - | 2025-04-09 | 14223.77 | 14352.77 | 123 | 12:00 Hr. | 75 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | -
2025-04-10 | 13585 | 13585 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-04-10 | 14100.15 | 14203.15 | 99 | 12:00 Hr. | 75 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | - | 0
2025-04-11 | 14148.55 | 14148.55 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-04-11 | 12102 | 12102 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-04-12 | 15200.2 | 15350.2 | 144 | 21:00 Hr. | 106 | 0 | 20 | 0 | 0 | 18 | 0 | 0 | 0 | - | 2025-04-12 | 13140 | 13345 | 196 | 12:00 Hr. | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 20 | -
2025-04-13 | 15285.93 | 15381.93 | 92 | 20:00 Hr | 65 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-04-13 | 12247.34 | 12247.34 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-04-14 | 14480 | 14550 | 67 | 21:00 Hr. | 32 | 0 | 15 | 20 | 0 | 0 | 0 | 0 | 0 | - | 2025-04-14 | 12850.78 | 12881.78 | 30 | 12:00 Hr. | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-04-15 | 15490.6 | 15642.6 | 145 | 19:30 Hr. | 110 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | - | 2025-04-15 | 13738.31 | 13783.31 | 43 | 12:00 Hr. | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-04-16 | 12625 | 12625 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-04-16 | 14052.27 | 14103.48 | 49 | 12:00 Hr. | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-04-17 | 12158 | 12158 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-04-17 | 11132.16 | 11132.16 | 0 | 10:00 Hr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-04-18 | 11820.5 | 11820.5 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-04-18 | 11046.36 | 11046.36 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-04-19 | 14451.41 | 14500.41 | 47 | 19:30 Hr. | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 12 | - | 2025-04-19 | 11971.09 | 11971.09 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-04-20 | 15577.7 | 15750.2 | 147 | 19:30 Hr. | 85 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | - | 2025-04-20 | 13359.05 | 13424.05 | 62 | 12:00 Hr. | 52 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
2025-04-21 | 15016 | 15085 | 66 | 19:30 Hr. | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-04-21 | 12364.26 | 12433.26 | 66 | 12:00 Hr. | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-04-22 | 15675.57 | 15775.57 | 96 | 19:30 Hr. | 50 | 0 | 10 | 30 | 0 | 0 | 0 | 6 | 0 | - | 2025-04-22 | 13617.61 | 13682.61 | 62 | 12:00 Hr. | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-04-23 | 15867.9 | 16050.9 | 175 | 21:00 Hr. | 100 | 0 | 0 | 50 | 0 | 0 | 0 | 25 | 0 | - | 2025-04-23 | 13783.65 | 13836.65 | 51 | 12:00 Hr. | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-04-24 | 16365.8 | 16510.8 | 139 | 19:30 Hr. | 55 | 0 | 0 | 60 | 0 | 0 | 0 | 11 | 13 | - | 2025-04-24 | 14594.67 | 14731.67 | 131 | 12:00 Hr. | 131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-04-25 | 15559.86 | 15691.86 | 126 | 21:00 Hr. | 12 | 0 | 5 | 74 | 0 | 0 | 0 | 15 | 20 | - | 2025-04-25 | 13325.59 | 13525.59 | 191 | 12:00 Hr. | 96 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | -
2025-04-26 | 14440.43 | 15998.43 | 1491 | 21:00 Hr. | 310 | 0 | 250 | 210 | 80 | 416 | 80 | 75 | 70 | - | 2025-04-26 | 13491.85 | 13551.85 | 57 | 12:00 Hr. | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | -
2025-04-27 | 15892.58 | 16050.58 | 151 | 19:30 Hr. | 55 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | - | 2025-04-27 | 14361.46 | 14482.46 | 116 | 12:00 Hr. | 116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-04-28 | 12820.5 | 12820.5 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-04-28 | 12234.72 | 12234.72 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-04-29 | 14163.22 | 14163.22 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2025-04-29 | 12746.45 | 12788.45 | 40 | 12:00 Hr. | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-04-30 | 14159.42 | 14159.42 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2025-04-30 | 13386.17 | 13421.7 | 34 | 12:00 Hr. | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
[16 empty] | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: April 2025
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 16365.8 | 2025-04-24 | 19:30 Hr.
2 | Maximum Day Peak Genaration | MW | 14594.67 | 2025-04-24 | 12:00 Hr.
3 | Maximum Evening Peak Demand | MW | 16510.8 | 2025-04-24 | 19:30 Hr.
4 | Minimum Generation | MW | 9058.19 | 2025-04-29 | 05:00 Hr.
5 | Average of the daily evening peak Genaration | MW | 14342.7523 | - | -
6 | Average of the daily day peak Genaration | MW | 12823.5187 | - | -
7 | Maximum load shed (Evening Peak) | MW | 1491 | 2025-04-26 | 21:00 Hr.
8 | Minimum load shed | MW | 0 | 2025-04-02 | 19:30 Hr.
9 | Total nos. of load shed days | Day | 21 | - | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW/Day | 104.3333 | - | -
11 | Total Generation | MkWh | 9278.7748 | - | -
12 | Total Generation by BPDB | MkWh | 1417.8481 | % of total Gen. | 15.28%
13 | Total Generation by IPP | MkWh | 3367.4554 | '' | 36.29%
14 | A) Total Generation by Generation Companies | MkWh | 2738.0106 | '' | 29.51%
| B) Total Generation by REB | MkWh | 116.0982 | " | 1.251%
| C) Total Generation by RENTAL | MkWh | 225.7863 | " | 2.433%
| D) Total Imported from India (BIPTC) | MkWh | 643.5664 | " | 6.936%
| E) Total Imported from Tripura, India (A.C) | MkWh | 17.2166 | " | 0.1855%
| F) Total Imported from Nepal | MkWh | 0 | " | 0%
| E) Total Imported from India (Adani Power Jharkhanda Ltd) | MkWh | 752.7931 | " | 8.113%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4009.324 | % of total Gen. | 43.21%
| B) Oil | MkWh | 1391.2326 | '' | 14.99%
| C) Hydro | MkWh | 0.70868 | '' | 0.007638%
| D) Solar | MkWh | 149.0391 | '' | 1.606%
| E) Coal | MkWh | 2314.7942 | '' | 24.95%
| F) BIPTC (Import from India) | MkWh | 643.5664 | '' | 6.936%
| G) A.C (Import from Tripura, India) | MkWh | 17.2166 | '' | 0.1855%
| H) Total Imported from Nepal | MkWh | 0 | '' | 0%
| I) Adani (Import from India) | MkWh | 752.7931 | '' | 8.113%
| J) Wind | MkWh | 0.1 | '' | 0.001078%
16 | Maximun of the daily total Generation . | MkWh | 355.1003 | 2025-04-24
17 | Monthly Load factor | % | 78.7446 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 59412.1063 | - | -
| A) Gas | M.Taka | 13725.3739 | - | -
| B) Coal | M.Taka | 16732.7749 | - | -
| C) HFO | M.Taka | 19660.0256 | - | -
| D) HSD | M.Taka | 4.4115 | - | -
| E) Hydro | M.Taka | 2.9819 | - | -
| F) Solar | M.Taka | 1864.2615 | - | -
| G) Total Import | M.Taka | 7348.3299 | - | -
| H) Wind | M.Taka | 73.9472 | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 2550.0319 | 2025-04-24
| A) Gas | M.Taka | 520.5298 | 2025-04-30
| B) Coal | M.Taka | 723.0166 | 2025-04-09
| C) HFO | M.Taka | 1111.5129 | 2025-04-24
| D) HSD | M.Taka | 2.6358 | 2025-04-08 | -
| E) Hydro | M.Taka | 0.10897 | 2025-04-03 | -
| F) Solar | M.Taka | 75.8285 | 2025-04-13 | -
| G) Total Import | M.Taka | 310.1458 | 2025-04-27
| H) Wind | M.Taka | 8.4326 | 2025-04-24
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 6.403
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 6.5081
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 82.2 | 30/04/2025 | 06:00
b) | Actual | FT (MSL) | 80.11 | 30/04/2025 | 06:00
22 | Peak Genaration of April 2024 | MW | 16477 | 2024-04-30 | 21:00
23 | Peak Demand of April 2024 | MW | 17200 | 2024-04-29 | 21:00
24 | Maximum peak Generation recorded upto 30/04/2025 | MW | 16477 | 2024-04-30 | 21:00
25 | Maximum peak Demand recorded upto 31/04/2025 | MW | 17200 | 29/04/2024 | 21:00
26 | Maximum load shed recorded upto 31/04/2025 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## FGMO Weekly
Power Grid Bangladesh PLC.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status | [8 empty] | SR at 50 Hz (MW)
SL | Plant Name | Owner | Installed capacity | Capability Status of Last Week | 24.04.2025 | 17.04.2025 | 10.04.2025 | 03.04.2025 | 27.03.2025 | 20.03.2025 | 13.03.2025 | 06.03.2025 | 27.02.2025 | 20.02.2025 | 13.02.2025 | 06.02.2025 | 30.01.2025 | 23.01.2025 | 16.01.2025 | 09.01.2025 | 02.01.2025 | 28.11.2024 | 21.11.2024 | 14.11.2024 | 07.11.2024 | 31.10.2024 | 24.10.2024 | 17.10.2024 | 10.10.2024 | 03.10.2024 | 26.09.2024 | 19.09.2024 | 05.09.2024 | 12.09.2024 | 29.08.2024 | 22.08.2024 | 15.08.2024 | 08.08.2024 | 01.08.2024 | 25.07.2024 | 18.07.2024 | 11.07.2024 | 04.07.2024 | 27.06.2024 | 20.06.2024 | 13.06.2024 | 06.06.2024 | 30.05.2024 | 22.05.2024 | 16.05.2024 | 09.05.2024 | 02.05.2024 | 25.04.2024 | 18.04.2024 | 11.04.2024 | 04.04.2024 | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
(MW)
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | Capable | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70 | Capable
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | Capable |  |  | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | Capable | [35 empty] | 20 | [7 empty] | 20 | 20 | 20 | 20
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 | Capable | [35 empty] | 20 |  | 15 | 15 |  | 15 |  |  |  | 20 | 20 | 20 | 20
6 | Meghnaghat CCPP(Summit) | IPP | 335 | Capable | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 15 | 30 | [7 empty] | 35 | [6 empty] | 25 | 15 | 15 | 15 | 15 | 30 | 30 | 30 |  |  |  | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
7 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | Capable | [16 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 |  |  | 30 | 30 | 30 |  |  |  | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
8 | Ashuganj 225 MW CCPP | APSCL | 221 | Capable | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | [11 empty] | 15 | 15 | 15 | 15 | [15 empty] | 16 | 16 | 16 | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
9 | Bheramara 410 MW CCPP | NWPGCL | 410 | Capable | [33 empty] | 40 | [6 empty] | 30 |  |  |  | 30 | 30 | 30 | 30 | 30
10 | Haripur 412 MW CCPP | EGCB | 412 | Capable | 30
11 | Fenchugonj CCPP Phase-1 | BPDB | 97 | Capable | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
12 | Chandpur 150 MW CCPP | BPDB | 163 | Capable
13 | Siddhirganj 2x120 MW GTPP | EGCB | 210 | Capable
14 | Shikalbaha 225 MW CCPP | BPDB | 225 | Capable
15 | Shikalbaha Peaking GT | BPDB | 150 | Capable
16 | Shahjibazar 330 MW CCPP | BPDB | 330 | Capable
17 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | Capable | [9 empty] | 40 | [20 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 |  |  |  | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
18 | Fenchugonj CCPP Phase-2 | BPDB | 104 | Capable | [6 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
19 | Bhola 225 MW CCPP | BPDB | 194 | Capable | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
20 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365 | Capable
21 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 | Capable | [33 empty] | 20 | [6 empty] | 15 | [6 empty] | 15 | 20 | 20 | 20
22 | Siddhirganj 335 MW CCPP | EGCB | 335 | Capable but not tested recently | 30
23 | Bibiyana-III 400 MW CCPP | BPDB | 400 | Capable | 35 | 35 | 35 |  | 35 | 35 | 35 |  |  |  |  | 35 | 35 | 35 | 35 | 35 | [14 empty] | 35 | 35 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
24 | Sylhet 225 MW CCPP | BPDB | 231 | Capable
25 | RPCL 210 MW CCPP | IPP | 210 | Capable but not tested recently
26 | Khulna 225 MW CCPP | NWPGCL | 230 | Capable but not tested recently
27 | a) Baghabari 71 MW GTPP | BPDB | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | 100 | Not Capable but feasible
28 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50 | Not Capable but feasible
29 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410 | Not Capable but feasible
30 | Bibiyana South 400 MW CCPP | BPDB | 383 | Capable | [14 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30
31 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274 | Not Capable but feasible
32 | Shajibazar 100 MW PP | BPDB | 100 | Not Capable but feasible
33 | Payra 1320 MW Unit-1 | BCPCL | 622 | Capable
34 | Kushiara 163 MW CCPP (KP) | IPP | 163 | Not Capable but feasible | 10 | 10 | 10
35 | Bhola Nutan Bidyut | IPP | 220 | Capable
36 | Haripur 360MW CCPP(HPL) | IPP | 360 | Not Capable but feasible
37 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450 | Not Capable but feasible
Total Installed capacity |  |  |  |  | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity |  |  |  |  | 2325 | 1595 | 1635 | 1072 | 1812 | 1432 | 1464 | 1064 | 592 | 1332 | 1282 | 1682 | 1302 | 1302 | 1685 | 1685 | 1315 | 1813 | 2027 | 1475 | 1475 | 1092 | 1124 | 744 | 712 | 712 | 1802 | 1492 | 1152 | 1492 | 2442 | 2442 | 2036 | 2956 | 2416 | 2476 | 1836 | 1696 | 1696 | 1876 | 3336 | 1196 | 1196 | 1796 | 3416 | 3436 | 3076 | 3038 | 2824 | 2996 | 2996 | 2024 | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve |  |  |  |  | 212 | 152 | 137 | 92 | 172 | 142 | 144 | 109 | 67 | 137 | 132 | 167 | 137 | 137 | 162 | 162 | 122 | 160 | 179 | 132 | 132 | 107 | 109 | 79 | 77 | 77 | 172 | 137 | 107 | 137 | 217 | 217 | 186 | 271 | 216 | 226 | 156 | 141 | 156 | 171 | 291 | 111 | 111 | 161 | 311 | 316 | 276 | 269 | 254 | 280 | 280 | 198 | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO |  |  |  |  | 9 | 7 | 7 | 5 | 7 | 6 | 7 | 6 | 3 | 5 | 5 | 6 | 5 | 5 | 6 | 6 | 5 | 6 | 8 | 5 | 5 | 4 | 5 | 4 | 3 | 3 | 6 | 5 | 4 | 5 | 8 | 8 | 8 | 11 | 9 | 10 | 7 | 7 | 7 | 7 | 12 | 5 | 5 | 7 | 12 | 12 | 11 | 11 | 10 | 11 | 11 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list |  |  |  |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list |  |  |  |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable |  |  |  |  | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently |  |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible |  |  |  |  | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD
New FGMO capable plants under BPSREIP:
Letter date: 09/06/2024
1. Anwara 300 MW Power Plant (United)
2.Chandpur 200 MW Power Plant (Desh energy)
3. Rupsha 105 MW Power Plant (Orion rupsha)
4. Gazipur 100 MW Power Ltd
5. United Payra Power Ltd
6.Sikalbaha 105 MW Power Plant (Baraka Sikalbaha)
7.Karnaphuli Power Ltd
8. Feni Lanka Power Ltd
9. Barisal 110 MW Power Plant (Summit)
10. Madanganj-55 MW Power Plant (Summit)
11. Madhumati 100 MW Power Plant
12. Nawabganj 55 MW Power Plant(Dhaka Southern Power)
13.Manikganj 55 MW Power plant ((Dhaka Southern Power)
14. Manikganj 162 MW Power Plant (MPGL)
15. Zodiac 54 MW Power Plant

## FGMO
Power Grid Bangladesh PLC.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month: April 2025
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | [12 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Bibiyana-III 400 MW CCPP | BPDB | 400 |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
3 | Bibiyana South 400 MW | BPDB | 383
4 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
5 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
6 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | [7 empty] | √ | √
7 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
8 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 |  |  |  | √ | √ | √ |  |  | √
9 | Bagura 113 MW PP (Confidence)-2 | IPP | 113 | [16 empty] | √ |  | √
10 | Energypac Power Venture Thakurgaon Ltd. | IPP | 115 | [16 empty] | √ |  | √
11 | Meghnaghat CCPP(Summit) | IPP | 335 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
12 | Nababganj 55 MW PP (Southern power ) | IPP | 55 | [16 empty] | √
13 | Ashuganj 225 MW CCPP | APSCL | 221 | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
14 | Ashuganj 450 MW CCPP(North) | APSCL | 361
15 | Ashuganj 450 MW CCPP(South) | APSCL | 360
16 | Ashuganj 420 MW CCPP(East) | APSCL | 400
17 | Ashuganj 55 MW PP (Precision) | QRPP | 55
18 | Bheramara 410 MW CCPP | NWPGCL | 410
19 | Haripur 412 MW CCPP | EGCB | 412 | [16 empty] | √ |  | √ | [6 empty] | √ | √
20 | Fenchugonj CCPP Phase-1 | BPDB | 97 | √ | √ | √ | √ | √ | √ | √ |  | √ | [15 empty] | √ |  |  |  | √
21 | Fenchugonj CCPP Phase-2 | BPDB | 104
22 | Siddhirganj 2x120 MW GTPP | EGCB | 210
23 | Shikalbaha 225 MW CCPP | BPDB | 225
24 | Shikalbaha Peaking GT | BPDB | 150
25 | Shahjibazar 330 MW CCPP | BPDB | 330
26 | Chandpur 150 MW CCPP | BPDB | 163
27 | Chandpur 200MW (Desh energy) | IPP | 200 | [16 empty] | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
28 | Feni Lanka Power | IPP | 114 | [16 empty] | √ | √ |  |  |  | √ | √ | √ | √ | √ | √ |  | √ | √
29 | Bhola 225 MW CCPP | BPDB | 194 | [19 empty] | √
30 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
31 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
32 | Siddhirganj 335 MW CCPP | EGCB | 335 | [25 empty] | √
33 | Bibiyana-III 400 MW CCPP | BPDB | 400
34 | Sylhet 225 MW CCPP | BPDB | 231
35 | RPCL 210 MW CCPP | IPP | 210
36 | Khulna 225 MW CCPP | NWPGCL | 230
37 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
38 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
39 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
40 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
41 | Shajibazar 100 MW PP | BPDB | 100
42 | Payra 1320 MW Unit-1 | BCPCL | 622 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
43 | Kushiara 163 MW CCPP (KP) | IPP | 163 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
44 | Haripur 360MW CCPP(HPL) | IPP | 360
45 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450