## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 27-06-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 26-06-2025 | during | 27-06-2025 | during | 27-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 401 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 420 | 450 | 450 | 370 | 370 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 148 | 151 | 335 | 335 | 134 | 134 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 29 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 333 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 80 | 143 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 22.5 | 24 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 21 | 21 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 34 | 25 | 52.19 | 52.19 | 34 | 34 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 195 | 278 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 122 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 88 | 105 | 105 | 88 | 88 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 32 | 51 | 104 | 104 | 50 | 50 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 126 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 35 | 0 | 34 | 0 | 34 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 480 | 450 | 584 | 584 | 400 | 400 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 108 | 125 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2671.5 | 3000 | 5128.4 | 5126.4 | 3092.08 | 3090.08
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 6 | 0 | 5 | 0 | 5 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 23 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 172 | 172 | 172 | 172 | 172 | 172 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 218 | 215 | 215 | 210 | 210 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 3 | 17 | 105 | 105 | 105 | 105 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 30 | 48 | 82 | 72 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 65 | 65 | 65 | 65 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 36 | 89 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 10 | 2 | 25 | 2 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2 | 0 | 2.11 | 0 | 2.11 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 80 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 17 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 48 | 88 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1055 | 1145 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 13 | 18 | 28 | 29 | 28 | 29 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 203 | 203 | 575 | 575 | 200 | 200 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1789 | 2152 | 3564.83 | 3615.72 | 3178.83 | 3182.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 192 | 200 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 343 | 345 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 335 | 340 | 340 | 340 | 340 | 340 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 15 | 13 | 46.7 | 46.7 | 10 | 10 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 42 | 45 | 55 | 55 | 40 | 40 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 8 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 40 | 142 | 150 | 150 | 145 | 145 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 36 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 123 | 178 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 34 | 42 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 1 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 19 | 24.5 | 24.5 | 10 | 10 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 99 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 17 | 28 | 113 | 113 | 28 | 28 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 115 | 115 | 115 | 115 | 115 | Fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 70 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1433 | 1728.2 | 2470.75 | 2400.75 | 2135.55 | 2065.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 26-06-2025 | during | 27-06-2025 | during | 27-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 30 | 34 | 157.5 | 157.5 | 10 | 10 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 158 | 168 | 200 | 200 | 160 | 160 | Fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 94 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 46.54 | 0 | 49.95 | 0 | 49.95 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 10 | 12 | 22 | 22 | 22 | 22 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 308.54 | 325 | 601.05 | 549 | 413.55 | 361.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage instructed by DS(Gen)
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 30 | 30 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 156 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 20 | 30 | 30 | 30 | 25 | 25 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 60 | 80 | 83 | 83 | 40 | 40 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 171 | 170 | 160 | 160 | 160 | 160 | Machine Problem
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 6 | 6 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 350 | 386 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | Authority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1380 | 1450 | 1555 | 1555 | 1362 | 1362
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 450 | 471 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 35 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 154 | 149 | 410 | 410 | 130 | 130 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 74 | 0 | 72 | 0 | 72 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 837 | 970 | 1234.2 | 1234.2 | 1204 | 1204 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1553 | 1695 | 3624.2 | 3552.2 | 3314 | 3242
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 617 | 615 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 6 | 11 | 10 | 10 | 4 | 4 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 897 | 1080 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 197 | 250 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.18 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 2057.18 | 2296 | 2172 | 2171 | 2084 | 2083
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 44 | 44 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 30 | 30 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 178 | 182 | 214 | 214 | 140 | 140 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 181 | 189 | 220 | 220 | 140 | 140 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 | 30 | 30 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 97 | 96 | 96 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.68 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1404 | 1324.56 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 48.18 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 106 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 2334.86 | 2271.56 | 3193.47 | 3026.87 | 2771.68 | 2605.08
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 47 | 50 | 50 | 50 | 47 | 47 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 192 | 198 | 190 | 190 | 190 | 190 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 70 | 98 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 1.1 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 50 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 87 | 0 | 166.22 | 0 | 166.22 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 478.1 | 461 | 704.82 | 502 | 701.82 | 499
System Total |  |  |  |  | 28565.2 | 27084.055 | 14005.18 | 15378.76 | 23014.52 | 22498.94 | 19053.51 | 18490.93
Forecast Scenario (27-06-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15100 |  | 0 |  | 15100
|  |  |  | 1:00 | 14810 |  | 0 |  | 14810
|  |  |  | 2:00 | 14420 |  | 0 |  | 14420
|  |  |  | 3:00 | 13940 |  | 0 |  | 13940
|  |  |  | 4:00 | 13530 |  | 0 |  | 13530
|  |  |  | 5:00 | 13110 |  | 0 |  | 13110
|  |  |  | 6:00 | 12560 |  | 0 |  | 12560
|  |  |  | 7:00 | 12310 |  | 0 |  | 12310
|  |  |  | 8:00 | 12320 |  | 0 |  | 12320
|  |  |  | 9:00 | 12280 |  | 0 |  | 12280
|  |  |  | 10:00 | 12240 |  | 0 |  | 12240
|  |  |  | 11:00 | 12730 |  | 0 |  | 12730
|  |  |  | 12:00 | 13250 |  | 0 |  | 13250
|  |  |  | 13:00 | 13920 |  | 0 |  | 13920
|  |  |  | 14:00 | 13310 |  | 0 |  | 13310
|  |  |  | 15:00 | 13120 |  | 0 |  | 13120
|  |  |  | 16:00 | 12650 |  | 0 |  | 12650
|  |  |  | 17:00 | 12260 |  | 0 |  | 12260
|  |  |  | 18:00 | 12390 |  | 0 |  | 12390
|  |  |  | 18:30 | 13000 |  | 0 |  | 13000
|  |  |  | 19:00 | 13780 |  | 0 |  | 13780
|  |  |  | 19:30 | 14820 |  | 0 |  | 14820
|  |  |  | 20:00 | 15030 |  | 0 |  | 15030
|  |  |  | 21:00 | 15370 |  | 0 |  | 15370
|  |  |  | 22:00 | 15460 |  | 0 |  | 15460
|  |  |  | 23:00 | 15590 |  | 0 |  | 15590
Probable Maximum Temperature: |  |  | 32.00°C
Probable Maximum Demand at Day Peak: |  |  | 13250.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15370.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15119.09 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 324.93 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:13 hrs on 27-06-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 26-06-2025 | [28 empty] | Date: | 26-06-2025 | [28 empty] | Date: | 26-06-2025 | [28 empty] | Date: | 26-06-2025 | [28 empty] | Date: | 26-06-2025 | [12 empty] | Date: | 26-06-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [12 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 35 | 149 | 143 | 245 | 32 | 0 | 35 | 54 | 420 | 151 | 0 | 0 | 17 | 333 | 0 | 0 | 0 | 90 | 22 | 21 | 0 | 450 | 16 | 15 | 0 | 0 | 55 | 66 | 77 | 17 | 100 | 100 | 0 | 172 | 0 | 22 | 203 | 35 | 0 | 33 | 25.5 | 17 | 218 | 0 | 0 | 0 | 1157 | 0 | 43 | 128 | 0 | 0 | 348 | 340 | 16 | 184 | 20 | 38 | 0 | 200 | 16 | 19 | 103 | 50 | 52.2 | 0 | 45 | 290 | 320 | 384 | 0 | 0 | 127 | 8 | 0 | 60 | 25 | 0 | 0 | 168 | 0 | 110 | 185 | 34 | 0 | 0 | 11 | 8302.7 | 355 | 131 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1207 | 17 | 1451 | 0 | 43 | 0 | 113 | 0 | 96 | 113 | 28 | 0 | 0 | 30 | 0 | 153 | 0 | 156 | 0 | 0 | 0 | 330 | 0 | 0 | 196 | 49 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 11 | 120 | 220 | 0 | 615 | 1244 | 0 | 7201 | 15503.7 | 98.59
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 35 | 149 | 143 | 245 | 55 | 0 | 17 | 50 | 420 | 151 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 90 | 22 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 41 | 33 | 77 | 0 | 12 | 100 | 0 | 172 | 0 | 23 | 206 | 35 | 0 | 0 | 23 | 0 | 218 | 0 | 0 | 0 | 1145 | 0 | 51 | 130 | 0 | 0 | 352 | 340 | 10 | 202 | 20 | 34 | 0 | 200 | 9 | 19 | 99 | 48 | 52.2 | 0 | 45 | 285 | 320 | 367 | 0 | 0 | 120 | 8 | 0 | 60 | 25 | 0 | 0 | 169 | 0 | 110 | 186 | 50 | 0 | 0 | 11 | 7984.2 | 450 | 136 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 17 | 1460 | 0 | 43 | 0 | 113 | 0 | 96 | 113 | 28 | 0 | 0 | 30 | 0 | 153 | 0 | 158 | 0 | 0 | 0 | 300 | 0 | 0 | 193 | 49 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 11 | 116 | 220 | 0 | 616 | 1244 | 0 | 7225 | 15209.2 | 98.53
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 35 | 149 | 144 | 195 | 55 | 0 | 17 | 50 | 420 | 153 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 90 | 19 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 53 | 33 | 0 | 0 | 12 | 48 | 0 | 172 | 0 | 30 | 203 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1145 | 0 | 51 | 133 | 0 | 0 | 355 | 340 | 10 | 212 | 20 | 34 | 0 | 200 | 9 | 19 | 100 | 46 | 52.2 | 0 | 45 | 285 | 320 | 367 | 0 | 0 | 120 | 8 | 0 | 60 | 25 | 0 | 0 | 169 | 0 | 111 | 177 | 50 | 0 | 0 | 11 | 7771.2 | 450 | 142 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1169 | 17 | 1453 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 158 | 0 | 0 | 0 | 350 | 0 | 0 | 196 | 49 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 10 | 120 | 220 | 0 | 618 | 1244 | 0 | 6901 | 14672.2 | 98.58
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 35 | 149 | 144 | 145 | 55 | 0 | 17 | 32 | 420 | 148 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 90 | 19 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 31 | 205 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1150 | 0 | 51 | 135 | 0 | 0 | 354 | 340 | 10 | 214 | 20 | 34 | 0 | 200 | 9 | 19 | 98 | 40 | 52.2 | 0 | 44 | 295 | 320 | 362 | 0 | 0 | 129 | 8 | 0 | 60 | 25 | 0 | 0 | 169 | 0 | 111 | 178 | 50 | 0 | 0 | 11 | 7601.2 | 450 | 147 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1172 | 17 | 1444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 161 | 0 | 0 | 0 | 350 | 0 | 0 | 194 | 49 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 10 | 120 | 220 | 0 | 618 | 1100 | 0 | 6727 | 14328.2 | 98.58
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 22 | 149 | 143 | 0 | 15 | 0 | 17 | 16 | 400 | 155 | 0 | 0 | 17 | 333 | 0 | 0 | 0 | 90 | 19 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 31 | 206 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1162 | 0 | 51 | 100 | 0 | 0 | 349 | 340 | 10 | 213 | 20 | 35 | 0 | 200 | 8 | 19 | 97 | 40 | 52.2 | 0 | 45 | 295 | 320 | 346 | 0 | 0 | 134 | 8 | 0 | 60 | 25 | 0 | 0 | 169 | 0 | 111 | 178 | 50 | 0 | 0 | 12 | 7306.2 | 450 | 154 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1137 | 0 | 1371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 165 | 0 | 0 | 0 | 350 | 0 | 0 | 195 | 49 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 10 | 120 | 220 | 0 | 616 | 1100 | 0 | 6565 | 13871.2 | 98.57
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 35 | 149 | 143 | 0 | 15 | 0 | 17 | 0 | 400 | 146 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 90 | 19 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 31 | 203 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1157 | 0 | 51 | 10 | 0 | 0 | 352 | 340 | 10 | 197 | 20 | 34 | 0 | 200 | 9 | 19 | 108 | 38 | 52.2 | 0 | 45 | 290 | 320 | 345 | 0 | 0 | 148 | 8 | 0 | 60 | 25 | 0 | 0 | 169 | 0 | 93 | 178 | 50 | 0 | 0 | 12 | 7131.2 | 450 | 160 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1078 | 0 | 1387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 165 | 0 | 0 | 0 | 380 | 0 | 0 | 198 | 49 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 8 | 120 | 220 | 0 | 616 | 1100 | 0 | 6538 | 13669.2 | 98.56
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 35 | 149 | 111 | 0 | 15 | 0 | 17 | 0 | 320 | 146 | 0 | 0 | 17 | 280 | 0 | 0 | 1 | 70 | 20 | 20 | 0 | 350 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 35 | 205 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1030 | 1 | 51 | 10 | 0 | 0 | 300 | 305 | 10 | 193 | 17 | 35 | 0 | 120 | 9 | 16 | 94 | 36 | 16 | 5 | 45 | 285 | 320 | 368 | 0 | 0 | 130 | 8 | 0 | 60 | 30 | 0 | 0 | 169 | 0 | 55 | 168 | 50 | 0 | 1.99 | 12 | 6568.99 | 450 | 166 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 948 | 0 | 1410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 4.54 | 169 | 0 | 169 | 0 | 0 | 0 | 300 | 0 | 0.33 | 197 | 49 | 70 | 1 | 70 | 0 | 0 | 0.3 | 2 | 0.03 | 0 | 200 | 8 | 120 | 180 | 0 | 616 | 1050 | 0 | 6224.2 | 12793.19 | 98.56
07:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 3 | 35 | 137 | 80 | 0 | 15 | 0 | 17 | 0 | 320 | 149 | 0 | 0 | 0 | 280 | 0 | 0 | 4 | 17 | 21 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 30 | 203 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1010 | 1 | 51 | 0 | 0 | 0 | 300 | 305 | 10 | 195 | 15 | 34 | 0 | 120 | 9 | 16 | 108 | 34 | 0 | 18 | 0 | 295 | 320 | 385 | 0 | 0 | 138 | 8 | 0 | 60 | 30 | 0 | 0 | 169 | 0 | 55 | 168 | 50 | 0 | 11.85 | 12 | 6468.85 | 449 | 174 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 25 | 900 | 0 | 1426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 9.46 | 173 | 0 | 177 | 0 | 0 | 0 | 300 | 0 | 1.02 | 196 | 49 | 70 | 5 | 70 | 0 | 0 | 1.8 | 48 | 0.18 | 0 | 201 | 7 | 120 | 180 | 0 | 617 | 950 | 0 | 6200.46 | 12669.31 | 98.56
08:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 17 | 35 | 149 | 80 | 0 | 15 | 0 | 17 | 0 | 320 | 152 | 0 | 0 | 17 | 280 | 0 | 0 | 8 | 35 | 23 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 1 | 172 | 0 | 4 | 207 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 989 | 6 | 51 | 0 | 0 | 0 | 300 | 305 | 10 | 207 | 15 | 34 | 0 | 120 | 9 | 16 | 101 | 32 | 0 | 35 | 0 | 290 | 320 | 399 | 0 | 0 | 136 | 8 | 0 | 60 | 30 | 0 | 0 | 170 | 0 | 55 | 168 | 44 | 1 | 21.71 | 11 | 6525.71 | 450 | 176 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 36 | 842 | 0 | 1360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 13.95 | 177 | 0 | 181 | 0 | 0 | 0 | 300 | 0 | 1.11 | 196 | 47 | 70 | 8 | 70 | 0 | 0 | 2.9 | 96 | 0.19 | 0 | 203 | 6 | 120 | 180 | 0 | 618 | 900 | 0 | 6128.15 | 12653.86 | 98.55
09:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 17 | 35 | 149 | 80 | 0 | 15 | 17 | 17 | 0 | 320 | 151 | 0 | 0 | 17 | 332 | 0 | 0 | 21 | 47 | 22.5 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 2 | 172 | 0 | 2 | 205 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 921 | 7 | 51 | 0 | 0 | 0 | 341 | 305 | 10 | 208 | 15 | 34 | 0 | 120 | 8 | 16 | 103 | 30 | 0 | 37 | 0 | 295 | 320 | 390 | 0 | 0 | 159 | 8 | 0 | 60 | 30 | 0 | 0 | 170 | 0 | 55 | 177 | 29 | 1 | 21.44 | 11 | 6688.94 | 450 | 176 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 77 | 880 | 0 | 1342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 40.35 | 178 | 0 | 181 | 0 | 0 | 0 | 320 | 0 | 3.25 | 196 | 49 | 70 | 15 | 70 | 0 | 0 | 5.5 | 76 | 0.29 | 0 | 204 | 6 | 120 | 220 | 0 | 616 | 898 | 0 | 6270.39 | 12959.33 | 98.55
10:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 35 | 130 | 48 | 0 | 15 | 20 | 17 | 16 | 420 | 150 | 0 | 0 | 17 | 328 | 0 | 0 | 27 | 70 | 22 | 21 | 0 | 430 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 2 | 203 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 948 | 11 | 51 | 0 | 0 | 0 | 338 | 320 | 10 | 210 | 15 | 50 | 0 | 120 | 9 | 16 | 103 | 36 | 0 | 51 | 0 | 295 | 320 | 390 | 0 | 0 | 159 | 8 | 0 | 60 | 28 | 0 | 0 | 170 | 12 | 45 | 160 | 29 | 1 | 32.02 | 11 | 6906.02 | 450 | 176 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 74 | 890 | 0 | 1340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 55.98 | 178 | 0 | 181 | 0 | 0 | 0 | 414 | 0 | 1.73 | 195 | 48 | 35 | 19 | 70 | 0 | 0 | 3.7 | 88 | 0.5 | 0 | 203 | 4 | 124 | 220 | 0 | 616 | 900 | 0 | 6366.91 | 13272.93 | 98.54
11:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 35 | 115 | 48 | 15 | 15 | 35 | 17 | 16 | 420 | 150 | 0 | 0 | 17 | 328 | 0 | 0 | 35 | 70 | 22.5 | 21 | 0 | 430 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 20 | 12 | 3 | 172 | 0 | 2 | 206 | 0 | 0 | 4 | 0 | 0 | 216 | 0 | 0 | 0 | 1060 | 8 | 51 | 12 | 0 | 0 | 337 | 340 | 28 | 208 | 15 | 51 | 0 | 118 | 9 | 20 | 103 | 34 | 0 | 64 | 0 | 300 | 320 | 390 | 0 | 0 | 158 | 8 | 0 | 60 | 28 | 0 | 0 | 170 | 17 | 45 | 158 | 30 | 1 | 31.5 | 11 | 7133 | 450 | 167 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 43 | 865 | 0 | 1326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 36.83 | 178 | 0 | 181 | 0 | 0 | 0 | 414 | 0 | 5.16 | 193 | 48 | 35 | 13 | 70 | 0 | 0 | 6.4 | 158 | 0.1 | 0 | 209 | 5 | 124 | 220 | 0 | 617 | 897 | 0 | 6365.49 | 13498.49 | 98.54
12:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 35 | 122 | 80 | 195 | 29 | 35 | 35 | 32 | 420 | 148 | 0 | 0 | 17 | 335 | 0 | 0 | 35 | 108 | 22.5 | 21 | 0 | 480 | 0 | 15 | 0 | 0 | 13 | 0 | 0 | 0 | 36 | 48 | 2 | 172 | 0 | 2 | 203 | 0 | 0 | 18 | 0 | 3 | 216 | 0 | 0 | 0 | 1055 | 6 | 51 | 40 | 0 | 0 | 343 | 335 | 42 | 192 | 15 | 51 | 0 | 123 | 17 | 20 | 99 | 34 | 1 | 70 | 0 | 295 | 320 | 350 | 0 | 0 | 156 | 8 | 0 | 60 | 20 | 0 | 0 | 171 | 17 | 45 | 158 | 30 | 2 | 46.54 | 10 | 7582.04 | 450 | 154 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 74 | 837 | 0 | 1404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 48.18 | 178 | 0 | 181 | 0 | 0 | 0 | 414 | 0 | 3.68 | 192 | 47 | 50 | 31 | 70 | 0 | 0 | 1.1 | 87 | 0.18 | 0 | 197 | 6 | 120 | 220 | 0 | 617 | 897 | 0 | 6423.14 | 14005.18 | 98.53
13:00 | 8 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 35 | 149 | 80 | 245 | 55 | 35 | 35 | 48 | 350 | 145 | 0 | 0 | 17 | 335 | 0 | 0 | 34 | 108 | 23 | 0 | 0 | 400 | 0 | 15 | 0 | 0 | 41 | 17 | 0 | 0 | 36 | 48 | 3 | 172 | 0 | 8 | 204 | 0 | 0 | 19 | 0 | 15 | 216 | 0 | 0 | 0 | 1051 | 11 | 51 | 103 | 0 | 0 | 338 | 340 | 41 | 199 | 14 | 51 | 0 | 161 | 12 | 20 | 99 | 40 | 16 | 41 | 7 | 295 | 320 | 375 | 0 | 0 | 144 | 8 | 0 | 60 | 25 | 0 | 0 | 171 | 17 | 45 | 158 | 30 | 3 | 42.83 | 7 | 7712.83 | 450 | 136 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 63.3 | 870 | 0 | 1414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 50.74 | 178 | 0 | 181 | 0 | 0 | 0 | 350 | 0 | 3.78 | 191 | 48 | 50 | 31 | 70 | 0 | 0 | 7.1 | 187 | 0.59 | 0 | 171 | 6 | 120 | 220 | 0 | 615 | 850 | 0 | 6325.51 | 14038.34 | 98.53
14:00 | 24 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 35 | 140 | 64 | 245 | 40 | 35 | 35 | 51 | 350 | 148 | 0 | 0 | 17 | 335 | 0 | 0 | 31 | 90 | 23 | 21 | 0 | 400 | 0 | 15 | 0 | 0 | 36 | 17 | 0 | 0 | 24 | 36 | 1 | 172 | 0 | 3 | 202 | 0 | 0 | 19 | 0 | 16 | 216 | 0 | 0 | 0 | 1050 | 11 | 51 | 127 | 36 | 0 | 342 | 340 | 44 | 198 | 14 | 51 | 0 | 165 | 16 | 20 | 64 | 42 | 16 | 72 | 39 | 300 | 320 | 375 | 0 | 0 | 139 | 8 | 0 | 57 | 28 | 0 | 0 | 171 | 17 | 45 | 144 | 30 | 2 | 48.92 | 8 | 7752.92 | 450 | 142 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 28 | 828 | 0 | 1411.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11.06 | 178 | 0 | 181 | 0 | 0 | 0 | 350 | 0 | 1.1 | 192 | 48 | 50 | 36 | 34 | 0 | 0 | 2.5 | 172 | 0.25 | 0 | 172 | 6 | 120 | 220 | 0 | 616 | 845 | 0 | 6152.59 | 13905.51 | 98.52
15:00 | 24 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 35 | 116 | 64 | 245 | 40 | 35 | 35 | 51 | 400 | 150 | 0 | 0 | 17 | 330 | 0 | 0 | 26 | 90 | 23 | 21 | 0 | 400 | 0 | 20 | 0 | 0 | 49 | 32 | 0 | 0 | 60 | 50 | 3 | 172 | 0 | 2 | 206 | 0 | 0 | 19 | 0 | 16 | 215 | 0 | 0 | 0 | 1098 | 17 | 51 | 132 | 36 | 0 | 337 | 340 | 44 | 206 | 14 | 68 | 0 | 170 | 12 | 19 | 67 | 42 | 16 | 43 | 38 | 305 | 320 | 385 | 0 | 0 | 152 | 8 | 0 | 64 | 28 | 0 | 0 | 171 | 17 | 42 | 124 | 31 | 1 | 1.27 | 9 | 7847.27 | 450 | 142 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 20.37 | 831 | 0 | 1428.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 55.85 | 179 | 0 | 183 | 0 | 0 | 0 | 400 | 0 | 3.58 | 188 | 48 | 50 | 15 | 34 | 0 | 0 | 6.7 | 158 | 0.1 | 0 | 170 | 6 | 120 | 220 | 0 | 616 | 851 | 0 | 6228.99 | 14076.26 | 98.52
16:00 | 24 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 0 | 35 | 35 | 112 | 63 | 245 | 40 | 35 | 54 | 51 | 400 | 150 | 0 | 0 | 35 | 328 | 0 | 0 | 18 | 90 | 23 | 21 | 0 | 450 | 0 | 45 | 0 | 0 | 52 | 32 | 0 | 0 | 60 | 72 | 2 | 172 | 0 | 2 | 203 | 0 | 0 | 19 | 0 | 39 | 219 | 0 | 0 | 0 | 1055 | 6 | 51 | 127 | 36 | 0 | 345 | 340 | 44 | 186 | 14 | 69 | 0 | 167 | 9 | 16 | 60 | 40 | 16 | 38 | 35 | 300 | 320 | 364 | 0 | 0 | 156 | 8 | 0 | 76 | 30 | 0 | 0 | 171 | 0 | 55 | 124 | 33 | 0 | 5.78 | 9 | 7921.78 | 450 | 141 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 26 | 801 | 0 | 1411.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 8.02 | 178 | 0 | 181 | 0 | 0 | 0 | 400 | 0 | 0.64 | 190 | 48 | 50 | 17 | 34 | 0 | 0 | 3.6 | 105 | 0.08 | 0 | 165 | 7 | 120 | 220 | 0 | 617 | 940 | 0 | 6218.86 | 14140.64 | 98.51
17:00 | 24 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 35 | 95 | 63 | 245 | 40 | 35 | 72 | 51 | 400 | 150 | 0 | 0 | 35 | 328 | 0 | 0 | 10 | 70 | 23 | 21 | 0 | 400 | 0 | 45 | 0 | 0 | 24 | 32 | 0 | 0 | 60 | 72 | 0 | 172 | 0 | 5 | 203 | 0 | 0 | 19 | 0 | 45 | 216 | 0 | 0 | 0 | 1034 | 2 | 51 | 130 | 16 | 0 | 346 | 340 | 46 | 196 | 13 | 69 | 0 | 151 | 9 | 19 | 57 | 36 | 16 | 6 | 35 | 300 | 320 | 364 | 0 | 0 | 156 | 7 | 0 | 78 | 30 | 0 | 0 | 170 | 0 | 55 | 135 | 33 | 0 | 7.06 | 10 | 7738.06 | 450 | 141 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5 | 755 | 0 | 1311.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 8.48 | 179 | 0 | 183 | 0 | 0 | 0 | 350 | 0 | 0.77 | 189 | 48 | 50 | 9 | 33 | 0 | 0 | 2.5 | 65 | 0.07 | 0 | 172 | 6 | 120 | 220 | 0 | 617 | 900 | 0 | 5877.19 | 13615.25 | 98.51
18:00 | 24 | 90 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 35 | 95 | 63 | 245 | 40 | 35 | 72 | 51 | 350 | 148 | 0 | 0 | 35 | 328 | 0 | 0 | 2 | 70 | 23 | 21 | 0 | 370 | 0 | 45 | 0 | 0 | 18 | 32 | 0 | 0 | 36 | 48 | 0 | 172 | 0 | 2 | 202 | 0 | 0 | 19 | 1 | 46 | 216 | 0 | 0 | 0 | 990 | 0 | 51 | 133 | 8 | 0 | 300 | 300 | 46 | 191 | 13 | 69 | 0 | 158 | 13 | 19 | 57 | 36 | 16 | 4 | 36 | 290 | 320 | 365 | 0 | 0 | 146 | 7 | 0 | 79 | 30 | 0 | 0 | 169 | 0 | 65 | 135 | 33 | 0 | 2.25 | 12 | 7488.25 | 450 | 141 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9.39 | 780 | 0 | 1223.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 2.56 | 178 | 0 | 184 | 0 | 0 | 0 | 300 | 0 | 0.23 | 190 | 48 | 115 | 1 | 53 | 0 | 0 | 1.8 | 12 | 0.06 | 0 | 170 | 6 | 120 | 220 | 0 | 616 | 800 | 0 | 5666.75 | 13155 | 98.5
19:00 | 24 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 35 | 35 | 95 | 100 | 264 | 45 | 35 | 139 | 51 | 320 | 150 | 0 | 0 | 35 | 329 | 0 | 0 | 0 | 125 | 23 | 21 | 0 | 370 | 7 | 100 | 0 | 0 | 24 | 64 | 39 | 0 | 76 | 88 | 0 | 172 | 5 | 9 | 202 | 17 | 0 | 19 | 2 | 46 | 218 | 0 | 0 | 0 | 1098 | 0 | 51 | 137 | 8 | 0 | 280 | 300 | 46 | 193 | 13 | 72 | 0 | 168 | 27 | 19 | 70 | 42 | 18 | 0 | 36 | 290 | 320 | 386 | 0 | 0 | 131 | 7 | 0 | 80 | 30 | 0 | 0 | 170 | 1 | 84 | 147 | 33 | 0 | 0 | 12 | 8068 | 455 | 144 | 0 | 5 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 785 | 17 | 1306.19 | 0 | 0 | 0 | 7 | 0 | 87 | 25 | 11 | 25 | 0 | 25 | 0 | 178 | 0 | 186 | 0 | 0 | 0 | 300 | 0 | 0 | 190 | 48 | 115 | 0 | 89 | 15 | 0 | 0 | 0 | 0 | 16 | 271 | 9 | 100 | 220 | 0 | 616 | 850 | 7 | 6155.19 | 14223.19 | 98.5
19:30 | 24 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 35 | 35 | 149 | 143 | 278 | 55 | 35 | 162 | 51 | 420 | 148 | 0 | 0 | 35 | 332 | 0 | 0 | 0 | 125 | 23 | 21 | 0 | 450 | 17 | 145 | 0 | 0 | 20 | 66 | 46 | 0 | 89 | 88 | 0 | 172 | 15 | 2 | 201 | 17 | 0 | 25 | 8 | 43 | 218 | 0 | 0 | 0 | 1064 | 0 | 51 | 136 | 8 | 0 | 296 | 300 | 46 | 184 | 14 | 115 | 0 | 165 | 27 | 19 | 114 | 40 | 25 | 0 | 36 | 295 | 320 | 356 | 0 | 0 | 139 | 7 | 0 | 80 | 30 | 0 | 0 | 170 | 17 | 84 | 175 | 33 | 0 | 0 | 12 | 8570 | 461 | 144 | 0 | 17 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 870 | 17 | 1307.14 | 0 | 0 | 0 | 35 | 0 | 90 | 35 | 13 | 25 | 0 | 30 | 0 | 181 | 0 | 189 | 0 | 0 | 0 | 350 | 0 | 0 | 193 | 48 | 115 | 0 | 90 | 15 | 0 | 0 | 0 | 0 | 16 | 269 | 10 | 100 | 220 | 0 | 615 | 930 | 17 | 6455.14 | 15025.14
20:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 35 | 35 | 138 | 127 | 278 | 55 | 55 | 162 | 51 | 420 | 145 | 0 | 0 | 35 | 333 | 0 | 0 | 0 | 125 | 24 | 21 | 0 | 450 | 0 | 145 | 0 | 0 | 12 | 66 | 53 | 0 | 89 | 88 | 0 | 172 | 33 | 7 | 203 | 0 | 0 | 31 | 8 | 45 | 218 | 0 | 0 | 0 | 1032 | 0 | 51 | 135 | 8 | 0 | 320 | 340 | 46 | 181 | 13 | 115 | 0 | 167 | 29 | 19 | 114 | 42 | 52.2 | 0 | 36 | 295 | 320 | 386 | 0 | 0 | 148 | 7 | 0 | 80 | 30 | 0 | 0 | 170 | 17 | 85 | 175 | 33 | 0 | 0 | 12 | 8632.2 | 461 | 143 | 0 | 39 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 850 | 17 | 1310.27 | 0 | 0 | 0 | 35 | 0 | 98 | 0 | 26 | 0 | 0 | 30 | 0 | 181 | 0 | 189 | 0 | 0 | 0 | 350 | 0 | 0 | 193 | 48 | 115 | 0 | 92 | 15 | 0 | 0 | 0 | 0 | 0 | 241 | 9 | 100 | 220 | 0 | 615 | 1070 | 17 | 6517.27 | 15149.47 | 98.49
21:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 35 | 149 | 143 | 278 | 55 | 55 | 126 | 51 | 420 | 151 | 0 | 0 | 35 | 333 | 0 | 0 | 0 | 125 | 24 | 21 | 0 | 450 | 0 | 80 | 0 | 0 | 18 | 34 | 30 | 0 | 89 | 88 | 0 | 172 | 17 | 10 | 203 | 0 | 0 | 23 | 8 | 17 | 218 | 0 | 0 | 0 | 1145 | 0 | 51 | 142 | 8 | 0 | 345 | 340 | 45 | 200 | 13 | 115 | 0 | 178 | 28 | 19 | 114 | 42 | 52.2 | 0 | 36 | 300 | 320 | 386 | 0 | 0 | 156 | 8 | 0 | 80 | 30 | 0 | 0 | 170 | 17 | 94 | 168 | 34 | 0 | 0 | 12 | 8655.2 | 471 | 149 | 0 | 35 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 970 | 17 | 1324.56 | 0 | 0 | 0 | 35 | 0 | 97 | 0 | 0 | 0 | 0 | 30 | 0 | 182 | 0 | 189 | 0 | 0 | 0 | 414 | 0 | 0 | 198 | 50 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 11 | 120 | 220 | 0 | 615 | 1080 | 0 | 6723.56 | 15378.76 | 98.49
22:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 35 | 149 | 143 | 278 | 55 | 0 | 90 | 51 | 420 | 151 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 125 | 23.2 | 0 | 0 | 500 | 0 | 15 | 0 | 0 | 16 | 34 | 8 | 0 | 100 | 88 | 0 | 172 | 16 | 11 | 203 | 0 | 0 | 19 | 8 | 15 | 218 | 0 | 0 | 0 | 1143 | 0 | 51 | 138 | 8 | 0 | 347 | 340 | 46 | 200 | 13 | 115 | 0 | 187 | 29 | 19 | 114 | 42 | 52.2 | 0 | 37 | 290 | 320 | 386 | 0 | 0 | 153 | 8 | 0 | 80 | 30 | 0 | 0 | 170 | 17 | 103 | 168 | 34 | 0 | 0 | 12 | 8477.4 | 425 | 149 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1000 | 17 | 1432.7 | 0 | 0 | 0 | 35 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 188 | 0 | 0 | 0 | 414 | 0 | 0 | 201 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 6 | 120 | 220 | 0 | 615 | 1140 | 0 | 6836.7 | 15314.1 | 98.48
23:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 35 | 35 | 149 | 143 | 278 | 55 | 0 | 89 | 51 | 420 | 151 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 125 | 23.9 | 18 | 0 | 500 | 0 | 15 | 0 | 0 | 25 | 34 | 8 | 0 | 100 | 88 | 0 | 172 | 16 | 17 | 202 | 0 | 0 | 19 | 8 | 17 | 219 | 0 | 0 | 0 | 1147 | 0 | 51 | 140 | 8 | 0 | 347 | 340 | 44 | 206 | 13 | 76 | 0 | 186 | 29 | 19 | 114 | 42 | 52.2 | 0 | 38 | 295 | 320 | 391 | 0 | 0 | 146 | 8 | 0 | 80 | 22 | 0 | 0 | 170 | 17 | 111 | 166 | 33 | 0 | 0 | 11 | 8465.1 | 393 | 149 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1040 | 17 | 1452.09 | 0 | 0 | 0 | 36 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 185 | 0 | 0 | 0 | 414 | 0 | 0 | 198 | 50 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 6 | 126 | 220 | 0 | 617 | 1244 | 0 | 6973.09 | 15438.19 | 98.48
Total KWH | 161424 | 1285440 | 509280 | 0 | 0 | 0 | 0 | 0 | 9626400 | 0 | 0 | 454320 | 840240 | 3278592 | 2388960 | 3867764 | 962296 | 462539 | 1228320 | 813120 | 9196000 | 3580305 | 0 | 0 | 464914 | 7864331 | 0 | 0 | 230218 | 2084400 | 528600 | 441000 | 0 | 10062272.73 | 37636 | 614727 | 0 | 0 | 704160 | 500447 | 282243 | 17288 | 933120 | 1045440 | 23398 | 4132920 | 112908 | 334080 | 4894545.45 | 56873 | 0 | 300960 | 68234.4 | 385563 | 5184655 | 0 | 0 | 0 | 25783634 | 76410 | 1184030 | 2209672 | 200727 | 0 | 8367700 | 7996000 | 700320 | 4901000 | 361008 | 1391040 | 0 | 3954720 | 349440 | 431810 | 2278860 | 939840 | 670968 | 508718 | 674192 | 7112000 | 7645200 | 9423000 | 0 | 0 | 3479481 | 183912 | 0 | 1592640 | 646272 | 0 | 0 | 4511370 | 195480 | 1767600 | 3844800 | 852480 | 12950 | 279560 | 267840 | 184754607.58 | 10740363 | 3699072 | 0 | 66240 | 0 | 912000 | 0 | 0 | 0 | 0 | 92592 | 556560 | 22429090 | 153600 | 33200234 | 0 | 58020 | 0 | 471360 | 0 | 634287 | 225024 | 56164 | 30576 | 497318 | 116841 | 345000 | 4259182 | 0 | 4495200 | 0 | 0 | 0 | 8758400 | 0 | 30840 | 4734000 | 1164218 | 2096568 | 221728 | 1838073 | 26000 | 0 | 46715.16 | 1339200 | 2631 | 23520 | 5302000 | 182445 | 2830000 | 5348450 | 0 | 14785454.54 | 24555636.36 | 30000 | 156354602.06 | 341109209.64

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 26-06-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14005.18 | MW | 12:00 Hr. | Energy Generated |  |  | 341.1092 |  | MKWHr.
| Day Peak Demand |  |  | 14005.18 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.628 |  | MKWHr.
| Evening Peak Generation |  |  | 15378.76 | MW | 21:00 Hr. | Energy Demand |  |  | 341.7372 |  | MKWHr.
| Evening Peak Demand |  |  | 15400.76 | MW | 21:00 Hr. | Maximum Temperature |  |  | 33.3 |  | °C
| Minimum Generation of the Day |  |  | 12653.86 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 972.76 |  | MMCFD
| Maximum Generation of the Day |  |  | 15503.7 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.7435 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 41.2989 | 0 | 18.8016 | 0 | 0 | 0.23022 | 0 | 0 | 60.3307 | Gas | 135.9793 | Gas | 476675579.3741
| Chattogram Zone |  |  | 5.5187 | 30.6782 | 4.3554 | 0 | 4.1329 | 0.099808 | 0 | 0.70416 | 45.4892 | Coal | 103.6486 | Coal | 604836773.103
| Cumilla Zone |  |  | 24.1426 | 0 | 11.5289 | 0 | 0 | 0.50872 | 0.93984 | 0 | 37.12 | HFO | 46.6545 | HFO | 881181041.748
| Mymensingh Zone |  |  | 0.85248 | 0 | 6.0757 | 0 | 0 | 0.29251 | 0 | 0 | 7.2207 | HSD | 0.026 | HSD | 1379560
| Sylhet Zone |  |  | 34.5939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.5939 | Hydro | 4.1329 | Hydro | 413292
| Khulna Zone |  |  | 3.6991 | 22.4291 | 0.31243 | 0 | 0 | 0.55656 | 11.6524 | 0 | 38.6495 | Solar | 4.1712 | Solar | 68064101.0076
| Barishal Zone |  |  | 8.3609 | 44.6431 | 0.05352 | 0 | 0 | 0.002631 | 0 | 0 | 53.0601 | Import | 45.7924 | Import | 257411167.29
| Rajshahi Zone |  |  | 17.5128 | 0 | 1.5923 | 0 | 0 | 0.87316 | 33.2002 | 0 | 53.1784 | Wind | 0.70416 | Wind | 10308902.4
| Rangpur Zone |  |  | 0 | 5.8982 | 3.9346 | 0.026 | 0 | 1.6076 | 0 | 0 | 11.4665
| Total |  |  | 135.9793 | 103.6486 | 46.6545 | 0.026 | 4.1329 | 4.1712 | 45.7924 | 0.70416 | 341.1092
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 476675579.3741 |  | Hydro | 413292
|  |  |  | Coal | 604836773.103 |  | Solar | 68064101.0076
|  |  |  | HFO | 881181041.748 |  | Import | 257411167.29
|  |  |  | HSD | 1379560 |  | Wind | 10308902.4
[5 empty] | Total: | 230,02,70,416 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 10.7404 | Peak Hr Flow | 471.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 46189709.15 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 33.2002 | Peak Hr Flow | 1324.56 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 740 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.93984 | Peak Hr Flow | 42.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 1000 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 44.8804 | Peak Hr Flow | 1837.56 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5464
|  |  |  | Chattogram |  | 0 |  | 1351
|  |  |  | Cumilla |  | 0 |  | 1436
|  |  |  | Mymensingh |  | 0 |  | 1192
|  |  |  | Sylhet |  | 0 |  | 626
|  |  |  | Khulna |  | 0 |  | 1755
|  |  |  | Barishal |  | 0 |  | 466
|  |  |  | Rajshahi |  | 0 |  | 1567
|  |  |  | Rangpur |  | 21 |  | 1024
|  |  |  | Total |  | 21 |  | 14881
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[5 empty] | Total | 300 |  |  |  | Total | 476
|  |  |  | Total Unavailable Capacity |  |  |  | 776
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:46 | 13:25 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) LT Scheduled S/D Due to Oil
filling
| 09:46 | 13:24 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT Scheduled S/D Due to Oil
filling
| 10:42 | 13:59 | Aminbazar-Meghnaghat 400kV Ckt-1 Scheduled S/D from Meghnaghat 400/230kV end Due to For
maintenance purpose
|  | 11:00 | AKSML-Baroaulia 132kV Ckt-1 is restored.
| 11:34 | 16:50 | Sunamganj 132/33kV S/S Chhatak-Sunamgonj CKT-2 Forced S/D Due to Eor chatak side tower
maintenance CKT-2 shutdown . NLDC AE inform us at 11.32 AM then we follow the NLDC AE
instructions and shutdown the CKT-2 .
| 12:45 |  | Madanganj 132/33kV S/S BUS Coupler Scheduled S/D
| 13:24 |  | Meghnaghat 230/132kV S/S Meghnaghat-GT-02(MPL) Scheduled S/D Due to DS maintenance
| 14:26 | 17:10 | Khulshi 132/33kV S/S Khulshi-Halishahar CKT-3 Scheduled S/D Due to To replace Damaged
loop in between CB and Bus isolator at Khulshi Side
| 14:32 | 17:09 | Halishahar-Julda 132kV Ckt-1 Forced S/D from Juldah 132/33kV end Due to Maintenance Work
of Khulsi End.
| 16:43 | 20:04 | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T HT Tripped showing SIPROTEC 7UT86 | [7 empty] | 50.0MW load
|  |  | relays Due to Mechanical trip | [7 empty] | interrup.
| 16:43 | 20:06 | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T LT Tripped showing ABB REB500 relays | [7 empty] | 50.0MW load
|  |  | Due to Mechanical Trip | [7 empty] | interrup.
|  | 17:12 | Halishahar-Julda 132kV Ckt-1 is restored.
|  | 17:57 | Madunaghat 132/33kV S/S ATR-1(705T) LT is restored.
|  | 17:57 | Madunaghat 132/33kV S/S ATR-1(705T) HT is restored.
| 18:26 |  | Raozan 25 MW PP Synchronized
|  | 18:46 | Jhenaidah-Magura 132 kV Ckt-1 is restored.
| 21:00 |  | Evening peak Generation is 15378 MW
|  | 21:08 | Aminbazar-Kallyanpur 132kV Ckt-1 is restored.
| 23:55 |  | Meghnaghat CCPP(Summit) GT-2 Ready with remarks:- None
| 01:53 |  | Meghnaghat CCPP(Summit) GT-2 Synchronized with remarks:- NLDC asked for GT 2 startup, GT
2 was under maintenance.
| 01:53 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- GT2
| 04:38 |  | Raozan 25 MW PP Shutdown
| 05:02 | 05:10 | Thakurgaon 132/33kV S/S T-3(432T) LT Tripped showing O/C relays Due to Pirganj ও | [7 empty] | 5.0MW load
|  |  | Ranisankail 33kV feeder trip by E/F and O/C একই সাথে T-3 incoming O/C এ Trip করে যায়। | [7 empty] | interrup.
| 05:35 |  | Meghnaghat 400/230kV S/S ATR-1 HT Scheduled S/D Due to For maintenance work
| 05:36 |  | Meghnaghat 400/230kV S/S ATR-1 LT Scheduled S/D Due to For maintenance work
| 06:09 |  | Aminbazar-Mirpur 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Main Bus Red
hot maintenance work.
| 06:16 |  | Kulaura 132/33kV S/S TR-2 LT Project Work S/D Due to PDB Project Work | [7 empty] | 12.0MW load
interrup.
| 06:17 |  | Kulaura 132/33kV S/S TR-2 HT Project Work S/D Due to PDB Project Work | [7 empty] | 12.0MW load
interrup.
| 06:23 |  | Barapukuria 230/132/33kV S/S 230/132 KV T-02, 713T LT Forced S/D Due to T-02 aux supply | [7 empty] | 70.0MW load
|  |  | CB Replace. | [7 empty] | interrup.
| 06:24 |  | Barapukuria 230/132/33kV S/S 230/132 KV T-02, 713T HT Forced S/D Due to T-02 aux supply | [7 empty] | 70.0MW load
|  |  | CB Replace. | [7 empty] | interrup.
| 06:43 |  | Jhenaidah 230/132kV S/S Transformer- 1 LT Scheduled S/D Due to CT clamp Change
| 06:44 |  | Jhenaidah 230/132kV S/S Transformer- 1 HT Scheduled S/D Due to CT clamp Change
| 06:54 |  | Daudkandi 132/33kV S/S Transformer-3 LT Scheduled S/D Due to Shutdown for Redhot | [7 empty] | 30.0MW load
|  |  | Maintenance work | [7 empty] | interrup.
| 06:54 |  | Daudkandi 132/33kV S/S Transformer-3 HT Scheduled S/D Due to Shutdown for Redhot | [7 empty] | 30.0MW load
|  |  | Maintenance work | [7 empty] | interrup.
| 07:00 |  | Minimum Generation: 11812 MW.
| 07:04 | 07:46 | Bhaluka 132/33kV S/S Transformer- 02 LT Scheduled S/D Due to Red hot minimize at 33 kV CT | [7 empty] | 15.0MW load
|  |  | outgoing. | [7 empty] | interrup.
| 07:05 | 07:47 | Bhaluka 132/33kV S/S Transformer- 02 HT Scheduled S/D Due to Red hot minimize at 33 kV | [7 empty] | 15.0MW load
|  |  | side | [7 empty] | interrup.
| 07:22 |  | Narshingdi 132/33kV S/S T-3 LT Scheduled S/D Due to T-3 transformer oil leakage repair
work on the buchholz relay.
| 07:23 |  | Narshingdi 132/33kV S/S T-3 HT Scheduled S/D Due to T-3 transformer oil leakage repair
work on the buchholz relay.
| 07:33 |  | Sylhet 132/33kV S/S T4 HT Project Work S/D Due to 33 KV ST.Aux-2 replacement work by BPDB | [7 empty] | 22.0MW load
|  |  | S&D-4. | [7 empty] | interrup.
| 07:33 |  | Sylhet 132/33kV S/S T4 LT Project Work S/D Due to 33 KV ST.Aux-2 replacement work by BPDB | [7 empty] | 22.0MW load
|  |  | S&D-4. | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 26-06-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 401 | 9626400 | Allocation limit by Titas, instructed by DS(Gen)
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9196000 | Allocation limit by Titas, instructed by DS(Gen)
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 151 | 3580305 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 962296 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 333 | 7864331 | Allocation limit by Titas, instructed by DS(Gen)
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 161424 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 454320 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 143 | 2388960 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 462539 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 464914 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 24 | 528600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 441000 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 509280 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 278 | 3867764 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3278592 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1285440 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 51 | 813120 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 1228320 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 230218 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 840240 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 450 | 10062272.73 | None
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 125 | 2084400 | -
Dhaka Area Total |  |  |  |  | 5939.724 | 3000 | 60330735.73
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 68234.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 76410 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 23 | 300960 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 172 | 4132920 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 5184655 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 385563 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 30 | 282243 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 500447 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 89 | 933120 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 10 | 334080 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 23398 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 80 | 614727 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 17288 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 112908 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 88 | 1045440 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 37636 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 56873 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1145 | 25783634 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 18 | 704160 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 203 | 4894545.45 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4895.72 | 2152 | 45489241.85
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 200 | 4901000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 345 | 8367700 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 7996000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 13 | 361008 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 45 | 700320 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 200727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1184030 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 142 | 2209672 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 674192 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 178 | 3954720 | -
| Import (Tripura) |  | Import | 0 | 160 | 42 | 939840 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 670968 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 431810 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2278860 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 349440 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1391040 | Fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 508718 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1728.2 | 37120045
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 34 | 852480 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12950 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 168 | 3844800 | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 94 | 1767600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 279560 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 267840 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 195480 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 325 | 7220710
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | Gas shortage instructed by DS(Gen)
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 156 | 3479481 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 646272 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1592640 | Under Maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 170 | 4511370 | Machine Problem
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 183912 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7112000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 386 | 9423000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7645200 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1450 | 34593875
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 471 | 10740363 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 35 | 66240 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 149 | 3699072 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 153600 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 92592 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 556560 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 970 | 22429090 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1695 | 38649517
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 615 | 14785454.54 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 23520 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 11 | 182445 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2830000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1080 | 24555636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5348450 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 30000 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 250 | 5302000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2631 | -
Barishal Area Total |  |  |  |  | 2236 | 2296 | 53060136.9
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 58020 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 56164 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 182 | 4259182 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 189 | 4495200 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8758400 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 116841 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 30576 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 97 | 634287 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 471360 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 225024 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 30840 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1324.56 | 33200234 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 345000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 497318 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2271.56 | 53178446
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1164218 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 198 | 4734000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 26000 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 1838073 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 46715.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2096568 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 221728 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1339200 | -
Rangpur Area Total |  |  |  |  | 950 | 461 | 11466502.16
Eastern Grid Total |  |  |  |  | 16705.895 | 8655.2 | 184754607.58
Western Grid Total |  |  |  |  | 10378.16 | 6723.56 | 156354602.06
National Grid Total |  |  |  |  | 27084.055 | 15378.76 | 341109209.64
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 26-06-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10069.91 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4791 | MW
i) Dhaka area |  |  | 5464.48 |  | MW | i) Khulna area |  |  |  | 1755 | MW
ii) Chattogram area |  |  | 1351 |  | MW | ii) Barishal area |  |  |  | 466 | MW
iii) Cumilla area |  |  | 1436.43 |  | MW | iii) Rajshahi area |  |  |  | 1567 | MW
iv) Mymensingh area |  |  | 1192 |  | MW | iv) Rangpur area |  |  |  | 1003 | MW
v) Sylhet area |  |  | 626 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14860.91 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 85 | 19:30 | 133 | Patuakhali | 80 | 21:00
2 | AKSML | 114 | 15:00 | 68 | Jaldhaka | 92 | 21:00 | 134 | Payra | 36 | 23:00
3 | Aftabnagar | 42 | 15:00 | 69 | Jamalpur | 122 | 00:00 | 135 | Postogola | 61 | 19:00
4 | Agargaon | 140 | 15:00 | 70 | Jashore | 142 | 19:30 | 136 | Purbachal | 23 | 00:00
5 | Agrabad | 98 | 17:00 | 71 | Jhenaidah | 122 | 00:00 | 137 | Purbasadipur | 142 | 00:00
6 | Amnura | 40 | 00:00 | 72 | Joydebpur | 145 | 19:00 | 138 | Rahanpur | 33 | 22:00
7 | Ashuganj | 103 | 23:00 | 73 | Joypurhat | 67 | 00:00 | 139 | Rahim | 33 | 14:00
8 | BSRM | 190 | 05:00 | 74 | Juldah | 15 | 02:00 | 140 | Rajbari | 83 | 23:00
9 | Bagerhat | 83 | 19:30 | 75 | KSRM | 30 | 08:00 | 141 | Rajendrapur | 134 | 00:00
10 | Bajitpur | 58 | 23:00 | 76 | Kabirpur | 251 | 19:00 | 142 | Rajshahi | 117 | 00:00
11 | Bakulia | 97 | 19:30 | 77 | Kachua | 94 | 00:00 | 143 | Rajshahi-230 | 87 | 21:00
12 | Banani | 26 | 11:00 | 78 | Kallyanpur | 108 | 00:00 | 144 | Ramganj | 112 | 19:00
13 | Bangabhaban | 19 | 10:00 | 79 | Kalurghat | 40 | 14:00 | 145 | Rampur | 42 | 00:00
14 | Barapukuria | 68 | 23:00 | 80 | Kamrangirchar | 68.8 | 13:00 | 146 | Rangamati | 17 | 19:30
15 | Barguna | 22 | 19:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 143 | 13:00
16 | Barishal | 107 | 12:00 | 82 | Kasba | 39 | 23:00 | 148 | Ruppur | 7.2 | 10:00
17 | Barishal-230 | 98 | 21:00 | 83 | Kazla | 102 | 19:30 | 149 | SSM | 2 | 04:00
18 | Baroaulia | 66 | 11:00 | 84 | Keranigonj | 91 | 23:00 | 150 | Saidpur | 124 | 21:00
19 | Baroirhat | 64 | 20:00 | 85 | Khagrachori | 32 | 19:00 | 151 | Satkhira | 130 | 00:00
20 | Bashundhara | 192 | 12:00 | 86 | Khulna | 65 | 13:00 | 152 | Satmasjid | 104 | 19:00
21 | BashundharaCement | 7 | 01:00 | 87 | Khulshi | 161 | 15:00 | 153 | Savar | 242 | 16:00
22 | Beanibazar | 85 | 23:00 | 88 | Kishoreganj | 148 | 19:30 | 154 | SevenRings | 19.31 | 03:00
23 | Benapole | 70 | 00:00 | 89 | Kodda | 301 | 11:00 | 155 | ShahCement | 28 | 00:00
24 | Bhaluka | 150 | 19:30 | 90 | Kulaura | 50 | 00:00 | 156 | Shahjadpur | 79 | 00:00
25 | Bhandaria | 56 | 21:00 | 91 | Kurigram | 70 | 23:00 | 157 | Shahjibazar | 135 | 23:00
26 | Bhangura | 40 | 21:00 | 92 | Kushtia | 156 | 21:00 | 158 | Shahmirpur | 62 | 01:00
27 | Bheramara(GK) | 68 | 22:00 | 93 | Lalbag | 58 | 13:00 | 159 | Shariatpur | 89 | 22:00
28 | Bhulta | 261 | 12:00 | 94 | Lalmonirhat | 65 | 21:00 | 160 | Sherpur | 160 | 23:00
29 | Bog-Sherpur | 68 | 23:00 | 95 | MI_Cement | 15.7 | 18:00 | 161 | Shikalbaha | 14 | 11:00
30 | Bogura | 178 | 21:00 | 96 | Madanganj | 38 | 00:00 | 162 | Shitalakhya | 86.2 | 12:00
31 | Borhanuddin | 89 | 23:00 | 97 | Madaripur | 119 | 23:00 | 163 | Sholosohor | 48 | 15:00
32 | Brahmanbaria | 138 | 01:00 | 98 | Madartek | 98 | 00:00 | 164 | Shyampur | 160 | 02:00
33 | Cantonment | 160 | 13:00 | 99 | Madunaghat | 57 | 19:30 | 165 | Siddhirganj | 120 | 12:00
34 | Chandina | 15.96 | 00:00 | 100 | Magura | 64 | 00:00 | 166 | Sirajganj | 106 | 23:00
35 | Chandpur | 80 | 00:00 | 101 | Mahasthangarh | 82 | 00:00 | 167 | Sonargaon | 99 | 11:00
36 | Chandraghona | 36 | 20:00 | 102 | Manikganj | 131 | 20:00 | 168 | Sreemongol | 93 | 00:00
37 | Chapai | 75 | 22:00 | 103 | Maniknagar | 84 | 13:00 | 169 | Sreepur | 108 | 21:00
38 | Charsaidpur | 48 | 01:00 | 104 | Matarbari | 51 | 21:00 | 170 | Srinagar | 49 | 22:00
39 | Chauddagram | 74 | 23:00 | 105 | Matuail | 67 | 12:00 | 171 | Sunamganj | 63 | 01:00
40 | Chhatak | 42 | 22:00 | 106 | Millgate | 98 | 15:00 | 172 | Sylhet | 53 | 00:00
41 | Chowmuhani | 205 | 19:30 | 107 | Mirpur | 125 | 14:00 | 173 | Sylhet-132 | 128 | 16:00
42 | Chuadanga | 116 | 00:00 | 108 | Mirsorai | 11 | 16:00 | 174 | TK | 30.5 | 00:00
43 | Coxsbazar | 143 | 19:00 | 109 | Mirzapur | 44 | 00:00 | 175 | Tangail | 186 | 22:00
44 | Cumilla(N) | 159 | 00:00 | 110 | Mithapukur | 70 | 01:00 | 176 | Thakurgaon | 114 | 21:00
45 | Cumilla(S) | 179 | 19:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 142 | 00:00
46 | Daudkandi | 159 | 21:00 | 112 | Mogbazar | 161.4 | 15:00 | 178 | Ullahpara | 40 | 19:30
47 | Dhaka | 60 | 11:00 | 113 | Mongla | 44 | 12:00 | 179 | Ullon | 42 | 00:00
48 | Dhamrai | 134 | 19:30 | 114 | Motijheel | 41 | 11:00 | 180 | Uttara | 86 | 11:00
49 | Dhanmondi | 158 | 15:00 | 115 | Muktagacha | 38 | 19:30 | 181 | UttaraNew | 62 | 00:00
50 | Dohazari | 105 | 20:00 | 116 | Munshiganj | 118 | 00:00 | 182 | Zigatola | 76 | 00:00
51 | Faridpur | 171 | 21:00 | 117 | Muradnagar | 30 | 00:00
52 | Fatullah | 99 | 12:00 | 118 | Mymensingh | 205 | 20:00
53 | Fenchuganj | 50 | 19:00 | 119 | Naogaon | 141 | 23:00
54 | Feni | 122 | 19:30 | 120 | Narail | 58 | 00:00
55 | GPH | 15 | 10:00 | 121 | Narinda | 88 | 13:00
56 | Ghatail | 78 | 01:00 | 122 | Narshingdi | 197 | 00:00
57 | Ghorashal | 14 | 00:00 | 123 | Natore | 156 | 21:00
58 | Ghorashal-230 | 94 | 00:00 | 124 | Nawabganj | 62.6 | 23:00
59 | Goalpara | 39 | 00:00 | 125 | Netrakona | 134 | 23:00
60 | Gollamari | 100 | 19:30 | 126 | New | 92.2 | 12:00
61 | Gopalganj | 110 | 22:00 | 127 | Niamatpur | 80 | 22:00
62 | Gulshan | 156 | 15:00 | 128 | Noapara | 45 | 22:00
63 | Halishahar | 75 | 10:00 | 129 | PHP | 6 | 18:00
64 | HaripurSBU | 161 | 16:00 | 130 | Pabna | 127 | 21:00
65 | Hasnabad | 63 | 23:00 | 131 | Palashbari | 124 | 00:00
66 | Hathazari | 85 | 21:00 | 132 | Panchagarh | 64 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 26-06-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15503.7 | 54 |  | 15559.7
1:00 | 15209.2 | 68 |  | 15280.2
2:00 | 14672.2 | 65 |  | 14740.2
3:00 | 14328.2 | 64 |  | 14395.2
4:00 | 13871.2 | 0 |  | 13871.2
5:00 | 13669.2 | 0 |  | 13669.2
6:00 | 12793.19 | 0 |  | 12793.19
7:00 | 12669.31 | 0 |  | 12669.31
8:00 | 12653.86 | 0 |  | 12653.86
9:00 | 12959.33 | 0 |  | 12959.33
10:00 | 13272.93 | 0 |  | 13272.93
11:00 | 13498.49 | 0 |  | 13498.49
12:00 | 14005.18 | 0 |  | 14005.18
13:00 | 14038.34 | 0 |  | 14038.34
14:00 | 13905.51 | 0 |  | 13905.51
15:00 | 14076.26 | 0 |  | 14076.26
16:00 | 14140.64 | 0 |  | 14140.64
17:00 | 13615.25 | 0 |  | 13615.25
18:00 | 13155 | 0 |  | 13155
19:00 | 14223.19 | 102 |  | 14330.19
19:30 | 15025.14 | 148 |  | 15180.14
20:00 | 15149.47 | 144 |  | 15299.47
21:00 | 15378.76 | 21 |  | 15400.76
22:00 | 15314.1 | 31 |  | 15346.5
23:00 | 15438.19 | 79 |  | 15520.75
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 26-06-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8302.7 | 7201 | 15503.7 | DAILY GENERATION CURVE
00:30 | 8143.45 | 7213 | 15356.45
01:00 | 7984.2 | 7225 | 15209.2 | 26-06-2025
01:30 | 7877.7 | 7063 | 14940.7
02:00 | 7771.2 | 6901 | 14672.2
02:30 | 7686.2 | 6814 | 14500.2
03:00 | 7601.2 | 6727 | 14328.2
03:30 | 7453.7 | 6646 | 14099.7
04:00 | 7306.2 | 6565 | 13871.2
04:30 | 7218.7 | 6551.5 | 13770.2
05:00 | 7131.2 | 6538 | 13669.2
05:30 | 6850.095 | 6381.1 | 13231.195
06:00 | 6568.99 | 6224.2 | 12793.19
06:30 | 6518.92 | 6212.33 | 12731.25
07:00 | 6468.85 | 6200.46 | 12669.31
07:30 | 6497.28 | 6164.305 | 12661.585
08:00 | 6525.71 | 6128.15 | 12653.86
08:30 | 6607.325 | 6199.27 | 12806.595
09:00 | 6688.94 | 6270.39 | 12959.33
09:30 | 6797.48 | 6318.65 | 13116.13
10:00 | 6906.02 | 6366.91 | 13272.93
10:30 | 7019.51 | 6366.2 | 13385.71
11:00 | 7133 | 6365.49 | 13498.49
11:30 | 7357.52 | 6394.315 | 13751.835
12:00 | 7582.04 | 6423.14 | 14005.18
12:30 | 7647.435 | 6374.325 | 14021.76
13:00 | 7712.83 | 6325.51 | 14038.34
13:30 | 7732.875 | 6239.05 | 13971.925
14:00 | 7752.92 | 6152.59 | 13905.51
14:30 | 7800.095 | 6190.79 | 13990.885
15:00 | 7847.27 | 6228.99 | 14076.26
15:30 | 7884.525 | 6223.925 | 14108.45
16:00 | 7921.78 | 6218.86 | 14140.64
16:30 | 7829.92 | 6048.025 | 13877.945
17:00 | 7738.06 | 5877.19 | 13615.25
17:30 | 7613.155 | 5771.97 | 13385.125
18:00 | 7488.25 | 5666.75 | 13155
18:30 | 7778.125 | 5910.97 | 13689.095
19:00 | 8068 | 6155.19 | 14223.19
19:30 | 8570 | 6455.14 | 15025.14
20:00 | 8632.2 | 6517.27 | 15149.47
20:30 | 8643.7 | 6620.415 | 15264.115 |  | Executive Engineer
21:00 | 8655.2 | 6723.56 | 15378.76 |  | Network Operation Division
21:30 | 8566.3 | 6780.13 | 15346.43
22:00 | 8477.4 | 6836.7 | 15314.1
22:30 | 8471.25 | 6904.895 | 15376.145
23:00 | 8465.1 | 6973.09 | 15438.19

## En-Curve
QF-LDC-12
Date | 26-06-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3666 | 1880 | 355 | 38 | 50 | 1451 | 172 | 4951 | 0 | 669 | 2216.7 | 0 | 0 | 55 | 54 | DAILY ENERGY CURVE
00:30 | 3664.5 | 1850.5 | 402.5 | 38 | 49 | 1455.5 | 172 | 4920 | 0 | 639.5 | 2116.95 | 0 | 0 | 48 | 61 | 26-06-2025
01:00 | 3663 | 1821 | 450 | 38 | 48 | 1460 | 172 | 4889 | 0 | 610 | 2017.2 | 0 | 0 | 41 | 68
01:30 | 3700 | 1823.5 | 450 | 38 | 47 | 1456.5 | 172 | 4893.5 | 0 | 473.5 | 1839.7 | 0 | 0 | 47 | 66.5 | Energy Generated | 341.1092 |  | MKWHr
02:00 | 3737 | 1826 | 450 | 38 | 46 | 1453 | 172 | 4898 | 0 | 337 | 1662.2 | 0 | 0 | 53 | 65 | Energy not Served | 0.628 |  | MKWHr
02:30 | 3738.5 | 1833.5 | 450 | 38 | 43 | 1448.5 | 172 | 4832.5 | 0 | 320 | 1581.2 | 0 | 0 | 43 | 64.5 | Total Energy Requirement | 341.7372 |  | MKWHr
03:00 | 3740 | 1841 | 450 | 38 | 40 | 1444 | 172 | 4767 | 0 | 303 | 1500.2 | 0 | 0 | 33 | 64
03:30 | 3734 | 1812 | 450 | 38 | 40 | 1407.5 | 172 | 4730 | 0 | 303 | 1367.2 | 0 | 0 | 46 | 32
04:00 | 3728 | 1783 | 450 | 38 | 40 | 1371 | 172 | 4693 | 0 | 303 | 1234.2 | 0 | 0 | 59 | 0
04:30 | 3748 | 1771.5 | 450 | 38 | 39 | 1379 | 172 | 4646 | 0 | 303 | 1184.2 | 0 | 0 | 39.5 | 0
05:00 | 3768 | 1760 | 450 | 38 | 38 | 1387 | 172 | 4599 | 0 | 303 | 1134.2 | 0 | 0 | 20 | 0
05:30 | 3661 | 1699.5 | 450 | 38 | 37 | 1398.5 | 172 | 4447 | 11.595 | 277 | 1013.1 | 0 | 0 | 26.5 | 0
06:00 | 3554 | 1639 | 450 | 38 | 36 | 1410 | 172 | 4295 | 23.19 | 251 | 892 | 0 | 0 | 33 | 0
06:30 | 3561.5 | 1647.5 | 449.5 | 38 | 35 | 1418 | 172 | 4210.5 | 80.75 | 212.5 | 872.5 | 0 | 0 | 33.5 | 0
07:00 | 3569 | 1656 | 449 | 38 | 34 | 1426 | 172 | 4126 | 138.31 | 174 | 853 | 0 | 0 | 34 | 0
07:30 | 3582.5 | 1641.5 | 449.5 | 38 | 33 | 1393 | 172 | 4064 | 202.585 | 183 | 870.5 | 0 | 0 | 32 | 0
08:00 | 3596 | 1627 | 450 | 38 | 32 | 1360 | 172 | 4002 | 266.86 | 192 | 888 | 0 | 0 | 30 | 0
08:30 | 3664.5 | 1684.25 | 450 | 38 | 31 | 1351 | 172 | 3985.5 | 306.345 | 198 | 901.5 | 0 | 0 | 24.5 | 0
09:00 | 3733 | 1741.5 | 450 | 38 | 30 | 1342 | 172 | 3969 | 345.83 | 204 | 915 | 0 | 0 | 19 | 0
09:30 | 3785.5 | 1804.75 | 450 | 38 | 33 | 1341 | 172 | 3986 | 376.38 | 213 | 898.5 | 0 | 0 | 18 | 0
10:00 | 3838 | 1868 | 450 | 38 | 36 | 1340 | 172 | 4003 | 406.93 | 222 | 882 | 0 | 0 | 17 | 0
10:30 | 3842.5 | 1881.75 | 450 | 38 | 35 | 1333 | 172 | 4049 | 438.96 | 222 | 914.5 | 0 | 0 | 9 | 0
11:00 | 3847 | 1895.5 | 450 | 38 | 34 | 1326 | 172 | 4095 | 470.99 | 222 | 947 | 0 | 0 | 1 | 0
11:30 | 3811 | 1923.5 | 450 | 38 | 34 | 1365 | 172 | 4070 | 491.835 | 257 | 1132.5 | 0 | 0 | 7 | 0
12:00 | 3775 | 1951.5 | 450 | 38 | 34 | 1404 | 172 | 4045 | 512.68 | 292 | 1318 | 0 | 0 | 13 | 0
12:30 | 3752 | 1861.25 | 450 | 38 | 37 | 1409 | 172 | 4022.5 | 507.51 | 303.5 | 1442 | 0 | 0 | 27 | 0
13:00 | 3729 | 1771 | 450 | 38 | 40 | 1414 | 172 | 4000 | 502.34 | 315 | 1566 | 0 | 0 | 41 | 0
13:30 | 3735 | 1798.5 | 450 | 38 | 41 | 1412.84 | 172 | 3976.5 | 469.585 | 314 | 1526 | 0 | 0 | 38.5 | 0
14:00 | 3741 | 1826 | 450 | 38 | 42 | 1411.68 | 172 | 3953 | 436.83 | 313 | 1486 | 0 | 0 | 36 | 0
14:30 | 3771.5 | 1863.5 | 450 | 38 | 42 | 1420.035 | 172 | 3980.5 | 401.35 | 306 | 1503.5 | 0 | 0 | 42.5 | 0
15:00 | 3802 | 1901 | 450 | 38 | 42 | 1428.39 | 172 | 4008 | 365.87 | 299 | 1521 | 0 | 0 | 49 | 0
15:30 | 3793.5 | 1930.5 | 450 | 38 | 41 | 1419.955 | 172 | 4013.5 | 331.495 | 297 | 1571 | 0 | 0 | 50.5 | 0
16:00 | 3785 | 1960 | 450 | 38 | 40 | 1411.52 | 172 | 4019 | 297.12 | 295 | 1621 | 0 | 0 | 52 | 0
16:30 | 3757.5 | 1929 | 450 | 38 | 38 | 1361.445 | 172 | 3968.5 | 218.5 | 285 | 1622 | 0 | 0 | 38 | 0
17:00 | 3730 | 1898 | 450 | 38 | 36 | 1311.37 | 172 | 3918 | 139.88 | 275 | 1623 | 0 | 0 | 24 | 0
17:30 | 3659.5 | 1842 | 450 | 38 | 36 | 1267.54 | 172 | 3857 | 91.085 | 295.5 | 1655.5 | 0 | 0 | 21 | 0
18:00 | 3589 | 1786 | 450 | 38 | 36 | 1223.71 | 172 | 3796 | 42.29 | 316 | 1688 | 0 | 0 | 18 | 0
18:30 | 3585.5 | 1770 | 452.5 | 38 | 39 | 1264.95 | 172 | 3928 | 21.145 | 468 | 1921.5 | 7.5 | 0 | 21 | 51
19:00 | 3582 | 1754 | 455 | 38 | 42 | 1306.19 | 172 | 4060 | 0 | 620 | 2155 | 15 | 0 | 24 | 102
19:30 | 3623 | 1939 | 461 | 38 | 40 | 1307.14 | 172 | 4190 | 0 | 694 | 2526 | 15 | 0 | 20 | 148
20:00 | 3709 | 1950 | 461 | 38 | 42 | 1310.27 | 172 | 4252 | 0 | 728 | 2460.2 | 15 | 0 | 12 | 144
20:30 | 3776.5 | 1962 | 466 | 38 | 42 | 1317.415 | 172 | 4381.5 | 0 | 693 | 2393.2 | 7.5 | 0 | 15 | 82.5
21:00 | 3844 | 1974 | 471 | 38 | 42 | 1324.56 | 172 | 4511 | 0 | 658 | 2326.2 | 0 | 0 | 18 | 21
21:30 | 3845 | 1980.1 | 448 | 38 | 42 | 1378.63 | 172 | 4570.5 | 0 | 615 | 2240.2 | 0 | 0 | 17 | 26
22:00 | 3846 | 1986.2 | 425 | 38 | 42 | 1432.7 | 172 | 4630 | 0 | 572 | 2154.2 | 0 | 0 | 16 | 31
22:30 | 3849.5 | 1996.55 | 409 | 38 | 42 | 1442.395 | 172 | 4704 | 0 | 563.5 | 2138.7 | 0 | 0 | 20.5 | 55
23:00 | 3853 | 2006.9 | 393 | 38 | 42 | 1452.09 | 172 | 4778 | 0 | 555 | 2123.2 | 0 | 0 | 25 | 79
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 26-06-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 379 | 07:00 | 365 | 11:00 | Payra | 411 | 08:00 | 404 | 00:00
Ashuganj | 398 | 6:00 | 370 | 11:00 | Rahanpur | 401 | 18:30 | 386 | 22:00
Bhulta | 396 | 05:00 | 359 | 10:00 | Rampal | 398 | 08:00 | 382 | 11:00
Bibiana | 386 | 06:00 | 378 | 11:00
BIPTC | 406 | 06:00 | 396 | 01:00
Bogura | 385 | 18:00 | 367 | 22:00
Gopalganj | 392 | 18:00 | 377 | 00:00
Kaliakoir | 371 | 07:00 | 355 | 11:00
Madunaghat | 393 | 19:00 | 387 | 02:00
Meghnaghat | 383 | 06:00 | 357 | 01:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 222 | 06:00 | 210 | 11:00 | Keranigonj | 220 | 07:00 | 209 | 11:00
AKSML | 231 | 00:00 | 223 | 02:00 | Khulna(S) | 228 | 18:00 | 212 | 23:00
Aminbazar | 224 | 04:00 | 211 | 11:00 | Madunaghat | 234 | 19:30 | 226 | 03:00
Ashuganj | 230 | 06:00 | 217 | 22:00 | Madunaghat-400 | 234 | 20:00 | 227 | 03:00
Ashuganj-400 | 230 | 06:00 | 217 | 22:00 | Maniknagar | 218 | 06:00 | 208 | 11:00
Baghabari | 231 | 05:00 | 223 | 20:00 | Meghnaghat | 232 | 17:00 | 220 | 00:00
Barapukuria | 225 | 18:00 | 215 | 21:00 | Meghnaghat-400 | 223 | 06:00 | 214 | 11:00
Barapukuria-230 | 225 | 18:00 | 215 | 21:00 | Mirsorai | 228 | 19:30 | 219 | 11:00
Barishal | 228 | 18:30 | 218 | 23:00 | Rajshahi | 232 | 05:00 | 220 | 21:00
Bheramara | 234 | 05:00 | 222 | 11:00 | Rampal | 227 | 18:00 | 215 | 00:00
Bhulta | 231 | 05:00 | 204 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 228 | 18:00 | 220 | 00:00 | Rampura | 230 | 06:00 | 202 | 10:00
BIPTC | 236 | 05:00 | 223 | 11:00 | Shikalbaha | 233 | 19:30 | 224 | 01:00
Bogura | 234 | 18:30 | 222 | 22:00 | Shyampur | 220 | 07:00 | 211 | 11:00
Bogura-400 | 234 | 18:30 | 223 | 22:00 | Siddhirganj | 218 | 18:30 | 211 | 11:00
Borhanuddin | 234 | 08:00 | 226 | 23:00 | Sirajgonj | 237 | 05:00 | 231 | 22:00
BSRM | 227 | 19:00 | 219 | 11:00 | Sreepur | 227 | 18:30 | 217 | 10:00
Cumilla(N) | 220 | 05:00 | 212 | 10:00 | Tongi | 226 | 04:00 | 214 | 09:00
Faridpur | 224 | 18:00 | 213 | 00:00
Fenchuganj | 227 | 06:00 | 220 | 00:00
Ghorashal | 234 | 01:00 | 220 | 10:00
Ghorashal-230 | 227 | 06:00 | 206 | 11:00
Gopalganj | 225 | 18:00 | 216 | 00:00
GPH | 230 | 19:30 | 222 | 11:00
Haripur | 220 | 07:00 | 212 | 11:00
Hasnabad | 220 | 03:00 | 211 | 11:00
Hathazari | 231 | 00:00 | 226 | 07:00
Ishurdi | 236 | 05:00 | 224 | 21:00
Jhenaidah | 230 | 06:00 | 214 | 23:00
Kaliakoir | 227 | 03:00 | 215 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 05:00 | 121 | 11:00 | Madartek | 135 | 06:00 | 120 | 10:00
Agargaon | 130 | 05:00 | 121 | 11:00 | Madunaghat | 133 | 19:00 | 128 | 02:00
Agrabad | 132 | 00:00 | 126 | 10:00 | Magura | 130 | 05:00 | 121 | 23:00
AKS | 130 | 00:00 | 126 | 09:00 | Mahasthangarh | 135 | 18:30 | 124 | 22:00
Aminbazar | 133 | 04:00 | 122 | 11:00 | Maijdee | N/A | N/A | N/A | N/A
Amnura | 136 | 01:00 | 125 | 00:00 | Manikganj | 128 | 05:00 | 118 | 11:00
Ashuganj | 135 | 01:00 | 130 | 10:00 | Maniknagar | 130 | 06:00 | 122 | 11:00
Bagerhat | 130 | 18:00 | 116 | 00:00 | Matarbari | 122 | 17:00 | 112 | 03:00
Bajitpur | 130 | 05:00 | 122 | 23:00 | Matuail | 128 | 03:00 | 122 | 11:00
Bakulia | 135 | 19:30 | 128 | 08:00 | Millgate | 132 | 06:00 | 118 | 11:00
Banani | 136 | 06:00 | 120 | 11:00 | Mirpur | 129 | 20:00 | 122 | 11:00
Bangabhaban | 130 | 05:00 | 122 | 11:00 | Mirzapur | 130 | 06:00 | 124 | 00:00
Barapukuria | 136 | 08:00 | 127 | 21:00 | Mithapukur | 131 | 18:30 | 117 | 00:00
Barguna | 134 | 18:00 | 128 | 01:00 | MI_Cement | 128 | 18:00 | 121 | 11:00
Barishal | 132 | 07:00 | 124 | 23:00 | Modern | N/A | N/A | N/A | N/A
Barishal-230 | 133 | 18:00 | 126 | 00:00 | Mogbazar | 136 | 05:00 | 120 | 11:00
Baroaulia | 132 | 00:00 | 128 | 11:00 | Mongla | 129 | 08:00 | 116 | 00:00
Baroirhat | 123 | 18:00 | 116 | 02:00 | Motijheel | 130 | 05:00 | 122 | 11:00
Bashundhara | 135 | 05:00 | 122 | 21:00 | Muktagacha | 135 | 07:00 | 127 | 19:00
BashundharaCement | 128 | 18:30 | 121 | 11:00 | Munshiganj | 126 | 06:00 | 120 | 11:00
Beanibazar | 126 | 06:00 | 121 | 00:00 | Muradnagar | 125 | 06:00 | 118 | 10:00
Benapole | 130 | 18:00 | 115 | 00:00 | Mymensingh | 136 | 07:00 | 114 | 22:00
Bhaluka | 129 | 05:00 | 122 | 11:00 | Naogaon | 134 | 18:30 | 120 | 22:00
Bhandaria | 128 | 10:00 | 117 | 00:00 | Narail | 130 | 09:00 | 120 | 23:00
Bhangura | 133 | 05:00 | 126 | 22:00 | Narinda | 130 | 06:00 | 122 | 11:00
Bheramara | 136 | 06:00 | 129 | 00:00 | Narshingdi | 132 | 07:00 | 112 | 10:00
Bheramara(GK) | 137 | 05:00 | 130 | 00:00 | Natore | 134 | 18:30 | 125 | 22:00
Bhulta | 124 | 06:00 | 113 | 11:00 | Nawabganj | 132 | 06:00 | 123 | 11:00
Bog-Sherpur | 135 | 18:00 | 126 | 22:00 | Netrakona | 128 | 07:00 | 112 | 23:00
Bogura | 138 | 18:30 | 129 | 22:00 | New | 132 | 03:00 | 119 | 11:00
Bogura-230 | 138 | 18:30 | 129 | 22:00 | Niamatpur | 137 | 18:30 | 129 | 23:00
Brahmanbaria | 128 | 04:00 | 119 | 11:00 | Noapara | 133 | 05:00 | 119 | 00:00
Cantonment | 129 | 05:00 | 122 | 11:00 | Pabna | 134 | 05:00 | 127 | 21:00
Chandina | 126 | 18:00 | 121 | 00:00 | Palashbari | 131 | 18:30 | 116 | 22:00
Chandpur | 126 | 18:00 | 117 | 01:00 | Panchagarh | 139 | 18:00 | 120 | 21:00
Chandraghona | 132 | 18:00 | 129 | 02:00 | Patuakhali | 133 | 07:00 | 130 | 00:00
Chapai | 132 | 18:00 | 125 | 23:00 | Payra | 135 | 06:00 | 132 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 128 | 18:00 | 122 | 10:00 | PHP | 123 | 18:30 | 115 | 02:00
Chauddagram | 123 | 18:30 | 117 | 00:00 | Postogola | 130 | 06:00 | 123 | 11:00
Chhatak | 126 | 05:00 | 119 | 00:00 | Purbachal | 135 | 05:00 | 118 | 11:00
Chowmuhani | 119 | 18:00 | 110 | 01:00 | Purbasadipur | 134 | 18:00 | 122 | 10:00
Chuadanga | 132 | 18:30 | 120 | 00:00 | Rahanpur | 137 | 18:30 | 131 | 22:00
Coxsbazar | 122 | 16:00 | 112 | 22:00 | Rahanpur-400 | 137 | 18:00 | 131 | 23:00
Cumilla(N) | 126 | 05:00 | 120 | 10:00 | Rahim | 128 | 07:00 | 123 | 11:00
Cumilla(S) | 132 | 05:00 | 119 | 11:00 | Rajbari | 131 | 08:00 | 123 | 00:00
Daudkandi | 124 | 18:30 | 115 | 11:00 | Rajendrapur | 135 | 06:00 | 122 | 11:00
Dhaka | 134 | 03:00 | 120 | 11:00 | Rajshahi | 134 | 02:00 | 126 | 23:00
Dhamrai | 128 | 05:00 | 120 | 11:00 | Rajshahi-230 | 134 | 05:00 | 120 | 00:00
Dhanmondi | 136 | 05:00 | 122 | 11:00 | Ramganj | 121 | 18:00 | 112 | 01:00
Dohazari | 129 | 19:30 | 124 | 01:00 | Rampur | 133 | 20:00 | 126 | 10:00
Faridpur | 132 | 06:00 | 125 | 23:00 | Rampura | 135 | 05:00 | 120 | 10:00
Fatullah | 127 | 06:00 | 121 | 11:00 | Rangamati | 131 | 00:00 | 127 | 11:00
Fenchuganj | 133 | 06:00 | 129 | 00:00 | Rangpur | 134 | 19:30 | 124 | 17:00
Feni | 122 | 18:30 | 114 | 00:00 | Ruppur | 137 | 04:00 | 130 | 22:00
Ghatail | 130 | 09:00 | 121 | 22:00 | Saidpur | 135 | 19:30 | 122 | 21:00
Ghorashal | 136 | 01:00 | 125 | 11:00 | Satkhira | 131 | 08:00 | 116 | 00:00
Goalpara | 134 | 07:00 | 121 | 00:00 | Satmasjid | 129 | 06:00 | 121 | 11:00
Gollamari | 135 | 18:00 | 124 | 00:00 | Savar | 132 | 20:00 | 119 | 11:00
Gopalganj | 133 | 09:00 | 123 | 00:00 | SevenRings | 136 | 06:00 | 125 | 11:00
Gopalganj-400 | 135 | 18:00 | 128 | 00:00 | ShahCement | 128 | 18:00 | 122 | 10:00
Gulshan | 136 | 05:00 | 120 | 11:00 | Shahjadpur | 135 | 05:00 | 131 | 23:00
Halishahar | 135 | 20:00 | 126 | 10:00 | Shahjibazar | 129 | 06:00 | 121 | 11:00
Haripur | 128 | 07:00 | 123 | 11:00 | Shahmirpur | 134 | 17:00 | 127 | 10:00
HaripurSBU | 129 | 18:30 | 123 | 11:00 | Shariatpur | 133 | 18:00 | 124 | 00:00
Hasnabad | 129 | 19:30 | 124 | 00:00 | Sherpur | 137 | 07:00 | 128 | 19:00
Hathazari | 135 | 00:00 | 131 | 09:00 | Shikalbaha | 123 | 00:00 | 117 | 10:00
Ishurdi | 138 | 05:00 | 131 | 21:00 | Shikalbaha-230 | 135 | 19:30 | 129 | 03:00
Jaldhaka | 132 | 18:00 | 117 | 21:00 | Shitalakhya | 128 | 18:00 | 121 | 11:00
Jamalpur | 140 | 07:00 | 129 | 15:00 | Sholosohor | 133 | 00:00 | 126 | 11:00
Jashore | 135 | 06:00 | 120 | 00:00 | Shyampur | 126 | 18:00 | 121 | 10:00
Jhenaidah | 137 | 05:00 | 120 | 00:00 | Shyampur-230 | 126 | 06:00 | 120 | 11:00
Jhenaidah-230 | 137 | 06:00 | 125 | 23:00 | Siddhirganj | 129 | 18:30 | 123 | 10:00
Joydebpur | 134 | 03:00 | 122 | 16:00 | Sirajganj | 132 | 08:00 | 124 | 22:00
Joypurhat | 132 | 18:00 | 118 | 22:00 | Sonargaon | 128 | 19:30 | 119 | 11:00
Juldah | 135 | 20:00 | 127 | 10:00 | Sreemongol | 129 | 18:00 | 122 | 00:00
Kabirpur | 132 | 07:00 | 117 | 11:00 | Sreepur | 132 | 05:00 | 125 | 10:00
Kachua | 125 | 18:00 | 116 | 01:00 | Srinagar | 131 | 06:00 | 124 | 11:00
Kaliakoir | 133 | 07:00 | 123 | 10:00 | SSM | 135 | 18:30 | 129 | 14:00
Kallyanpur | 130 | 05:00 | 122 | 11:00 | Sunamganj | 125 | 18:30 | 116 | 00:00
Kalurghat | 132 | 20:00 | 126 | 11:00 | Sylhet | 128 | 07:00 | 123 | 00:00
Kamrangirchar | 131 | 06:00 | 123 | 11:00 | Sylhet-132 | 128 | 06:00 | 124 | 00:00
Kaptai | 134 | 1:00 | 132 | 9:00 | Tangail | 128 | 08:00 | 121 | 22:00
Kasba | 125 | 18:30 | 117 | 11:00 | Thakurgaon | 139 | 18:00 | 120 | 21:00
Kazla | 129 | 06:00 | 122 | 11:00 | TK | 132 | 20:00 | 128 | 08:00
Keranigonj | 132 | 06:00 | 124 | 11:00 | Tongi | 134 | 04:00 | 125 | 11:00
Khagrachori | 130 | 07:00 | 126 | 03:00 | Ullahpara | 134 | 18:30 | 126 | 22:00
Khulna | 133 | 18:00 | 121 | 00:00 | Ullon | 134 | 03:00 | 119 | 11:00
Khulna(S) | 136 | 18:30 | 124 | 23:00 | Uttara | 129 | 06:00 | 120 | 11:00
Khulshi | 132 | 20:00 | 126 | 09:00 | UttaraNew | 129 | 20:00 | 121 | 10:00
Kishoreganj | 128 | 06:00 | 121 | 22:00 | Zigatola | 132 | 07:00 | 125 | 11:00
Kodda | 135 | 02:00 | 120 | 11:00
KSRM | 135 | 03:00 | 127 | 12:00
Kulaura | 132 | 06:00 | 127 | 00:00
Kurigram | 130 | 09:00 | 118 | 21:00
Kushtia | 132 | 05:00 | 124 | 01:00
Lalbag | 130 | 05:00 | 124 | 11:00
Lalmonirhat | 130 | 18:00 | 121 | 17:00
Madanganj | 128 | 18:30 | 121 | 11:00
Madaripur | 135 | 18:00 | 127 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division