## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 30-06-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 29-06-2025 | during | 30-06-2025 | during | 30-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 404 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 330 | 320 | 450 | 450 | 420 | 420 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 294 | 287 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 329 | 300 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 16 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 64 | 132 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 47 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 26 | 26 | 33 | 33 | 26 | 26 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 245 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 105 | 107 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 70 | 105 | 105 | 88 | 88 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 16 | 70 | 104 | 104 | 50 | 50 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 112 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 25 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 430 | 350 | 584 | 584 | 400 | 400
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 125 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2271 | 2804 | 5111.2 | 5173.2 | 3302.08 | 3364.08
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 3 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 172 | 166 | 172 | 172 | 172 | 172 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 221 | 215 | 215 | 216 | 216 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 9 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 56 | 82 | 82 | 60 | 60 | Machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 66 | 68 | 68 | 65 | 65 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 48 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 5 | 10 | 2 | 20 | 16 | 21 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2 | 0 | 2.2 | 0 | 2.2 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 75 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 35 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1096 | 1080 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 32 | 28 | 51 | 40 | 51 | 40 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 203 | 203 | 205 | 205 | 205 | 205 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1764 | 1977 | 3268.92 | 3254.72 | 3228.92 | 3201.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 197 | 188 | 221 | 221 | 209 | 209 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 343 | 352 | 353.35 | 353.35 | 353.35 | 353.35
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 335 | 340 | 340 | 340 | 340 | 340 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 21 | 21 | 46.7 | 46.7 | 10 | 10 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 45 | 47 | 55 | 55 | 40 | 40 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 71 | 80 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 118 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 37 | 47 | 47 | 47 | 47 | Machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 139 | 144 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 34 | 42 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 20 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 19 | 24.5 | 24.5 | 10 | 10 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 48 | 74 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 10 | 27 | 113 | 113 | 28 | 28 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 115 | 115 | 115 | 115 | 115
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 41 | 0 | 68 | 0 | 68 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1426 | 1707.2 | 2468.75 | 2400.75 | 2142.55 | 2074.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 29-06-2025 | during | 30-06-2025 | during | 30-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 61 | 72 | 157.5 | 157.5 | 50 | 50 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 100 | 158 | 200 | 200 | 160 | 160 | Fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 75 | 99 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 35.92 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 4 | 12 | 22 | 22 | 22 | 22
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 293.92 | 358 | 599.1 | 549 | 451.6 | 401.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage instructed by DS(Gen)
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 150 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 25 | 25 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 78 | 83 | 83 | 50 | 50 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 170 | 168 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 8 | 25 | 25 | 0 | 0 | Machine problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 275 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 380 | 306 | 380 | 380 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 360 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1472 | 1335 | 1502 | 1502 | 1366 | 1366
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 933 | 933 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 22 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 18 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 298 | 247 | 410 | 410 | 265 | 265 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 23.01 | 0 | 60 | 0 | 60 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 872 | 1108 | 1234.2 | 1234.2 | 1204 | 1204 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2164.01 | 2383 | 3612.2 | 3552.2 | 3437 | 3377
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 616 | 617 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 2 | 11 | 10 | 10 | 4 | 4 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 110 | 130 | 130 | 118 | 118 | FGMO
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 925 | 940 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 225 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 169 | 211 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.25 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 2052.25 | 2114 | 2172 | 2171 | 2094 | 2093
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 44 | 44 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 30 | 30 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 13 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 169 | 167 | 214 | 214 | 172 | 172 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 175 | 190 | 220 | 220 | 202 | 202 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 395 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 | 30 | 30 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 96 | 96 | 96 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.21 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1166.51 | 1339.04 | 1435.88 | 1435.88 | 1355 | 1355 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 19.13 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 95 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 2039.85 | 2280.04 | 3193.37 | 3026.87 | 2826.49 | 2659.99
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 47 | 46 | 48 | 48 | 46 | 46 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 202 | 197 | 200 | 200 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 98 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 108 | 0 | 139.35 | 0 | 139.35 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 429 | 456 | 685.35 | 510 | 683.35 | 508
System Total |  |  |  |  | 28565.2 | 27084.055 | 13912.03 | 15414.24 | 22612.89 | 22139.74 | 19531.99 | 19045.84
Forecast Scenario (30-06-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15110 |  | 0 |  | 15110
|  |  |  | 1:00 | 14970 |  | 0 |  | 14970
|  |  |  | 2:00 | 14480 |  | 0 |  | 14480
|  |  |  | 3:00 | 14250 |  | 0 |  | 14250
|  |  |  | 4:00 | 13930 |  | 0 |  | 13930
|  |  |  | 5:00 | 13730 |  | 0 |  | 13730
|  |  |  | 6:00 | 12720 |  | 0 |  | 12720
|  |  |  | 7:00 | 12530 |  | 0 |  | 12530
|  |  |  | 8:00 | 12520 |  | 0 |  | 12520
|  |  |  | 9:00 | 12840 |  | 0 |  | 12840
|  |  |  | 10:00 | 13160 |  | 0 |  | 13160
|  |  |  | 11:00 | 13470 |  | 0 |  | 13470
|  |  |  | 12:00 | 13910 |  | 0 |  | 13910
|  |  |  | 13:00 | 14110 |  | 0 |  | 14110
|  |  |  | 14:00 | 14010 |  | 0 |  | 14010
|  |  |  | 15:00 | 14100 |  | 0 |  | 14100
|  |  |  | 16:00 | 14190 |  | 0 |  | 14190
|  |  |  | 17:00 | 13930 |  | 0 |  | 13930
|  |  |  | 18:00 | 13190 |  | 0 |  | 13190
|  |  |  | 18:30 | 13650 |  | 0 |  | 13650
|  |  |  | 19:00 | 14260 |  | 0 |  | 14260
|  |  |  | 19:30 | 15460 |  | 0 |  | 15460
|  |  |  | 20:00 | 15410 |  | 0 |  | 15410
|  |  |  | 21:00 | 15380 |  | 0 |  | 15380
|  |  |  | 22:00 | 15370 |  | 0 |  | 15370
|  |  |  | 23:00 | 15200 |  | 0 |  | 15200
Probable Maximum Temperature: |  |  | 32.50°C
Probable Maximum Demand at Day Peak: |  |  | 13910.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 15460.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14724.86 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 333.27329 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:28 hrs on 30-06-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 29-06-2025 | [28 empty] | Date: | 29-06-2025 | [28 empty] | Date: | 29-06-2025 | [28 empty] | Date: | 29-06-2025 | [28 empty] | Date: | 29-06-2025 | [12 empty] | Date: | 29-06-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [12 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 17 | 35 | 105 | 145 | 0 | 0 | 0 | 17 | 35 | 350 | 305 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 125 | 26 | 21 | 0 | 430 | 0 | 0 | 0 | 0 | 13 | 17 | 16 | 0 | 12 | 72 | 0 | 172 | 0 | 26 | 203 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1100 | 0 | 51 | 12 | 45 | 0 | 349 | 340 | 50 | 215 | 22 | 51 | 0 | 200 | 20 | 20 | 80 | 48 | 52.2 | 0 | 45 | 290 | 320 | 392 | 0 | 0 | 157 | 8 | 0 | 80 | 30 | 0 | 0 | 170 | 35 | 100 | 138 | 83 | 0 | 0 | 12 | 7643.2 | 919 | 325 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1101 | 17 | 1436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 195 | 0 | 0 | 0 | 370 | 0 | 0 | 200 | 46 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 11 | 120 | 220 | 0 | 617 | 1090 | 0 | 7384 | 15027.2 | 98.07
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 17 | 35 | 105 | 46 | 0 | 0 | 0 | 17 | 28 | 350 | 297 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 108 | 25.5 | 21 | 0 | 430 | 0 | 0 | 0 | 0 | 4 | 17 | 16 | 0 | 12 | 72 | 0 | 166 | 0 | 27 | 203 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1076 | 0 | 51 | 12 | 45 | 0 | 355 | 340 | 49 | 215 | 22 | 38 | 0 | 200 | 19 | 20 | 80 | 44 | 52.2 | 0 | 45 | 285 | 320 | 361 | 0 | 0 | 156 | 8 | 0 | 79 | 30 | 0 | 0 | 170 | 35 | 100 | 138 | 84 | 0 | 0 | 12 | 7411.7 | 919 | 324 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1109 | 17 | 1421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 197 | 0 | 0 | 0 | 414 | 0 | 0 | 195 | 45 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 10 | 120 | 220 | 0 | 616 | 1100 | 0 | 7424 | 14835.7 | 98.06
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 17 | 35 | 105 | 48 | 0 | 0 | 0 | 0 | 16 | 350 | 298 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 108 | 25.5 | 21 | 0 | 430 | 0 | 0 | 0 | 0 | 7 | 17 | 0 | 0 | 12 | 20 | 0 | 166 | 0 | 32 | 203 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1010 | 0 | 51 | 0 | 45 | 0 | 354 | 340 | 49 | 214 | 22 | 34 | 0 | 200 | 12 | 20 | 80 | 44 | 52.2 | 0 | 45 | 280 | 320 | 387 | 0 | 0 | 155 | 8 | 0 | 79 | 30 | 0 | 0 | 170 | 35 | 100 | 139 | 84 | 0 | 0 | 12 | 7257.7 | 920 | 342 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1082 | 0 | 1221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 192 | 0 | 0 | 0 | 414 | 0 | 0 | 195 | 50 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 120 | 220 | 0 | 620 | 1080 | 0 | 7105 | 14362.7 | 98.06
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 17 | 17 | 105 | 48 | 0 | 0 | 0 | 0 | 16 | 350 | 308 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 108 | 23 | 21 | 0 | 430 | 0 | 0 | 0 | 0 | 24 | 17 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 32 | 206 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1011 | 0 | 51 | 0 | 45 | 0 | 355 | 340 | 50 | 214 | 22 | 34 | 0 | 200 | 9 | 20 | 80 | 42 | 52.2 | 0 | 45 | 285 | 320 | 388 | 0 | 0 | 158 | 8 | 0 | 80 | 30 | 0 | 0 | 170 | 35 | 100 | 139 | 86 | 0 | 0 | 12 | 7245.2 | 919 | 343 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1028 | 0 | 1132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 200 | 0 | 0 | 0 | 414 | 0 | 0 | 196 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 10 | 120 | 220 | 0 | 618 | 1000 | 0 | 6896 | 14141.2 | 98.05
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 0 | 17 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 350 | 298 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 23 | 21 | 0 | 430 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 32 | 206 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 955 | 0 | 51 | 0 | 45 | 0 | 356 | 340 | 50 | 215 | 22 | 35 | 0 | 200 | 9 | 20 | 80 | 40 | 52.2 | 0 | 23 | 285 | 320 | 388 | 0 | 0 | 156 | 0 | 0 | 80 | 30 | 0 | 0 | 170 | 35 | 100 | 130 | 86 | 0 | 0 | 12 | 7070.2 | 919 | 330 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 942 | 0 | 1121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 194 | 0 | 0 | 0 | 414 | 0 | 0 | 196 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 10 | 120 | 220 | 0 | 617 | 1000 | 0 | 6771 | 13841.2 | 98.05
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 0 | 0 | 17 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 350 | 291 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 23 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 33 | 202 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 962 | 0 | 51 | 0 | 45 | 0 | 357 | 340 | 50 | 199 | 20 | 34 | 0 | 200 | 9 | 20 | 80 | 34 | 52.2 | 0 | 24 | 290 | 320 | 379 | 0 | 0 | 158 | 8 | 0 | 80 | 30 | 0 | 0 | 170 | 35 | 100 | 130 | 88 | 0 | 0 | 12 | 7024.2 | 919 | 329 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 851 | 0 | 1116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 199 | 0 | 0 | 0 | 414 | 0 | 0 | 197 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 9 | 120 | 220 | 0 | 617 | 1000 | 0 | 6656 | 13680.2 | 98.04
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 104 | 48 | 0 | 0 | 0 | 0 | 0 | 300 | 299 | 0 | 0 | 0 | 250 | 0 | 0 | 1 | 52 | 23 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 34 | 201 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 840 | 0 | 51 | 0 | 45 | 0 | 353 | 340 | 50 | 201 | 20 | 34 | 0 | 155 | 9 | 20 | 42 | 30 | 8 | 8 | 0 | 290 | 320 | 381 | 0 | 0 | 139 | 8 | 0 | 80 | 30 | 0 | 0 | 170 | 35 | 100 | 130 | 88 | 0 | 3.73 | 12 | 6599.73 | 919 | 324 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4.42 | 773 | 0 | 943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 3.47 | 170 | 0 | 176 | 0 | 0 | 0 | 360 | 0 | 0.31 | 196 | 49 | 50 | 1 | 98 | 0 | 0 | 0.4 | 20 | 0.01 | 0 | 174 | 8 | 120 | 220 | 0 | 617 | 840 | 0 | 6110.61 | 12710.34 | 98.04
07:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 68 | 48 | 0 | 0 | 0 | 0 | 0 | 300 | 289 | 0 | 0 | 0 | 250 | 0 | 0 | 3 | 35 | 23 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 1 | 166 | 0 | 31 | 201 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 851 | 1 | 51 | 0 | 45 | 0 | 353 | 340 | 50 | 197 | 20 | 34 | 0 | 118 | 9 | 20 | 16 | 30 | 8 | 21 | 0 | 290 | 320 | 388 | 0 | 0 | 139 | 8 | 0 | 79 | 30 | 0 | 0 | 171 | 35 | 100 | 130 | 82 | 0 | 13.58 | 12 | 6576.58 | 919 | 321 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 23.98 | 808 | 0 | 878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 13.68 | 169 | 0 | 175 | 0 | 0 | 0 | 360 | 0 | 1.07 | 200 | 49 | 50 | 6 | 34 | 0 | 0 | 1.8 | 47 | 0.06 | 0 | 174 | 6 | 120 | 220 | 0 | 618 | 700 | 0 | 5956.59 | 12533.17 | 98.03
08:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 68 | 48 | 0 | 0 | 0 | 0 | 0 | 300 | 303 | 0 | 0 | 0 | 250 | 0 | 0 | 9 | 35 | 23 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 3 | 166 | 0 | 6 | 202 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 864 | 2 | 51 | 0 | 45 | 0 | 346 | 340 | 48 | 208 | 20 | 34 | 0 | 114 | 9 | 20 | 16 | 36 | 8 | 18 | 0 | 285 | 320 | 391 | 0 | 0 | 141 | 8 | 0 | 79 | 30 | 0 | 0 | 171 | 35 | 75 | 100 | 70 | 1 | 29.62 | 12 | 6531.62 | 921 | 320 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 25.71 | 810 | 0 | 879.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 12.39 | 170 | 0 | 176 | 0 | 0 | 0 | 360 | 0 | 1.22 | 193 | 49 | 35 | 20 | 34 | 0 | 0 | 3.6 | 63 | 0.38 | 0 | 174 | 6 | 120 | 220 | 0 | 617 | 698 | 0 | 5997.85 | 12529.47 | 98.03
09:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 68 | 80 | 0 | 0 | 4 | 0 | 0 | 330 | 295 | 0 | 0 | 0 | 328 | 0 | 0 | 5 | 35 | 25 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 2 | 172 | 0 | 2 | 203 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 905 | 3 | 51 | 0 | 45 | 0 | 340 | 340 | 47 | 207 | 21 | 34 | 0 | 117 | 9 | 20 | 17 | 34 | 8 | 54 | 0 | 290 | 320 | 385 | 0 | 0 | 142 | 0 | 0 | 76 | 30 | 0 | 0 | 170 | 35 | 75 | 100 | 70 | 2 | 44.72 | 12 | 6703.72 | 923 | 314 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 68.53 | 818 | 0 | 878.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 43.3 | 171 | 0 | 178 | 0 | 0 | 0 | 360 | 0 | 3.82 | 203 | 49 | 35 | 17 | 34 | 0 | 0 | 3.1 | 53 | 0.16 | 0 | 173 | 6 | 120 | 220 | 0 | 618 | 740 | 0 | 6140.84 | 12844.56 | 98.03
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 2 | 0 | 68 | 80 | 0 | 0 | 18 | 0 | 10 | 330 | 297 | 0 | 0 | 0 | 332 | 0 | 0 | 21 | 35 | 26 | 21 | 0 | 430 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 2 | 172 | 0 | 2 | 203 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 989 | 6 | 51 | 0 | 45 | 0 | 346 | 340 | 47 | 198 | 21 | 46 | 0 | 115 | 9 | 20 | 47 | 36 | 8 | 58 | 0 | 295 | 320 | 354 | 0 | 0 | 149 | 0 | 0 | 75 | 30 | 0 | 0 | 169 | 35 | 75 | 100 | 70 | 1 | 16.18 | 12 | 6885.18 | 923 | 307 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 77.05 | 816 | 0 | 863.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 21.9 | 171 | 0 | 178 | 0 | 0 | 0 | 360 | 0 | 2.12 | 202 | 47 | 35 | 24 | 34 | 0 | 0 | 3 | 177 | 0.23 | 0 | 171 | 5 | 110 | 220 | 0 | 616 | 804 | 0 | 6279.75 | 13164.93 | 98.02
11:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 89 | 80 | 0 | 0 | 35 | 54 | 16 | 330 | 304 | 0 | 0 | 0 | 327 | 0 | 0 | 27 | 35 | 26 | 21 | 0 | 430 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 5 | 172 | 0 | 2 | 203 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1005 | 6 | 51 | 0 | 71 | 0 | 342 | 340 | 46 | 202 | 21 | 51 | 0 | 112 | 9 | 20 | 47 | 34 | 8 | 46 | 0 | 300 | 320 | 381 | 0 | 0 | 154 | 0 | 0 | 77 | 30 | 0 | 0 | 169 | 35 | 75 | 100 | 68 | 0 | 12.9 | 12 | 7037.9 | 923 | 303 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 70.3 | 805 | 0 | 935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 13.44 | 167 | 0 | 173 | 0 | 0 | 0 | 414 | 0 | 0.8 | 200 | 47 | 35 | 37 | 34 | 0 | 0 | 1.2 | 211 | 0.45 | 0 | 171 | 5 | 120 | 220 | 0 | 617 | 854 | 0 | 6439.19 | 13477.09 | 98.01
12:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 105 | 64 | 0 | 0 | 47 | 54 | 16 | 330 | 294 | 0 | 0 | 0 | 329 | 0 | 0 | 25 | 35 | 26 | 21 | 0 | 430 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 2 | 172 | 0 | 5 | 203 | 35 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 1096 | 3 | 51 | 0 | 71 | 0 | 343 | 335 | 45 | 197 | 21 | 51 | 0 | 139 | 10 | 20 | 48 | 34 | 20 | 41 | 0 | 300 | 360 | 380 | 0 | 0 | 155 | 0 | 0 | 77 | 30 | 0 | 0 | 170 | 17 | 75 | 100 | 61 | 1 | 35.92 | 4 | 7226.92 | 933 | 298 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 23.01 | 872 | 0 | 1166.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 19.13 | 169 | 0 | 175 | 0 | 0 | 0 | 414 | 0 | 1.21 | 202 | 47 | 35 | 32 | 0 | 0 | 0 | 5 | 108 | 0.25 | 0 | 169 | 2 | 120 | 220 | 0 | 616 | 925 | 0 | 6685.11 | 13912.03 | 98.01
13:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 105 | 64 | 0 | 0 | 55 | 74 | 16 | 330 | 300 | 0 | 0 | 0 | 327 | 0 | 0 | 7 | 70 | 26 | 21 | 0 | 430 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 1 | 166 | 0 | 6 | 201 | 35 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1150 | 3 | 51 | 0 | 71 | 0 | 337 | 340 | 45 | 200 | 21 | 51 | 0 | 148 | 28 | 20 | 45 | 38 | 25 | 74 | 0 | 295 | 320 | 393 | 0 | 0 | 155 | 0 | 0 | 59 | 30 | 0 | 0 | 168 | 17 | 77 | 109 | 59 | 1 | 22.05 | 4 | 7343.05 | 933 | 289 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 45.81 | 894 | 0 | 1267.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 25.21 | 171 | 0 | 178 | 0 | 0 | 0 | 414 | 0 | 2.15 | 203 | 47 | 35 | 19 | 0 | 0 | 0 | 3.8 | 27 | 0.26 | 0 | 172 | 5 | 120 | 220 | 0 | 618 | 1000 | 0 | 6769.07 | 14112.12 | 98
14:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 105 | 63 | 0 | 0 | 35 | 97 | 16 | 330 | 305 | 0 | 0 | 0 | 288 | 0 | 0 | 34 | 70 | 25 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 2 | 166 | 0 | 5 | 202 | 35 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 1151 | 8 | 51 | 0 | 71 | 0 | 300 | 295 | 43 | 198 | 20 | 53 | 0 | 141 | 10 | 20 | 71 | 38 | 25 | 70 | 0 | 300 | 320 | 383 | 0 | 0 | 144 | 0 | 0 | 75 | 30 | 0 | 0 | 168 | 17 | 101 | 109 | 59 | 3 | 21.65 | 12 | 7200.65 | 933 | 266 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 58.76 | 854 | 0 | 1285.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 29.76 | 163 | 0 | 168 | 0 | 0 | 0 | 350 | 0 | 4.4 | 194 | 47 | 35 | 25 | 34 | 0 | 0 | 7.6 | 185 | 0.58 | 0 | 168 | 6 | 104 | 180 | 0 | 622 | 950 | 0 | 6818.6 | 14019.25 | 98
15:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 17 | 0 | 105 | 62 | 0 | 0 | 35 | 95 | 16 | 420 | 304 | 0 | 0 | 10 | 322 | 0 | 0 | 23 | 70 | 25 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 2 | 166 | 0 | 3 | 203 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 1167 | 4 | 51 | 1 | 71 | 0 | 338 | 340 | 43 | 210 | 19 | 72 | 0 | 155 | 9 | 20 | 70 | 38 | 25 | 50 | 0 | 290 | 320 | 375 | 0 | 0 | 153 | 0 | 0 | 75 | 30 | 0 | 0 | 168 | 17 | 75 | 109 | 59 | 1 | 44.23 | 12 | 7369.23 | 933 | 260 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18.18 | 860 | 0 | 1290.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 36.63 | 179 | 0 | 185 | 0 | 0 | 0 | 400 | 0 | 4.08 | 203 | 47 | 0 | 9 | 0 | 0 | 0 | 6.1 | 95 | 0.15 | 0 | 178 | 8 | 112 | 220 | 0 | 617 | 950 | 0 | 6735.42 | 14104.65 | 97.99
16:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 105 | 62 | 45 | 0 | 35 | 103 | 29 | 420 | 296 | 0 | 0 | 35 | 329 | 0 | 0 | 24 | 70 | 25 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 3 | 166 | 0 | 3 | 205 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1131 | 2 | 51 | 60 | 100 | 0 | 343 | 340 | 46 | 196 | 21 | 72 | 0 | 160 | 9 | 20 | 74 | 38 | 52.2 | 32 | 0 | 290 | 320 | 364 | 0 | 0 | 153 | 0 | 0 | 77 | 30 | 0 | 0 | 169 | 17 | 75 | 109 | 70 | 1 | 27.08 | 12 | 7513.28 | 933 | 257 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4.56 | 820 | 0 | 1308.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 7.11 | 187 | 0 | 184 | 0 | 0 | 0 | 414 | 0 | 0.78 | 200 | 47 | 0 | 17 | 0 | 0 | 0 | 5 | 130 | 0.12 | 0 | 171 | 0 | 116 | 220 | 0 | 618 | 950 | 0 | 6683.78 | 14197.06 | 97.99
17:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 33 | 105 | 62 | 45 | 0 | 35 | 97 | 40 | 420 | 295 | 0 | 0 | 35 | 328 | 0 | 0 | 10 | 70 | 25 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 22 | 0 | 6 | 0 | 0 | 0 | 0 | 166 | 0 | 9 | 203 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1010 | 1 | 51 | 100 | 100 | 0 | 343 | 340 | 46 | 196 | 21 | 72 | 0 | 155 | 9 | 20 | 74 | 38 | 43 | 7 | 37 | 290 | 320 | 358 | 0 | 0 | 134 | 0 | 0 | 77 | 30 | 0 | 0 | 168 | 17 | 75 | 128 | 70 | 1 | 16.63 | 12 | 7466.63 | 934 | 253 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4.61 | 806 | 0 | 1321.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 10.56 | 182 | 0 | 167 | 0 | 0 | 0 | 350 | 0 | 1.13 | 202 | 47 | 0 | 9 | 0 | 0 | 0 | 2.8 | 83 | 0.22 | 0 | 170 | 0 | 116 | 220 | 0 | 618 | 920 | 0 | 6467.12 | 13933.75 | 97.98
18:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 54 | 42 | 105 | 62 | 45 | 0 | 35 | 95 | 59 | 320 | 291 | 0 | 0 | 35 | 280 | 0 | 0 | 2 | 70 | 26 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 19 | 66 | 31 | 0 | 0 | 0 | 0 | 166 | 0 | 2 | 203 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 899 | 1 | 51 | 100 | 100 | 0 | 300 | 280 | 46 | 186 | 21 | 72 | 0 | 141 | 13 | 19 | 74 | 34 | 43 | 5 | 37 | 285 | 320 | 300 | 0 | 0 | 129 | 8 | 0 | 78 | 20 | 0 | 0 | 168 | 17 | 55 | 155 | 70 | 0 | 0.63 | 12 | 7115.63 | 933 | 253 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6.91 | 788 | 0 | 1135.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 3.18 | 162 | 0 | 163 | 0 | 0 | 0 | 350 | 0 | 0.31 | 202 | 46 | 35 | 1 | 30 | 0 | 0 | 0.4 | 21 | 0.04 | 0 | 163 | 8 | 94 | 180 | 0 | 618 | 850 | 0 | 6083.12 | 13198.75 | 97.98
19:00 | 16 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 54 | 55 | 105 | 64 | 275 | 7 | 35 | 93 | 69 | 420 | 308 | 0 | 0 | 35 | 260 | 0 | 0 | 0 | 108 | 26 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 22 | 66 | 32 | 0 | 12 | 12 | 0 | 166 | 0 | 10 | 203 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1108 | 0 | 51 | 100 | 53 | 0 | 310 | 280 | 47 | 176 | 21 | 83 | 0 | 143 | 27 | 19 | 74 | 42 | 52.2 | 0 | 37 | 290 | 320 | 376 | 0 | 0 | 130 | 8 | 0 | 78 | 20 | 0 | 0 | 168 | 17 | 55 | 147 | 72 | 0 | 0.19 | 12 | 7768.39 | 933 | 220 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 960 | 17 | 1205.32 | 0 | 0 | 0 | 10 | 0 | 22 | 0 | 6 | 0 | 0 | 24 | 0 | 155 | 0 | 165 | 0 | 0 | 0 | 350 | 0 | 0 | 200 | 46 | 113 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 10 | 110 | 180 | 0 | 618 | 840 | 0 | 6500.32 | 14268.71 | 97.97
19:30 | 16 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 54 | 55 | 107 | 132 | 245 | 15 | 35 | 112 | 70 | 320 | 287 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 125 | 26 | 21 | 0 | 350 | 0 | 15 | 0 | 0 | 28 | 66 | 56 | 0 | 48 | 75 | 0 | 166 | 0 | 10 | 203 | 0 | 0 | 0 | 0 | 9 | 221 | 0 | 0 | 0 | 1080 | 0 | 51 | 118 | 80 | 0 | 352 | 340 | 47 | 188 | 21 | 115 | 0 | 144 | 27 | 19 | 74 | 42 | 52.2 | 0 | 37 | 275 | 320 | 306 | 0 | 0 | 150 | 8 | 0 | 78 | 30 | 0 | 0 | 168 | 17 | 99 | 158 | 72 | 0 | 0 | 12 | 8181.2 | 933 | 247 | 0 | 22 | 18 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1108 | 17 | 1339.04 | 0 | 0 | 0 | 50 | 0 | 96 | 0 | 13 | 0 | 0 | 30 | 0 | 167 | 0 | 190 | 0 | 0 | 0 | 395 | 0 | 0 | 197 | 46 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 211 | 11 | 110 | 225 | 0 | 617 | 940 | 0 | 7233.04 | 15414.24 | 97.97
20:00 | 16 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 52 | 55 | 111 | 145 | 145 | 15 | 35 | 116 | 45 | 320 | 291 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 125 | 26 | 21 | 0 | 350 | 0 | 15 | 0 | 0 | 25 | 66 | 56 | 0 | 12 | 75 | 0 | 172 | 0 | 16 | 203 | 0 | 0 | 4 | 0 | 17 | 221 | 0 | 0 | 0 | 1125 | 0 | 51 | 75 | 105 | 0 | 349 | 340 | 47 | 189 | 21 | 114 | 0 | 156 | 27 | 19 | 74 | 40 | 52.2 | 0 | 37 | 285 | 320 | 306 | 0 | 0 | 139 | 8 | 0 | 78 | 30 | 0 | 0 | 170 | 17 | 101 | 157 | 72 | 0 | 0 | 12 | 8097.2 | 933 | 246 | 0 | 32 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1052 | 22 | 1324.44 | 0 | 24 | 0 | 35 | 0 | 65 | 0 | 23 | 0 | 0 | 30 | 0 | 160 | 0 | 177 | 0 | 0 | 0 | 370 | 0 | 0 | 200 | 46 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 11 | 116 | 220 | 0 | 618 | 1045 | 0 | 7274.44 | 15371.64 | 97.97
21:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 55 | 120 | 145 | 0 | 0 | 35 | 156 | 0 | 400 | 308 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 125 | 26 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 59 | 66 | 0 | 0 | 12 | 75 | 0 | 166 | 0 | 21 | 203 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1160 | 0 | 51 | 0 | 100 | 0 | 342 | 340 | 48 | 209 | 21 | 115 | 0 | 164 | 29 | 20 | 74 | 36 | 52.2 | 0 | 37 | 285 | 320 | 355 | 0 | 0 | 145 | 8 | 0 | 78 | 30 | 0 | 0 | 171 | 17 | 101 | 158 | 72 | 0 | 0 | 12 | 7936.2 | 933 | 247 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1140 | 34 | 1437.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 179 | 0 | 0 | 0 | 414 | 0 | 0 | 201 | 46 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 284 | 11 | 120 | 220 | 0 | 618 | 1090 | 0 | 7395.29 | 15331.49 | 97.96
22:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 35 | 120 | 145 | 0 | 0 | 0 | 155 | 0 | 400 | 309 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 125 | 26 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 23 | 66 | 0 | 0 | 40 | 100 | 0 | 166 | 0 | 24 | 203 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1157 | 0 | 51 | 0 | 100 | 0 | 344 | 340 | 44 | 208 | 19 | 106 | 0 | 175 | 28 | 20 | 74 | 36 | 52.2 | 0 | 37 | 295 | 320 | 358 | 0 | 0 | 153 | 8 | 0 | 79 | 30 | 0 | 0 | 171 | 17 | 100 | 149 | 68 | 0 | 0 | 12 | 7903.2 | 933 | 244 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1144 | 34 | 1436.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 184 | 0 | 0 | 0 | 414 | 0 | 0 | 201 | 46 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 10 | 120 | 220 | 0 | 618 | 1095 | 0 | 7406.99 | 15310.19 | 97.96
23:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 35 | 120 | 145 | 0 | 0 | 0 | 132 | 25 | 400 | 305 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 125 | 26 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 38 | 66 | 0 | 0 | 75 | 100 | 0 | 166 | 0 | 28 | 204 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1175 | 0 | 51 | 0 | 123 | 0 | 343 | 340 | 44 | 211 | 19 | 59 | 0 | 188 | 28 | 20 | 74 | 40 | 52.2 | 0 | 38 | 290 | 320 | 360 | 0 | 0 | 158 | 8 | 0 | 79 | 30 | 0 | 0 | 171 | 17 | 100 | 149 | 68 | 0 | 0 | 12 | 8023.2 | 933 | 245 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 54 | 1416.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 183 | 0 | 0 | 0 | 414 | 0 | 0 | 200 | 46 | 115 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 11 | 120 | 220 | 0 | 617 | 1140 | 0 | 7462.17 | 15485.37 | 97.95
Total KWH | 24480 | 1116480 | 474240 | 0 | 0 | 0 | 0 | 0 | 9658800 | 0 | 0 | 370080 | 564120 | 2461104 | 1860480 | 525655 | 26516 | 462032 | 1401120 | 449280 | 8501000 | 7213469 | 0 | 0 | 202675 | 7618440 | 0 | 0 | 160571 | 1917600 | 607200 | 497160 | 0 | 9606818.18 | 0 | 15055 | 0 | 0 | 708960 | 465181 | 116685 | 0 | 238080 | 566400 | 21840 | 4020000 | 0 | 379680 | 4901818.18 | 110400 | 0 | 13440 | 0 | 40145 | 5195530 | 0 | 0 | 0 | 24889088 | 40905 | 1185910 | 513527 | 1672727 | 0 | 8535400 | 8102000 | 1126080 | 4936000 | 502128 | 1394880 | 0 | 3829920 | 367080 | 460340 | 1467180 | 912000 | 872664 | 467527 | 479024 | 6996000 | 7694900 | 9155000 | 0 | 0 | 3564164 | 109296 | 0 | 1844160 | 704832 | 0 | 0 | 4504900 | 633600 | 2103600 | 3031200 | 1688640 | 9750 | 299750 | 281520 | 176888226.36 | 22175273 | 6958656 | 0 | 17280 | 13184 | 912000 | 0 | 0 | 0 | 0 | 0 | 469440 | 22130910 | 210240 | 27577455 | 0 | 10207 | 0 | 98784 | 0 | 78944 | 0 | 11687 | 0 | 698880 | 37282 | 261000 | 4267545 | 0 | 4544636 | 0 | 0 | 0 | 9384000 | 0 | 23460 | 4896000 | 1063854 | 1679735 | 237459 | 1423545 | 0 | 0 | 51887.16 | 1340640 | 3828 | 0 | 4844000 | 188140 | 2830000 | 5355750 | 0 | 14842152 | 23512727.27 | 0 | 162150580.43 | 339038806.79

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 29-06-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13912.03 | MW | 12:00 Hr. | Energy Generated |  |  | 339.0388 |  | MKWHr.
| Day Peak Demand |  |  | 13912.03 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.821 |  | MKWHr.
| Evening Peak Generation |  |  | 15414.24 | MW | 19:30 Hr. | Energy Demand |  |  | 339.8598 |  | MKWHr.
| Evening Peak Demand |  |  | 15469.24 | MW | 19:30 Hr. | Maximum Temperature |  |  | 31.9 |  | °C
| Minimum Generation of the Day |  |  | 12529.47 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 1020.42 |  | MMCFD
| Maximum Generation of the Day |  |  | 15485.37 | MW | 23:00 Hr. | Production Cost per KWHr |  |  | 5.9963 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 43.7029 | 0 | 11.8559 | 0 | 0 | 0.16057 | 0 | 0 | 55.7193 | Gas | 145.5893 | Gas | 514510301.4406
| Chattogram Zone |  |  | 5.5752 | 29.7909 | 1.5654 | 0 | 4.02 | 0.062745 | 0 | 0.70896 | 41.7232 | Coal | 101.0805 | Coal | 586635205.1885
| Cumilla Zone |  |  | 26.5206 | 0 | 8.9243 | 0 | 0 | 0.46753 | 0.912 | 0 | 36.8244 | HFO | 31.9763 | HFO | 605307103.49
| Mymensingh Zone |  |  | 1.6886 | 0 | 6.0499 | 0 | 0 | 0.3095 | 0 | 0 | 8.0481 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 34.5733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.5733 | Hydro | 4.02 | Hydro | 402000
| Khulna Zone |  |  | 6.9587 | 22.1309 | 0.2407 | 0 | 0 | 0.46944 | 23.0873 | 0 | 52.887 | Solar | 4.0869 | Solar | 66902806.8176
| Barishal Zone |  |  | 8.3739 | 43.1989 | 0 | 0 | 0 | 0.003828 | 0 | 0 | 51.5766 | Import | 51.5767 | Import | 248858556.45
| Rajshahi Zone |  |  | 18.1962 | 0 | 0.2369 | 0 | 0 | 0.98334 | 27.5775 | 0 | 46.9939 | Wind | 0.70896 | Wind | 10379174.4
| Rangpur Zone |  |  | 0 | 5.9599 | 3.1033 | 0 | 0 | 1.63 | 0 | 0 | 10.6931
| Total |  |  | 145.5893 | 101.0805 | 31.9763 | 0 | 4.02 | 4.0869 | 51.5767 | 0.70896 | 339.0388
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 514510301.4406 |  | Hydro | 402000
|  |  |  | Coal | 586635205.1885 |  | Solar | 66902806.8176
|  |  |  | HFO | 605307103.49 |  | Import | 248858556.45
|  |  |  | HSD | 0 |  | Wind | 10379174.4
[5 empty] | Total: | 203,29,95,147 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.1753 | Peak Hr Flow | 933.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 49808981.91 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.5775 | Peak Hr Flow | 1339.04 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 756 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.912 | Peak Hr Flow | 42.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 988 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.6647 | Peak Hr Flow | 2314.04 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 23 |  | 5448
|  |  |  | Chattogram |  | 0 |  | 1417
|  |  |  | Cumilla |  | 0 |  | 1297
|  |  |  | Mymensingh |  | 0 |  | 1238
|  |  |  | Sylhet |  | 0 |  | 634
|  |  |  | Khulna |  | 0 |  | 1816
|  |  |  | Barishal |  | 0 |  | 467
|  |  |  | Rajshahi |  | 0 |  | 1514
|  |  |  | Rangpur |  | 30 |  | 1046
|  |  |  | Total |  | 53 |  | 14877
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[5 empty] | Total | 300 |  |  |  | Total | 476
|  |  |  | Total Unavailable Capacity |  |  |  | 776
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:00 | 15:51 | KSRM 132/33kV S/S Transformer-01 HT Scheduled S/D Due to 33 KV Bus Maintenance
|  | 08:10 | Munshiganj 132/33kV S/S Transformer-1 LT is restored.
|  | 08:16 | Munshiganj 132/33kV S/S Transformer-2 LT is restored.
|  | 08:33 | Feni 132/33kV S/S T-1(405T) HT is restored.
|  | 08:33 | Feni 132/33kV S/S T-1(405T) LT is restored.
|  | 09:12 | Madanganj 132/33kV S/S BUS Coupler is restored.
| 09:47 | 10:47 | Satmasjid 132/33kV S/S 132/33 KV Transformer-1 LT Tripped showing Over Current & Earth
Fault Protection Relay. relays Due to Over Current & Earth Fault.
| 09:47 | 10:43 | Satmasjid 132/33kV S/S 132/33 KV Transformer-1 HT Tripped showing SIPROTEC, Over Current
& Earth Fault Protection Relay. relays Due to Over current fault, Earth fault.
| 10:32 | 13:25 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Forced S/D Due to Oil Leakage Chek
| 10:53 | 13:16 | Siddhirganj-Ullon (T at Maniknagar) 132kV Ckt-1 Tripped from Siddhirganj 132/33kV end
showing Distance Realy relays Due to Transmission Line Faulty
| 11:11 | 11:55 | BIPTC S/S 20DF11 Scheduled S/D Due to Maintenance Work
| 12:00 |  | Day Peak Generation: 13910 MW.
| 12:06 | 12:47 | BIPTC S/S 10CF13 Scheduled S/D Due to Maintenance Work
| 13:24 | 13:54 | Ishurdi 132/33kV S/S 132/33 kV T-1 LT Forced S/D Due to short ckt at AC MCB | [7 empty] | 45.0MW load interrup.
| 13:24 | 13:54 | Ishurdi 132/33kV S/S 132/33 kV T-1 HT Forced S/D Due to short ckt at AC MCB | [7 empty] | 45.0MW load interrup.
| 13:24 | 13:46 | Ishurdi 132/33kV S/S 132/33 kV T-2 LT Forced S/D Due to short ckt at AC MCB | [7 empty] | 30.0MW load interrup.
| 13:24 | 13:46 | Ishurdi 132/33kV S/S 132/33 kV T-2 HT Forced S/D Due to short ckt at AC MCB | [7 empty] | 30.0MW load interrup.
| 13:34 | 15:48 | Faridpur 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Red hot maintenance | [7 empty] | 10.0MW load interrup.
| 13:34 | 15:48 | Faridpur 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Red hot maintenance
| 14:20 | 16:10 | Ashuganj-Brahmanbaria 132kV Ckt-1 Scheduled S/D from Brahmanbaria 132/33kV end Due to Project-1
| 16:31 | 17:47 | Ashuganj-Brahmanbaria 132kV Ckt-1 Scheduled S/D from Brahmanbaria 132/33kV end Due to Project-1
| 16:47 |  | BSRM-Feni 230kV ckt-2 and Feni-Cumilla north 230kV ckt.-2 was switched on for the first time.
| 17:02 |  | Feni-Cumilla north 230kV ckt.-2 was switched on 17:02 hrs for the first time.
| 17:42 | 20:56 | Daudkandi 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Bus Maintenance Work By | [7 empty] | 30.0MW load
|  |  | PBS-3 Team | [7 empty] | interrup.
| 17:43 | 20:55 | Daudkandi 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Bus Maintenance Work By | [7 empty] | 30.0MW load
|  |  | PBS-3 Team | [7 empty] | interrup.
|  | 19:00 | Gopalganj 400/132kV S/S 400kV Rooppur is restored.
|  | 19:06 | Bogura 400/230kV S/S Bogura - Rooppur 400 KV Line-1 is restored.
| 19:30 |  | Evening Peak Generation 15414 MW.
| 00:14 |  | Kachua 230/132 kV ATR-01 transformer was charged from Kachua 132 kV end for the first time.
| 00:17 |  | Kachua 230 kV Bus-1 was charged for the first time.
| 00:20 |  | Kachua 230 kV Bus-2 was charged for the first time.
| 00:22 |  | Kachua-Chowmuhoni 230 kV ckt-2 was charged from Kachua 230 kV end in no-load condition
for the first time.
| 02:00 |  | Chandpur 132/33kV S/S 200KVA Aux. T-2 LT Forced S/D Due to Auxiliary load shift
| 06:47 |  | Saidpur 132/33kV S/S TR-3 (424T) LT Scheduled S/D Due to Saidpur Nesco work | [7 empty] | 23.0MW load interrup.
| 06:48 |  | Saidpur 132/33kV S/S TR-3 (424T) HT Scheduled S/D
| 06:51 |  | Ramganj 132/33kV S/S Ramgonj- Desh Energy Ckt-01 Scheduled S/D Due to Temperature raising
point maintenance
| 07:00 |  | Bhulta-Narsingdi 132 kV Ckt-1 Project Work S/D from Bhulta 132/33kV end Due to STRINGING,
DISMANTLING, SCAFFOLDING
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 29-06-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 404 | 9658800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 320 | 8501000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 287 | 7213469 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 26516 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 7618440 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 24480 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 370080 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 132 | 1860480 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 462032 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 202675 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 26 | 607200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 497160 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 474240 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 245 | 525655 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 107 | 2461104 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1116480 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 70 | 449280 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 112 | 1401120 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 160571 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 564120 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 350 | 9606818.18 | None
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 125 | 1917600 | -
Dhaka Area Total |  |  |  |  | 5939.724 | 2804 | 55719320.18
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 40905 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 13440 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 166 | 4020000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 221 | 5195530 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 9 | 40145 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 56 | 116685 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 465181 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 48 | 238080 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 10 | 379680 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21840 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 15055 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 75 | 566400 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 110400 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1080 | 24889088 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 28 | 708960 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 203 | 4901818.18 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4895.72 | 1977 | 41723207.18
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 188 | 4936000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 352 | 8535400 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 8102000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 21 | 502128 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 47 | 1126080 | Gas shortage instructed by DS(Gen)
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 80 | 1672727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1185910 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 118 | 513527 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 37 | 479024 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 144 | 3829920 | -
| Import (Tripura) |  | Import | 0 | 160 | 42 | 912000 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 872664 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 460340 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 74 | 1467180 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 367080 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1394880 | Fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 467527 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1707.2 | 36824387
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 72 | 1688640 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9750 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 158 | 3031200 | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 99 | 2103600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 299750 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 281520 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 633600 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 358 | 8048060
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | Gas shortage instructed by DS(Gen)
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 150 | 3564164 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 704832 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1844160 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 168 | 4504900 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 109296 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 275 | 6996000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 306 | 9155000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7694900 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1335 | 34573252
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 933 | 22175273 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 22 | 17280 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 18 | 13184 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 247 | 6958656 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 210240 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 469440 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1108 | 22130910 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2383 | 52886983
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 617 | 14842152 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 11 | 188140 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2830000 | FGMO
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 940 | 23512727.27 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 225 | 5355750 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 211 | 4844000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3828 | -
Barishal Area Total |  |  |  |  | 2236 | 2114 | 51576597.27
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 10207 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 13 | 11687 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 167 | 4267545 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 190 | 4544636 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 395 | 9384000 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 37282 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 78944 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 98784 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 23460 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1339.04 | 27577455 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 261000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 698880 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2280.04 | 46993880
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 46 | 1063854 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 197 | 4896000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 1423545 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 51887.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1679735 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 237459 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1340640 | -
Rangpur Area Total |  |  |  |  | 950 | 456 | 10693120.16
Eastern Grid Total |  |  |  |  | 16705.895 | 8181.2 | 176888226.36
Western Grid Total |  |  |  |  | 10378.16 | 7233.04 | 162150580.43
National Grid Total |  |  |  |  | 27084.055 | 15414.24 | 339038806.79
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 29-06-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10010.39 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4812.8 | MW
i) Dhaka area |  |  | 5424.78 |  | MW | i) Khulna area |  |  |  | 1816 | MW
ii) Chattogram area |  |  | 1416.7 |  | MW | ii) Barishal area |  |  |  | 467 | MW
iii) Cumilla area |  |  | 1296.91 |  | MW | iii) Rajshahi area |  |  |  | 1513.8 | MW
iv) Mymensingh area |  |  | 1238 |  | MW | iv) Rangpur area |  |  |  | 1016 | MW
v) Sylhet area |  |  | 634 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14823.19 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 84 | 19:30 | 133 | Patuakhali | 82.2 | 23:00
2 | AKSML | 123.8 | 11:00 | 68 | Jaldhaka | 94 | 00:00 | 134 | Payra | 34 | 22:00
3 | Aftabnagar | 40 | 12:00 | 69 | Jamalpur | 129 | 00:00 | 135 | Postogola | 59 | 13:00
4 | Agargaon | 136 | 13:00 | 70 | Jashore | 142 | 20:00 | 136 | Purbachal | 22 | 21:00
5 | Agrabad | 92 | 16:00 | 71 | Jhenaidah | 129 | 21:00 | 137 | Purbasadipur | 149 | 23:00
6 | Amnura | 44 | 00:00 | 72 | Joydebpur | 148 | 16:00 | 138 | Rahanpur | 36 | 01:00
7 | Ashuganj | 109 | 00:00 | 73 | Joypurhat | 68 | 23:00 | 139 | Rahim | 37 | 17:00
8 | BSRM | 198 | 17:00 | 74 | Juldah | 14 | 13:00 | 140 | Rajbari | 86 | 23:00
9 | Bagerhat | 83 | 19:30 | 75 | KSRM | 17 | 02:00 | 141 | Rajendrapur | 138 | 20:00
10 | Bajitpur | 56 | 19:00 | 76 | Kabirpur | 249 | 19:00 | 142 | Rajshahi | 119 | 22:00
11 | Bakulia | 90 | 19:30 | 77 | Kachua | 90 | 20:00 | 143 | Rajshahi-230 | 98 | 23:00
12 | Banani | 25 | 13:00 | 78 | Kallyanpur | 105 | 23:00 | 144 | Ramganj | 112 | 20:00
13 | Bangabhaban | 19 | 10:00 | 79 | Kalurghat | 38 | 10:00 | 145 | Rampur | 38 | 00:00
14 | Barapukuria | 71 | 22:00 | 80 | Kamrangirchar | 69 | 13:00 | 146 | Rangamati | 14 | 11:00
15 | Barguna | 22 | 19:30 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 149 | 19:00
16 | Barishal | 109 | 19:30 | 82 | Kasba | 38 | 19:30 | 148 | Ruppur | 7 | 09:00
17 | Barishal-230 | 104 | 23:00 | 83 | Kazla | 102 | 23:00 | 149 | SSM | 14 | 00:00
18 | Baroaulia | 64 | 19:00 | 84 | Keranigonj | 93 | 19:30 | 150 | Saidpur | 123 | 19:30
19 | Baroirhat | 61 | 14:00 | 85 | Khagrachori | 34 | 20:00 | 151 | Satkhira | 126 | 19:30
20 | Bashundhara | 198 | 16:00 | 86 | Khulna | 67 | 19:30 | 152 | Satmasjid | 102 | 19:30
21 | BashundharaCement | 16 | 00:00 | 87 | Khulshi | 150 | 19:30 | 153 | Savar | 228 | 16:00
22 | Beanibazar | 88 | 19:00 | 88 | Kishoreganj | 150 | 22:00 | 154 | SevenRings | 15.98 | 03:00
23 | Benapole | 72 | 22:00 | 89 | Kodda | 301 | 19:00 | 155 | ShahCement | 27 | 00:00
24 | Bhaluka | 153 | 00:00 | 90 | Kulaura | 61 | 19:00 | 156 | Shahjadpur | 80 | 19:30
25 | Bhandaria | 58 | 21:00 | 91 | Kurigram | 64 | 05:00 | 157 | Shahjibazar | 132 | 00:00
26 | Bhangura | 38 | 00:00 | 92 | Kushtia | 166 | 20:00 | 158 | Shahmirpur | 61 | 18:30
27 | Bheramara(GK) | 70 | 22:00 | 93 | Lalbag | 56 | 12:00 | 159 | Shariatpur | 89 | 23:00
28 | Bhulta | 248 | 22:00 | 94 | Lalmonirhat | 64 | 00:00 | 160 | Sherpur | 162 | 22:00
29 | Bog-Sherpur | 66 | 00:00 | 95 | MI_Cement | 15.5 | 00:00 | 161 | Shikalbaha | 9 | 16:00
30 | Bogura | 177 | 21:00 | 96 | Madanganj | 46 | 23:00 | 162 | Shitalakhya | 84.4 | 12:00
31 | Borhanuddin | 87 | 20:00 | 97 | Madaripur | 115 | 21:00 | 163 | Sholosohor | 45 | 15:00
32 | Brahmanbaria | 137 | 02:00 | 98 | Madartek | 90 | 00:00 | 164 | Shyampur | 156 | 12:00
33 | Cantonment | 156 | 13:00 | 99 | Madunaghat | 53 | 19:30 | 165 | Siddhirganj | 118 | 16:00
34 | Chandina | 15.48 | 23:00 | 100 | Magura | 65 | 20:00 | 166 | Sirajganj | 108 | 19:00
35 | Chandpur | 82 | 01:00 | 101 | Mahasthangarh | 88 | 23:00 | 167 | Sonargaon | 113 | 17:00
36 | Chandraghona | 35 | 19:30 | 102 | Manikganj | 135 | 19:30 | 168 | Sreemongol | 87 | 00:00
37 | Chapai | 65 | 20:00 | 103 | Maniknagar | 88 | 15:00 | 169 | Sreepur | 105 | 19:30
38 | Charsaidpur | 37 | 00:00 | 104 | Matarbari | 46 | 22:00 | 170 | Srinagar | 58.71 | 22:00
39 | Chauddagram | 69 | 23:00 | 105 | Matuail | 62 | 10:00 | 171 | Sunamganj | 64 | 23:00
40 | Chhatak | 44 | 23:00 | 106 | Millgate | 122 | 15:00 | 172 | Sylhet | 55 | 15:00
41 | Chowmuhani | 204 | 19:30 | 107 | Mirpur | 124 | 19:30 | 173 | Sylhet-132 | 138 | 19:00
42 | Chuadanga | 113 | 21:00 | 108 | Mirsorai | 10 | 10:00 | 174 | TK | 36.5 | 19:30
43 | Coxsbazar | 129 | 19:00 | 109 | Mirzapur | 45 | 22:00 | 175 | Tangail | 198 | 19:30
44 | Cumilla(N) | 158 | 00:00 | 110 | Mithapukur | 76 | 19:30 | 176 | Thakurgaon | 121 | 22:00
45 | Cumilla(S) | 187 | 13:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 148 | 15:00
46 | Daudkandi | 149 | 22:00 | 112 | Mogbazar | 162.6 | 16:00 | 178 | Ullahpara | 40 | 19:30
47 | Dhaka | 80 | 13:00 | 113 | Mongla | 46 | 12:00 | 179 | Ullon | 40 | 00:00
48 | Dhamrai | 138 | 19:00 | 114 | Motijheel | 42 | 13:00 | 180 | Uttara | 92 | 15:00
49 | Dhanmondi | 150 | 13:00 | 115 | Muktagacha | 40 | 19:30 | 181 | UttaraNew | 62 | 00:00
50 | Dohazari | 98 | 19:30 | 116 | Munshiganj | 119 | 20:00 | 182 | Zigatola | 78 | 16:00
51 | Faridpur | 166 | 19:30 | 117 | Muradnagar | 30 | 22:00
52 | Fatullah | 101 | 15:00 | 118 | Mymensingh | 209 | 20:00
53 | Fenchuganj | 51 | 23:00 | 119 | Naogaon | 144 | 21:00
54 | Feni | 110 | 21:00 | 120 | Narail | 59.5 | 23:00
55 | GPH | 75 | 20:00 | 121 | Narinda | 78 | 13:00
56 | Ghatail | 76 | 00:00 | 122 | Narshingdi | 200 | 01:00
57 | Ghorashal | 15 | 15:00 | 123 | Natore | 157 | 00:00
58 | Ghorashal-230 | 89 | 00:00 | 124 | Nawabganj | 58.2 | 00:00
59 | Goalpara | 39 | 19:30 | 125 | Netrakona | 139 | 19:30
60 | Gollamari | 98 | 19:30 | 126 | New | 55 | 12:00
61 | Gopalganj | 112 | 19:30 | 127 | Niamatpur | 83 | 23:00
62 | Gulshan | 144 | 13:00 | 128 | Noapara | 50 | 19:30
63 | Halishahar | 70 | 15:00 | 129 | PHP | 2 | 02:00
64 | HaripurSBU | 169 | 00:00 | 130 | Pabna | 126 | 21:00
65 | Hasnabad | 67 | 23:00 | 131 | Palashbari | 120 | 20:00
66 | Hathazari | 80 | 22:00 | 132 | Panchagarh | 69 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 29-06-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15027.2 | 79 |  | 15110.2
1:00 | 14835.7 | 129 |  | 14970.7
2:00 | 14362.7 | 117 |  | 14484.7
3:00 | 14141.2 | 109 |  | 14255.2
4:00 | 13841.2 | 85 |  | 13930.2
5:00 | 13680.2 | 53 |  | 13735.2
6:00 | 12710.34 | 16 |  | 12727.34
7:00 | 12533.17 | 0 |  | 12533.17
8:00 | 12529.47 | 0 |  | 12529.47
9:00 | 12844.56 | 0 |  | 12844.56
10:00 | 13164.93 | 0 |  | 13164.93
11:00 | 13477.09 | 0 |  | 13477.09
12:00 | 13912.03 | 0 |  | 13912.03
13:00 | 14112.12 | 0 |  | 14112.12
14:00 | 14019.25 | 0 |  | 14019.25
15:00 | 14104.65 | 0 |  | 14104.65
16:00 | 14197.06 | 0 |  | 14197.06
17:00 | 13933.75 | 0 |  | 13933.75
18:00 | 13198.75 | 0 |  | 13198.75
19:00 | 14268.71 | 0 |  | 14268.71
19:30 | 15414.24 | 53 |  | 15469.24
20:00 | 15371.64 | 37 |  | 15410.64
21:00 | 15331.49 | 52 |  | 15385.49
22:00 | 15310.19 | 63 |  | 15376.19
23:00 | 15485.37 | 81 |  | 15570.37
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 29-06-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7643.2 | 7384 | 15027.2 | DAILY GENERATION CURVE
00:30 | 7527.45 | 7404 | 14931.45
01:00 | 7411.7 | 7424 | 14835.7 | 29-06-2025
01:30 | 7334.7 | 7264.5 | 14599.2
02:00 | 7257.7 | 7105 | 14362.7
02:30 | 7251.45 | 7000.5 | 14251.95
03:00 | 7245.2 | 6896 | 14141.2
03:30 | 7157.7 | 6833.5 | 13991.2
04:00 | 7070.2 | 6771 | 13841.2
04:30 | 7047.2 | 6713.5 | 13760.7
05:00 | 7024.2 | 6656 | 13680.2
05:30 | 6811.965 | 6383.305 | 13195.27
06:00 | 6599.73 | 6110.61 | 12710.34
06:30 | 6588.155 | 6033.6 | 12621.755
07:00 | 6576.58 | 5956.59 | 12533.17
07:30 | 6554.1 | 5977.22 | 12531.32
08:00 | 6531.62 | 5997.85 | 12529.47
08:30 | 6617.67 | 6069.345 | 12687.015
09:00 | 6703.72 | 6140.84 | 12844.56
09:30 | 6794.45 | 6210.295 | 13004.745
10:00 | 6885.18 | 6279.75 | 13164.93
10:30 | 6961.54 | 6359.47 | 13321.01
11:00 | 7037.9 | 6439.19 | 13477.09
11:30 | 7132.41 | 6562.15 | 13694.56
12:00 | 7226.92 | 6685.11 | 13912.03
12:30 | 7284.985 | 6727.09 | 14012.075
13:00 | 7343.05 | 6769.07 | 14112.12
13:30 | 7271.85 | 6793.835 | 14065.685
14:00 | 7200.65 | 6818.6 | 14019.25
14:30 | 7284.94 | 6777.01 | 14061.95
15:00 | 7369.23 | 6735.42 | 14104.65
15:30 | 7441.255 | 6709.6 | 14150.855
16:00 | 7513.28 | 6683.78 | 14197.06
16:30 | 7489.955 | 6575.45 | 14065.405
17:00 | 7466.63 | 6467.12 | 13933.75
17:30 | 7291.13 | 6275.12 | 13566.25
18:00 | 7115.63 | 6083.12 | 13198.75
18:30 | 7442.01 | 6291.72 | 13733.73
19:00 | 7768.39 | 6500.32 | 14268.71
19:30 | 8181.2 | 7233.04 | 15414.24
20:00 | 8097.2 | 7274.44 | 15371.64
20:30 | 8016.7 | 7334.865 | 15351.565 |  | Executive Engineer
21:00 | 7936.2 | 7395.29 | 15331.49 |  | Network Operation Division
21:30 | 7919.7 | 7401.14 | 15320.84
22:00 | 7903.2 | 7406.99 | 15310.19
22:30 | 7963.2 | 7434.58 | 15397.78
23:00 | 8023.2 | 7462.17 | 15485.37

## En-Curve
QF-LDC-12
Date | 29-06-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4051 | 2090 | 919 | 38 | 48 | 1436 | 172 | 4638 | 0 | 399 | 1223.2 | 0 | 0 | 13 | 79 | DAILY ENERGY CURVE
00:30 | 4070.5 | 2081.75 | 919 | 38 | 46 | 1428.5 | 169 | 4629.5 | 0 | 328 | 1212.7 | 0 | 0 | 8.5 | 104 | 29-06-2025
01:00 | 4090 | 2073.5 | 919 | 38 | 44 | 1421 | 166 | 4621 | 0 | 257 | 1202.2 | 0 | 0 | 4 | 129
01:30 | 4109 | 2073.5 | 919.5 | 38 | 44 | 1321 | 166 | 4530.5 | 0 | 250 | 1142.2 | 0 | 0 | 5.5 | 123 | Energy Generated | 339.0388 |  | MKWHr
02:00 | 4128 | 2073.5 | 920 | 38 | 44 | 1221 | 166 | 4440 | 0 | 243 | 1082.2 | 0 | 0 | 7 | 117 | Energy not Served | 0.821 |  | MKWHr
02:30 | 4138 | 2082.25 | 919.5 | 38 | 43 | 1176.5 | 166 | 4374.5 | 0 | 243 | 1055.7 | 0 | 0 | 15.5 | 113 | Total Energy Requirement | 339.8598 |  | MKWHr
03:00 | 4148 | 2091 | 919 | 38 | 42 | 1132 | 166 | 4309 | 0 | 243 | 1029.2 | 0 | 0 | 24 | 109
03:30 | 4137 | 2081 | 919 | 38 | 41 | 1126.5 | 166 | 4236.5 | 0 | 214.5 | 1008.7 | 0 | 0 | 23 | 97
04:00 | 4126 | 2071 | 919 | 38 | 40 | 1121 | 166 | 4164 | 0 | 186 | 988.2 | 0 | 0 | 22 | 85
04:30 | 4119.5 | 2060 | 919 | 38 | 37 | 1118.5 | 166 | 4107 | 0 | 186.5 | 987.7 | 0 | 0 | 21.5 | 69
05:00 | 4113 | 2049 | 919 | 38 | 34 | 1116 | 166 | 4050 | 0 | 187 | 987.2 | 0 | 0 | 21 | 53
05:30 | 4020 | 2018.5 | 919 | 38 | 32 | 1029.5 | 166 | 3870 | 24.17 | 156 | 890.6 | 0 | 0 | 31.5 | 34.5
06:00 | 3927 | 1988 | 919 | 38 | 30 | 943 | 166 | 3690 | 48.34 | 125 | 794 | 0 | 0 | 42 | 16
06:30 | 3922.5 | 1980 | 919 | 38 | 30 | 910.5 | 166 | 3645.5 | 102.755 | 142.5 | 712.5 | 0 | 0 | 52.5 | 8
07:00 | 3918 | 1972 | 919 | 38 | 30 | 878 | 166 | 3601 | 157.17 | 160 | 631 | 0 | 0 | 63 | 0
07:30 | 3914 | 1964 | 920 | 38 | 33 | 878.775 | 166 | 3604 | 198.545 | 160 | 594 | 0 | 0 | 61 | 0
08:00 | 3910 | 1956 | 921 | 38 | 36 | 879.55 | 166 | 3607 | 239.92 | 160 | 557 | 0 | 0 | 59 | 0
08:30 | 3941.5 | 1952.5 | 922 | 38 | 35 | 879.24 | 169 | 3658 | 306.275 | 176 | 552.5 | 0 | 0 | 57 | 0
09:00 | 3973 | 1949 | 923 | 38 | 34 | 878.93 | 172 | 3709 | 372.63 | 192 | 548 | 0 | 0 | 55 | 0
09:30 | 3950 | 1981 | 923 | 38 | 35 | 871.19 | 172 | 3778.5 | 428.055 | 192 | 581 | 0 | 0 | 55 | 0
10:00 | 3927 | 2013 | 923 | 38 | 36 | 863.45 | 172 | 3848 | 483.48 | 192 | 614 | 0 | 0 | 55 | 0
10:30 | 3960 | 2035 | 923 | 38 | 35 | 899.225 | 172 | 3875 | 479.285 | 192 | 671.5 | 0 | 0 | 41 | 0
11:00 | 3993 | 2057 | 923 | 38 | 34 | 935 | 172 | 3902 | 475.09 | 192 | 729 | 0 | 0 | 27 | 0
11:30 | 4006 | 2052 | 928 | 38 | 34 | 1050.755 | 172 | 4016 | 433.305 | 184 | 751 | 0 | 0 | 29.5 | 0
12:00 | 4019 | 2047 | 933 | 38 | 34 | 1166.51 | 172 | 4130 | 391.52 | 176 | 773 | 0 | 0 | 32 | 0
12:30 | 4001 | 2040.5 | 933 | 38 | 36 | 1217.175 | 169 | 4207.5 | 331.9 | 193.5 | 807 | 0 | 0 | 37.5 | 0
13:00 | 3983 | 2034 | 933 | 38 | 38 | 1267.84 | 166 | 4285 | 272.28 | 211 | 841 | 0 | 0 | 43 | 0
13:30 | 3856 | 1980 | 933 | 38 | 38 | 1276.67 | 166 | 4236.5 | 416.015 | 210.5 | 877 | 0 | 0 | 38 | 0
14:00 | 3729 | 1926 | 933 | 38 | 38 | 1285.5 | 166 | 4188 | 559.75 | 210 | 913 | 0 | 0 | 33 | 0
14:30 | 3829 | 1990 | 933 | 38 | 38 | 1287.89 | 166 | 4206.5 | 469.56 | 209.5 | 868 | 0 | 0 | 26.5 | 0
15:00 | 3929 | 2054 | 933 | 38 | 38 | 1290.28 | 166 | 4225 | 379.37 | 209 | 823 | 0 | 0 | 20 | 0
15:30 | 3942.5 | 2063 | 933 | 38 | 38 | 1299.245 | 166 | 4183.5 | 344.51 | 209 | 916.1 | 0 | 0 | 18 | 0
16:00 | 3956 | 2072 | 933 | 38 | 38 | 1308.21 | 166 | 4142 | 309.65 | 209 | 1009.2 | 0 | 0 | 16 | 0
16:30 | 3908 | 2065 | 933.5 | 38 | 38 | 1315.005 | 166 | 4059 | 233.8 | 230.5 | 1059.6 | 0 | 0 | 19 | 0
17:00 | 3860 | 2058 | 934 | 38 | 38 | 1321.8 | 166 | 3976 | 157.95 | 252 | 1110 | 0 | 0 | 22 | 0
17:30 | 3714.5 | 1986 | 933.5 | 38 | 36 | 1228.54 | 166 | 3872.5 | 100.71 | 306.5 | 1163.5 | 0 | 0 | 20.5 | 0
18:00 | 3569 | 1914 | 933 | 38 | 34 | 1135.28 | 166 | 3769 | 43.47 | 361 | 1217 | 0 | 0 | 19 | 0
18:30 | 3577.5 | 1932.5 | 933 | 38 | 38 | 1170.3 | 166 | 3963.5 | 21.83 | 410 | 1462.6 | 0 | 0 | 20.5 | 0
19:00 | 3586 | 1951 | 933 | 38 | 42 | 1205.32 | 166 | 4158 | 0.19 | 459 | 1708.2 | 0 | 0 | 22 | 0
19:30 | 3831 | 1958 | 933 | 38 | 42 | 1339.04 | 166 | 4402 | 0 | 690 | 1987.2 | 0 | 0 | 28 | 53
20:00 | 3788 | 1987 | 933 | 38 | 40 | 1324.44 | 172 | 4563 | 0 | 698 | 1803.2 | 0 | 0 | 25 | 37
20:30 | 3863 | 2039.5 | 933 | 38 | 38 | 1380.865 | 169 | 4652.5 | 0 | 583 | 1612.7 | 0 | 0 | 42 | 44.5
21:00 | 3938 | 2092 | 933 | 38 | 36 | 1437.29 | 166 | 4742 | 0 | 468 | 1422.2 | 0 | 0 | 59 | 52
21:30 | 3941.5 | 2101 | 933 | 38 | 36 | 1437.14 | 166 | 4743 | 0 | 468 | 1416.2 | 0 | 0 | 41 | 57.5
22:00 | 3945 | 2110 | 933 | 38 | 36 | 1436.99 | 166 | 4744 | 0 | 468 | 1410.2 | 0 | 0 | 23 | 63
22:30 | 3946 | 2147 | 933 | 38 | 38 | 1426.58 | 166 | 4783 | 0 | 468.5 | 1421.2 | 0 | 0 | 30.5 | 72
23:00 | 3947 | 2184 | 933 | 38 | 40 | 1416.17 | 166 | 4822 | 0 | 469 | 1432.2 | 0 | 0 | 38 | 81
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 29-06-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 382 | 07:00 | 367 | 00:00 | Payra | 413 | 07:00 | 406 | 00:00
Ashuganj | 402 | 6:00 | 379 | 21:00 | Rahanpur | 404 | 10:00 | 385 | 00:00
Bhulta | 404 | 05:00 | 373 | 14:00 | Rampal | 399 | 08:00 | 380 | 21:00
Bibiana | 389 | 18:30 | 379 | 00:00
BIPTC | 403 | 08:00 | 393 | 21:00
Bogura | 387 | 10:00 | 367 | 00:00
Gopalganj | 393 | 07:00 | 379 | 00:00
Kaliakoir | 373 | 18:30 | 358 | 15:00
Madunaghat | 393 | 06:00 | 385 | 15:00
Meghnaghat | 384 | 06:00 | 374 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 223 | 06:00 | 212 | 15:00 | Keranigonj | 221 | 06:00 | 211 | 13:00
AKSML | 232 | 18:00 | 221 | 15:00 | Khulna(S) | 228 | 08:00 | 215 | 22:00
Aminbazar | 224 | 07:00 | 214 | 15:00 | Madunaghat | 232 | 18:00 | 225 | 15:00
Ashuganj | 232 | 05:00 | 219 | 13:00 | Madunaghat-400 | 232 | 06:00 | 226 | 15:00
Ashuganj-400 | 230 | 6:00 | 218 | 20:00 | Maniknagar | 220 | 04:00 | 211 | 12:00
Baghabari | 234 | 05:00 | 224 | 16:00 | Meghnaghat | 227 | 18:30 | 220 | 11:00
Barapukuria | 223 | 05:00 | 214 | 00:00 | Meghnaghat-400 | 223 | 06:00 | 215 | 13:00
Barapukuria-230 | 223 | 5:00 | 215 | 21:00 | Mirsorai | 228 | 07:00 | 219 | 23:00
Barishal | 228 | 08:00 | 218 | 00:00 | Rajshahi | 234 | 05:00 | 220 | 21:00
Bheramara | 233 | 04:00 | 221 | 13:00 | Rampal | 230 | 13:00 | 216 | 23:00
Bhulta | 228 | 05:00 | 208 | 14:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 228 | 18:30 | 220 | 00:00 | Rampura | 226 | 06:00 | 205 | 13:00
BIPTC | 237 | 05:00 | 221 | 15:00 | Shikalbaha | 229 | 07:00 | 223 | 15:00
Bogura | 234 | 10:00 | 222 | 00:00 | Shyampur | 221 | 06:00 | 213 | 12:00
Bogura-400 | 234 | 10:00 | 222 | 00:00 | Siddhirganj | 222 | 18:00 | 213 | 12:00
Borhanuddin | 235 | 08:00 | 226 | 23:00 | Sirajgonj | 269 | 06:00 | 231 | 00:00
BSRM | 228 | 07:00 | 219 | 15:00 | Sreepur | 229 | 05:00 | 216 | 15:00
Cumilla(N) | 225 | 18:30 | 212 | 15:00 | Tongi | 225 | 19:30 | 211 | 15:00
Faridpur | 225 | 18:00 | 213 | 00:00
Fenchuganj | 229 | 18:00 | 221 | 00:00
Ghorashal | 230 | 02:00 | 220 | 00:00
Ghorashal-230 | 227 | 07:00 | 210 | 13:00
Gopalganj | 225 | 06:00 | 216 | 00:00
GPH | 230 | 05:00 | 221 | 15:00
Haripur | 221 | 18:30 | 213 | 12:00
Hasnabad | 222 | 18:30 | 212 | 12:00
Hathazari | 232 | 18:00 | 225 | 15:00
Ishurdi | 236 | 06:00 | 224 | 13:00
Jhenaidah | 229 | 06:00 | 214 | 22:00
Kaliakoir | 230 | 06:00 | 218 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 05:00 | 120 | 12:00 | Madartek | 135 | 05:00 | 121 | 12:00
Agargaon | 131 | 06:00 | 122 | 13:00 | Madunaghat | 131 | 06:00 | 127 | 12:00
Agrabad | 131 | 06:00 | 124 | 15:00 | Magura | 131 | 05:00 | 119 | 21:00
AKS | 130 | 18:00 | 125 | 15:00 | Mahasthangarh | 134 | 09:00 | 123 | 00:00
Aminbazar | 131 | 05:00 | 125 | 00:00 | Maijdee | N/A | N/A | N/A | N/A
Amnura | 136 | 06:00 | 123 | 00:00 | Manikganj | 129 | 19:30 | 119 | 23:00
Ashuganj | 140 | 05:00 | 132 | 00:00 | Maniknagar | 131 | 06:00 | 124 | 12:00
Bagerhat | 130 | 07:00 | 119 | 00:00 | Matarbari | 122 | 09:00 | 112 | 18:00
Bajitpur | 131 | 18:30 | 124 | 01:00 | Matuail | 129 | 18:30 | 123 | 13:00
Bakulia | 133 | 18:00 | 126 | 15:00 | Millgate | 132 | 03:00 | 122 | 12:00
Banani | 136 | 05:00 | 122 | 12:00 | Mirpur | 129 | 04:00 | 123 | 00:00
Bangabhaban | 131 | 06:00 | 123 | 15:00 | Mirzapur | 130 | 18:00 | 122 | 12:00
Barapukuria | 136 | 05:00 | 125 | 15:00 | Mithapukur | 130 | 10:00 | 116 | 00:00
Barguna | 134 | 07:00 | 129 | 00:00 | MI_Cement | 128 | 06:00 | 121 | 13:00
Barishal | 134 | 07:00 | 126 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal-230 | 134 | 18:00 | 126 | 00:00 | Mogbazar | 137 | 05:00 | 120 | 13:00
Baroaulia | 132 | 02:00 | 126 | 13:00 | Mongla | 131 | 18:30 | 119 | 00:00
Baroirhat | 127 | 18:30 | 117 | 01:00 | Motijheel | 131 | 06:00 | 19 | 02:00
Bashundhara | 136 | 05:00 | 119 | 13:00 | Muktagacha | 136 | 18:00 | 127 | 00:00
BashundharaCement | 127 | 04:00 | 121 | 12:00 | Munshiganj | 128 | 18:30 | 120 | 00:00
Beanibazar | 127 | 06:00 | 121 | 00:00 | Muradnagar | 129 | 18:30 | 117 | 15:00
Benapole | 130 | 18:30 | 117 | 22:00 | Mymensingh | 138 | 18:00 | 114 | 22:00
Bhaluka | 130 | 06:00 | 120 | 15:00 | Naogaon | 133 | 18:30 | 120 | 23:00
Bhandaria | 128 | 08:00 | 117 | 22:00 | Narail | 130 | 08:00 | 116 | 22:00
Bhangura | 133 | 06:00 | 126 | 22:00 | Narinda | 131 | 6:00 | 124 | 12:00
Bheramara | 137 | 05:00 | 131 | 21:00 | Narshingdi | 134 | 18:30 | 117 | 15:00
Bheramara(GK) | 137 | 05:00 | 131 | 21:00 | Natore | 134 | 06:00 | 126 | 21:00
Bhulta | 124 | 18:30 | 117 | 12:00 | Nawabganj | 132 | 06:00 | 125 | 12:00
Bog-Sherpur | 136 | 10:00 | 126 | 00:00 | Netrakona | 124 | 18:00 | 111 | 22:00
Bogura | 137 | 09:00 | 128 | 00:00 | New | 132 | 06:00 | 122 | 15:00
Bogura-230 | 137 | 06:00 | 128 | 00:00 | Niamatpur | 137 | 10:00 | 129 | 00:00
Brahmanbaria | 136 | 18:30 | 126 | 00:00 | Noapara | 133 | 18:30 | 123 | 00:00
Cantonment | 130 | 05:00 | 122 | 12:00 | Pabna | 134 | 06:00 | 127 | 22:00
Chandina | 130 | 18:00 | 120 | 15:00 | Palashbari | 130 | 08:00 | 115 | 23:00
Chandpur | 131 | 18:30 | 115 | 22:00 | Panchagarh | 136 | 04:00 | 117 | 15:00
Chandraghona | 132 | 06:00 | 128 | 15:00 | Patuakhali | 134 | 18:00 | 129 | 23:00
Chapai | 132 | 05:00 | 125 | 00:00 | Payra | 135 | 06:00 | 132 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 18:30 | 121 | 13:00 | PHP | 127 | 18:30 | 115 | 22:00
Chauddagram | 127 | 18:00 | 115 | 22:00 | Postogola | 130 | 05:00 | 124 | 12:00
Chhatak | 126 | 06:00 | 118 | 00:00 | Purbachal | 136 | 05:00 | 121 | 13:00
Chowmuhani | 124 | 18:30 | 107 | 01:00 | Purbasadipur | 129 | 04:00 | 117 | 15:00
Chuadanga | 130 | 06:00 | 117 | 21:00 | Rahanpur | 137 | 05:00 | 130 | 00:00
Coxsbazar | 123 | 18:00 | 113 | 00:00 | Rahanpur-400 | 138 | 18:00 | 131 | 00:00
Cumilla(N) | 129 | 18:00 | 120 | 22:00 | Rahim | 128 | 06:00 | 123 | 12:00
Cumilla(S) | 132 | 05:00 | 118 | 15:00 | Rajbari | 131 | 06:00 | 123 | 00:00
Daudkandi | 129 | 18:30 | 114 | 15:00 | Rajendrapur | 133 | 06:00 | 120 | 15:00
Dhaka | 136 | 05:00 | 122 | 12:00 | Rajshahi | 135 | 06:00 | 126 | 21:00
Dhamrai | 131 | 19:30 | 122 | 12:00 | Rajshahi-230 | 135 | 06:00 | 117 | 00:00
Dhanmondi | 137 | 05:00 | 122 | 13:00 | Ramganj | 115 | 05:00 | 108 | 22:00
Dohazari | 130 | 18:00 | 124 | 00:00 | Rampur | 132 | 07:00 | 125 | 15:00
Faridpur | 134 | 06:00 | 126 | 00:00 | Rampura | 135 | 06:00 | 121 | 13:00
Fatullah | 128 | 06:00 | 122 | 01:00 | Rangamati | 131 | 05:00 | 127 | 15:00
Fenchuganj | 135 | 18:00 | 130 | 00:00 | Rangpur | 130 | 10:00 | 120 | 16:00
Feni | 125 | 18:00 | 115 | 10:00 | Ruppur | 137 | 03:00 | 131 | 21:00
Ghatail | 132 | 18:30 | 122 | 23:00 | Saidpur | 130 | 05:00 | 119 | 15:00
Ghorashal | 136 | 07:00 | 127 | 12:00 | Satkhira | 131 | 08:00 | 120 | 22:00
Goalpara | 135 | 18:00 | 125 | 22:00 | Satmasjid | 130 | 06:00 | 122 | 13:00
Gollamari | 135 | 05:00 | 126 | 21:00 | Savar | 130 | 19:30 | 122 | 23:00
Gopalganj | 133 | 08:00 | 125 | 00:00 | SevenRings | 136 | 05:00 | 126 | 13:00
Gopalganj-400 | 135 | 07:00 | 128 | 00:00 | ShahCement | 129 | 18:30 | 121 | 13:00
Gulshan | 136 | 05:00 | 122 | 12:00 | Shahjadpur | 135 | 05:00 | 130 | 22:00
Halishahar | 132 | 06:00 | 125 | 15:00 | Shahjibazar | 135 | 18:30 | 126 | 00:00
Haripur | 128 | 07:00 | 123 | 12:00 | Shahmirpur | 133 | 02:00 | 127 | 15:00
HaripurSBU | 128 | 06:00 | 123 | 12:00 | Shariatpur | 133 | 18:30 | 124 | 00:00
Hasnabad | 129 | 18:00 | 123 | 11:00 | Sherpur | 137 | 18:00 | 126 | 00:00
Hathazari | 134 | 01:00 | 130 | 11:00 | Shikalbaha | 122 | 18:00 | 116 | 15:00
Ishurdi | 138 | 05:00 | 131 | 21:00 | Shikalbaha-230 | 134 | 18:00 | 128 | 16:00
Jaldhaka | 129 | 19:00 | 117 | 00:00 | Shitalakhya | 128 | 06:00 | 121 | 13:00
Jamalpur | 139 | 18:00 | 129 | 00:00 | Sholosohor | 131 | 06:00 | 125 | 15:00
Jashore | 129 | 05:00 | 115 | 19:30 | Shyampur | 127 | 02:00 | 121 | 10:00
Jhenaidah | 135 | 04:00 | 120 | 21:00 | Shyampur-230 | 127 | 06:00 | 121 | 13:00
Jhenaidah-230 | 134 | 06:00 | 124 | 19:30 | Siddhirganj | 129 | 18:30 | 123 | 12:00
Joydebpur | 140 | 18:30 | 126 | 15:00 | Sirajganj | 133 | 09:00 | 124 | 21:00
Joypurhat | 131 | 08:00 | 117 | 23:00 | Sonargaon | 126 | 00:00 | 120 | 15:00
Juldah | 132 | 18:00 | 127 | 15:00 | Sreemongol | 134 | 18:30 | 124 | 00:00
Kabirpur | 130 | 18:00 | 120 | 15:00 | Sreepur | 132 | 05:00 | 124 | 15:00
Kachua | 130 | 18:30 | 115 | 22:00 | Srinagar | 132 | 06:00 | 125 | 13:00
Kaliakoir | 133 | 18:00 | 124 | 12:00 | SSM | 136 | 18:30 | 130 | 13:00
Kallyanpur | 131 | 05:00 | 125 | 00:00 | Sunamganj | 125 | 06:00 | 117 | 22:00
Kalurghat | 131 | 06:00 | 126 | 19:00 | Sylhet | 129 | 07:00 | 123 | 00:00
Kamrangirchar | 133 | 05:00 | 125 | 12:00 | Sylhet-132 | 129 | 06:00 | 125 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Tangail | 130 | 05:00 | 121 | 23:00
Kasba | 128 | 18:00 | 116 | 15:00 | Thakurgaon | 134 | 04:00 | 113 | 15:00
Kazla | 130 | 07:00 | 123 | 13:00 | TK | 130 | 02:00 | 128 | 12:00
Keranigonj | 133 | 06:00 | 125 | 13:00 | Tongi | 133 | 19:30 | 125 | 12:00
Khagrachori | 131 | 06:00 | 126 | 15:00 | Ullahpara | 135 | 04:00 | 126 | 22:00
Khulna | 133 | 07:00 | 124 | 00:00 | Ullon | 135 | 05:00 | 121 | 13:00
Khulna(S) | 135 | 07:00 | 126 | 22:00 | Uttara | 130 | 06:00 | 122 | 23:00
Khulshi | 130 | 18:00 | 124 | 15:00 | UttaraNew | 130 | 05:00 | 122 | 23:00
Kishoreganj | 130 | 18:00 | 119 | 00:00 | Zigatola | 133 | 07:00 | 125 | 13:00
Kodda | 135 | 07:00 | 121 | 15:00
KSRM | 137 | 14:00 | 127 | 15:00
Kulaura | 134 | 07:00 | 128 | 00:00
Kurigram | 128 | 18:00 | 119 | 00:00
Kushtia | 134 | 05:00 | 125 | 21:00
Lalbag | 132 | 06:00 | 125 | 12:00
Lalmonirhat | 132 | 19:00 | 118 | 15:00
Madanganj | 127 | 04:00 | 121 | 12:00
Madaripur | 134 | 06:00 | 127 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division