## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 02-07-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-07-2025 | during | 02-07-2025 | during | 02-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 402 | 403 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 340 | 420 | 450 | 450 | 420 | 420 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 297 | 304 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 2 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 328 | 332 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 35 | 54 | 53.97 | 53.97 | 54 | 54 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 32 | 143 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 25 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19 | 25 | 33 | 33 | 26 | 26 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 21 | 21 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 24 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 224 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 87 | 135 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 88 | 105 | 105 | 70 | 70 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 67 | 104 | 104 | 68 | 68 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 86 | 152 | 162 | 162 | 108 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 19 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 400 | 400 | 584 | 584 | 450 | 450 | None
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 108 | 52 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2592 | 2745 | 5111.2 | 5111.2 | 3874.11 | 3928.11
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 3 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 166 | 172 | 165 | 165 | 165 | 165 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 219 | 213 | 213 | 214 | 214 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 9 | 97 | 105 | 105 | 105 | 105 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 38 | 48 | 82 | 48 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 65 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 11 | 2 | 25 | 2 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 5 | 0 | 5.18 | 0 | 5.18 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 150 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 66 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 48 | 88 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 15 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1155 | 1145 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 38 | 32 | 38 | 16 | 38 | 16 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 203 | 203 | 575 | 575 | 200 | 200 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1873 | 2459 | 3574.9 | 3594.72 | 3200.9 | 3220.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 0 | 0 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 341 | 348 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 340 | 340 | 340 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 19 | 20 | 46.7 | 46.7 | 21 | 21 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 47 | 47 | 55 | 55 | 49 | 49 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 135 | 173 | 195 | 195 | 153 | 153 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 40 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 30 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 119 | 170 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 42 | 48 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20.84 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 87 | 95 | 114 | 114 | 80 | 80 | Engine Problem
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 27 | 113 | 113 | 9 | 28 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 78 | 115 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 75 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1363 | 1576.2 | 2467.09 | 2400.75 | 2075.55 | 2024.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-07-2025 | during | 02-07-2025 | during | 02-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 44 | 49 | 157.5 | 157.5 | 72 | 72 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 128 | 161 | 200 | 200 | 160 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 82 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 19.93 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 35 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 266.93 | 339 | 599.1 | 549 | 463.6 | 413.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage instructed by DS(Gen)
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 157 | 144 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 80 | 83 | 83 | 80 | 80 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 171 | 171 | 160 | 160 | 165 | 165 | Machine Problem
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 8 | 8 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 285 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 381 | 347 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1423 | 1385 | 1520 | 1520 | 1425 | 1425
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 920 | 898 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 237 | 215 | 410 | 410 | 261 | 261 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 36 | 105 | 105 | 70 | 70 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 105 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 51 | 0 | 52 | 0 | 52 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 968 | 600 | 617.1 | 617.1 | 617.1 | 617.1 | U#2 under shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2214 | 1892 | 2989.1 | 2937.1 | 2805.1 | 2753.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 301 | 545 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 6 | 10 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1025 | 1244 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 276 | 279 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.23 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1948.23 | 2418 | 2172 | 2171 | 2172 | 2171
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 38 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 184 | 199 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 190 | 188 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 381 | 395 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 95 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 108 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.69 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1184 | 1362.19 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 65.12 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 86 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 2095.81 | 2487.19 | 3193.37 | 3026.87 | 3108.59 | 2942.09
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 49 | 47 | 50 | 50 | 50 | 50 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 201 | 200 | 200 | 200 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 98 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.1 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 203 | 0 | 116.43 | 0 | 116.43 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 490.1 | 460 | 645.43 | 498 | 645.43 | 498
System Total |  |  |  |  | 28565.2 | 27084.055 | 14266.07 | 15761.39 | 22272.19 | 21808.64 | 19770.28 | 19376.07
Forecast Scenario (02-07-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15360 |  | 0 |  | 15360
|  |  |  | 1:00 | 15320 |  | 0 |  | 15320
|  |  |  | 2:00 | 14900 |  | 0 |  | 14900
|  |  |  | 3:00 | 14610 |  | 0 |  | 14610
|  |  |  | 4:00 | 14270 |  | 0 |  | 14270
|  |  |  | 5:00 | 14070 |  | 0 |  | 14070
|  |  |  | 6:00 | 13370 |  | 0 |  | 13370
|  |  |  | 7:00 | 13350 |  | 0 |  | 13350
|  |  |  | 8:00 | 13250 |  | 0 |  | 13250
|  |  |  | 9:00 | 13270 |  | 0 |  | 13270
|  |  |  | 10:00 | 13470 |  | 0 |  | 13470
|  |  |  | 11:00 | 13800 |  | 0 |  | 13800
|  |  |  | 12:00 | 14460 |  | 0 |  | 14460
|  |  |  | 13:00 | 14700 |  | 0 |  | 14700
|  |  |  | 14:00 | 14600 |  | 0 |  | 14600
|  |  |  | 15:00 | 14680 |  | 0 |  | 14680
|  |  |  | 16:00 | 14570 |  | 0 |  | 14570
|  |  |  | 17:00 | 14100 |  | 0 |  | 14100
|  |  |  | 18:00 | 13670 |  | 0 |  | 13670
|  |  |  | 18:30 | 14100 |  | 0 |  | 14100
|  |  |  | 19:00 | 14790 |  | 0 |  | 14790
|  |  |  | 19:30 | 15750 |  | 0 |  | 15750
|  |  |  | 20:00 | 15930 |  | 0 |  | 15930
|  |  |  | 21:00 | 16120 |  | 0 |  | 16120
|  |  |  | 22:00 | 15800 |  | 0 |  | 15800
|  |  |  | 23:00 | 15700 |  | 0 |  | 15700
Probable Maximum Temperature: |  |  | 30.60°C
Probable Maximum Demand at Day Peak: |  |  | 14460.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16120.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15157.40 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 345.18317 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:36 hrs on 02-07-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 01-07-2025 | [28 empty] | Date: | 01-07-2025 | [28 empty] | Date: | 01-07-2025 | [28 empty] | Date: | 01-07-2025 | [28 empty] | Date: | 01-07-2025 | [12 empty] | Date: | 01-07-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [12 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 35 | 35 | 149 | 96 | 15 | 0 | 17 | 98 | 50 | 340 | 299 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 108 | 24.5 | 21 | 0 | 450 | 0 | 15 | 0 | 0 | 29 | 65 | 56 | 0 | 72 | 100 | 0 | 166 | 0 | 23 | 202 | 0 | 0 | 0 | 0 | 15 | 219 | 0 | 0 | 0 | 1155 | 0 | 51 | 100 | 8 | 0 | 300 | 335 | 49 | 204 | 21 | 34 | 0 | 199 | 17 | 20 | 96 | 46 | 52.2 | 0 | 38 | 275 | 320 | 388 | 0 | 0 | 154 | 8 | 0 | 79 | 30 | 0 | 0 | 171 | 17 | 100 | 159 | 47 | 0 | 0 | 12 | 7936.7 | 929 | 232 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 52 | 1451 | 0 | 0 | 0 | 70 | 0 | 88 | 0 | 26 | 0 | 0 | 30 | 0 | 164 | 0 | 161 | 0 | 0 | 0 | 350 | 0 | 0 | 200 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 10 | 120 | 220 | 0 | 299 | 1110 | 0 | 7190 | 15126.7 | 97.76
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 35 | 35 | 149 | 48 | 0 | 0 | 0 | 99 | 0 | 420 | 289 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 108 | 24.5 | 21 | 0 | 450 | 0 | 15 | 0 | 0 | 57 | 65 | 56 | 0 | 72 | 100 | 0 | 166 | 0 | 23 | 202 | 0 | 0 | 0 | 0 | 15 | 219 | 0 | 0 | 0 | 1150 | 0 | 51 | 100 | 8 | 0 | 354 | 335 | 49 | 193 | 21 | 57 | 0 | 199 | 6 | 20 | 96 | 50 | 52.2 | 0 | 38 | 275 | 320 | 362 | 0 | 0 | 154 | 8 | 0 | 80 | 30 | 0 | 0 | 170 | 17 | 90 | 160 | 47 | 0 | 0 | 10 | 7878.7 | 908 | 232 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1096 | 17 | 1450 | 0 | 0 | 0 | 70 | 0 | 88 | 0 | 26 | 0 | 0 | 30 | 0 | 165 | 0 | 163 | 0 | 0 | 0 | 350 | 0 | 0 | 197 | 50 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 10 | 120 | 220 | 0 | 299 | 1105 | 0 | 7123 | 15001.7 | 97.75
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 35 | 35 | 149 | 48 | 0 | 0 | 0 | 97 | 0 | 420 | 293 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 108 | 24.5 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 27 | 0 | 56 | 0 | 72 | 100 | 0 | 166 | 0 | 30 | 201 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1140 | 0 | 51 | 80 | 8 | 0 | 355 | 340 | 49 | 192 | 21 | 110 | 0 | 199 | 9 | 20 | 96 | 48 | 52.2 | 0 | 38 | 280 | 320 | 371 | 0 | 0 | 152 | 8 | 0 | 80 | 30 | 0 | 0 | 170 | 17 | 90 | 159 | 47 | 0 | 0 | 10 | 7802.7 | 914 | 234 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1108 | 0 | 1434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 158 | 0 | 0 | 0 | 350 | 0 | 0 | 198 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 11 | 120 | 220 | 0 | 299 | 1102 | 0 | 6808 | 14610.7 | 97.74
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 35 | 35 | 149 | 48 | 0 | 0 | 0 | 96 | 0 | 420 | 289 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 108 | 24.5 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 72 | 100 | 0 | 166 | 0 | 32 | 202 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1140 | 0 | 51 | 0 | 8 | 0 | 354 | 340 | 49 | 195 | 21 | 115 | 0 | 200 | 9 | 20 | 96 | 46 | 52.2 | 0 | 38 | 275 | 320 | 360 | 0 | 0 | 152 | 8 | 0 | 80 | 30 | 0 | 0 | 171 | 17 | 91 | 150 | 48 | 0 | 0 | 12 | 7632.7 | 913 | 237 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1097 | 0 | 1446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 158 | 0 | 0 | 0 | 350 | 0 | 0 | 200 | 50 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 11 | 120 | 220 | 0 | 300 | 1000 | 0 | 6713 | 14345.7 | 97.73
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 35 | 149 | 48 | 0 | 0 | 0 | 17 | 0 | 420 | 291 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 108 | 25 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 12 | 0 | 166 | 0 | 32 | 202 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1150 | 0 | 51 | 0 | 8 | 0 | 355 | 340 | 49 | 195 | 21 | 115 | 0 | 199 | 9 | 20 | 96 | 44 | 52.2 | 0 | 6 | 280 | 320 | 377 | 0 | 0 | 151 | 8 | 0 | 80 | 30 | 0 | 0 | 171 | 17 | 91 | 141 | 49 | 0 | 0 | 12 | 7355.2 | 915 | 239 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1063 | 0 | 1448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 160 | 0 | 0 | 0 | 350 | 0 | 0 | 201 | 50 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 11 | 120 | 220 | 0 | 300 | 990 | 0 | 6679 | 14034.2 | 97.72
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 35 | 149 | 48 | 0 | 0 | 0 | 15 | 0 | 420 | 291 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 108 | 25.4 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 12 | 0 | 166 | 0 | 32 | 202 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1090 | 0 | 51 | 0 | 8 | 0 | 354 | 340 | 49 | 192 | 21 | 115 | 0 | 200 | 9 | 20 | 96 | 44 | 52.2 | 0 | 8 | 280 | 320 | 360 | 0 | 0 | 153 | 8 | 0 | 80 | 30 | 0 | 0 | 170 | 17 | 81 | 140 | 49 | 0 | 0 | 12 | 7285.6 | 914 | 243 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 952 | 0 | 1436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 165 | 0 | 0 | 0 | 350 | 0 | 0 | 200 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 10 | 116 | 220 | 0 | 300 | 987 | 0 | 6554 | 13839.6 | 97.71
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 35 | 149 | 80 | 0 | 0 | 0 | 0 | 0 | 380 | 293 | 0 | 0 | 0 | 280 | 0 | 0 | 2 | 108 | 25.4 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 12 | 0 | 166 | 0 | 34 | 202 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1000 | 1 | 51 | 0 | 8 | 0 | 353 | 340 | 49 | 0 | 19 | 115 | 0 | 155 | 9 | 20 | 96 | 40 | 0 | 6 | 0 | 275 | 320 | 386 | 0 | 0 | 150 | 8 | 0 | 80 | 30 | 0 | 0 | 170 | 17 | 82 | 141 | 49 | 0 | 1.84 | 12 | 6900.24 | 913 | 245 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2.33 | 946 | 0 | 1257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.65 | 159 | 0 | 161 | 0 | 0 | 0 | 350 | 0 | 0.22 | 170 | 49 | 70 | 2 | 70 | 0 | 0 | 0.3 | 12 | 0.02 | 0 | 201 | 9 | 120 | 220 | 0 | 299 | 975 | 0 | 6271.52 | 13171.76 | 97.7
07:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 35 | 149 | 80 | 0 | 0 | 0 | 0 | 0 | 380 | 287 | 0 | 0 | 0 | 280 | 0 | 0 | 10 | 108 | 21 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 1 | 166 | 0 | 33 | 202 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 950 | 0 | 51 | 0 | 8 | 0 | 354 | 340 | 49 | 0 | 19 | 115 | 0 | 120 | 9 | 20 | 70 | 38 | 0 | 14 | 0 | 275 | 320 | 350 | 0 | 0 | 153 | 8 | 0 | 80 | 30 | 0 | 0 | 170 | 17 | 81 | 141 | 49 | 0 | 8.24 | 12 | 6793.24 | 914 | 246 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 17.11 | 914 | 0 | 1257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 6.45 | 162 | 0 | 165 | 0 | 0 | 0 | 350 | 0 | 0.55 | 202 | 49 | 70 | 6 | 70 | 0 | 0 | 1.2 | 43 | 0.14 | 0 | 193 | 8 | 116 | 220 | 0 | 300 | 985 | 0 | 6360.45 | 13153.69 | 97.69
08:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 35 | 115 | 80 | 0 | 0 | 0 | 0 | 0 | 350 | 291 | 0 | 0 | 0 | 250 | 0 | 0 | 12 | 108 | 21 | 14 | 0 | 400 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 12 | 2 | 166 | 0 | 7 | 200 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1000 | 12 | 51 | 0 | 8 | 0 | 349 | 340 | 49 | 0 | 19 | 80 | 0 | 120 | 9 | 20 | 70 | 38 | 0 | 28 | 0 | 280 | 320 | 367 | 0 | 0 | 146 | 8 | 0 | 80 | 30 | 0 | 0 | 170 | 17 | 81 | 139 | 49 | 1 | 16.8 | 12 | 6710.8 | 929 | 247 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 39.53 | 913 | 0 | 1263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 20.61 | 160 | 0 | 162 | 0 | 0 | 0 | 350 | 0 | 2.12 | 204 | 49 | 35 | 11 | 34 | 0 | 0 | 4.3 | 101 | 0.2 | 0 | 199 | 7 | 120 | 220 | 0 | 300 | 900 | 0 | 6343.76 | 13054.56 | 97.68
09:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 35 | 105 | 32 | 0 | 0 | 30 | 0 | 0 | 350 | 305 | 0 | 0 | 0 | 250 | 0 | 0 | 5 | 108 | 20 | 14 | 0 | 400 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 3 | 166 | 0 | 2 | 203 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1000 | 7 | 51 | 0 | 8 | 0 | 343 | 340 | 49 | 0 | 19 | 68 | 0 | 120 | 9 | 20 | 52 | 36 | 0 | 59 | 0 | 285 | 320 | 389 | 0 | 0 | 136 | 8 | 0 | 76 | 30 | 0 | 0 | 171 | 17 | 45 | 139 | 48 | 1 | 31.94 | 12 | 6652.94 | 930 | 245 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 56 | 880 | 0 | 1272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 25.12 | 164 | 0 | 167 | 0 | 0 | 0 | 350 | 0 | 3.04 | 200 | 49 | 35 | 23 | 16 | 0 | 0 | 3.2 | 136 | 0.27 | 0 | 202 | 7 | 120 | 220 | 0 | 301 | 900 | 0 | 6423.63 | 13076.57 | 97.67
10:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 35 | 87 | 32 | 0 | 0 | 0 | 0 | 0 | 350 | 297 | 0 | 0 | 0 | 329 | 0 | 0 | 23 | 108 | 0 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 3 | 166 | 0 | 2 | 203 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1100 | 2 | 51 | 0 | 45 | 0 | 343 | 340 | 48 | 0 | 19 | 70 | 0 | 105 | 9 | 20 | 36 | 36 | 0 | 66 | 0 | 290 | 320 | 389 | 0 | 0 | 154 | 8 | 0 | 75 | 30 | 0 | 0 | 171 | 17 | 45 | 129 | 49 | 1 | 17.08 | 12 | 6808.08 | 920 | 243 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 86 | 930 | 0 | 1182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 52.34 | 176 | 0 | 180 | 0 | 0 | 0 | 362 | 0 | 5.26 | 198 | 49 | 0 | 23 | 0 | 0 | 0 | 3.7 | 151 | 0.43 | 0 | 201 | 6 | 120 | 220 | 0 | 301 | 920 | 0 | 6469.73 | 13277.81 | 97.66
11:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 86 | 32 | 0 | 0 | 34 | 40 | 0 | 340 | 307 | 0 | 0 | 0 | 327 | 0 | 0 | 27 | 108 | 20 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 2 | 166 | 0 | 2 | 203 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1163 | 3 | 51 | 0 | 78 | 0 | 336 | 340 | 44 | 0 | 19 | 69 | 0 | 100 | 9 | 20 | 42 | 38 | 0 | 71 | 0 | 285 | 320 | 386 | 0 | 0 | 159 | 8 | 0 | 74 | 30 | 0 | 0 | 171 | 17 | 45 | 128 | 48 | 1 | 34.59 | 12 | 6996.59 | 920 | 237 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 94 | 950 | 0 | 1148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 0 | 60.04 | 181 | 0 | 191 | 0 | 0 | 0 | 414 | 0 | 4.05 | 198 | 49 | 0 | 37 | 0 | 0 | 0 | 3.6 | 166 | 0.26 | 0 | 210 | 6 | 123 | 220 | 0 | 301 | 950 | 0 | 6608.95 | 13605.54 | 97.65
12:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 35 | 17 | 87 | 32 | 224 | 2 | 55 | 86 | 0 | 340 | 297 | 0 | 0 | 25 | 328 | 0 | 0 | 19 | 108 | 19 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 12 | 48 | 5 | 166 | 0 | 2 | 203 | 0 | 0 | 3 | 0 | 9 | 214 | 0 | 0 | 0 | 1155 | 18 | 51 | 0 | 135 | 0 | 341 | 340 | 47 | 0 | 19 | 78 | 0 | 119 | 9 | 20 | 87 | 42 | 0 | 75 | 0 | 280 | 320 | 381 | 0 | 0 | 157 | 8 | 0 | 76 | 30 | 0 | 0 | 171 | 17 | 45 | 128 | 44 | 1 | 19.93 | 12 | 7517.93 | 920 | 237 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 51 | 968 | 0 | 1184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 65.12 | 184 | 0 | 190 | 0 | 0 | 0 | 381 | 0 | 5.69 | 201 | 49 | 0 | 30 | 0 | 0 | 0 | 7.1 | 203 | 0.23 | 0 | 276 | 6 | 120 | 220 | 0 | 301 | 1025 | 0 | 6748.14 | 14266.07 | 97.64
13:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 17 | 81 | 32 | 293 | 0 | 55 | 96 | 30 | 340 | 286 | 0 | 0 | 17 | 324 | 0 | 0 | 33 | 108 | 23 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 12 | 36 | 5 | 166 | 0 | 9 | 203 | 0 | 0 | 6 | 0 | 0 | 213 | 0 | 0 | 0 | 1116 | 2 | 51 | 0 | 155 | 0 | 339 | 340 | 47 | 0 | 19 | 94 | 0 | 132 | 9 | 19 | 72 | 44 | 0 | 70 | 0 | 285 | 320 | 386 | 0 | 0 | 152 | 8 | 0 | 77 | 30 | 0 | 0 | 171 | 30 | 45 | 138 | 45 | 2 | 51.82 | 13 | 7649.82 | 920 | 233 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 104 | 1053 | 0 | 1158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 28.42 | 170 | 0 | 182 | 0 | 0 | 0 | 401 | 0 | 0.94 | 197 | 49 | 35 | 39 | 0 | 0 | 0 | 7.8 | 184 | 0.18 | 0 | 211 | 7 | 120 | 220 | 0 | 300 | 1100 | 0 | 6855.34 | 14505.16 | 97.63
14:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 17 | 70 | 32 | 293 | 0 | 55 | 105 | 32 | 420 | 304 | 0 | 0 | 17 | 324 | 0 | 0 | 35 | 108 | 25 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 12 | 24 | 3 | 166 | 0 | 8 | 203 | 0 | 0 | 6 | 0 | 0 | 214 | 0 | 0 | 0 | 1050 | 8 | 51 | 0 | 155 | 0 | 336 | 340 | 46 | 0 | 20 | 107 | 0 | 143 | 9 | 19 | 78 | 44 | 0 | 59 | 32 | 290 | 320 | 335 | 0 | 0 | 144 | 8 | 0 | 74 | 30 | 0 | 0 | 170 | 35 | 45 | 140 | 44 | 2 | 30.81 | 13 | 7653.81 | 924 | 227 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 17 | 1070 | 0 | 1200.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 24.43 | 176 | 0 | 179 | 0 | 0 | 0 | 404 | 0 | 1.76 | 200 | 48 | 35 | 26 | 0 | 0 | 0 | 4.4 | 177 | 0.48 | 0 | 200 | 6 | 100 | 220 | 0 | 301 | 1110 | 0 | 6748.23 | 14402.04 | 97.62
15:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 54 | 0 | 68 | 31 | 300 | 0 | 55 | 106 | 32 | 420 | 293 | 0 | 0 | 17 | 324 | 0 | 0 | 21 | 108 | 0 | 7 | 0 | 450 | 0 | 10 | 0 | 0 | 22 | 0 | 0 | 0 | 60 | 75 | 3 | 166 | 0 | 2 | 202 | 0 | 0 | 6 | 0 | 0 | 216 | 0 | 0 | 0 | 1125 | 12 | 51 | 0 | 153 | 0 | 339 | 335 | 46 | 0 | 20 | 109 | 0 | 155 | 9 | 20 | 76 | 44 | 0 | 56 | 35 | 285 | 320 | 339 | 0 | 0 | 152 | 8 | 0 | 74 | 30 | 0 | 0 | 170 | 35 | 45 | 139 | 44 | 2 | 25.51 | 13 | 7788.51 | 930 | 222 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 11 | 992 | 0 | 1162.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 46.54 | 192 | 0 | 184 | 0 | 0 | 0 | 394 | 0 | 3.47 | 195 | 48 | 0 | 22 | 0 | 0 | 0 | 2.7 | 166 | 0.3 | 0 | 249 | 7 | 100 | 220 | 0 | 300 | 1130 | 0 | 6695.07 | 14483.58 | 97.61
16:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 12 | 68 | 31 | 300 | 0 | 55 | 97 | 50 | 380 | 295 | 0 | 0 | 17 | 326 | 0 | 0 | 19 | 108 | 24 | 21 | 0 | 450 | 0 | 65 | 0 | 0 | 12 | 0 | 0 | 0 | 60 | 75 | 0 | 166 | 20 | 2 | 202 | 0 | 0 | 18 | 0 | 47 | 216 | 0 | 0 | 0 | 1137 | 4 | 51 | 10 | 153 | 0 | 339 | 300 | 46 | 0 | 19 | 90 | 0 | 139 | 9 | 20 | 86 | 44 | 25 | 27 | 28 | 285 | 320 | 345 | 0 | 0 | 143 | 8 | 0 | 72 | 30 | 0 | 0 | 171 | 35 | 45 | 139 | 43 | 1 | 22.27 | 14 | 7867.27 | 903 | 222 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 28 | 927 | 0 | 1158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 32.75 | 196 | 0 | 188 | 0 | 0 | 0 | 350 | 0 | 2.03 | 195 | 48 | 0 | 8 | 0 | 0 | 0 | 1.1 | 81 | 0.1 | 0 | 250 | 7 | 100 | 220 | 0 | 300 | 1200 | 0 | 6510.98 | 14378.25 | 97.6
17:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 24 | 68 | 31 | 300 | 0 | 49 | 102 | 50 | 380 | 290 | 0 | 0 | 17 | 330 | 0 | 0 | 7 | 108 | 18.5 | 21 | 0 | 450 | 0 | 65 | 0 | 0 | 23 | 0 | 0 | 0 | 60 | 75 | 0 | 166 | 30 | 7 | 201 | 0 | 0 | 19 | 0 | 63 | 219 | 0 | 0 | 0 | 1110 | 3 | 51 | 10 | 153 | 0 | 341 | 300 | 46 | 0 | 20 | 100 | 0 | 144 | 9 | 20 | 86 | 40 | 25 | 17 | 29 | 290 | 320 | 312 | 0 | 0 | 150 | 8 | 0 | 74 | 30 | 0 | 0 | 170 | 35 | 55 | 147 | 46 | 1 | 11.36 | 14 | 7871.86 | 902 | 221 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 13 | 591 | 0 | 1142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 1.61 | 195 | 0 | 188 | 0 | 0 | 0 | 380 | 0 | 0 | 199 | 47 | 0 | 9 | 0 | 0 | 0 | 0.9 | 31 | 0.13 | 0 | 232 | 5 | 100 | 220 | 0 | 299 | 1200 | 0 | 6027.64 | 13899.5 | 97.59
18:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 35 | 68 | 60 | 145 | 0 | 35 | 100 | 51 | 330 | 293 | 0 | 0 | 17 | 300 | 0 | 0 | 3 | 108 | 24 | 21 | 0 | 400 | 1 | 65 | 0 | 0 | 21 | 0 | 0 | 0 | 48 | 75 | 0 | 166 | 30 | 3 | 201 | 0 | 0 | 19 | 0 | 64 | 219 | 0 | 0 | 0 | 1032 | 1 | 51 | 10 | 164 | 0 | 341 | 300 | 46 | 0 | 20 | 103 | 0 | 143 | 15 | 20 | 70 | 38 | 25 | 3 | 29 | 290 | 320 | 328 | 0 | 0 | 154 | 8 | 0 | 74 | 30 | 0 | 0 | 169 | 35 | 55 | 150 | 47 | 0 | 4.31 | 14 | 7540.31 | 902 | 217 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 6 | 557 | 2 | 1057 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0.44 | 195 | 0 | 188 | 0 | 0 | 0 | 394 | 0 | 0 | 200 | 48 | 35 | 2 | 30 | 0 | 0 | 0.7 | 13 | 0.05 | 0 | 197 | 6 | 100 | 220 | 0 | 341 | 1120 | 0 | 5930.19 | 13470.5 | 97.58
19:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 35 | 70 | 79 | 45 | 0 | 35 | 100 | 52 | 420 | 306 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 108 | 24 | 21 | 0 | 500 | 15 | 90 | 0 | 0 | 13 | 65 | 25 | 0 | 80 | 88 | 0 | 166 | 31 | 10 | 202 | 0 | 0 | 19 | 1 | 65 | 218 | 0 | 0 | 0 | 1180 | 0 | 51 | 10 | 170 | 0 | 340 | 330 | 45 | 0 | 20 | 103 | 0 | 143 | 26 | 20 | 85 | 50 | 25 | 0 | 29 | 295 | 320 | 383 | 0 | 0 | 140 | 8 | 0 | 76 | 30 | 0 | 0 | 169 | 35 | 64 | 150 | 48 | 0 | 0 | 13 | 8125 | 897 | 218 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 36 | 0 | 573 | 18 | 1191 | 0 | 45 | 0 | 1 | 0 | 86 | 0 | 12 | 0 | 0 | 28 | 0 | 197 | 0 | 188 | 0 | 0 | 0 | 414 | 0 | 0 | 202 | 49 | 90 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 258 | 8 | 120 | 220 | 0 | 384 | 1120 | 0 | 6473 | 14598 | 97.57
19:30 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 35 | 70 | 140 | 45 | 0 | 55 | 149 | 62 | 420 | 310 | 0 | 0 | 35 | 330 | 0 | 0 | 0 | 90 | 24 | 21 | 0 | 500 | 15 | 150 | 0 | 0 | 11 | 65 | 30 | 0 | 100 | 88 | 0 | 166 | 42 | 4 | 202 | 0 | 0 | 32 | 8 | 75 | 219 | 0 | 0 | 0 | 1130 | 0 | 51 | 40 | 170 | 0 | 346 | 340 | 46 | 0 | 18 | 115 | 0 | 167 | 28 | 20 | 96 | 46 | 43 | 0 | 29 | 285 | 320 | 352 | 0 | 0 | 151 | 8 | 0 | 76 | 30 | 0 | 0 | 169 | 35 | 81 | 150 | 48 | 0 | 0 | 14 | 8464 | 897 | 217 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 75 | 0 | 600 | 35 | 1337.81 | 0 | 46 | 0 | 80 | 0 | 95 | 35 | 33 | 0 | 0 | 30 | 0 | 198 | 0 | 188 | 0 | 0 | 0 | 414 | 0 | 0 | 204 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 8 | 120 | 220 | 0 | 445 | 1200 | 0 | 7055.81 | 15519.81
20:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 35 | 117 | 144 | 0 | 0 | 55 | 151 | 68 | 420 | 300 | 0 | 0 | 35 | 333 | 0 | 0 | 0 | 70 | 25 | 21 | 0 | 500 | 16 | 150 | 0 | 0 | 30 | 65 | 38 | 0 | 100 | 88 | 0 | 172 | 54 | 8 | 203 | 0 | 0 | 32 | 8 | 94 | 220 | 0 | 0 | 0 | 1110 | 0 | 51 | 36 | 170 | 0 | 351 | 340 | 46 | 0 | 18 | 115 | 0 | 164 | 27 | 20 | 96 | 48 | 52.2 | 0 | 29 | 285 | 320 | 317 | 0 | 0 | 155 | 8 | 0 | 79 | 30 | 0 | 0 | 169 | 35 | 82 | 169 | 48 | 0 | 0 | 14 | 8503.2 | 897 | 215 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 594 | 35 | 1366.36 | 0 | 38 | 0 | 92 | 0 | 95 | 35 | 37 | 0 | 0 | 30 | 0 | 199 | 0 | 188 | 0 | 0 | 0 | 391 | 0 | 0 | 201 | 47 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 10 | 120 | 220 | 0 | 464 | 1220 | 0 | 7125.36 | 15628.56 | 97.56
21:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 54 | 35 | 135 | 143 | 0 | 0 | 55 | 152 | 67 | 420 | 304 | 0 | 0 | 35 | 332 | 0 | 0 | 0 | 52 | 25 | 21 | 0 | 400 | 15 | 150 | 0 | 0 | 32 | 65 | 38 | 0 | 100 | 88 | 0 | 172 | 66 | 11 | 203 | 0 | 0 | 50 | 8 | 97 | 219 | 0 | 0 | 0 | 1145 | 0 | 51 | 40 | 173 | 0 | 348 | 340 | 47 | 0 | 20 | 115 | 0 | 170 | 27 | 20 | 95 | 48 | 52.2 | 0 | 30 | 285 | 320 | 347 | 0 | 0 | 144 | 8 | 0 | 80 | 30 | 0 | 0 | 171 | 35 | 82 | 161 | 49 | 0 | 0 | 12 | 8504.2 | 898 | 215 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 600 | 36 | 1362.19 | 0 | 38 | 0 | 108 | 0 | 95 | 35 | 37 | 0 | 0 | 30 | 0 | 199 | 0 | 188 | 0 | 0 | 0 | 395 | 0 | 0 | 200 | 47 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 10 | 120 | 220 | 0 | 545 | 1244 | 0 | 7257.19 | 15761.39 | 97.55
22:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 54 | 35 | 149 | 143 | 0 | 0 | 55 | 142 | 67 | 420 | 294 | 0 | 0 | 35 | 333 | 0 | 0 | 0 | 35 | 25 | 21 | 0 | 400 | 13 | 150 | 0 | 0 | 35 | 65 | 68 | 0 | 100 | 88 | 0 | 172 | 62 | 18 | 203 | 0 | 0 | 50 | 8 | 90 | 220 | 0 | 0 | 0 | 1109 | 0 | 51 | 40 | 170 | 0 | 352 | 340 | 48 | 0 | 21 | 115 | 0 | 170 | 28 | 20 | 95 | 48 | 52.2 | 0 | 30 | 280 | 320 | 317 | 0 | 0 | 149 | 8 | 0 | 80 | 30 | 0 | 0 | 172 | 35 | 82 | 161 | 49 | 0 | 0 | 12 | 8451.2 | 899 | 211 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 598 | 36 | 1351.54 | 0 | 47 | 0 | 113 | 0 | 95 | 0 | 37 | 0 | 0 | 30 | 0 | 199 | 0 | 188 | 0 | 0 | 0 | 333 | 0 | 0 | 202 | 45 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 10 | 120 | 220 | 0 | 544 | 1244 | 0 | 7150.54 | 15601.74 | 97.54
23:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 54 | 35 | 149 | 145 | 0 | 0 | 17 | 146 | 67 | 420 | 308 | 0 | 0 | 17 | 332 | 0 | 0 | 0 | 52 | 26 | 21 | 0 | 400 | 13 | 150 | 0 | 0 | 32 | 65 | 70 | 0 | 100 | 88 | 0 | 172 | 65 | 21 | 203 | 0 | 0 | 50 | 8 | 89 | 221 | 0 | 0 | 0 | 1150 | 0 | 51 | 40 | 173 | 0 | 350 | 340 | 47 | 0 | 21 | 115 | 0 | 170 | 28 | 19 | 95 | 50 | 52.2 | 0 | 30 | 290 | 320 | 345 | 0 | 0 | 152 | 8 | 0 | 80 | 30 | 0 | 0 | 172 | 35 | 83 | 161 | 49 | 0 | 0 | 12 | 8484.2 | 898 | 214 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 604 | 51 | 1369.76 | 0 | 45 | 0 | 113 | 0 | 95 | 0 | 37 | 0 | 0 | 30 | 0 | 200 | 0 | 188 | 0 | 0 | 0 | 361 | 0 | 0 | 200 | 47 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 11 | 120 | 220 | 0 | 447 | 1120 | 0 | 7007.76 | 15491.96 | 97.53
Total KWH | 0 | 1241482 | 479971 | 0 | 0 | 0 | 0 | 0 | 9802800 | 0 | 0 | 782964 | 748800 | 2747520 | 1608960 | 1884327 | 12484 | 750034 | 1899360 | 619200 | 9316000 | 7177338 | 0 | 0 | 314175 | 7329894 | 0 | 0 | 222774 | 2332800 | 535800 | 459000 | 0 | 10149090.91 | 91456 | 1072636 | 0 | 0 | 690720 | 423781 | 378768 | 0 | 1027200 | 1295040 | 24117 | 4028980 | 439100 | 356160 | 4901818.18 | 0 | 0 | 490080 | 42723 | 768618 | 4970705 | 0 | 0 | 0 | 26476361 | 78300 | 1188347 | 498472 | 2241454.54 | 0 | 8645000 | 8116000 | 1138560 | 1078000 | 487728 | 2396160 | 0 | 3768000 | 321720 | 450150 | 1996140 | 1034880 | 608995 | 528373 | 466064 | 6832000 | 7677400 | 8997000 | 0 | 0 | 3620618 | 181416 | 0 | 1862400 | 715008 | 0 | 0 | 4512550 | 641160 | 1639200 | 3456000 | 1080000 | 12400 | 287470 | 303840 | 184753842.63 | 22045090 | 5553504 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 532656 | 496080 | 20654545 | 289056 | 30752727 | 0 | 260158 | 0 | 667008 | 0 | 606160 | 92544 | 182362 | 0 | 699620 | 173500 | 315752 | 4393000 | 0 | 4470855 | 0 | 0 | 0 | 9144800 | 0 | 18720 | 4868000 | 1134109 | 1615016 | 241939 | 1292121 | 0 | 0 | 39505.08 | 1443600 | 3496 | 0 | 5563000 | 208475 | 2754000 | 5437900 | 0 | 8195544 | 26496000 | 0 | 161552842.08 | 346306684.71

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 01-07-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14266.07 | MW | 12:00 Hr. | Energy Generated |  |  | 346.3067 |  | MKWHr.
| Day Peak Demand |  |  | 14266.07 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.025 |  | MKWHr.
| Evening Peak Generation |  |  | 15761.39 | MW | 21:00 Hr. | Energy Demand |  |  | 347.3317 |  | MKWHr.
| Evening Peak Demand |  |  | 15920.39 | MW | 21:00 Hr. | Maximum Temperature |  |  | 34 |  | °C
| Minimum Generation of the Day |  |  | 13054.56 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 1008.46 |  | MMCFD
| Maximum Generation of the Day |  |  | 15761.39 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.5646 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 44.7699 | 0 | 15.4221 | 0 | 0 | 0.22277 | 0 | 0 | 60.4148 | Gas | 140.883 | Gas | 497747473.0565
| Chattogram Zone |  |  | 5.3269 | 31.3782 | 6.0294 | 0 | 4.029 | 0.10242 | 0 | 0.69072 | 47.5566 | Coal | 98.2894 | Coal | 611916079.49
| Cumilla Zone |  |  | 23.3452 | 0 | 10.0556 | 0 | 0 | 0.52837 | 1.0349 | 0 | 34.964 | HFO | 43.2578 | HFO | 810424477.62
| Mymensingh Zone |  |  | 1.08 | 0 | 6.0402 | 0 | 0 | 0.29987 | 0 | 0 | 7.4201 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 34.3984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.3984 | Hydro | 4.029 | Hydro | 402898
| Khulna Zone |  |  | 5.5535 | 20.6545 | 0.82171 | 0 | 0 | 0.49608 | 22.9571 | 0 | 50.4829 | Solar | 4.4121 | Solar | 71911649.9788
| Barishal Zone |  |  | 8.4004 | 40.2545 | 0 | 0 | 0 | 0.003496 | 0 | 0 | 48.6584 | Import | 54.7447 | Import | 270838803.72
| Rajshahi Zone |  |  | 18.0087 | 0 | 1.9817 | 0 | 0 | 1.0341 | 30.7527 | 0 | 51.7772 | Wind | 0.69072 | Wind | 10112140.8
| Rangpur Zone |  |  | 0 | 6.0021 | 2.9071 | 0 | 0 | 1.725 | 0 | 0 | 10.6343
| Total |  |  | 140.883 | 98.2894 | 43.2578 | 0 | 4.029 | 4.4121 | 54.7447 | 0.69072 | 346.3067
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 497747473.0565 |  | Hydro | 402898
|  |  |  | Coal | 611916079.49 |  | Solar | 71911649.9788
|  |  |  | HFO | 810424477.62 |  | Import | 270838803.72
|  |  |  | HSD | 0 |  | Wind | 10112140.8
[5 empty] | Total: | 227,33,53,522 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.0451 | Peak Hr Flow | 898.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 47007072.82 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 30.7527 | Peak Hr Flow | 1362.19 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 882 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.0349 | Peak Hr Flow | 48.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 1088 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 53.8327 | Peak Hr Flow | 2308.19 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5435
|  |  |  | Chattogram |  | 0 |  | 1496
|  |  |  | Cumilla |  | 15 |  | 1441
|  |  |  | Mymensingh |  | 90 |  | 1251
|  |  |  | Sylhet |  | 0 |  | 697
|  |  |  | Khulna |  | 0 |  | 1815
|  |  |  | Barishal |  | 0 |  | 482
|  |  |  | Rajshahi |  | 0 |  | 1607
|  |  |  | Rangpur |  | 47 |  | 1085
|  |  |  | Total |  | 152 |  | 15309
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[5 empty] | Total | 300 |  |  |  | Total | 476
|  |  |  | Total Unavailable Capacity |  |  |  | 776
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:42 | Chowmuhani-Ramganj 132 kV Ckt-1 is restored.
| 09:32 |  | Haripur 230/132kV S/S 132KV Bhulta-1 (Old Narsingdi) Project Work S/D Due to GND Project
Work
| 10:51 | 18:10 | Meghnaghat 230/132kV S/S Meghnaghat-Start Up(MPL) Scheduled S/D Due to Maintenance Work
| 12:00 |  | Day peak Generation is 14264 MW
| 13:10 | 16:35 | Jhenaidah-Magura 132 kV Ckt-1 Scheduled S/D from Magura 132/33kV end Due to Relay
Testing.
| 13:12 | 16:34 | Jhenaidah 132/33kV S/S Jhenaidah-Magura, 132kV Circuit-1(L7) Scheduled S/D Due to Relay
Testing work for Magura CKT- 1 at Magura Grid End.
| 14:06 | 14:41 | Brahmanbaria 132/33kV S/S 402T HT Forced S/D | [7 empty] | 50.0MW load
interrup.
| 14:06 | 14:41 | Brahmanbaria 132/33kV S/S 402T LT Forced S/D | [7 empty] | 50.0MW load
interrup.
| 14:26 | 15:36 | Jamalpur 132/33kV S/S T-1 HT Scheduled S/D Due to 33kv feeder breaker connector redhot | [7 empty] | 10.0MW load
|  |  | maintenance work by S.PDB. | [7 empty] | interrup.
| 14:26 | 15:36 | Jamalpur 132/33kV S/S T-1 LT Scheduled S/D Due to 33kv sarishabari feeder breaker D.S | [7 empty] | 10.0MW load
|  |  | connector RedHot maintenance work by S.PDB | [7 empty] | interrup.
| 14:48 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is OFF with remarks:-
| 15:29 | 15:38 | Satkhira 132/33kV S/S Transformer-1 (T-1) LT Tripped showing Over current relay & Earth
fault relay. relays Due to Due to 33kV Tala & 33kV Ashasuni feeder fault.
| 15:55 |  | Kaliakor 400/132 Kv transformer TR-3 (new) charged from 132Kv side for the first time
| 16:08 |  | Rampal 1320 MW (BIFPCL) Shutdown with remarks:- U2
| 16:18 | 17:43 | BIPTC S/S 20DF12 Tripped showing 20DF12 relays.
| 17:00 |  | Rampal 1320 MW (BIFPCL) Synchronized
|  | 17:20 | Bog-Sherpur 132/33kV S/S Main Bus-1 is restored.
|  | 18:07 | Mirzapur 132/33kV S/S Transformer-02(E07) HT is restored.
| 18:28 |  | Raozan 25 MW PP Synchronized
| 21:00 |  | Peak generation 15761 MW
| 21:18 | 00:47 | Kodda(300MW)-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Bus CT
hotspot maintenance
| 22:20 | 23:33 | Amnura 132/33kV S/S T-2 (416T) LT Scheduled S/D Due to Emergency maintenance work (Red | [7 empty] | 19.0MW load
|  |  | Hot) for GOMOSTAPUR 33KV feeder under Transformer-02 & 33kV bus Section-3 | [7 empty] | interrup.
| 22:21 | 23:26 | Amnura 132/33kV S/S T-2 (416T) HT Scheduled S/D Due to Emergency maintenance work (Red | [7 empty] | 19.0MW load
|  |  | Hot) for GOMOSTAPUR 33KV feeder under Transformer-02 & 33kV bus Section-3 | [7 empty] | interrup.
| 22:54 | 23:02 | Noapara 132/33kV S/S T-2 LT Tripped showing SIEMENS 7SJ81 relays Due to Due to Reb-01 | [7 empty] | 22.5MW load
|  |  | Feeder fault. | [7 empty] | interrup.
| 22:54 | 23:02 | Noapara 132/33kV S/S T-1 LT Tripped showing SIEMENS 7SJ81 relays Due to Due to Reb-01 | [7 empty] | 22.5MW load
|  |  | Feeder fault. | [7 empty] | interrup.
| 01:27 |  | Raozan 25 MW PP Shutdown
| 04:51 |  | Sirajgonj 225MW CCPP Unit-1, FGMO is OFF with remarks:-
| 05:08 | 06:44 | Baroaulia 132/33kV S/S 132kv Main Bus Forced S/D Due to 132kv Main BUS DS Y-phase Redhot | [7 empty] | 24.0MW load
|  |  | work. | [7 empty] | interrup.
| 05:22 | 06:39 | AKSML-Baroaulia 132kV Ckt-1 Scheduled S/D from AKS 132/33kV end Due to Baraulia sub
station maintenance due to red hot.
| 06:30 |  | Rangpur 132/33kV S/S T-1(414T) LT Forced S/D Due to 33kV Lalbagh-2 under 33kV BUS | [7 empty] | 25.0MW load
|  |  | Section-1 D/S raiser Red Hot rectification work. | [7 empty] | interrup.
| 06:30 |  | Rangpur 132/33kV S/S T-1(414T) HT Forced S/D Due to 33kV Lalbagh-2 under 33kV BUS | [7 empty] | 25.0MW load
|  |  | Section-1 D/S raiser Red Hot rectification work. | [7 empty] | interrup.
| 07:00 |  | Minimum Generation: 12954 MW.
| 07:42 |  | Dhamrai 132/33kV S/S Transformer-1 LT Scheduled S/D Due to PBs maintenance work
| 07:43 |  | Dhamrai 132/33kV S/S Transformer-1 HT Scheduled S/D Due to PBs maintenance work
| 07:43 |  | Dhamrai 132/33kV S/S Transformer-1 HT Scheduled S/D Due to PBs maintenance work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 01-07-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 403 | 9802800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9316000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 304 | 7177338 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 12484 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 332 | 7329894 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 782964 | Liquid fuel shortage
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 143 | 1608960 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 750034 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 314175 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 25 | 535800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 459000 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 24 | 479971 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 1884327 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 135 | 2747520 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1241482 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 67 | 619200 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 152 | 1899360 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 222774 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 748800 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 400 | 10149090.91 | None
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 52 | 2332800 | -
Dhaka Area Total |  |  |  |  | 5939.724 | 2745 | 60414773.91
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 42723 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 78300 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 490080 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 172 | 4028980 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 219 | 4970705 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 97 | 768618 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 38 | 378768 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 423781 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1027200 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 11 | 356160 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 24117 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 150 | 1072636 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 66 | 439100 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 88 | 1295040 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 15 | 91456 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1145 | 26476361 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 32 | 690720 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 203 | 4901818.18 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4895.72 | 2459 | 47556563.18
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 0 | 1078000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 348 | 8645000 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 8116000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 20 | 487728 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 47 | 1138560 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 173 | 2241454.54 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1188347 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 40 | 498472 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 30 | 466064 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 170 | 3768000 | -
| Import (Tripura) |  | Import | 0 | 160 | 48 | 1034880 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 608995 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 450150 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 95 | 1996140 | Engine Problem
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 321720 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 2396160 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 528373 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1576.2 | 34964043.54
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 49 | 1080000 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12400 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 161 | 3456000 | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 82 | 1639200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 287470 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 303840 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 641160 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 339 | 7420070
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | Gas shortage instructed by DS(Gen)
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 144 | 3620618 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 715008 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1862400 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 171 | 4512550 | Machine Problem
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 181416 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 6832000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 347 | 8997000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7677400 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1385 | 34398392
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 898 | 22045090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 215 | 5553504 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 36 | 289056 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 532656 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 496080 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 600 | 20654545 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1892 | 50482931
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 545 | 8195544 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 10 | 208475 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2754000 | FGMO
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 26496000 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5437900 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 279 | 5563000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3496 | -
Barishal Area Total |  |  |  |  | 2236 | 2418 | 48658415
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 38 | 260158 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 182362 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 199 | 4393000 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 188 | 4470855 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 395 | 9144800 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 173500 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 606160 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 108 | 667008 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 92544 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 18720 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1362.19 | 30752727 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 315752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 699620 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2487.19 | 51777206
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 47 | 1134109 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4868000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 1292121 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 39505.08 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1615016 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 241939 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1443600 | -
Rangpur Area Total |  |  |  |  | 950 | 460 | 10634290.08
Eastern Grid Total |  |  |  |  | 16705.895 | 8504.2 | 184753842.63
Western Grid Total |  |  |  |  | 10378.16 | 7257.19 | 161552842.08
National Grid Total |  |  |  |  | 27084.055 | 15761.39 | 346306684.71
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 01-07-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10215.11 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4941.6 | MW
i) Dhaka area |  |  | 5435.12 |  | MW | i) Khulna area |  |  |  | 1815 | MW
ii) Chattogram area |  |  | 1496 |  | MW | ii) Barishal area |  |  |  | 482 | MW
iii) Cumilla area |  |  | 1425.99 |  | MW | iii) Rajshahi area |  |  |  | 1606.6 | MW
iv) Mymensingh area |  |  | 1161 |  | MW | iv) Rangpur area |  |  |  | 1038 | MW
v) Sylhet area |  |  | 697 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15156.71 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 85 | 21:00 | 133 | Patuakhali | 82.5 | 23:00
2 | AKSML | 129 | 12:00 | 68 | Jaldhaka | 98 | 01:00 | 134 | Payra | 34 | 23:00
3 | Aftabnagar | 42 | 15:00 | 69 | Jamalpur | 145 | 19:30 | 135 | Postogola | 60 | 13:00
4 | Agargaon | 139 | 13:00 | 70 | Jashore | 128 | 00:00 | 136 | Purbachal | 22 | 00:00
5 | Agrabad | 92 | 19:00 | 71 | Jhenaidah | 118 | 01:00 | 137 | Purbasadipur | 150 | 00:00
6 | Amnura | 40 | 20:00 | 72 | Joydebpur | 140 | 15:00 | 138 | Rahanpur | 31 | 21:00
7 | Ashuganj | 107 | 23:00 | 73 | Joypurhat | 66 | 01:00 | 139 | Rahim | 35 | 01:00
8 | BSRM | 205 | 02:00 | 74 | Juldah | 16 | 23:00 | 140 | Rajbari | 82 | 19:30
9 | Bagerhat | 86 | 22:00 | 75 | KSRM | 23 | 00:00 | 141 | Rajendrapur | 136 | 20:00
10 | Bajitpur | 55 | 19:30 | 76 | Kabirpur | 250 | 11:00 | 142 | Rajshahi | 119 | 23:00
11 | Bakulia | 94 | 15:00 | 77 | Kachua | 96 | 22:00 | 143 | Rajshahi-230 | 91 | 13:00
12 | Banani | 44 | 13:00 | 78 | Kallyanpur | 108 | 00:00 | 144 | Ramganj | 120 | 22:00
13 | Bangabhaban | 15 | 11:00 | 79 | Kalurghat | 40 | 15:00 | 145 | Rampur | 39 | 00:00
14 | Barapukuria | 74 | 22:00 | 80 | Kamrangirchar | 70 | 12:00 | 146 | Rangamati | 18 | 19:30
15 | Barguna | 22 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 147 | 19:00
16 | Barishal | 109 | 20:00 | 82 | Kasba | 38 | 22:00 | 148 | Ruppur | 7.6 | 15:00
17 | Barishal-230 | 100 | 19:30 | 83 | Kazla | 98 | 19:30 | 149 | SSM | 8 | 00:00
18 | Baroaulia | 64 | 08:00 | 84 | Keranigonj | 93 | 22:00 | 150 | Saidpur | 115 | 00:00
19 | Baroirhat | 63 | 19:00 | 85 | Khagrachori | 32 | 00:00 | 151 | Satkhira | 124 | 00:00
20 | Bashundhara | 210 | 15:00 | 86 | Khulna | 74 | 00:00 | 152 | Satmasjid | 102 | 14:00
21 | BashundharaCement | 13 | 00:00 | 87 | Khulshi | 153 | 12:00 | 153 | Savar | 221 | 19:30
22 | Beanibazar | 91 | 21:00 | 88 | Kishoreganj | 148 | 02:00 | 154 | SevenRings | 17.49 | 20:00
23 | Benapole | 81 | 20:00 | 89 | Kodda | 314 | 14:00 | 155 | ShahCement | 18 | 00:00
24 | Bhaluka | 151 | 17:00 | 90 | Kulaura | 61 | 19:30 | 156 | Shahjadpur | 86 | 21:00
25 | Bhandaria | 58 | 22:00 | 91 | Kurigram | 67.9 | 04:00 | 157 | Shahjibazar | 131 | 01:00
26 | Bhangura | 40 | 22:00 | 92 | Kushtia | 163 | 19:30 | 158 | Shahmirpur | 67 | 00:00
27 | Bheramara(GK) | 69 | 22:00 | 93 | Lalbag | 56 | 12:00 | 159 | Shariatpur | 89 | 00:00
28 | Bhulta | 244 | 00:00 | 94 | Lalmonirhat | 72 | 19:00 | 160 | Sherpur | 162 | 22:00
29 | Bog-Sherpur | 68 | 21:00 | 95 | MI_Cement | 17 | 00:00 | 161 | Shikalbaha | 15 | 01:00
30 | Bogura | 182 | 22:00 | 96 | Madanganj | 50 | 19:30 | 162 | Shitalakhya | 84.6 | 15:00
31 | Borhanuddin | 89 | 23:00 | 97 | Madaripur | 113 | 23:00 | 163 | Sholosohor | 46 | 15:00
32 | Brahmanbaria | 136 | 00:00 | 98 | Madartek | 96 | 00:00 | 164 | Shyampur | 164 | 12:00
33 | Cantonment | 158 | 12:00 | 99 | Madunaghat | 56 | 19:00 | 165 | Siddhirganj | 120 | 15:00
34 | Chandina | 16.41 | 23:00 | 100 | Magura | 67 | 22:00 | 166 | Sirajganj | 120 | 21:00
35 | Chandpur | 81 | 21:00 | 101 | Mahasthangarh | 92 | 00:00 | 167 | Sonargaon | 113 | 00:00
36 | Chandraghona | 38 | 20:00 | 102 | Manikganj | 130 | 20:00 | 168 | Sreemongol | 84 | 19:00
37 | Chapai | 77 | 21:00 | 103 | Maniknagar | 88 | 13:00 | 169 | Sreepur | 108 | 19:30
38 | Charsaidpur | 40 | 01:00 | 104 | Matarbari | 49 | 20:00 | 170 | Srinagar | 49.65 | 22:00
39 | Chauddagram | 75 | 23:00 | 105 | Matuail | 66 | 15:00 | 171 | Sunamganj | 63 | 01:00
40 | Chhatak | 45 | 19:30 | 106 | Millgate | 120 | 15:00 | 172 | Sylhet | 55 | 00:00
41 | Chowmuhani | 198 | 19:30 | 107 | Mirpur | 127 | 15:00 | 173 | Sylhet-132 | 138 | 19:00
42 | Chuadanga | 116 | 21:00 | 108 | Mirsorai | 11 | 15:00 | 174 | TK | 33.6 | 23:00
43 | Coxsbazar | 133 | 19:30 | 109 | Mirzapur | 42 | 19:00 | 175 | Tangail | 184 | 21:00
44 | Cumilla(N) | 159 | 23:00 | 110 | Mithapukur | 74 | 01:00 | 176 | Thakurgaon | 118 | 20:00
45 | Cumilla(S) | 185 | 18:30 | 111 | Modern | N/A | N/A | 177 | Tongi | 144 | 15:00
46 | Daudkandi | 159 | 21:00 | 112 | Mogbazar | 151.4 | 13:00 | 178 | Ullahpara | 40 | 01:00
47 | Dhaka | 82 | 13:00 | 113 | Mongla | 43 | 08:00 | 179 | Ullon | 42 | 00:00
48 | Dhamrai | 128 | 12:00 | 114 | Motijheel | 45 | 13:00 | 180 | Uttara | 90 | 15:00
49 | Dhanmondi | 131.4 | 13:00 | 115 | Muktagacha | 40 | 20:00 | 181 | UttaraNew | 78 | 15:00
50 | Dohazari | 106 | 21:00 | 116 | Munshiganj | 121 | 00:00 | 182 | Zigatola | 78 | 00:00
51 | Faridpur | 170 | 21:00 | 117 | Muradnagar | 31 | 22:00
52 | Fatullah | 101 | 15:00 | 118 | Mymensingh | 209 | 22:00
53 | Fenchuganj | 51 | 21:00 | 119 | Naogaon | 143 | 23:00
54 | Feni | 120 | 19:00 | 120 | Narail | 59 | 21:00
55 | GPH | 82 | 12:00 | 121 | Narinda | 78 | 13:00
56 | Ghatail | 82 | 21:00 | 122 | Narshingdi | 195 | 21:00
57 | Ghorashal | 14 | 00:00 | 123 | Natore | 156 | 21:00
58 | Ghorashal-230 | 93 | 21:00 | 124 | Nawabganj | 62 | 22:00
59 | Goalpara | 39 | 00:00 | 125 | Netrakona | 140 | 19:00
60 | Gollamari | 96 | 21:00 | 126 | New | 56 | 13:00
61 | Gopalganj | 113.1 | 20:00 | 127 | Niamatpur | 84 | 23:00
62 | Gulshan | 128 | 13:00 | 128 | Noapara | 50 | 19:30
63 | Halishahar | 70 | 10:00 | 129 | PHP | 7 | 18:30
64 | HaripurSBU | 164 | 16:00 | 130 | Pabna | 126 | 21:00
65 | Hasnabad | 70 | 14:00 | 131 | Palashbari | 122 | 21:00
66 | Hathazari | 85 | 19:00 | 132 | Panchagarh | 66 | 03:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 01-07-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15126.7 | 32 |  | 15160.14
1:00 | 15001.7 | 114 |  | 15120.7
2:00 | 14610.7 | 86 |  | 14700.7
3:00 | 14345.7 | 62 |  | 14410.7
4:00 | 14034.2 | 34 |  | 14070.2
5:00 | 13839.6 | 30 |  | 13870.6
6:00 | 13171.76 | 0 |  | 13171.76
7:00 | 13153.69 | 0 |  | 13153.69
8:00 | 13054.56 | 0 |  | 13054.56
9:00 | 13076.57 | 0 |  | 13076.57
10:00 | 13277.81 | 0 |  | 13277.81
11:00 | 13605.54 | 0 |  | 13605.54
12:00 | 14266.07 | 0 |  | 14266.07
13:00 | 14505.16 | 0 |  | 14505.16
14:00 | 14402.04 | 0 |  | 14402.04
15:00 | 14483.58 | 0 |  | 14483.58
16:00 | 14378.25 | 0 |  | 14378.25
17:00 | 13899.5 | 0 |  | 13899.5
18:00 | 13470.5 | 0 |  | 13470.5
19:00 | 14598 | 0 |  | 14598
19:30 | 15519.81 | 30 |  | 15550.81
20:00 | 15628.56 | 97 |  | 15729.56
21:00 | 15761.39 | 152 |  | 15920.39
22:00 | 15601.74 | 209 |  | 15819.74
23:00 | 15491.96 | 209 |  | 15709.96
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 01-07-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7936.7 | 7190 | 15126.7 | DAILY GENERATION CURVE
00:30 | 7907.7 | 7156.5 | 15064.2
01:00 | 7878.7 | 7123 | 15001.7 | 01-07-2025
01:30 | 7840.7 | 6965.5 | 14806.2
02:00 | 7802.7 | 6808 | 14610.7
02:30 | 7717.7 | 6760.5 | 14478.2
03:00 | 7632.7 | 6713 | 14345.7
03:30 | 7493.95 | 6696 | 14189.95
04:00 | 7355.2 | 6679 | 14034.2
04:30 | 7320.4 | 6616.5 | 13936.9
05:00 | 7285.6 | 6554 | 13839.6
05:30 | 7092.92 | 6412.76 | 13505.68
06:00 | 6900.24 | 6271.52 | 13171.76
06:30 | 6846.74 | 6315.985 | 13162.725
07:00 | 6793.24 | 6360.45 | 13153.69
07:30 | 6752.02 | 6352.105 | 13104.125
08:00 | 6710.8 | 6343.76 | 13054.56
08:30 | 6681.87 | 6383.695 | 13065.565
09:00 | 6652.94 | 6423.63 | 13076.57
09:30 | 6730.51 | 6446.68 | 13177.19
10:00 | 6808.08 | 6469.73 | 13277.81
10:30 | 6902.335 | 6539.34 | 13441.675
11:00 | 6996.59 | 6608.95 | 13605.54
11:30 | 7257.26 | 6678.545 | 13935.805
12:00 | 7517.93 | 6748.14 | 14266.07
12:30 | 7583.875 | 6801.74 | 14385.615
13:00 | 7649.82 | 6855.34 | 14505.16
13:30 | 7651.815 | 6801.785 | 14453.6
14:00 | 7653.81 | 6748.23 | 14402.04
14:30 | 7721.16 | 6721.65 | 14442.81
15:00 | 7788.51 | 6695.07 | 14483.58
15:30 | 7827.89 | 6603.025 | 14430.915
16:00 | 7867.27 | 6510.98 | 14378.25
16:30 | 7869.565 | 6269.31 | 14138.875
17:00 | 7871.86 | 6027.64 | 13899.5
17:30 | 7706.085 | 5978.915 | 13685
18:00 | 7540.31 | 5930.19 | 13470.5
18:30 | 7832.655 | 6201.595 | 14034.25
19:00 | 8125 | 6473 | 14598
19:30 | 8464 | 7055.81 | 15519.81
20:00 | 8503.2 | 7125.36 | 15628.56
20:30 | 8503.7 | 7191.275 | 15694.975 |  | Executive Engineer
21:00 | 8504.2 | 7257.19 | 15761.39 |  | Network Operation Division
21:30 | 8477.7 | 7203.865 | 15681.565
22:00 | 8451.2 | 7150.54 | 15601.74
22:30 | 8467.7 | 7079.15 | 15546.85
23:00 | 8484.2 | 7007.76 | 15491.96

## En-Curve
QF-LDC-12
Date | 01-07-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3745 | 2031.5 | 929 | 38 | 46 | 1451 | 166 | 4393 | 0 | 559 | 1739.2 | 0 | 0 | 29 | 32 | DAILY ENERGY CURVE
00:30 | 3754.5 | 2067 | 918.5 | 38 | 48 | 1450.5 | 166 | 4384 | 0 | 521.5 | 1673.2 | 0 | 0 | 43 | 73 | 01-07-2025
01:00 | 3764 | 2102.5 | 908 | 38 | 50 | 1450 | 166 | 4375 | 0 | 484 | 1607.2 | 0 | 0 | 57 | 114
01:30 | 3767.5 | 2110 | 911 | 38 | 49 | 1442 | 166 | 4336 | 0 | 379.5 | 1565.2 | 0 | 0 | 42 | 100 | Energy Generated | 346.3067 |  | MKWHr
02:00 | 3771 | 2117.5 | 914 | 38 | 48 | 1434 | 166 | 4297 | 0 | 275 | 1523.2 | 0 | 0 | 27 | 86 | Energy not Served | 1.025 |  | MKWHr
02:30 | 3769 | 2110.5 | 913.5 | 38 | 47 | 1440 | 166 | 4243 | 0 | 247 | 1482.7 | 0 | 0 | 21.5 | 74 | Total Energy Requirement | 347.3317 |  | MKWHr
03:00 | 3767 | 2103.5 | 913 | 38 | 46 | 1446 | 166 | 4189 | 0 | 219 | 1442.2 | 0 | 0 | 16 | 62
03:30 | 3779 | 2106.75 | 914 | 38 | 45 | 1447 | 166 | 4172.5 | 0 | 203 | 1300.2 | 0 | 0 | 18.5 | 48
04:00 | 3791 | 2110 | 915 | 38 | 44 | 1448 | 166 | 4156 | 0 | 187 | 1158.2 | 0 | 0 | 21 | 34
04:30 | 3783.5 | 2110.7 | 914.5 | 38 | 44 | 1442 | 166 | 4067.5 | 0 | 188 | 1152.2 | 0 | 0 | 30.5 | 32
05:00 | 3776 | 2111.4 | 914 | 38 | 44 | 1436 | 166 | 3979 | 0 | 189 | 1146.2 | 0 | 0 | 40 | 30
05:30 | 3691.5 | 2088.9 | 913.5 | 38 | 42 | 1346.5 | 166 | 3910.5 | 15.18 | 201 | 1054.6 | 0 | 0 | 38 | 15
06:00 | 3607 | 2066.4 | 913 | 38 | 40 | 1257 | 166 | 3842 | 30.36 | 213 | 963 | 0 | 0 | 36 | 0
06:30 | 3592.5 | 2061.7 | 913.5 | 38 | 39 | 1257 | 166 | 3818.5 | 82.525 | 238 | 932 | 0 | 0 | 24 | 0
07:00 | 3578 | 2057 | 914 | 38 | 38 | 1257 | 166 | 3795 | 134.69 | 263 | 901 | 0 | 0 | 12 | 0
07:30 | 3566.5 | 2004.5 | 921.5 | 38 | 38 | 1260 | 166 | 3780 | 210.125 | 263 | 830 | 0 | 0 | 26.5 | 0
08:00 | 3555 | 1952 | 929 | 38 | 38 | 1263 | 166 | 3765 | 285.56 | 263 | 759 | 0 | 0 | 41 | 0
08:30 | 3566 | 1951.5 | 929.5 | 38 | 37 | 1267.5 | 166 | 3750 | 360.065 | 239 | 721 | 0 | 0 | 40 | 0
09:00 | 3577 | 1951 | 930 | 38 | 36 | 1272 | 166 | 3735 | 434.57 | 215 | 683 | 0 | 0 | 39 | 0
09:30 | 3632 | 1969 | 925 | 38 | 36 | 1227 | 166 | 3818.5 | 485.19 | 225 | 614 | 0 | 0 | 41.5 | 0
10:00 | 3687 | 1987 | 920 | 38 | 36 | 1182 | 166 | 3902 | 535.81 | 235 | 545 | 0 | 0 | 44 | 0
10:30 | 3713 | 2011 | 920 | 38 | 37 | 1165 | 166 | 3963 | 573.675 | 235 | 572 | 0 | 0 | 48 | 0
11:00 | 3739 | 2035 | 920 | 38 | 38 | 1148 | 166 | 4024 | 611.54 | 235 | 599 | 0 | 0 | 52 | 0
11:30 | 3720.5 | 2057 | 920 | 38 | 40 | 1166 | 166 | 4101 | 598.805 | 235 | 848.5 | 0 | 0 | 45 | 0
12:00 | 3702 | 2079 | 920 | 38 | 42 | 1184 | 166 | 4178 | 586.07 | 235 | 1098 | 0 | 0 | 38 | 0
12:30 | 3698 | 2089.5 | 920 | 38 | 43 | 1171 | 166 | 4203.5 | 605.615 | 235 | 1181.5 | 0 | 0 | 34.5 | 0
13:00 | 3694 | 2100 | 920 | 38 | 44 | 1158 | 166 | 4229 | 625.16 | 235 | 1265 | 0 | 0 | 31 | 0
13:30 | 3657 | 2145.5 | 922 | 38 | 44 | 1179.08 | 166 | 4205.5 | 536.52 | 241.5 | 1277.5 | 0 | 0 | 41 | 0
14:00 | 3620 | 2191 | 924 | 38 | 44 | 1200.16 | 166 | 4182 | 447.88 | 248 | 1290 | 0 | 0 | 51 | 0
14:30 | 3623.5 | 2189.5 | 927 | 38 | 44 | 1181.11 | 166 | 4211.5 | 449.7 | 249 | 1327 | 0 | 0 | 36.5 | 0
15:00 | 3627 | 2188 | 930 | 38 | 44 | 1162.06 | 166 | 4241 | 451.52 | 250 | 1364 | 0 | 0 | 22 | 0
15:30 | 3596.5 | 2182.5 | 916.5 | 38 | 44 | 1160.03 | 166 | 4250 | 366.885 | 246.5 | 1447 | 0 | 0 | 17 | 0
16:00 | 3566 | 2177 | 903 | 38 | 44 | 1158 | 166 | 4259 | 282.25 | 243 | 1530 | 0 | 0 | 12 | 0
16:30 | 3569.5 | 2180.25 | 902.5 | 38 | 42 | 1150 | 166 | 4069 | 195.125 | 243.5 | 1565.5 | 0 | 0 | 17.5 | 0
17:00 | 3573 | 2183.5 | 902 | 38 | 40 | 1142 | 166 | 3879 | 108 | 244 | 1601 | 0 | 0 | 23 | 0
17:30 | 3571 | 2143.75 | 902 | 38 | 39 | 1099.5 | 166 | 3787.5 | 73.75 | 295 | 1547.5 | 0 | 0 | 22 | 0
18:00 | 3569 | 2104 | 902 | 38 | 38 | 1057 | 166 | 3696 | 39.5 | 346 | 1494 | 0 | 0 | 21 | 0
18:30 | 3632.5 | 2209 | 899.5 | 38 | 44 | 1124 | 166 | 3832 | 19.75 | 485.5 | 1567 | 0 | 0 | 17 | 0
19:00 | 3696 | 2314 | 897 | 38 | 50 | 1191 | 166 | 3968 | 0 | 625 | 1640 | 0 | 0 | 13 | 0
19:30 | 3710 | 2314 | 897 | 38 | 46 | 1337.81 | 166 | 4108 | 0 | 745 | 2147 | 0 | 0 | 11 | 30
20:00 | 3660 | 2318 | 897 | 38 | 48 | 1366.36 | 172 | 4114 | 0 | 763 | 2222.2 | 0 | 0 | 30 | 97
20:30 | 3678 | 2268.5 | 897.5 | 38 | 48 | 1364.275 | 172 | 4188.5 | 0 | 754 | 2255.2 | 0 | 0 | 31 | 124.5
21:00 | 3696 | 2219 | 898 | 38 | 48 | 1362.19 | 172 | 4263 | 0 | 745 | 2288.2 | 0 | 0 | 32 | 152
21:30 | 3653 | 2216.5 | 898.5 | 38 | 48 | 1356.865 | 172 | 4240 | 0 | 756 | 2269.2 | 0 | 0 | 33.5 | 180.5
22:00 | 3610 | 2214 | 899 | 38 | 48 | 1351.54 | 172 | 4217 | 0 | 767 | 2250.2 | 0 | 0 | 35 | 209
22:30 | 3638.5 | 2230.5 | 898.5 | 38 | 49 | 1360.65 | 172 | 4134.5 | 0 | 758.5 | 2233.2 | 0 | 0 | 33.5 | 209
23:00 | 3667 | 2247 | 898 | 38 | 50 | 1369.76 | 172 | 4052 | 0 | 750 | 2216.2 | 0 | 0 | 32 | 209
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 01-07-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 384 | 07:00 | 372 | 11:00 | Payra | 414 | 07:00 | 406 | 21:00
Ashuganj | 410 | 7:00 | 376 | 10:00 | Rahanpur | 404 | 18:30 | 389 | 01:00
Bhulta | 404 | 07:00 | 376 | 10:00 | Rampal | 401 | 07:00 | 385 | 22:00
Bibiana | 387 | 18:00 | 380 | 11:00
BIPTC | 403 | 06:00 | 393 | 22:00
Bogura | 387 | 18:00 | 371 | 02:00
Gopalganj | 397 | 08:00 | 383 | 21:00
Kaliakoir | 376 | 02:00 | 363 | 10:00
Madunaghat | 398 | 03:00 | 387 | 11:00
Meghnaghat | 386 | 07:00 | 376 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 224 | 07:00 | 214 | 11:00 | Keranigonj | 222 | 07:00 | 212 | 11:00
AKSML | 230 | 05:00 | 222 | 11:00 | Khulna(S) | 230 | 08:00 | 216 | 21:00
Aminbazar | 223 | 04:00 | 217 | 10:00 | Madunaghat | 234 | 17:00 | 225 | 10:00
Ashuganj | 231 | 05:00 | 220 | 10:00 | Madunaghat-400 | 234 | 18:00 | 227 | 11:00
Ashuganj-400 | 231 | 05:00 | 220 | 10:00 | Maniknagar | 219 | 07:00 | 211 | 11:00
Baghabari | 234 | 07:00 | 225 | 00:00 | Meghnaghat | 227 | 05:00 | 220 | 10:00
Barapukuria | 223 | 18:30 | 216 | 00:00 | Meghnaghat-400 | 223 | 05:00 | 216 | 11:00
Barapukuria-230 | 223 | 18:30 | 216 | 00:00 | Mirsorai | 228 | 18:30 | 218 | 11:00
Barishal | 229 | 08:00 | 220 | 21:00 | Rajshahi | 233 | 07:00 | 222 | 21:00
Bheramara | 233 | 07:00 | 221 | 20:00 | Rampal | 229 | 08:00 | 217 | 20:00
Bhulta | 229 | 07:00 | 209 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 229 | 07:00 | 221 | 11:00 | Rampura | 229 | 07:00 | 207 | 11:00
BIPTC | 236 | 07:00 | 221 | 20:00 | Shikalbaha | 232 | 19:00 | 224 | 09:00
Bogura | 234 | 18:00 | 224 | 02:00 | Shyampur | 222 | 07:00 | 213 | 11:00
Bogura-400 | 234 | 09:00 | 225 | 02:00 | Siddhirganj | 221 | 18:30 | 214 | 11:00
Borhanuddin | 234 | 08:00 | 228 | 21:00 | Sirajgonj | 238 | 06:00 | 233 | 00:00
BSRM | 228 | 18:00 | 218 | 11:00 | Sreepur | 228 | 07:00 | 219 | 11:00
Cumilla(N) | 223 | 18:00 | 213 | 11:00 | Tongi | 227 | 07:00 | 210 | 09:00
Faridpur | 226 | 08:00 | 216 | 21:00
Fenchuganj | 228 | 07:00 | 221 | 01:00
Ghorashal | 232 | 01:00 | 220 | 09:00
Ghorashal-230 | 227 | 07:00 | 212 | 11:00
Gopalganj | 227 | 08:00 | 218 | 21:00
GPH | 228 | 07:00 | 221 | 11:00
Haripur | 221 | 07:00 | 213 | 11:00
Hasnabad | 221 | 05:00 | 213 | 11:00
Hathazari | 234 | 18:00 | 226 | 10:00
Ishurdi | 236 | 07:00 | 223 | 20:00
Jhenaidah | 230 | 07:00 | 214 | 20:00
Kaliakoir | 231 | 07:00 | 219 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 05:00 | 122 | 11:00 | Madartek | 137 | 07:00 | 123 | 11:00
Agargaon | 131 | 07:00 | 124 | 11:00 | Madunaghat | 134 | 17:00 | 126 | 10:00
Agrabad | 133 | 18:00 | 126 | 11:00 | Magura | 134 | 07:00 | 121 | 21:00
AKS | 131 | 18:00 | 125 | 11:00 | Mahasthangarh | 134 | 08:00 | 124 | 02:00
Aminbazar | 131 | 04:00 | 127 | 09:00 | Maijdee | N/A | N/A | N/A | N/A
Amnura | 137 | 19:00 | 126 | 00:00 | Manikganj | 127 | 07:00 | 116 | 11:00
Ashuganj | 140 | 06:00 | 133 | 15:00 | Maniknagar | 130 | 04:00 | 124 | 11:00
Bagerhat | 131 | 08:00 | 121 | 21:00 | Matarbari | 122 | 17:00 | 115 | 00:00
Bajitpur | 130 | 06:00 | 123 | 11:00 | Matuail | 128.6 | 18:30 | 123 | 11:00
Bakulia | 135 | 19:00 | 125 | 11:00 | Millgate | 132 | 07:00 | 121 | 11:00
Banani | 136 | 07:00 | 122 | 11:00 | Mirpur | 129 | 07:00 | 123 | 10:00
Bangabhaban | 130 | 05:00 | 124 | 11:00 | Mirzapur | 130 | 18:00 | 123 | 21:00
Barapukuria | 135 | 05:00 | 127 | 16:00 | Mithapukur | 130 | 09:00 | 119 | 01:00
Barguna | 134 | 07:00 | 128 | 22:00 | MI_Cement | 129 | 18:00 | 121 | 11:00
Barishal | 133 | 08:00 | 126 | 21:00 | Modern | N/A | N/A | N/A | N/A
Barishal-230 | 134 | 08:00 | 127 | 21:00 | Mogbazar | 135 | 08:00 | 124 | 11:00
Baroaulia | 134 | 17:00 | 128 | 11:00 | Mongla | 131 | 07:00 | 123 | 21:00
Baroirhat | 126 | 18:00 | 117 | 01:00 | Motijheel | 130 | 05:00 | 124 | 11:00
Bashundhara | 137 | 05:00 | 118 | 11:00 | Muktagacha | 133 | 08:00 | 122 | 21:00
BashundharaCement | 128 | 18:00 | 121 | 11:00 | Munshiganj | 128 | 18:00 | 121 | 10:00
Beanibazar | 127 | 06:00 | 120 | 20:00 | Muradnagar | 126 | 18:00 | 118 | 10:00
Benapole | 132 | 09:00 | 118 | 20:00 | Mymensingh | 134 | 08:00 | 114 | 00:00
Bhaluka | 130 | 05:00 | 121 | 19:30 | Naogaon | 133 | 09:00 | 124 | 23:00
Bhandaria | 128 | 08:00 | 118 | 21:00 | Narail | 134 | 08:00 | 120 | 21:00
Bhangura | 133 | 07:00 | 127 | 20:00 | Narinda | 0 | 00:00 | N/A | N/A
Bheramara | 137 | 06:00 | 131 | 20:00 | Narshingdi | 132 | 01:00 | 115 | 11:00
Bheramara(GK) | 137 | 06:00 | 130 | 21:00 | Natore | 135 | 07:00 | 128 | 00:00
Bhulta | 124 | 06:00 | 118 | 21:00 | Nawabganj | 132 | 06:00 | 126 | 11:00
Bog-Sherpur | 135 | 08:00 | 127 | 02:00 | Netrakona | 123 | 18:00 | 112 | 19:30
Bogura | 137 | 07:00 | 131 | 22:00 | New | 132 | 06:00 | 123 | 10:00
Bogura-230 | 137 | 07:00 | 130 | 02:00 | Niamatpur | 137 | 18:00 | 129 | 00:00
Brahmanbaria | 132 | 04:00 | 124 | 19:30 | Noapara | 134 | 06:00 | 124 | 20:00
Cantonment | 130 | 05:00 | 123 | 11:00 | Pabna | 134 | 06:00 | 127 | 20:00
Chandina | 128 | 18:00 | 120 | 11:00 | Palashbari | 129 | 09:00 | 118 | 00:00
Chandpur | 129 | 18:00 | 116 | 00:00 | Panchagarh | 137 | 19:00 | 117 | 12:00
Chandraghona | 133 | 17:00 | 128 | 10:00 | Patuakhali | 134 | 07:00 | 130 | 22:00
Chapai | 133 | 18:00 | 127 | 00:00 | Payra | 135 | 07:00 | 133 | 20:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 18:00 | 120 | 11:00 | PHP | 126 | 18:30 | 116 | 01:00
Chauddagram | 125 | 18:30 | 115 | 10:00 | Postogola | 130 | 18:00 | 118 | 11:00
Chhatak | 126 | 04:00 | 119 | 19:00 | Purbachal | 137 | 07:00 | 121 | 11:00
Chowmuhani | 121 | 18:30 | 108 | 15:00 | Purbasadipur | 132 | 19:00 | 117 | 16:00
Chuadanga | 133 | 18:00 | 119 | 22:00 | Rahanpur | 137 | 18:30 | 132 | 00:00
Coxsbazar | 123 | 17:00 | 115 | 00:00 | Rahanpur-400 | 138 | 18:00 | 133 | 00:00
Cumilla(N) | 128 | 18:00 | 120 | 10:00 | Rahim | 128 | 07:00 | 123 | 11:00
Cumilla(S) | 132 | 06:00 | 118 | 10:00 | Rajbari | 132 | 07:00 | 125 | 21:00
Daudkandi | 124 | 18:00 | 115 | 11:00 | Rajendrapur | 137 | 07:00 | 122 | 15:00
Dhaka | 137 | 05:00 | 123 | 11:00 | Rajshahi | 135 | 05:00 | 128 | 20:00
Dhamrai | 130 | 18:30 | 122 | 11:00 | Rajshahi-230 | 135 | 07:00 | 120 | 00:00
Dhanmondi | 138 | 07:00 | 122.5 | 11:00 | Ramganj | 124 | 18:30 | 110 | 15:00
Dohazari | 129 | 18:00 | 124 | 11:00 | Rampur | 133 | 17:00 | 127 | 10:00
Faridpur | 134 | 08:00 | 128 | 22:00 | Rampura | 138 | 07:00 | 123 | 11:00
Fatullah | 129 | 18:00 | 122 | 10:00 | Rangamati | 132 | 17:00 | 127 | 10:00
Fenchuganj | 135 | 06:00 | 130 | 19:30 | Rangpur | 131 | 19:00 | 120 | 17:00
Feni | 124 | 18:30 | 117 | 01:00 | Ruppur | 137 | 07:00 | 130 | 20:00
Ghatail | 130 | 08:00 | 118 | 21:00 | Saidpur | 131 | 19:00 | 118 | 16:00
Ghorashal | 140 | 07:00 | 129 | 12:00 | Satkhira | 133 | 09:00 | 121 | 21:00
Goalpara | 136 | 08:00 | 126 | 20:00 | Satmasjid | 131 | 07:00 | 124 | 11:00
Gollamari | 136 | 08:00 | 128 | 21:00 | Savar | 130 | 22:00 | 122 | 10:00
Gopalganj | 135 | 18:00 | 128 | 00:00 | SevenRings | 139 | 07:00 | 127 | 11:00
Gopalganj-400 | 136 | 08:00 | 130 | 02:00 | ShahCement | 129 | 18:00 | 122 | 10:00
Gulshan | 136 | 05:00 | 123 | 10:00 | Shahjadpur | 136 | 18:00 | 130 | 23:00
Halishahar | 135 | 23:00 | 125 | 11:00 | Shahjibazar | 133 | 06:00 | 124 | 19:30
Haripur | 129 | 18:30 | 123 | 11:00 | Shahmirpur | 135 | 17:00 | 129 | 09:00
HaripurSBU | 129 | 18:30 | 123 | 11:00 | Shariatpur | 134 | 18:00 | 127 | 00:00
Hasnabad | 131 | 18:00 | 125 | 10:00 | Sherpur | 134 | 18:00 | 122 | 19:30
Hathazari | 135 | 00:00 | 130 | 10:00 | Shikalbaha | 124 | 18:00 | 117 | 10:00
Ishurdi | 138 | 07:00 | 131 | 20:00 | Shikalbaha-230 | 138 | 12:00 | 129 | 10:00
Jaldhaka | 129 | 19:00 | 118 | 16:00 | Shitalakhya | 129 | 18:00 | 121 | 11:00
Jamalpur | 137 | 01:00 | 126 | 21:00 | Sholosohor | 134 | 18:00 | 127 | 10:00
Jashore | 131 | 07:00 | 119 | 20:00 | Shyampur | 130 | 18:30 | 121 | 11:00
Jhenaidah | 135 | 07:00 | 120 | 10:00 | Shyampur-230 | 130 | 18:30 | 122 | 11:00
Jhenaidah-230 | 136 | 08:00 | 124 | 20:00 | Siddhirganj | 128 | 18:00 | 123 | 10:00
Joydebpur | 135 | 07:00 | 124 | 15:00 | Sirajganj | 133 | 08:00 | 126 | 22:00
Joypurhat | 131 | 08:00 | 121 | 00:00 | Sonargaon | 126 | 18:00 | 120 | 10:00
Juldah | 136 | 18:30 | 129 | 08:00 | Sreemongol | 132 | 07:00 | 124 | 21:00
Kabirpur | 132 | 07:00 | 117 | 11:00 | Sreepur | 133 | 07:00 | 125 | 20:00
Kachua | 128 | 18:30 | 114 | 00:00 | Srinagar | 132 | 06:00 | 126 | 11:00
Kaliakoir | 134 | 07:00 | 125 | 11:00 | SSM | 139 | 07:00 | 130 | 11:00
Kallyanpur | 130 | 03:00 | 125 | 09:00 | Sunamganj | 124 | 07:00 | 117 | 19:00
Kalurghat | 132 | 17:00 | 127 | 10:00 | Sylhet | 129 | 07:00 | 122 | 21:00
Kamrangirchar | 132 | 05:00 | 126 | 10:00 | Sylhet-132 | 128 | 07:00 | 124 | 19:30
Kaptai | 135 | 18:00 | 131 | 11:00 | Tangail | 128 | 08:00 | 118 | 21:00
Kasba | 126 | 18:30 | 117 | 11:00 | Thakurgaon | 136 | 19:00 | 115 | 12:00
Kazla | 130 | 07:00 | 124 | 11:00 | TK | 132 | 22:00 | 126 | 11:00
Keranigonj | 133 | 07:00 | 127 | 11:00 | Tongi | 135 | 07:00 | 124 | 10:00
Khagrachori | 131 | 17:00 | 126 | 03:00 | Ullahpara | 134 | 07:00 | 128 | 00:00
Khulna | 135 | 08:00 | 125 | 20:00 | Ullon | 140 | 06:00 | 123 | 11:00
Khulna(S) | 137 | 08:00 | 128 | 20:00 | Uttara | 129 | 06:00 | 123 | 10:00
Khulshi | 132 | 17:00 | 125 | 11:00 | UttaraNew | 129 | 05:00 | 123 | 10:00
Kishoreganj | 130 | 05:00 | 121 | 19:00 | Zigatola | 132 | 06:00 | 126 | 11:00
Kodda | 137 | 06:00 | 122 | 14:00
KSRM | 134 | 17:00 | 128 | 11:00
Kulaura | 134 | 07:00 | 128 | 19:00
Kurigram | 129 | 19:00 | 119 | 16:00
Kushtia | 134 | 08:00 | 126 | 20:00
Lalbag | 133 | 07:00 | 126 | 11:00
Lalmonirhat | 130 | 19:00 | 118 | 12:00
Madanganj | 128 | 18:00 | 121 | 11:00
Madaripur | 135 | 09:00 | 129 | 21:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division