## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 02-07-2025 | [28 empty] | Date: | 02-07-2025 | [28 empty] | Date: | 02-07-2025 | [28 empty] | Date: | 02-07-2025 | [28 empty] | Date: | 02-07-2025 | [12 empty] | Date: | 02-07-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [12 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 19 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 54 | 35 | 149 | 145 | 0 | 0 | 17 | 147 | 67 | 420 | 300 | 0 | 0 | 17 | 333 | 0 | 0 | 0 | 52 | 26 | 22 | 0 | 400 | 16 | 150 | 0 | 0 | 27 | 65 | 70 | 0 | 100 | 88 | 0 | 172 | 68 | 22 | 203 | 0 | 0 | 50 | 8 | 99 | 221 | 0 | 0 | 0 | 1140 | 0 | 51 | 40 | 165 | 0 | 350 | 335 | 48 | 0 | 21 | 115 | 0 | 170 | 13 | 19 | 95 | 52 | 52.2 | 0 | 30 | 285 | 320 | 346 | 0 | 0 | 158 | 8 | 0 | 80 | 30 | 0 | 0 | 172 | 35 | 83 | 152 | 49 | 0 | 0 | 12 | 8408.2 | 898 | 215 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 610 | 51 | 1443.13 | 0 | 45 | 0 | 113 | 0 | 95 | 0 | 35 | 0 | 0 | 30 | 0 | 199 | 0 | 186 | 0 | 0 | 0 | 410 | 0 | 0 | 199 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 10 | 120 | 220 | 0 | 416 | 1120 | 0 | 7100.13 | 15508.33 | 97.52
01:00 | 0 | 17 | 12 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 54 | 35 | 149 | 145 | 0 | 0 | 17 | 138 | 50 | 420 | 298 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 52 | 27 | 21 | 0 | 400 | 15 | 100 | 0 | 0 | 14 | 62 | 70 | 0 | 100 | 88 | 0 | 172 | 66 | 22 | 205 | 0 | 0 | 50 | 8 | 59 | 222 | 0 | 0 | 0 | 1120 | 0 | 51 | 40 | 167 | 0 | 351 | 340 | 48 | 0 | 21 | 102 | 0 | 170 | 9 | 19 | 95 | 48 | 52.2 | 0 | 30 | 285 | 320 | 327 | 0 | 0 | 156 | 8 | 0 | 80 | 30 | 0 | 0 | 172 | 35 | 79 | 152 | 49 | 0 | 0 | 10 | 8210.2 | 897 | 214 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 0 | 605 | 36 | 1428.26 | 0 | 0 | 0 | 113 | 0 | 95 | 0 | 0 | 0 | 0 | 30 | 0 | 199 | 0 | 185 | 0 | 0 | 0 | 394 | 0 | 0 | 200 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 10 | 116 | 220 | 0 | 347 | 1107 | 0 | 6838.26 | 15048.46 | 97.51
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 54 | 35 | 149 | 145 | 0 | 0 | 0 | 129 | 50 | 420 | 299 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 27 | 22 | 0 | 400 | 0 | 100 | 0 | 0 | 13 | 17 | 15 | 0 | 89 | 88 | 0 | 172 | 34 | 22 | 203 | 0 | 0 | 50 | 0 | 60 | 221 | 0 | 0 | 0 | 1135 | 0 | 51 | 40 | 173 | 0 | 355 | 335 | 49 | 0 | 21 | 93 | 0 | 170 | 9 | 20 | 95 | 48 | 52.2 | 0 | 30 | 290 | 320 | 314 | 0 | 0 | 153 | 8 | 0 | 80 | 30 | 0 | 0 | 172 | 35 | 82 | 152 | 49 | 0 | 0 | 11 | 8021.2 | 904 | 213 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 605 | 31 | 1443.05 | 0 | 0 | 0 | 113 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 185 | 0 | 0 | 0 | 348 | 0 | 0 | 202 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 9 | 120 | 220 | 0 | 299 | 1105 | 0 | 6683.05 | 14704.25 | 97.5
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 54 | 35 | 149 | 112 | 0 | 0 | 0 | 129 | 16 | 420 | 298 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 27 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 88 | 88 | 0 | 172 | 30 | 31 | 203 | 0 | 0 | 10 | 0 | 34 | 222 | 0 | 0 | 0 | 1135 | 0 | 51 | 40 | 180 | 0 | 353 | 340 | 49 | 0 | 21 | 93 | 0 | 170 | 9 | 20 | 95 | 44 | 52.2 | 0 | 30 | 285 | 320 | 302 | 0 | 0 | 151 | 8 | 0 | 80 | 30 | 0 | 0 | 172 | 35 | 83 | 152 | 49 | 0 | 0 | 12 | 7750.2 | 904 | 214 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 595 | 0 | 1456.62 | 0 | 0 | 0 | 70 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 185 | 0 | 0 | 0 | 342 | 0 | 0 | 202 | 50 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 10 | 120 | 220 | 0 | 300 | 1104 | 0 | 6540.62 | 14290.82 | 97.49
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 42 | 19 | 149 | 112 | 0 | 0 | 0 | 100 | 16 | 420 | 298 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 27 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 48 | 88 | 0 | 172 | 0 | 31 | 203 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1140 | 0 | 51 | 0 | 185 | 0 | 355 | 335 | 49 | 0 | 21 | 94 | 0 | 170 | 9 | 20 | 95 | 44 | 52.2 | 0 | 30 | 290 | 320 | 307 | 0 | 0 | 153 | 8 | 0 | 80 | 30 | 0 | 0 | 172 | 35 | 83 | 152 | 49 | 0 | 0 | 12 | 7578.2 | 912 | 222 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 592 | 0 | 1460.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 185 | 0 | 0 | 0 | 342 | 0 | 0 | 202 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 10 | 120 | 220 | 0 | 300 | 1106 | 0 | 6449.46 | 14027.66 | 97.48
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 17 | 34 | 134 | 98 | 0 | 0 | 0 | 50 | 16 | 420 | 299 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 27 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 48 | 88 | 0 | 172 | 0 | 34 | 205 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1110 | 0 | 51 | 0 | 172 | 0 | 355 | 340 | 49 | 0 | 21 | 96 | 0 | 170 | 9 | 20 | 95 | 44 | 52.2 | 0 | 30 | 290 | 320 | 295 | 0 | 0 | 156 | 8 | 0 | 80 | 30 | 0 | 0 | 172 | 35 | 83 | 152 | 49 | 0 | 0 | 12 | 7469.2 | 919 | 219 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 590 | 0 | 1350.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 185 | 0 | 0 | 0 | 345 | 0 | 0 | 203 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 9 | 120 | 220 | 0 | 300 | 1050 | 0 | 6289.46 | 13758.66 | 97.47
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 17 | 35 | 118 | 80 | 0 | 0 | 0 | 15 | 16 | 370 | 296 | 0 | 0 | 0 | 335 | 0 | 0 | 2 | 70 | 27 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 24 | 48 | 0 | 172 | 0 | 34 | 205 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1035 | 0 | 51 | 0 | 197 | 0 | 300 | 340 | 39 | 0 | 20 | 93 | 0 | 170 | 9 | 20 | 95 | 42 | 8 | 1 | 30 | 285 | 320 | 303 | 0 | 0 | 150 | 8 | 0 | 80 | 30 | 0 | 0 | 172 | 35 | 83 | 152 | 49 | 0 | 1.77 | 12 | 7101.77 | 919 | 221 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4.31 | 582 | 0 | 1249.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 2.83 | 200 | 0 | 185 | 0 | 0 | 0 | 341 | 0 | 0 | 204 | 48 | 35 | 2 | 98 | 0 | 0 | 0.4 | 13 | 0.03 | 0 | 277 | 7 | 120 | 220 | 0 | 300 | 950 | 0 | 6021.02 | 13122.79 | 97.46
07:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 17 | 35 | 144 | 80 | 0 | 0 | 0 | 0 | 0 | 370 | 300 | 0 | 0 | 0 | 335 | 0 | 0 | 4 | 70 | 27 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 24 | 24 | 1 | 172 | 0 | 29 | 203 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 199 | 0 | 300 | 340 | 0 | 0 | 20 | 68 | 0 | 136 | 9 | 8 | 64 | 40 | 8 | 23 | 31 | 290 | 320 | 305 | 0 | 0 | 152 | 8 | 0 | 80 | 30 | 0 | 0 | 172 | 35 | 65 | 152 | 49 | 0 | 5.82 | 12 | 6968.82 | 918 | 222 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 16.3 | 590 | 0 | 1263.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 7.03 | 199 | 0 | 185 | 0 | 0 | 0 | 341 | 0 | 0.57 | 203 | 48 | 35 | 9 | 70 | 0 | 0 | 2.4 | 38 | 0.05 | 0 | 228 | 7 | 120 | 220 | 0 | 300 | 922 | 0 | 6005.16 | 12973.98 | 97.45
08:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 35 | 149 | 64 | 0 | 0 | 0 | 0 | 0 | 370 | 296 | 0 | 0 | 0 | 335 | 0 | 0 | 10 | 70 | 25.5 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 12 | 12 | 2 | 172 | 0 | 8 | 203 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 200 | 0 | 300 | 340 | 0 | 0 | 20 | 68 | 0 | 120 | 9 | 20 | 47 | 38 | 8 | 35 | 30 | 290 | 320 | 296 | 0 | 0 | 152 | 0 | 0 | 80 | 30 | 0 | 0 | 172 | 35 | 65 | 130 | 49 | 1 | 18.69 | 12 | 6860.19 | 920 | 223 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 24.86 | 592 | 0 | 1253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 20.15 | 200 | 0 | 185 | 0 | 0 | 0 | 332 | 0 | 1.99 | 200 | 48 | 35 | 15 | 34 | 0 | 0 | 2.3 | 62 | 0.41 | 0 | 195 | 7 | 120 | 220 | 0 | 299 | 950 | 0 | 6019.71 | 12879.9 | 97.44
09:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 35 | 149 | 48 | 0 | 0 | 8 | 0 | 0 | 370 | 308 | 0 | 0 | 0 | 332 | 0 | 0 | 24 | 70 | 21 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 12 | 12 | 3 | 172 | 0 | 2 | 204 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1008 | 0 | 51 | 0 | 200 | 0 | 300 | 340 | 4 | 0 | 20 | 68 | 0 | 114 | 9 | 20 | 47 | 36 | 8 | 24 | 30 | 290 | 320 | 326 | 0 | 0 | 136 | 8 | 0 | 76 | 30 | 0 | 0 | 172 | 35 | 65 | 120 | 49 | 1 | 28.79 | 12 | 6859.79 | 919 | 223 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 55 | 594 | 0 | 1285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 24.49 | 201 | 0 | 185 | 0 | 0 | 0 | 372 | 0 | 1.98 | 200 | 48 | 35 | 9 | 0 | 0 | 0 | 3.8 | 65 | 0.68 | 0 | 201 | 6 | 120 | 220 | 0 | 301 | 950 | 0 | 6097.95 | 12957.74 | 97.43
10:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 35 | 138 | 32 | 0 | 0 | 18 | 0 | 0 | 370 | 305 | 0 | 0 | 0 | 330 | 0 | 0 | 26 | 70 | 20 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 36 | 48 | 4 | 172 | 0 | 2 | 204 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 1005 | 0 | 51 | 0 | 200 | 0 | 341 | 340 | 28 | 0 | 17 | 71 | 0 | 123 | 10 | 15 | 68 | 34 | 8 | 72 | 30 | 285 | 320 | 326 | 0 | 0 | 145 | 8 | 0 | 76 | 30 | 0 | 0 | 172 | 35 | 55 | 120 | 48 | 2 | 16.41 | 12 | 7017.41 | 919 | 221 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 79 | 608 | 0 | 1271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 41.22 | 140 | 0 | 191 | 0 | 0 | 0 | 382 | 0 | 3.11 | 200 | 48 | 35 | 23 | 0 | 0 | 0 | 4.5 | 50 | 0.41 | 0 | 202 | 4 | 120 | 220 | 0 | 301 | 955 | 0 | 6125.24 | 13142.65 | 97.42
11:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0.36 | 35 | 114 | 32 | 0 | 0 | 35 | 17 | 0 | 370 | 303 | 0 | 0 | 0 | 330 | 0 | 0 | 9 | 90 | 23 | 14 | 0 | 400 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 36 | 48 | 5 | 172 | 0 | 2 | 204 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1097 | 0 | 51 | 3 | 200 | 0 | 346 | 335 | 42 | 0 | 17 | 89 | 0 | 136 | 9 | 17 | 67 | 36 | 8 | 47 | 29 | 290 | 320 | 385 | 0 | 0 | 150 | 8 | 0 | 80 | 30 | 0 | 16 | 171 | 35 | 55 | 120 | 48 | 1 | 49.85 | 12 | 7275.21 | 919 | 218 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 77 | 607 | 0 | 1264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 31.28 | 140 | 0 | 188 | 0 | 0 | 0 | 414 | 0 | 3.34 | 201 | 48 | 35 | 28 | 0 | 0 | 0 | 4.9 | 137 | 0.52 | 0 | 249 | 7 | 120 | 220 | 0 | 301 | 1025 | 0 | 6314.04 | 13589.25 | 97.41
12:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 35 | 124 | 48 | 0 | 0 | 35 | 80 | 0 | 370 | 297 | 0 | 0 | 0 | 329 | 0 | 0 | 6 | 90 | 23 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 60 | 0 | 24 | 0 | 62 | 88 | 4 | 172 | 0 | 2 | 205 | 0 | 0 | 3 | 0 | 0 | 216 | 0 | 0 | 0 | 1150 | 4 | 51 | 30 | 200 | 0 | 348 | 335 | 43 | 0 | 17 | 114 | 0 | 139 | 9 | 17 | 64 | 40 | 8 | 79 | 29 | 280 | 320 | 363 | 0 | 0 | 154 | 8 | 0 | 79 | 30 | 0 | 16 | 172 | 35 | 65 | 130 | 48 | 1 | 37.3 | 14 | 7595.3 | 891 | 221 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 94 | 600 | 0 | 1376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 62.99 | 140 | 0 | 188 | 0 | 0 | 0 | 343 | 0 | 2.56 | 201 | 48 | 35 | 12 | 0 | 0 | 0 | 5.7 | 184 | 0.79 | 0 | 275 | 7 | 120 | 220 | 0 | 300 | 1105 | 0 | 6565.04 | 14160.34 | 97.4
13:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 35 | 149 | 80 | 0 | 0 | 35 | 90 | 0 | 340 | 298 | 0 | 0 | 0 | 331 | 0 | 0 | 7 | 90 | 23 | 0 | 0 | 430 | 0 | 0 | 0 | 0 | 54 | 0 | 31 | 0 | 87 | 88 | 3 | 172 | 0 | 8 | 203 | 0 | 0 | 15 | 0 | 27 | 220 | 0 | 0 | 0 | 1100 | 1 | 51 | 60 | 200 | 0 | 345 | 340 | 43 | 0 | 17 | 114 | 0 | 143 | 12 | 20 | 75 | 42 | 25 | 64 | 29 | 280 | 320 | 363 | 0 | 0 | 153 | 8 | 0 | 79 | 30 | 0 | 16 | 172 | 35 | 61 | 140 | 44 | 1 | 43.47 | 13 | 7785.47 | 890 | 222 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 102 | 593 | 0 | 1407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 17.73 | 162 | 0 | 188 | 0 | 0 | 0 | 338 | 0 | 2.8 | 201 | 48 | 35 | 18 | 0 | 0 | 0 | 0.5 | 211 | 0.05 | 0 | 274 | 7 | 112 | 180 | 0 | 301 | 1100 | 0 | 6541.08 | 14326.55 | 97.39
14:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 54 | 35 | 149 | 48 | 0 | 0 | 35 | 54 | 0 | 320 | 306 | 0 | 0 | 0 | 290 | 0 | 0 | 13 | 90 | 23.5 | 0 | 0 | 380 | 0 | 15 | 0 | 0 | 62 | 0 | 31 | 0 | 70 | 88 | 0 | 172 | 0 | 4 | 206 | 0 | 0 | 18 | 0 | 48 | 196 | 0 | 0 | 0 | 1106 | 2 | 51 | 50 | 200 | 0 | 315 | 320 | 44 | 0 | 17 | 115 | 0 | 145 | 10 | 20 | 82 | 44 | 25 | 49 | 29 | 285 | 320 | 370 | 0 | 0 | 149 | 8 | 0 | 79 | 30 | 0 | 16 | 172 | 6 | 60 | 110 | 44 | 1 | 39.1 | 14 | 7514.6 | 891 | 218 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 94 | 595 | 0 | 1372 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 38.57 | 140 | 0 | 170 | 0 | 0 | 0 | 379 | 0 | 2.7 | 200 | 47 | 35 | 17 | 0 | 0 | 0 | 7.2 | 174 | 0.88 | 0 | 225 | 5 | 120 | 220 | 0 | 301 | 1050 | 0 | 6406.35 | 13920.95 | 97.38
15:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 35 | 149 | 48 | 0 | 0 | 35 | 54 | 0 | 420 | 309 | 0 | 0 | 0 | 329 | 0 | 0 | 13 | 90 | 23.5 | 22 | 0 | 380 | 0 | 15 | 0 | 0 | 58 | 0 | 31 | 0 | 78 | 88 | 0 | 172 | 0 | 3 | 206 | 0 | 0 | 18 | 0 | 51 | 217 | 0 | 0 | 0 | 1142 | 1 | 51 | 50 | 195 | 0 | 341 | 335 | 46 | 0 | 17 | 109 | 0 | 153 | 10 | 20 | 46 | 42 | 25 | 10 | 29 | 285 | 320 | 386 | 0 | 0 | 154 | 8 | 0 | 79 | 30 | 0 | 16 | 171 | 21 | 60 | 110 | 44 | 2 | 19.94 | 14 | 7718.44 | 890 | 218 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 53 | 600 | 0 | 1411 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 36.68 | 171 | 0 | 181 | 0 | 0 | 0 | 414 | 0 | 2.91 | 199 | 46 | 35 | 17 | 0 | 0 | 0 | 6.8 | 107 | 0.22 | 0 | 288 | 7 | 120 | 220 | 0 | 300 | 1080 | 0 | 6541.61 | 14260.05 | 97.37
16:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 44 | 149 | 46 | 0 | 0 | 54 | 82 | 0 | 420 | 299 | 0 | 0 | 0 | 329 | 0 | 0 | 8 | 108 | 23.5 | 22 | 0 | 380 | 0 | 30 | 0 | 0 | 40 | 0 | 52 | 0 | 100 | 100 | 0 | 172 | 4 | 3 | 202 | 0 | 0 | 25 | 0 | 59 | 219 | 0 | 0 | 0 | 1160 | 2 | 51 | 50 | 195 | 0 | 343 | 335 | 48 | 0 | 17 | 94 | 0 | 158 | 8 | 20 | 61 | 40 | 25 | 29 | 29 | 280 | 320 | 375 | 0 | 0 | 155 | 5 | 0 | 78 | 30 | 0 | 16 | 171 | 17 | 75 | 110 | 44 | 1 | 9.73 | 12 | 7865.23 | 891 | 215 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12 | 595 | 0 | 1438 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 21.45 | 167 | 0 | 184 | 0 | 0 | 0 | 394 | 0 | 1.55 | 200 | 47 | 35 | 10 | 0 | 0 | 0 | 1.9 | 52 | 0.09 | 0 | 278 | 7 | 116 | 220 | 0 | 299 | 1115 | 0 | 6416.99 | 14282.22 | 97.36
17:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 54 | 127 | 46 | 0 | 0 | 55 | 54 | 0 | 420 | 307 | 0 | 0 | 0 | 329 | 0 | 0 | 7 | 108 | 23.5 | 22 | 0 | 380 | 0 | 30 | 0 | 0 | 40 | 0 | 52 | 0 | 100 | 60 | 1 | 172 | 15 | 10 | 200 | 0 | 0 | 19 | 0 | 66 | 217 | 0 | 0 | 0 | 1100 | 2 | 51 | 24 | 195 | 0 | 339 | 340 | 47 | 0 | 17 | 68 | 0 | 160 | 9 | 20 | 61 | 38 | 25 | 6 | 29 | 285 | 320 | 379 | 0 | 0 | 154 | 5 | 0 | 80 | 30 | 0 | 16 | 171 | 17 | 75 | 80 | 46 | 1 | 12.75 | 13 | 7642.25 | 889 | 212 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 8 | 605 | 0 | 1411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 22.12 | 165 | 0 | 186 | 0 | 0 | 0 | 360 | 0 | 2.31 | 195 | 47 | 35 | 6 | 0 | 0 | 0 | 0.5 | 46 | 0.12 | 0 | 221 | 6 | 120 | 220 | 0 | 298 | 1050 | 0 | 6166.05 | 13808.3 | 97.35
18:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17 | 54 | 114 | 46 | 0 | 0 | 17 | 48 | 0 | 420 | 286 | 0 | 0 | 0 | 333 | 0 | 0 | 2 | 90 | 23.5 | 22 | 0 | 380 | 0 | 30 | 0 | 0 | 37 | 0 | 52 | 0 | 48 | 60 | 0 | 172 | 15 | 11 | 201 | 0 | 0 | 19 | 0 | 51 | 218 | 0 | 0 | 0 | 1077 | 0 | 51 | 24 | 195 | 0 | 348 | 340 | 46 | 0 | 17 | 67 | 0 | 136 | 16 | 20 | 44 | 36 | 25 | 2 | 31 | 290 | 320 | 307 | 0 | 0 | 136 | 5 | 0 | 80 | 30 | 0 | 16 | 171 | 27 | 80 | 80 | 48 | 0 | 5.22 | 14 | 7364.72 | 888 | 213 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7 | 586 | 0 | 1303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 5.82 | 160 | 0 | 186 | 0 | 0 | 0 | 338 | 0 | 0.9 | 200 | 46 | 50 | 1 | 49 | 0 | 0 | 0.3 | 7 | 0.07 | 0 | 215 | 5 | 120 | 220 | 0 | 300 | 1040 | 0 | 5992.09 | 13356.81 | 97.34
19:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 54 | 114 | 82 | 10 | 0 | 19 | 51 | 4 | 380 | 304 | 0 | 0 | 15 | 330 | 0 | 0 | 0 | 135 | 26 | 22 | 0 | 420 | 1 | 32 | 0 | 0 | 44 | 65 | 70 | 17 | 88 | 85 | 0 | 172 | 15 | 11 | 202 | 0 | 0 | 19 | 0 | 55 | 218 | 0 | 0 | 0 | 1155 | 0 | 51 | 36 | 195 | 0 | 345 | 340 | 46 | 0 | 20 | 71 | 0 | 132 | 26 | 20 | 89 | 46 | 34 | 0 | 37 | 290 | 320 | 386 | 0 | 0 | 141 | 8 | 0 | 80 | 30 | 0 | 16 | 171 | 35 | 80 | 106 | 47 | 0 | 0 | 12 | 7949 | 888 | 216 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 20 | 0 | 602 | 27 | 1417 | 0 | 0 | 0 | 4 | 0 | 60 | 30 | 24 | 0 | 0 | 30 | 0 | 163 | 0 | 186 | 0 | 0 | 0 | 366 | 0 | 0 | 200 | 46 | 90 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 267 | 9 | 126 | 220 | 0 | 300 | 1050 | 4 | 6475 | 14424 | 97.33
19:30 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 54 | 54 | 134 | 133 | 95 | 0 | 55 | 162 | 27 | 380 | 309 | 0 | 0 | 17 | 330 | 0 | 0 | 0 | 142 | 26 | 14 | 0 | 450 | 15 | 95 | 0 | 0 | 50 | 65 | 70 | 17 | 88 | 100 | 0 | 172 | 20 | 13 | 204 | 0 | 0 | 33 | 0 | 85 | 218 | 0 | 0 | 0 | 1166 | 0 | 51 | 50 | 185 | 0 | 343 | 335 | 46 | 0 | 20 | 70 | 0 | 182 | 29 | 20 | 98 | 46 | 52.2 | 0 | 37 | 290 | 320 | 389 | 0 | 0 | 155 | 8 | 0 | 80 | 30 | 0 | 16 | 171 | 35 | 101 | 158 | 48 | 0 | 0 | 13 | 8677.2 | 888 | 213 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 605 | 35 | 1414 | 0 | 0 | 0 | 56 | 0 | 85 | 35 | 30 | 0 | 0 | 30 | 0 | 173 | 0 | 186 | 0 | 0 | 0 | 391 | 0 | 0 | 201 | 47 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 9 | 124 | 220 | 0 | 300 | 1120 | 17 | 6760 | 15437.2
20:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 49 | 54 | 138 | 145 | 95 | 0 | 54 | 148 | 35 | 380 | 299 | 0 | 0 | 17 | 333 | 0 | 0 | 0 | 142 | 26 | 22 | 0 | 450 | 13 | 95 | 0 | 0 | 58 | 65 | 70 | 17 | 88 | 100 | 0 | 172 | 30 | 16 | 204 | 0 | 0 | 42 | 0 | 98 | 218 | 0 | 0 | 0 | 1143 | 0 | 51 | 50 | 185 | 0 | 348 | 335 | 47 | 0 | 20 | 69 | 0 | 173 | 29 | 20 | 95 | 44 | 52.2 | 0 | 37 | 285 | 320 | 371 | 0 | 0 | 157 | 5 | 0 | 80 | 30 | 0 | 16 | 171 | 35 | 101 | 161 | 48 | 0 | 0 | 14 | 8671.2 | 888 | 213 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 601 | 52 | 1402 | 0 | 40 | 0 | 76 | 0 | 85 | 35 | 37 | 0 | 0 | 30 | 0 | 169 | 0 | 186 | 0 | 0 | 0 | 350 | 0 | 0 | 202 | 47 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 10 | 120 | 220 | 0 | 299 | 1120 | 48 | 6808 | 15479.2 | 97.32
21:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 54 | 54 | 149 | 110 | 95 | 0 | 55 | 147 | 65 | 380 | 299 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 142 | 27 | 22 | 0 | 450 | 15 | 100 | 0 | 0 | 43 | 65 | 70 | 17 | 88 | 100 | 0 | 172 | 30 | 2 | 204 | 0 | 0 | 0 | 0 | 94 | 219 | 0 | 0 | 0 | 1160 | 0 | 51 | 12 | 185 | 0 | 350 | 340 | 48 | 0 | 20 | 60 | 0 | 178 | 28 | 20 | 95 | 46 | 52.2 | 0 | 36 | 280 | 320 | 387 | 0 | 0 | 152 | 8 | 0 | 80 | 30 | 0 | 16 | 171 | 35 | 101 | 162 | 49 | 0 | 0 | 14 | 8594.2 | 889 | 215 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 594 | 53 | 1425 | 0 | 47 | 0 | 113 | 0 | 96 | 35 | 37 | 0 | 0 | 30 | 0 | 161 | 0 | 185 | 0 | 0 | 0 | 356 | 0 | 0 | 203 | 47 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 10 | 120 | 220 | 0 | 300 | 1110 | 66 | 6891 | 15485.2 | 97.31
22:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 54 | 54 | 149 | 80 | 95 | 0 | 55 | 146 | 66 | 380 | 294 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 142 | 27 | 22 | 0 | 450 | 13 | 100 | 0 | 0 | 45 | 65 | 70 | 17 | 88 | 100 | 0 | 172 | 31 | 21 | 204 | 0 | 0 | 0 | 0 | 94 | 220 | 0 | 0 | 0 | 1150 | 0 | 51 | 12 | 185 | 0 | 354 | 335 | 48 | 0 | 20 | 61 | 0 | 175 | 29 | 20 | 81 | 48 | 52.2 | 0 | 37 | 275 | 320 | 364 | 0 | 0 | 153 | 8 | 0 | 80 | 30 | 0 | 16 | 171 | 35 | 101 | 162 | 48 | 0 | 0 | 12 | 8528.2 | 889 | 215 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 595 | 53 | 1408.91 | 0 | 48 | 0 | 113 | 0 | 96 | 35 | 37 | 0 | 0 | 30 | 0 | 161 | 0 | 186 | 0 | 0 | 0 | 344 | 0 | 0 | 202 | 47 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 10 | 120 | 220 | 0 | 300 | 1110 | 65 | 6859.91 | 15388.11 | 97.3
23:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 54 | 54 | 149 | 80 | 95 | 0 | 55 | 145 | 68 | 380 | 283 | 0 | 0 | 17 | 333 | 0 | 0 | 0 | 142 | 27 | 22 | 0 | 450 | 13 | 100 | 0 | 0 | 46 | 65 | 70 | 17 | 88 | 100 | 0 | 172 | 31 | 29 | 204 | 0 | 0 | 0 | 0 | 91 | 220 | 0 | 0 | 0 | 1160 | 0 | 51 | 12 | 185 | 0 | 352 | 335 | 48 | 0 | 20 | 40 | 0 | 173 | 28 | 20 | 95 | 50 | 52.2 | 0 | 37 | 280 | 320 | 381 | 0 | 0 | 138 | 8 | 0 | 80 | 30 | 0 | 16 | 172 | 35 | 101 | 168 | 48 | 0 | 0 | 12 | 8520.2 | 889 | 217 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 595 | 53 | 1419.57 | 0 | 48 | 0 | 113 | 0 | 96 | 35 | 37 | 0 | 0 | 30 | 0 | 162 | 0 | 186 | 0 | 0 | 0 | 354 | 0 | 0 | 202 | 47 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 8 | 120 | 220 | 0 | 299 | 1110 | 65 | 6884.57 | 15404.77 | 97.29
Total KWH | 0 | 1191360 | 439200 | 0 | 0 | 0 | 0 | 0 | 9878400 | 0 | 0 | 817920 | 1000440 | 3380833 | 1946880 | 467945 | 0 | 662413 | 1893600 | 458880 | 9418000 | 7222167 | 0 | 0 | 78379 | 7968458 | 0 | 0 | 157791 | 2245200 | 583200 | 436680 | 0 | 9759545.45 | 90327 | 948436 | 0 | 0 | 900480 | 429988 | 759113 | 92360 | 1629120 | 1834560 | 22562 | 4150000 | 358800 | 398880 | 4923636.36 | 0 | 0 | 388320 | 9583.2 | 1093963 | 5448381 | 0 | 0 | 0 | 26536361 | 13230 | 1150321 | 680800 | 4549818.18 | 0 | 8480500 | 8206000 | 957600 | 0 | 465264 | 1968960 | 0 | 3764160 | 342720 | 433470 | 1850220 | 1006080 | 763378 | 367164 | 756096 | 6880500 | 7684900 | 8701000 | 0 | 0 | 3603682 | 170304 | 0 | 1906560 | 726816 | 0 | 224000 | 3540370 | 774360 | 1836000 | 3249600 | 1090560 | 11450 | 289660 | 308880 | 186776585.19 | 21803636 | 5249376 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 387072 | 558000 | 14581820 | 337010 | 32940000 | 0 | 206121 | 0 | 1005696 | 0 | 655184 | 190848 | 164200 | 0 | 608830 | 180450 | 327744 | 4280091 | 0 | 4675836 | 0 | 0 | 0 | 8790181 | 0 | 28320 | 4944000 | 1103999 | 1733791 | 185451 | 1350518 | 0 | 0 | 39674.04 | 1245600 | 3828 | 0 | 6175000 | 286305 | 2848000 | 5418960 | 0 | 7294545.45 | 25854545.45 | 289200 | 156655831.94 | 343432417.13

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 03-07-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 02-07-2025 | during | 03-07-2025 | during | 03-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 404 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 370 | 380 | 450 | 450 | 400 | 400 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 297 | 299 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 329 | 332 | 335 | 335 | 330 | 330 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 48 | 110 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23 | 27 | 33 | 33 | 27 | 27 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 16 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 95 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 124 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 88 | 105 | 105 | 70 | 90 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 65 | 104 | 104 | 68 | 68 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 80 | 147 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 6 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 54 | 55 | 55 | 35 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 400 | 450 | 584 | 584 | 401 | 401 | None
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage instructed by DS(Gen)
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 90 | 142 | 160 | 160 | 108 | 108 | Dirty Fuel
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2330 | 2889 | 5107.2 | 5111.2 | 3183.08 | 3207.08
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 4 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 3 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 172 | 172 | 165 | 165 | 165 | 165 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 219 | 213 | 213 | 214 | 214 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 94 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 24 | 70 | 48 | 72 | 48 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 65 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 62 | 88 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 2 | 2 | 25 | 2 | 11 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4 | 0 | 5.18 | 0 | 5.18 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 100 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 17 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 30 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 88 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 15 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1150 | 1160 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 60 | 43 | 35 | 47 | 35 | 47 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 205 | 204 | 575 | 575 | 200 | 200 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1990 | 2379 | 3571.9 | 3615.72 | 3167.9 | 3197.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 0 | 0 | 221 | 221 | 0 | 0 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 348 | 350 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 335 | 340 | 340 | 340 | 340 | 340 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 17 | 20 | 46.7 | 46.7 | 17 | 17 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 43 | 48 | 55 | 55 | 40 | 40 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 200 | 185 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 30 | 12 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 29 | 36 | 46 | 46 | 46 | 46 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 139 | 178 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 40 | 46 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 20 | 24.5 | 24.5 | 15 | 15 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 64 | 95 | 114 | 114 | 98 | 98 | Engine Problem
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 28 | 113 | 113 | 9 | 28 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 114 | 60 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 79 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1523 | 1521.2 | 2459.75 | 2399.75 | 1901.55 | 1860.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 02-07-2025 | during | 03-07-2025 | during | 03-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 48 | 49 | 157.5 | 157.5 | 40 | 40 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 130 | 162 | 200 | 200 | 160 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 65 | 101 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 37.3 | 0 | 39 | 0 | 39 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 14 | 14 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 35 | 35 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 330.3 | 361 | 590.1 | 549 | 422.6 | 381.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage instructed by DS(Gen)
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 30 | 30 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 154 | 152 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 80 | 83 | 83 | 70 | 70 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 172 | 171 | 165 | 165 | 165 | 165 | Machine Problem
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 8 | 8 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 280 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 363 | 387 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1422 | 1444 | 1557 | 1557 | 1399 | 1399
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 891 | 889 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 221 | 215 | 410 | 410 | 210 | 210 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 53 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 50 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 94 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 600 | 594 | 617.1 | 617.1 | 617.1 | 617.1 | U#2 under shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1844 | 1839 | 3011.1 | 2931.1 | 2251.1 | 2171.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 7 | 10 | 10 | 10 | 4 | 4 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1105 | 1110 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 66 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 275 | 278 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.79 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 2027.79 | 2104 | 2172 | 2171 | 2126 | 2125
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 47 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 140 | 161 | 0 | 0 | 140 | 140 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 188 | 185 | 220 | 220 | 160 | 160 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 343 | 356 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 96 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.56 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1376 | 1425 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 62.99 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 95 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 2207.55 | 2485 | 2979.47 | 2812.87 | 2798.09 | 2631.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 47 | 50 | 50 | 50 | 50 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 201 | 203 | 200 | 200 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 98 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.7 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 12 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 184 | 0 | 182.55 | 0 | 182.55 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 485.7 | 463 | 731.15 | 512 | 697.15 | 478
System Total |  |  |  |  | 28565.2 | 27084.055 | 14160.34 | 15485.2 | 22179.67 | 21659.64 | 17946.47 | 17451.44
Forecast Scenario (03-07-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15160 |  | 0 |  | 15160
|  |  |  | 1:00 | 15120 |  | 0 |  | 15120
|  |  |  | 2:00 | 14700 |  | 0 |  | 14700
|  |  |  | 3:00 | 14410 |  | 0 |  | 14410
|  |  |  | 4:00 | 14070 |  | 0 |  | 14070
|  |  |  | 5:00 | 13870 |  | 0 |  | 13870
|  |  |  | 6:00 | 13170 |  | 0 |  | 13170
|  |  |  | 7:00 | 13150 |  | 0 |  | 13150
|  |  |  | 8:00 | 13050 |  | 0 |  | 13050
|  |  |  | 9:00 | 13070 |  | 0 |  | 13070
|  |  |  | 10:00 | 13270 |  | 0 |  | 13270
|  |  |  | 11:00 | 13600 |  | 0 |  | 13600
|  |  |  | 12:00 | 14260 |  | 0 |  | 14260
|  |  |  | 13:00 | 14500 |  | 0 |  | 14500
|  |  |  | 14:00 | 14400 |  | 0 |  | 14400
|  |  |  | 15:00 | 14480 |  | 0 |  | 14480
|  |  |  | 16:00 | 14370 |  | 0 |  | 14370
|  |  |  | 17:00 | 13900 |  | 0 |  | 13900
|  |  |  | 18:00 | 13470 |  | 0 |  | 13470
|  |  |  | 18:30 | 14000 |  | 0 |  | 14000
|  |  |  | 19:00 | 14590 |  | 0 |  | 14590
|  |  |  | 19:30 | 15550 |  | 0 |  | 15550
|  |  |  | 20:00 | 15730 |  | 0 |  | 15730
|  |  |  | 21:00 | 15920 |  | 0 |  | 15920
|  |  |  | 22:00 | 15820 |  | 0 |  | 15820
|  |  |  | 23:00 | 15710 |  | 0 |  | 15710
Probable Maximum Temperature: |  |  | 31.00°C
Probable Maximum Demand at Day Peak: |  |  | 14260.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 15920.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14957.78 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 339.83185 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:25 hrs on 03-07-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 02-07-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14160.34 | MW | 12:00 Hr. | Energy Generated |  |  | 343.4324 |  | MKWHr.
| Day Peak Demand |  |  | 14160.34 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.911 |  | MKWHr.
| Evening Peak Generation |  |  | 15485.2 | MW | 21:00 Hr. | Energy Demand |  |  | 344.3434 |  | MKWHr.
| Evening Peak Demand |  |  | 15540.2 | MW | 21:00 Hr. | Maximum Temperature |  |  | 32.4 |  | °C
| Minimum Generation of the Day |  |  | 12879.9 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 991.54 |  | MMCFD
| Maximum Generation of the Day |  |  | 15508.33 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.6202 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 45.2665 | 0 | 14.5831 | 0 | 0 | 0.15779 | 0 | 0 | 60.0073 | Gas | 141.4341 | Gas | 501917821.8671
| Chattogram Zone |  |  | 5.8473 | 31.46 | 7.6346 | 0 | 4.15 | 0.035792 | 0 | 0.90048 | 50.0281 | Coal | 91.4139 | Coal | 569099042.9075
| Cumilla Zone |  |  | 24.243 | 0 | 10.1263 | 0 | 0 | 0.36716 | 1.0061 | 0 | 35.7426 | HFO | 45.0129 | HFO | 841135672.454
| Mymensingh Zone |  |  | 1.0906 | 0 | 6.1688 | 0 | 0 | 0.30111 | 0 | 0 | 7.5605 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 33.4381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.4381 | Hydro | 4.15 | Hydro | 415000
| Khulna Zone |  |  | 5.2494 | 14.5818 | 0.72408 | 0 | 0 | 0.558 | 22.7156 | 0 | 43.8289 | Solar | 3.8593 | Solar | 63309768.3744
| Barishal Zone |  |  | 8.5533 | 39.3241 | 0.2892 | 0 | 0 | 0.003828 | 0 | 0 | 48.1704 | Import | 56.6617 | Import | 284517310.2
| Rajshahi Zone |  |  | 17.7461 | 0 | 2.4025 | 0 | 0 | 0.96489 | 32.94 | 0 | 54.0535 | Wind | 0.90048 | Wind | 13183027.2
| Rangpur Zone |  |  | 0 | 6.048 | 3.0843 | 0 | 0 | 1.4707 | 0 | 0 | 10.603
| Total |  |  | 141.4341 | 91.4139 | 45.0129 | 0 | 4.15 | 3.8593 | 56.6617 | 0.90048 | 343.4324
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 501917821.8671 |  | Hydro | 415000
|  |  |  | Coal | 569099042.9075 |  | Solar | 63309768.3744
|  |  |  | HFO | 841135672.454 |  | Import | 284517310.2
|  |  |  | HSD | 0 |  | Wind | 13183027.2
[5 empty] | Total: | 227,35,77,643 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.8036 | Peak Hr Flow | 889.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 12765618.27 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 32.94 | Peak Hr Flow | 1425.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 948 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.0061 | Peak Hr Flow | 46.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 984 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 55.7497 | Peak Hr Flow | 2360.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5161
|  |  |  | Chattogram |  | 0 |  | 1426
|  |  |  | Cumilla |  | 0 |  | 1419
|  |  |  | Mymensingh |  | 0 |  | 1249
|  |  |  | Sylhet |  | 0 |  | 623
|  |  |  | Khulna |  | 0 |  | 1829
|  |  |  | Barishal |  | 0 |  | 478
|  |  |  | Rajshahi |  | 0 |  | 1602
|  |  |  | Rangpur |  | 53 |  | 1078
|  |  |  | Total |  | 53 |  | 14865
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[5 empty] | Total | 300 |  |  |  | Total | 476
|  |  |  | Total Unavailable Capacity |  |  |  | 776
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:10 | 08:22 | Barishal 132/33kV S/S T-1 (405T) LT Tripped showing O/C relays Due to 33 kv polaspur | [7 empty] | 50.0MW load
|  |  | feeder fault | [7 empty] | interrup.
|  | 08:20 | Rangpur 132/33kV S/S T-1(414T) LT is restored.
|  | 08:20 | Rangpur 132/33kV S/S T-1(414T) HT is restored.
| 08:36 | 11:32 | Chauddagram 132/33kV S/S 132 kv T-1 HT Scheduled S/D Due to 33kV Bus-1 Maintenance for | [7 empty] | 27.0MW load
|  |  | PBS | [7 empty] | interrup.
| 08:36 | 11:32 | Chauddagram 132/33kV S/S 132 kv T-1 LT Scheduled S/D Due to 33kV Bus-1 Maintenance for | [7 empty] | 27.0MW load
|  |  | PBS | [7 empty] | interrup.
| 08:37 |  | Kaliakoir 400/230/132kV S/S 400kV Bus 1 Scheduled S/D Due to Project Works
| 09:24 | 10:44 | Bogura 230/132kV S/S 132KV Main 1 Scheduled S/D Due to red Hot Maintenance
| 09:28 |  | Hathazari 230/132/33kV S/S MT-02 HT Scheduled S/D Due to Oil centrifusing
|  | 10:29 | Dhamrai 132/33kV S/S Transformer-1 HT is restored.
|  | 10:30 | Dhamrai 132/33kV S/S Transformer-1 LT is restored.
|  | 14:20 | Mongla 132/33kV S/S T-2 HT is restored.
|  | 14:20 | Mongla 132/33kV S/S T-2 LT is restored.
|  | 17:22 | Gopalganj 400/132kV S/S ATR-01 HT is restored.
|  | 17:23 | Gopalganj 400/132kV S/S ATR-01 LT is restored.
| 17:57 |  | Mirzapur 132/33kV S/S Transformer-02(E07) HT Scheduled S/D Due to OIL centrifuging
| 19:20 | 20:21 | Madunaghat 132/33kV S/S TR-2(517T) LT Forced S/D Due to T-02(33kV) Bus shutdown due to | [7 empty] | 3.0MW load
|  |  | Ononna feeder maintenance. | [7 empty] | interrup.
| 19:40 | 22:34 | Kabirpur 132/33kV S/S XFR, T-I HT Scheduled S/D Due to Shutdown taken by DPBS-1 due to 33 | [7 empty] | 104.0MW load
|  |  | KV Section bus DS high temperature maintenance work | [7 empty] | interrup.
| 21:00 |  | Evening peak Generation is 15485 MW
| 00:39 |  | Sirajgonj 225MW CCPP Unit-1 Shutdown with remarks:- ST
| 00:48 |  | Sirajgonj 225MW CCPP Unit-1 Shutdown with remarks:- GT
| 01:19 |  | Sirajgonj 225MW CCPP Unit-3 Synchronized with remarks:- GT
| 04:19 |  | Sirajgonj 225MW CCPP Unit-3 Synchronized with remarks:- ST
| 07:00 |  | Minimum generation 12614 MW
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 02-07-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 404 | 9878400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 380 | 9418000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 299 | 7222167 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 332 | 7968458 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 817920 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 110 | 1946880 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 662413 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 78379 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 27 | 583200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 436680 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 439200 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 95 | 467945 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3380833 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1191360 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 65 | 458880 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 147 | 1893600 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 157791 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 1000440 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 450 | 9759545.45 | None
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 142 | 2245200 | -
Dhaka Area Total |  |  |  |  | 5939.724 | 2889 | 60007291.45
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 9583.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 13230 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 388320 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 172 | 4150000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 219 | 5448381 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 94 | 1093963 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 70 | 759113 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 429988 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 88 | 1629120 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 2 | 398880 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22562 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 100 | 948436 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 17 | 92360 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 30 | 358800 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1834560 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 15 | 90327 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1160 | 26536361 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 43 | 900480 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 204 | 4923636.36 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4895.72 | 2379 | 50028100.56
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 0 | 0 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 350 | 8480500 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 8206000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 20 | 465264 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 48 | 957600 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 185 | 4549818.18 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1150321 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 12 | 680800 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 756096 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 178 | 3764160 | -
| Import (Tripura) |  | Import | 0 | 160 | 46 | 1006080 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 763378 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 433470 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 95 | 1850220 | Engine Problem
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 342720 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 60 | 1968960 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 367164 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1521.2 | 35742551.18
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 49 | 1090560 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 162 | 3249600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 101 | 1836000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 289660 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 14 | 308880 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 774360 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 361 | 7560510
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | Gas shortage instructed by DS(Gen)
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3603682 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 726816 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1906560 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 171 | 3540370 | Machine Problem
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 224000 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 170304 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 6880500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 387 | 8701000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7684900 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1444 | 33438132
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 889 | 21803636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 215 | 5249376 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 337010 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 50 | 387072 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 558000 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 594 | 14581820 | U#2 under shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1839 | 43828914
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 300 | 7294545.45 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 10 | 286305 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2848000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1110 | 25854545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5418960 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 66 | 289200 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 278 | 6175000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3828 | -
Barishal Area Total |  |  |  |  | 2236 | 2104 | 48170383.9
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 47 | 206121 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 164200 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 161 | 4280091 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 185 | 4675836 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 356 | 8790181 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 180450 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 655184 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1005696 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 190848 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 28320 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1425 | 32940000 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 327744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 608830 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2485 | 54053501
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 47 | 1103999 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 203 | 4944000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 1350518 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 39674.04 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1733791 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 185451 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1245600 | -
Rangpur Area Total |  |  |  |  | 950 | 463 | 10603033.04
Eastern Grid Total |  |  |  |  | 16705.895 | 8594.2 | 186776585.19
Western Grid Total |  |  |  |  | 10378.16 | 6891 | 156655831.94
National Grid Total |  |  |  |  | 27084.055 | 15485.2 | 343432417.13
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 02-07-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9877.97 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4933.1 | MW
i) Dhaka area |  |  | 5161.14 |  | MW | i) Khulna area |  |  |  | 1829 | MW
ii) Chattogram area |  |  | 1426 |  | MW | ii) Barishal area |  |  |  | 477.5 | MW
iii) Cumilla area |  |  | 1418.83 |  | MW | iii) Rajshahi area |  |  |  | 1601.6 | MW
iv) Mymensingh area |  |  | 1249 |  | MW | iv) Rangpur area |  |  |  | 1025 | MW
v) Sylhet area |  |  | 623 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14811.07 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 81 | 20:00 | 133 | Patuakhali | 78.5 | 20:00
2 | AKSML | 127 | 01:00 | 68 | Jaldhaka | 93 | 21:00 | 134 | Payra | 32 | 00:00
3 | Aftabnagar | 40 | 00:00 | 69 | Jamalpur | 135 | 21:00 | 135 | Postogola | 62 | 13:00
4 | Agargaon | 138 | 13:00 | 70 | Jashore | 146 | 19:30 | 136 | Purbachal | 23 | 00:00
5 | Agrabad | 94 | 16:00 | 71 | Jhenaidah | 132 | 19:30 | 137 | Purbasadipur | 146 | 00:00
6 | Amnura | 44 | 21:00 | 72 | Joydebpur | 144 | 12:00 | 138 | Rahanpur | 32 | 00:00
7 | Ashuganj | 106 | 00:00 | 73 | Joypurhat | 69 | 23:00 | 139 | Rahim | 31 | 11:00
8 | BSRM | 208 | 04:00 | 74 | Juldah | 16 | 00:00 | 140 | Rajbari | 84 | 19:30
9 | Bagerhat | 86 | 20:00 | 75 | KSRM | 25 | 19:00 | 141 | Rajendrapur | 138 | 19:30
10 | Bajitpur | 70 | 22:00 | 76 | Kabirpur | 249 | 18:00 | 142 | Rajshahi | 122 | 21:00
11 | Bakulia | 90 | 13:00 | 77 | Kachua | 92 | 00:00 | 143 | Rajshahi-230 | 99 | 13:00
12 | Banani | 40.6 | 11:00 | 78 | Kallyanpur | 108 | 00:00 | 144 | Ramganj | 116 | 22:00
13 | Bangabhaban | 18 | 10:00 | 79 | Kalurghat | 38 | 10:00 | 145 | Rampur | 42 | 00:00
14 | Barapukuria | 68 | 00:00 | 80 | Kamrangirchar | 68 | 12:00 | 146 | Rangamati | 17 | 20:00
15 | Barguna | 24 | 22:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 149 | 20:00
16 | Barishal | 105 | 00:00 | 82 | Kasba | 37 | 23:00 | 148 | Ruppur | 7 | 09:00
17 | Barishal-230 | 110 | 19:30 | 83 | Kazla | 99 | 12:00 | 149 | SSM | 10 | 23:00
18 | Baroaulia | 69 | 12:00 | 84 | Keranigonj | 103 | 21:00 | 150 | Saidpur | 111 | 19:30
19 | Baroirhat | 63 | 14:00 | 85 | Khagrachori | 32 | 20:00 | 151 | Satkhira | 123 | 22:00
20 | Bashundhara | 194 | 13:00 | 86 | Khulna | 72 | 21:00 | 152 | Satmasjid | 100 | 14:00
21 | BashundharaCement | 12 | 01:00 | 87 | Khulshi | 158 | 14:00 | 153 | Savar | 234 | 12:00
22 | Beanibazar | 86 | 00:00 | 88 | Kishoreganj | 152 | 21:00 | 154 | SevenRings | 15.9 | 16:00
23 | Benapole | 76 | 00:00 | 89 | Kodda | 319 | 14:00 | 155 | ShahCement | 17 | 22:00
24 | Bhaluka | 160 | 19:00 | 90 | Kulaura | 57 | 22:00 | 156 | Shahjadpur | 86 | 19:30
25 | Bhandaria | 59 | 23:00 | 91 | Kurigram | 66 | 07:00 | 157 | Shahjibazar | 134 | 21:00
26 | Bhangura | 39 | 20:00 | 92 | Kushtia | 160 | 19:00 | 158 | Shahmirpur | 62 | 00:00
27 | Bheramara(GK) | 69 | 21:00 | 93 | Lalbag | 58 | 13:00 | 159 | Shariatpur | 90 | 22:00
28 | Bhulta | 244 | 00:00 | 94 | Lalmonirhat | 74 | 19:30 | 160 | Sherpur | 164 | 20:00
29 | Bog-Sherpur | 68 | 01:00 | 95 | MI_Cement | 15.3 | 02:00 | 161 | Shikalbaha | 8 | 09:00
30 | Bogura | 183 | 00:00 | 96 | Madanganj | 50 | 00:00 | 162 | Shitalakhya | 93 | 12:00
31 | Borhanuddin | 90 | 22:00 | 97 | Madaripur | 112 | 23:00 | 163 | Sholosohor | 47 | 19:00
32 | Brahmanbaria | 137 | 22:00 | 98 | Madartek | 97.59 | 00:00 | 164 | Shyampur | 162 | 10:00
33 | Cantonment | 162 | 13:00 | 99 | Madunaghat | 54 | 00:00 | 165 | Siddhirganj | 117 | 13:00
34 | Chandina | 19.97 | 05:00 | 100 | Magura | 69 | 19:30 | 166 | Sirajganj | 115 | 21:00
35 | Chandpur | 84 | 00:00 | 101 | Mahasthangarh | 90 | 00:00 | 167 | Sonargaon | 98 | 00:00
36 | Chandraghona | 40 | 19:30 | 102 | Manikganj | 131 | 21:00 | 168 | Sreemongol | 81 | 00:00
37 | Chapai | 78 | 22:00 | 103 | Maniknagar | 88 | 13:00 | 169 | Sreepur | 104 | 12:00
38 | Charsaidpur | 25 | 02:00 | 104 | Matarbari | 48 | 00:00 | 170 | Srinagar | 48.39 | 22:00
39 | Chauddagram | 74 | 23:00 | 105 | Matuail | 66 | 14:00 | 171 | Sunamganj | 63 | 00:00
40 | Chhatak | 43 | 00:00 | 106 | Millgate | 117 | 12:00 | 172 | Sylhet | 52 | 01:00
41 | Chowmuhani | 193 | 19:30 | 107 | Mirpur | 125 | 19:00 | 173 | Sylhet-132 | 138 | 19:00
42 | Chuadanga | 113 | 00:00 | 108 | Mirsorai | 10 | 10:00 | 174 | TK | 38 | 23:00
43 | Coxsbazar | 136 | 19:00 | 109 | Mirzapur | 46 | 21:00 | 175 | Tangail | 184 | 21:00
44 | Cumilla(N) | 160 | 21:00 | 110 | Mithapukur | 76 | 02:00 | 176 | Thakurgaon | 116 | 00:00
45 | Cumilla(S) | 175 | 14:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 144 | 11:00
46 | Daudkandi | 156 | 22:00 | 112 | Mogbazar | 154.8 | 12:00 | 178 | Ullahpara | 42 | 20:00
47 | Dhaka | 82 | 13:00 | 113 | Mongla | 38 | 12:00 | 179 | Ullon | 42 | 00:00
48 | Dhamrai | 128 | 19:30 | 114 | Motijheel | 46 | 13:00 | 180 | Uttara | 86 | 13:00
49 | Dhanmondi | 150 | 13:00 | 115 | Muktagacha | 40 | 20:00 | 181 | UttaraNew | 62 | 23:00
50 | Dohazari | 103 | 00:00 | 116 | Munshiganj | 119 | 00:00 | 182 | Zigatola | 78 | 00:00
51 | Faridpur | 166 | 22:00 | 117 | Muradnagar | 30 | 00:00
52 | Fatullah | 97 | 11:00 | 118 | Mymensingh | 212 | 03:00
53 | Fenchuganj | 49 | 23:00 | 119 | Naogaon | 140 | 20:00
54 | Feni | 117 | 19:30 | 120 | Narail | 58 | 22:00
55 | GPH | 85 | 19:30 | 121 | Narinda | 78 | 13:00
56 | Ghatail | 84 | 01:00 | 122 | Narshingdi | 192 | 00:00
57 | Ghorashal | 15 | 22:00 | 123 | Natore | 160 | 22:00
58 | Ghorashal-230 | 92 | 22:00 | 124 | Nawabganj | 60.6 | 22:00
59 | Goalpara | 39 | 00:00 | 125 | Netrakona | 136 | 19:00
60 | Gollamari | 98 | 19:30 | 126 | New | 60.4 | 12:00
61 | Gopalganj | 109 | 21:00 | 127 | Niamatpur | 86 | 22:00
62 | Gulshan | 122 | 12:00 | 128 | Noapara | 45 | 19:30
63 | Halishahar | 75 | 11:00 | 129 | PHP | 7 | 15:00
64 | HaripurSBU | 164 | 17:00 | 130 | Pabna | 130 | 20:00
65 | Hasnabad | 67 | 00:00 | 131 | Palashbari | 119 | 00:00
66 | Hathazari | 82 | 00:00 | 132 | Panchagarh | 66 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 02-07-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15508.33 | 202 |  | 15719.42
1:00 | 15048.46 | 174 |  | 15230.29
2:00 | 14704.25 | 120 |  | 14829.65
3:00 | 14290.82 | 96 |  | 14391.14
4:00 | 14027.66 | 60 |  | 14090.36
5:00 | 13758.66 | 0 |  | 13758.66
6:00 | 13122.79 | 0 |  | 13122.79
7:00 | 12973.98 | 0 |  | 12973.98
8:00 | 12879.9 | 0 |  | 12879.9
9:00 | 12957.74 | 0 |  | 12957.74
10:00 | 13142.65 | 0 |  | 13142.65
11:00 | 13589.25 | 0 |  | 13589.25
12:00 | 14160.34 | 0 |  | 14160.34
13:00 | 14326.55 | 0 |  | 14326.55
14:00 | 13920.95 | 0 |  | 13920.95
15:00 | 14260.05 | 0 |  | 14260.05
16:00 | 14282.22 | 0 |  | 14282.22
17:00 | 13808.3 | 0 |  | 13808.3
18:00 | 13356.81 | 0 |  | 13356.81
19:00 | 14424 | 0 |  | 14424
19:30 | 15437.2 | 0 |  | 15437.2
20:00 | 15479.2 | 44 |  | 15525.2
21:00 | 15485.2 | 53 |  | 15540.2
22:00 | 15388.11 | 51 |  | 15441.41
23:00 | 15404.77 | 111 |  | 15520.77
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 02-07-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8408.2 | 7100.13 | 15508.33 | DAILY GENERATION CURVE
00:30 | 8309.2 | 6969.195 | 15278.395
01:00 | 8210.2 | 6838.26 | 15048.46 | 02-07-2025
01:30 | 8115.7 | 6760.655 | 14876.355
02:00 | 8021.2 | 6683.05 | 14704.25
02:30 | 7885.7 | 6611.835 | 14497.535
03:00 | 7750.2 | 6540.62 | 14290.82
03:30 | 7664.2 | 6495.04 | 14159.24
04:00 | 7578.2 | 6449.46 | 14027.66
04:30 | 7523.7 | 6369.46 | 13893.16
05:00 | 7469.2 | 6289.46 | 13758.66
05:30 | 7285.485 | 6155.24 | 13440.725
06:00 | 7101.77 | 6021.02 | 13122.79
06:30 | 7035.295 | 6013.09 | 13048.385
07:00 | 6968.82 | 6005.16 | 12973.98
07:30 | 6914.505 | 6012.435 | 12926.94
08:00 | 6860.19 | 6019.71 | 12879.9
08:30 | 6859.99 | 6058.83 | 12918.82
09:00 | 6859.79 | 6097.95 | 12957.74
09:30 | 6938.6 | 6111.595 | 13050.195
10:00 | 7017.41 | 6125.24 | 13142.65
10:30 | 7146.31 | 6219.64 | 13365.95
11:00 | 7275.21 | 6314.04 | 13589.25
11:30 | 7435.255 | 6439.54 | 13874.795
12:00 | 7595.3 | 6565.04 | 14160.34
12:30 | 7690.385 | 6553.06 | 14243.445
13:00 | 7785.47 | 6541.08 | 14326.55
13:30 | 7650.035 | 6473.715 | 14123.75
14:00 | 7514.6 | 6406.35 | 13920.95
14:30 | 7616.52 | 6473.98 | 14090.5
15:00 | 7718.44 | 6541.61 | 14260.05
15:30 | 7791.835 | 6479.3 | 14271.135
16:00 | 7865.23 | 6416.99 | 14282.22
16:30 | 7753.74 | 6291.52 | 14045.26
17:00 | 7642.25 | 6166.05 | 13808.3
17:30 | 7503.485 | 6079.07 | 13582.555
18:00 | 7364.72 | 5992.09 | 13356.81
18:30 | 7656.86 | 6233.545 | 13890.405
19:00 | 7949 | 6475 | 14424
19:30 | 8677.2 | 6760 | 15437.2
20:00 | 8671.2 | 6808 | 15479.2
20:30 | 8632.7 | 6849.5 | 15482.2 |  | Executive Engineer
21:00 | 8594.2 | 6891 | 15485.2 |  | Network Operation Division
21:30 | 8561.2 | 6875.455 | 15436.655
22:00 | 8528.2 | 6859.91 | 15388.11
22:30 | 8524.2 | 6872.24 | 15396.44
23:00 | 8520.2 | 6884.57 | 15404.77

## En-Curve
QF-LDC-12
Date | 02-07-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3710 | 2234 | 898 | 38 | 52 | 1443.13 | 172 | 4017 | 0 | 708 | 2209.2 | 0 | 0 | 27 | 202 | DAILY ENERGY CURVE
00:30 | 3694.5 | 2233 | 897.5 | 38 | 50 | 1435.695 | 172 | 3962.5 | 0 | 644 | 2130.7 | 0 | 0 | 20.5 | 188 | 02-07-2025
01:00 | 3679 | 2232 | 897 | 38 | 48 | 1428.26 | 172 | 3908 | 0 | 580 | 2052.2 | 0 | 0 | 14 | 174
01:30 | 3650.5 | 2237.5 | 900.5 | 38 | 48 | 1435.655 | 172 | 3891.5 | 0 | 496 | 1993.2 | 0 | 0 | 13.5 | 147 | Energy Generated | 343.4324 |  | MKWHr
02:00 | 3622 | 2243 | 904 | 38 | 48 | 1443.05 | 172 | 3875 | 0 | 412 | 1934.2 | 0 | 0 | 13 | 120 | Energy not Served | 0.911 |  | MKWHr
02:30 | 3616 | 2247.5 | 904 | 38 | 46 | 1449.835 | 172 | 3870.5 | 0 | 345 | 1795.7 | 0 | 0 | 13 | 108 | Total Energy Requirement | 344.3434 |  | MKWHr
03:00 | 3610 | 2252 | 904 | 38 | 44 | 1456.62 | 172 | 3866 | 0 | 278 | 1657.2 | 0 | 0 | 13 | 96
03:30 | 3615 | 2258 | 908 | 38 | 44 | 1458.54 | 172 | 3868 | 0 | 257.5 | 1517.2 | 0 | 0 | 23 | 78
04:00 | 3620 | 2264 | 912 | 38 | 44 | 1460.46 | 172 | 3870 | 0 | 237 | 1377.2 | 0 | 0 | 33 | 60
04:30 | 3616.5 | 2260.5 | 915.5 | 38 | 44 | 1405.46 | 172 | 3828 | 0 | 230 | 1340.7 | 0 | 0 | 42.5 | 30
05:00 | 3613 | 2257 | 919 | 38 | 44 | 1350.46 | 172 | 3786 | 0 | 223 | 1304.2 | 0 | 0 | 52 | 0
05:30 | 3589 | 2231.5 | 919 | 38 | 43 | 1299.955 | 172 | 3693.5 | 15.67 | 214 | 1183.6 | 0 | 0 | 41.5 | 0
06:00 | 3565 | 2206 | 919 | 38 | 42 | 1249.45 | 172 | 3601 | 31.34 | 205 | 1063 | 0 | 0 | 31 | 0
06:30 | 3565.5 | 2184.5 | 918.5 | 38 | 41 | 1256.63 | 172 | 3547.5 | 80.255 | 230.5 | 980.5 | 0 | 0 | 33.5 | 0
07:00 | 3566 | 2163 | 918 | 38 | 40 | 1263.81 | 172 | 3494 | 129.17 | 256 | 898 | 0 | 0 | 36 | 0
07:30 | 3558 | 2152.25 | 919 | 38 | 39 | 1258.405 | 172 | 3490.5 | 182.285 | 247.5 | 834.5 | 0 | 0 | 35.5 | 0
08:00 | 3550 | 2141.5 | 920 | 38 | 38 | 1253 | 172 | 3487 | 235.4 | 239 | 771 | 0 | 0 | 35 | 0
08:30 | 3581.5 | 2137.75 | 919.5 | 38 | 37 | 1269 | 172 | 3496.5 | 258.07 | 231 | 750 | 0 | 0 | 28.5 | 0
09:00 | 3613 | 2134 | 919 | 38 | 36 | 1285 | 172 | 3506 | 280.74 | 223 | 729 | 0 | 0 | 22 | 0
09:30 | 3604 | 2142.5 | 919 | 38 | 35 | 1278 | 172 | 3514.5 | 335.695 | 215 | 770.5 | 0 | 0 | 26 | 0
10:00 | 3595 | 2151 | 919 | 38 | 34 | 1271 | 172 | 3523 | 390.65 | 207 | 812 | 0 | 0 | 30 | 0
10:30 | 3645.5 | 2164 | 919 | 38 | 35 | 1267.5 | 172 | 3627.5 | 411.27 | 216.5 | 833.18 | 0 | 0 | 36.5 | 0
11:00 | 3696 | 2177 | 919 | 38 | 36 | 1264 | 172 | 3732 | 431.89 | 226 | 854.36 | 0 | 0 | 43 | 0
11:30 | 3651.5 | 2164 | 905 | 38 | 38 | 1320 | 172 | 3808 | 510.115 | 246 | 970.68 | 0 | 0 | 51.5 | 0
12:00 | 3607 | 2151 | 891 | 38 | 40 | 1376 | 172 | 3884 | 588.34 | 266 | 1087 | 0 | 0 | 60 | 0
12:30 | 3614 | 2135.5 | 890.5 | 38 | 41 | 1391.5 | 172 | 3852 | 576.445 | 285.5 | 1190 | 0 | 0 | 57 | 0
13:00 | 3621 | 2120 | 890 | 38 | 42 | 1407 | 172 | 3820 | 564.55 | 305 | 1293 | 0 | 0 | 54 | 0
13:30 | 3570.5 | 2107.25 | 890.5 | 38 | 43 | 1389.5 | 172 | 3775 | 530 | 290 | 1260 | 0 | 0 | 58 | 0
14:00 | 3520 | 2094.5 | 891 | 38 | 44 | 1372 | 172 | 3730 | 495.45 | 275 | 1227 | 0 | 0 | 62 | 0
14:30 | 3615.5 | 2158.5 | 890.5 | 38 | 43 | 1391.5 | 172 | 3795.5 | 416 | 275 | 1235 | 0 | 0 | 60 | 0
15:00 | 3711 | 2222.5 | 890 | 38 | 42 | 1411 | 172 | 3861 | 336.55 | 275 | 1243 | 0 | 0 | 58 | 0
15:30 | 3693.5 | 2214.5 | 890.5 | 38 | 41 | 1424.5 | 172 | 3878.5 | 264.635 | 293 | 1312 | 0 | 0 | 49 | 0
16:00 | 3676 | 2206.5 | 891 | 38 | 40 | 1438 | 172 | 3896 | 192.72 | 311 | 1381 | 0 | 0 | 40 | 0
16:30 | 3662 | 2216 | 890 | 38 | 39 | 1424.5 | 172 | 3806 | 165.26 | 311 | 1281.5 | 0 | 0 | 40 | 0
17:00 | 3648 | 2225.5 | 889 | 38 | 38 | 1411 | 172 | 3716 | 137.8 | 311 | 1182 | 0 | 0 | 40 | 0
17:30 | 3607.5 | 2208 | 888.5 | 38 | 37 | 1357 | 172 | 3690.5 | 91.055 | 321 | 1133.5 | 0 | 0 | 38.5 | 0
18:00 | 3567 | 2190.5 | 888 | 38 | 36 | 1303 | 172 | 3665 | 44.31 | 331 | 1085 | 0 | 0 | 37 | 0
18:30 | 3625 | 2206.75 | 888 | 38 | 41 | 1360 | 172 | 3743.5 | 22.155 | 479 | 1274.5 | 0 | 0 | 40.5 | 0
19:00 | 3683 | 2223 | 888 | 38 | 46 | 1417 | 172 | 3822 | 0 | 627 | 1464 | 0 | 0 | 44 | 0
19:30 | 3709 | 2256 | 888 | 38 | 46 | 1414 | 172 | 3923 | 0 | 746 | 2195.2 | 0 | 0 | 50 | 0
20:00 | 3650 | 2253 | 888 | 38 | 44 | 1402 | 172 | 3893 | 0 | 805 | 2276.2 | 0 | 0 | 58 | 44
20:30 | 3662.5 | 2243.5 | 888.5 | 38 | 45 | 1413.5 | 172 | 3894.5 | 0 | 796 | 2278.2 | 0 | 0 | 50.5 | 48.5
21:00 | 3675 | 2234 | 889 | 38 | 46 | 1425 | 172 | 3896 | 0 | 787 | 2280.2 | 0 | 0 | 43 | 53
21:30 | 3658 | 2239 | 889 | 38 | 47 | 1416.955 | 172 | 3889 | 0 | 773 | 2270.7 | 0 | 0 | 44 | 52
22:00 | 3641 | 2244 | 889 | 38 | 48 | 1408.91 | 172 | 3882 | 0 | 759 | 2261.2 | 0 | 0 | 45 | 51
22:30 | 3656 | 2236.5 | 889 | 38 | 49 | 1414.24 | 172 | 3888.5 | 0 | 741 | 2266.7 | 0 | 0 | 45.5 | 81
23:00 | 3671 | 2229 | 889 | 38 | 50 | 1419.57 | 172 | 3895 | 0 | 723 | 2272.2 | 0 | 0 | 46 | 111
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 02-07-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 384 | 06:00 | 373 | 11:00 | Payra | 414 | 07:00 | 408 | 00:00
Ashuganj | 409 | 5:00 | 383 | 11:00 | Rahanpur | 400 | 08:00 | 390 | 00:00
Bhulta | 404 | 05:00 | 382 | 11:00 | Rampal | 400 | 08:00 | 388 | 00:00
Bibiana | 388 | 07:00 | 382 | 12:00
BIPTC | 401 | 04:00 | 391 | 22:00
Bogura | 386 | 08:00 | 373 | 00:00
Gopalganj | 397 | 08:00 | 387 | 00:00
Kaliakoir | 375 | 07:00 | 360 | 11:00
Madunaghat | 395 | 21:00 | 390 | 12:00
Meghnaghat | 387 | 06:00 | 378 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 224 | 06:00 | 215 | 11:00 | Keranigonj | 222 | 06:00 | 214 | 12:00
AKSML | 234 | 19:30 | 225 | 06:00 | Khulna(S) | 229 | 08:00 | 219 | 00:00
Aminbazar | 225 | 05:00 | 215 | 11:00 | Madunaghat | 234 | 00:00 | 229 | 08:00
Ashuganj | 233 | 06:00 | 224 | 11:00 | Madunaghat-400 | 235 | 20:00 | 230 | 11:00
Ashuganj-400 | 233 | 06:00 | 224 | 11:00 | Maniknagar | 221 | 04:00 | 213 | 11:00
Baghabari | 233 | 08:00 | 226 | 00:00 | Meghnaghat | 229 | 06:00 | 221 | 11:00
Barapukuria | 222 | 08:00 | 216 | 16:00 | Meghnaghat-400 | 224 | 05:00 | 218 | 11:00
Barapukuria-230 | 222 | 08:00 | 216 | 16:00 | Mirsorai | 228 | 22:00 | 222 | 15:00
Barishal | 228 | 07:00 | 222 | 00:00 | Rajshahi | 233 | 08:00 | 223 | 00:00
Bheramara | 232 | 08:00 | 222 | 00:00 | Rampal | 228 | 08:00 | 219 | 00:00
Bhulta | 229 | 07:00 | 213 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 229 | 05:00 | 222 | 00:00 | Rampura | 228 | 05:00 | 212 | 11:00
BIPTC | 235 | 08:00 | 223 | 00:00 | Shikalbaha | 234 | 21:00 | 227 | 12:00
Bogura | 233 | 08:00 | 225 | 00:00 | Shyampur | 222 | 05:00 | 215 | 12:00
Bogura-400 | 234 | 08:00 | 226 | 00:00 | Siddhirganj | 222 | 05:00 | 216 | 11:00
Borhanuddin | 234 | 08:00 | 229 | 00:00 | Sirajgonj | 238 | 05:00 | 233 | 00:00
BSRM | 227 | 08:00 | 221 | 15:00 | Sreepur | 228 | 07:00 | 220 | 15:00
Cumilla(N) | 223 | 05:00 | 217 | 12:00 | Tongi | 225 | 07:00 | 212 | 11:00
Faridpur | 226 | 08:00 | 218 | 00:00
Fenchuganj | 229 | 06:00 | 222 | 19:00
Ghorashal | 225 | 00:00 | 220 | 14:00
Ghorashal-230 | 228 | 05:00 | 214 | 15:00
Gopalganj | 227 | 08:00 | 220 | 00:00
GPH | 231 | 20:00 | 224 | 00:00
Haripur | 221 | 05:00 | 215 | 12:00
Hasnabad | 222 | 05:00 | 216 | 15:00
Hathazari | 235 | 21:00 | 225 | 11:00
Ishurdi | 235 | 08:00 | 225 | 00:00
Jhenaidah | 229 | 08:00 | 217 | 19:30
Kaliakoir | 234 | 06:00 | 221 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 03:00 | 125 | 11:00 | Madanganj | 128 | 21:00 | 124 | 01:00
Agargaon | 131 | 04:00 | 124 | 12:00 | Madaripur | 135 | 08:00 | 130 | 00:00
Agrabad | 134 | 20:00 | 129 | 08:00 | Madartek | 137 | 05:00 | 125 | 11:00
AKS | 131 | 20:00 | 127 | 10:00 | Madunaghat | 133 | 00:00 | 129 | 10:00
Aminbazar | 132 | 18:00 | 125 | 11:00 | Magura | 133 | 07:00 | 123 | 00:00
Amnura | 137 | 19:00 | 125 | 23:00 | Mahasthangarh | 134 | 08:00 | 126 | 00:00
Ashuganj | 138 | 07:00 | 133 | 00:00 | Maijdee | 122 | 14:00 | 105 | 22:00
Bagerhat | 131 | 08:00 | 124 | 00:00 | Manikganj | 127 | 05:00 | 119 | 12:00
Bajitpur | 130 | 05:00 | 122 | 19:00 | Maniknagar | 131 | 06:00 | 125 | 12:00
Bakulia | 135 | 20:00 | 130 | 11:00 | Matarbari | 123 | 08:00 | 115 | 02:00
Banani | 137 | 03:00 | 126 | 10:00 | Matuail | 129 | 05:00 | 124 | 12:00
Bangabhaban | 131 | 06:00 | 125 | 12:00 | Millgate | 132 | 06:00 | 124 | 10:00
Barapukuria | 136 | 19:00 | 128 | 09:00 | Mirpur | 130 | 04:00 | 124 | 10:00
Barguna | 135 | 20:00 | 129 | 00:00 | Mirzapur | 130 | 06:00 | 124 | 15:00
Barishal | 134 | 07:00 | 128 | 00:00 | Mithapukur | 129 | 18:00 | 120 | 01:00
Barishal-230 | 133 | 07:00 | 127 | 00:00 | MI_Cement | 129 | 06:00 | 124 | 11:00
Baroaulia | 134 | 19:30 | 130 | 11:00 | Modern | N/A | N/A | N/A | N/A
Baroirhat | 125 | 06:00 | 118 | 01:00 | Mogbazar | 138 | 04:00 | 126 | 11:00
Bashundhara | 137 | 05:00 | 124 | 11:00 | Mongla | 131 | 07:00 | 124 | 00:00
BashundharaCement | 128 | 21:00 | 124 | 01:00 | Motijheel | 131 | 05:00 | 125 | 12:00
Beanibazar | 127 | 06:00 | 122 | 00:00 | Muktagacha | 135 | 09:00 | 125 | 19:00
Benapole | 130 | 07:00 | 121 | 00:00 | Munshiganj | 128 | 02:00 | 123 | 12:00
Bhaluka | 129 | 08:00 | 123 | 15:00 | Muradnagar | 125 | 06:00 | 120 | 15:00
Bhandaria | 128 | 09:00 | 118 | 00:00 | Mymensingh | 136 | 09:00 | 115 | 22:00
Bhangura | 138 | 22:00 | 128 | 00:00 | Naogaon | 132 | 18:00 | 124 | 00:00
Bheramara | 137 | 08:00 | 131 | 00:00 | Narail | 134 | 18:00 | 123 | 19:30
Bheramara(GK) | 136 | 08:00 | 131 | 00:00 | Narinda | 131 | 06:00 | 125 | 12:00
Bhulta | 125 | 03:00 | 118 | 22:00 | Narshingdi | 130 | 18:00 | 118 | 00:00
Bog-Sherpur | 135 | 08:00 | 129 | 00:00 | Natore | 134 | 08:00 | 128 | 00:00
Bogura | 137 | 07:00 | 131 | 00:00 | Nawabganj | 133 | 05:00 | 126 | 12:00
Bogura-230 | 137 | 08:00 | 132 | 00:00 | Netrakona | 122 | 05:00 | 112 | 19:00
Brahmanbaria | 132 | 07:00 | 124 | 00:00 | New Tongi | 133 | 07:00 | 124 | 12:00
Cantonment | 131 | 04:00 | 124 | 11:00 | Niamatpur | 135 | 08:00 | 130 | 00:00
Chandina | 127 | 06:00 | 123 | 00:00 | Noapara | 133 | 08:00 | 127 | 00:00
Chandpur | 126 | 07:00 | 114 | 23:00 | Pabna | 134 | 08:00 | 128 | 19:30
Chandraghona | 134 | 22:00 | 131 | 03:00 | Palashbari | 129 | 08:00 | 118 | 00:00
Chapai | 131 | 18:00 | 126 | 23:00 | Panchagarh | 136 | 19:00 | 122 | 20:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 05:00 | 124 | 12:00 | Patuakhali | 136 | 00:00 | 131 | 01:00
Chauddagram | 123 | 09:00 | 117 | 15:00 | Payra | 166 | 21:00 | 133 | 00:00
Chhatak | 126 | 06:00 | 120 | 01:00 | PHP | 123 | 06:00 | 116 | 23:00
Chowmuhani | 120 | 18:00 | 110 | 23:00 | Postogola | 131 | 07:00 | 126 | 11:00
Chuadanga | 131 | 08:00 | 120 | 22:00 | Purbachal | 137 | 03:00 | 123 | 12:00
Coxsbazar | 126 | 14:00 | 117 | 03:00 | Purbasadipur | 131 | 19:00 | 121 | 12:00
Cumilla(N) | 128 | 05:00 | 123 | 00:00 | Rahanpur | 136 | 06:00 | 132 | 00:00
Cumilla(S) | 132 | 04:00 | 121 | 00:00 | Rahanpur-400 | 137 | 08:00 | 133 | 00:00
Daganbhuiyan | 0 | 23:00 | N/A | N/A | Rahim | 129 | 05:00 | 125 | 12:00
Daudkandi | 124 | 08:00 | 118 | 00:00 | Rajbari | 133 | 08:00 | 126 | 00:00
Dhaka | 137 | 03:00 | 125 | 11:00 | Rajendrapur | 140 | 08:00 | 122 | 00:00
Dhamrai | 133 | 08:00 | 125 | 11:00 | Rajshahi | 135 | 08:00 | 129 | 00:00
Dhanmondi | 137.6 | 05:00 | 125 | 11:00 | Rajshahi-230 | 135 | 08:00 | 118 | 13:00
Dohazari | 131 | 20:00 | 127 | 12:00 | Ramganj | 122 | 18:30 | 110 | 23:00
Faridpur | 134 | 08:00 | 129 | 00:00 | Rampur | 133 | 20:00 | 128 | 11:00
Fatullah | 130 | 05:00 | 125 | 12:00 | Rampura | 138 | 05:00 | 126 | 11:00
Fenchuganj | 135 | 06:00 | 130 | 00:00 | Rangamati | 132 | 20:00 | 129 | 11:00
Feni | 123 | 07:00 | 119 | 12:00 | Rangpur | 131 | 19:00 | 121 | 16:00
Ghatail | 130 | 08:00 | 123 | 00:00 | Ruppur | 137 | 08:00 | 131 | 00:00
Ghorashal | 138 | 06:00 | 131 | 11:00 | Saidpur | 131 | 19:00 | 122 | 13:00
Goalpara | 135 | 08:00 | 128 | 00:00 | Satkhira | 133 | 08:00 | 124 | 00:00
Gollamari | 136 | 07:00 | 130 | 02:00 | Satmasjid | 131 | 06:00 | 124 | 12:00
Gopalganj | 134 | 08:00 | 130 | 02:00 | Savar | 132 | 19:30 | 123 | 11:00
Gopalganj-400 | 136 | 08:00 | 132 | 00:00 | SevenRings | 139 | 08:00 | 131 | 11:00
Gulshan | 137 | 05:00 | 126 | 15:00 | ShahCement | 129 | 05:00 | 124 | 12:00
Halishahar | 135 | 19:30 | 128 | 11:00 | Shahjadpur | 135 | 05:00 | 131 | 22:00
Haripur | 129 | 05:00 | 125 | 12:00 | Shahjibazar | 133 | 08:00 | 125 | 00:00
HaripurSBU | 129 | 05:00 | 125 | 15:00 | Shahmirpur | 135 | 19:30 | 131 | 09:00
Hasnabad | 131 | 05:00 | 126 | 11:00 | Shariatpur | 134 | 08:00 | 128 | 01:00
Hathazari | 135 | 00:00 | 132 | 12:00 | Sherpur | 135 | 13:00 | 123 | 19:00
Ishurdi | 138 | 08:00 | 131 | 00:00 | Shikalbaha | 124 | 19:30 | 119 | 11:00
Jaldhaka | 129 | 18:00 | 118 | 20:00 | Shikalbaha-230 | 136 | 20:00 | 132 | 04:00
Jamalpur | 138 | 09:00 | 127 | 19:00 | Shitalakhya | 129 | 06:00 | 124 | 11:00
Jashore | 130 | 08:00 | 119 | 23:00 | Sholosohor | 133 | 00:00 | 129 | 04:00
Jhenaidah | 134 | 09:00 | 121 | 19:30 | Shyampur | 130 | 05:00 | 125 | 10:00
Jhenaidah-230 | 135 | 08:00 | 126 | 00:00 | Shyampur-230 | 130 | 06:00 | 124 | 12:00
Joydebpur | 139 | 20:00 | 128 | 10:00 | Siddhirganj | 129 | 03:00 | 125 | 12:00
Joypurhat | 130 | 18:00 | 121 | 00:00 | Sirajganj | 132 | 07:00 | 125 | 01:00
Juldah | 136 | 22:00 | 132 | 03:00 | Sonargaon | 128 | 05:00 | 122 | 11:00
Kabirpur | 133 | 08:00 | 120 | 12:00 | Sreemongol | 132 | 07:00 | 125 | 00:00
Kachua | 126 | 06:00 | 116 | 23:00 | Sreepur | 132 | 06:00 | 126 | 15:00
Kaliakoir | 134 | 07:00 | 127 | 11:00 | Srinagar | 133 | 06:00 | 126 | 12:00
Kallyanpur | 132 | 03:00 | 126 | 10:00 | SSM | 138 | 00:00 | 132 | 13:00
Kalurghat | 133 | 19:30 | 129 | 04:00 | Sunamganj | 124 | 06:00 | 117 | 00:00
Kamrangirchar | 133 | 06:00 | 126 | 11:00 | Sylhet | 128 | 06:00 | 123 | 00:00
Kaptai | 135 | 1:00 | 133 | 10:00 | Sylhet-132 | 128 | 06:00 | 125 | 00:00
Kasba | 124 | 05:00 | 119 | 15:00 | Tangail | 128 | 08:00 | 122 | 00:00
Kazla | 131 | 06:00 | 125 | 12:00 | Thakurgaon | 135 | 19:00 | 121 | 20:00
Keranigonj | 133 | 05:00 | 120 | 16:00 | TK | 133 | 20:00 | 129 | 10:00
Khagrachori | 131 | 15:00 | 128 | 11:00 | Tongi | 134 | 07:00 | 126 | 12:00
Khulna | 134 | 08:00 | 127 | 00:00 | Ullahpara | 134 | 08:00 | 129 | 00:00
Khulna(S) | 136 | 08:00 | 130 | 00:00 | Ullon | 137 | 05:00 | 125 | 11:00
Khulshi | 132 | 00:00 | 127 | 11:00 | Uttara | 131 | 04:00 | 124 | 10:00
Kishoreganj | 129 | 18:00 | 123 | 15:00 | UttaraNew | 130 | 03:00 | 124 | 11:00
Kodda | 138 | 05:00 | 123 | 12:00 | Zigatola | 133 | 06:00 | 127 | 12:00
KSRM | 134 | 19:30 | 130 | 10:00
Kulaura | 134 | 07:00 | 129 | 00:00
Kurigram | 130 | 19:00 | 120 | 09:00
Kushtia | 133 | 09:00 | 126 | 19:00
Lakshmipur | 120 | 4:00 | 110 | 22:00
Lalbag | 133 | 06:00 | 126 | 12:00
Lalmonirhat | 130 | 19:00 | 120 | 09:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division