## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 04-07-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 03-07-2025 | during | 04-07-2025 | during | 04-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 403 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 380 | 380 | Allocation limit by Titas, instructed by DS(Gen)
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 305 | 294 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 333 | 335 | 335 | 330 | 330 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 64 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 17 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 24 | 26 | 33 | 33 | 27 | 27 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 16 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 15 | 80 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 51 | 88 | 105 | 105 | 70 | 90 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 50 | 104 | 104 | 68 | 68 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 90 | 113 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 13 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 54 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 350 | 500 | 584 | 584 | 401 | 401 | FGMO
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage instructed by DS(Gen)
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 90 | 142 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2411 | 2910 | 5110.2 | 5111.2 | 3220.08 | 3241.08
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 11 | 0 | 3 | 0 | 3 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 15 | 33 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 172 | 172 | 165 | 165 | 165 | 165 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 220 | 213 | 213 | 214 | 214 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 46 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 4 | 70 | 48 | 82 | 48 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 65 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 85 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 24 | 35 | 42 | 2 | 2 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 5 | 0 | 5.38 | 0 | 5.38 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 15 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 65 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1158 | 1133 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 57 | 31 | 32 | 35 | 32 | 35 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 205 | 206 | 575 | 575 | 200 | 200 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1935 | 2223 | 3595.1 | 3630.72 | 3158.1 | 3176.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 0 | 0 | 221 | 221 | 0 | 0 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 336 | 349 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 340 | 340 | 340 | 340 | 340 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 20 | 20 | 46.7 | 46.7 | 17 | 17 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 42 | 48 | 55 | 55 | 40 | 40 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 195 | 194 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 60 | 80 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 29 | 37 | 46 | 46 | 46 | 46 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 155 | 173 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 36 | 42 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 25 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 15 | 15 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 64 | 78 | 114 | 114 | 98 | 98 | Engine Problem
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 28 | 113 | 113 | 9 | 28 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 16 | 115 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 69 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1467 | 1591 | 2469.75 | 2399.75 | 1911.55 | 1860.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 03-07-2025 | during | 04-07-2025 | during | 04-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 45 | 49 | 157.5 | 157.5 | 40 | 40 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 100 | 180 | 200 | 200 | 160 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 91 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 37.55 | 0 | 25 | 0 | 25 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 257.55 | 349 | 576.1 | 549 | 408.6 | 381.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage instructed by DS(Gen)
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 148 | 153 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 79 | 83 | 83 | 70 | 70 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 170 | 172 | 160 | 160 | 160 | 160 | Machine Problem
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 18 | 20 | 20 | 16 | 16 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 8 | 8 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 285 | 341 | 341 | 290 | 290 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 380 | 387 | 385 | 385 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1440 | 1452 | 1527 | 1527 | 1393 | 1393
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 888 | 888 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 246 | 232 | 410 | 410 | 210 | 210 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 51 | 105 | 105 | 70 | 70 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 94 | 0 | 65 | 0 | 65 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 560 | 586 | 617.1 | 617.1 | 617.1 | 617.1 | U#2 under shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1826 | 1795 | 2994.1 | 2929.1 | 2199.1 | 2134.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 302 | 301 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 6 | 10 | 10 | 10 | 4 | 4 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1100 | 1244 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 265 | 277 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.65 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 2013.65 | 2189 | 2172 | 2171 | 2114 | 2113
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 42 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 198 | 195 | 220 | 220 | 160 | 160 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 160 | 195 | 220 | 220 | 180 | 180 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 401 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 57 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.09 | 0 | 5.65 | 0 | 5.65 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1220.97 | 1455 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 42.2 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 28 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 2066.26 | 2445 | 2979.52 | 2812.87 | 2838.14 | 2671.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 49 | 50 | 50 | 50 | 50 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 203 | 178 | 200 | 200 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 98 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.2 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 21 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 195 | 0 | 160 | 0 | 160 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 472.2 | 440 | 708 | 512 | 708 | 512
System Total |  |  |  |  | 28565.2 | 27084.055 | 13888.66 | 15394 | 22131.77 | 21642.64 | 17950.57 | 17483.44
Forecast Scenario (04-07-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15220 |  | 0 |  | 15220
|  |  |  | 1:00 | 14820 |  | 0 |  | 14820
|  |  |  | 2:00 | 14442 |  | 0 |  | 14442
|  |  |  | 3:00 | 13980 |  | 0 |  | 13980
|  |  |  | 4:00 | 13660 |  | 0 |  | 13660
|  |  |  | 5:00 | 13220 |  | 0 |  | 13220
|  |  |  | 6:00 | 12030 |  | 0 |  | 12030
|  |  |  | 7:00 | 11580 |  | 0 |  | 11580
|  |  |  | 8:00 | 11260 |  | 0 |  | 11260
|  |  |  | 9:00 | 10900 |  | 0 |  | 10900
|  |  |  | 10:00 | 10930 |  | 0 |  | 10930
|  |  |  | 11:00 | 11140 |  | 0 |  | 11140
|  |  |  | 12:00 | 11920 |  | 0 |  | 11920
|  |  |  | 13:00 | 12530 |  | 0 |  | 12530
|  |  |  | 14:00 | 12150 |  | 0 |  | 12150
|  |  |  | 15:00 | 12150 |  | 0 |  | 12150
|  |  |  | 16:00 | 11640 |  | 0 |  | 11640
|  |  |  | 17:00 | 11320 |  | 0 |  | 11320
|  |  |  | 18:00 | 10730 |  | 0 |  | 10730
|  |  |  | 18:30 | 11400 |  | 0 |  | 11400
|  |  |  | 19:00 | 12080 |  | 0 |  | 12080
|  |  |  | 19:30 | 13710 |  | 0 |  | 13710
|  |  |  | 20:00 | 13770 |  | 0 |  | 13770
|  |  |  | 21:00 | 14060 |  | 0 |  | 14060
|  |  |  | 22:00 | 14150 |  | 0 |  | 14150
|  |  |  | 23:00 | 14260 |  | 0 |  | 14260
Probable Maximum Temperature: |  |  | 31.30°C
Probable Maximum Demand at Day Peak: |  |  | 11920.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14060.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14060.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 303.942 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:37 hrs on 04-07-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 03-07-2025 | [28 empty] | Date: | 03-07-2025 | [28 empty] | Date: | 03-07-2025 | [28 empty] | Date: | 03-07-2025 | [28 empty] | Date: | 03-07-2025 | [12 empty] | Date: | 03-07-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [12 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 54 | 54 | 149 | 80 | 95 | 0 | 55 | 155 | 67 | 380 | 286 | 0 | 0 | 17 | 333 | 0 | 0 | 0 | 142 | 25 | 22 | 0 | 450 | 15 | 100 | 0 | 0 | 28 | 65 | 70 | 17 | 88 | 100 | 0 | 172 | 33 | 30 | 203 | 0 | 0 | 11 | 0 | 98 | 221 | 0 | 0 | 0 | 1156 | 0 | 51 | 12 | 185 | 0 | 352 | 340 | 48 | 0 | 20 | 17 | 0 | 190 | 21 | 20 | 95 | 50 | 52.2 | 0 | 37 | 280 | 320 | 388 | 0 | 0 | 140 | 8 | 0 | 80 | 30 | 0 | 16 | 172 | 35 | 101 | 171 | 49 | 0 | 0 | 12 | 8492.2 | 889 | 217 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 604 | 53 | 1404.64 | 0 | 48 | 0 | 113 | 0 | 96 | 35 | 35 | 0 | 0 | 30 | 0 | 150 | 0 | 186 | 0 | 0 | 0 | 360 | 0 | 0 | 204 | 47 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 10 | 120 | 220 | 0 | 300 | 1110 | 65 | 6875.64 | 15367.84 | 97.28
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 54 | 54 | 149 | 80 | 45 | 0 | 55 | 142 | 68 | 380 | 274 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 125 | 25 | 22 | 0 | 450 | 15 | 100 | 0 | 0 | 54 | 65 | 70 | 17 | 88 | 100 | 0 | 172 | 31 | 30 | 205 | 0 | 0 | 40 | 0 | 91 | 223 | 0 | 0 | 0 | 1110 | 0 | 51 | 12 | 185 | 0 | 354 | 335 | 48 | 0 | 20 | 17 | 0 | 198 | 9 | 20 | 95 | 48 | 52.2 | 0 | 37 | 285 | 320 | 348 | 0 | 0 | 131 | 8 | 0 | 80 | 30 | 0 | 16 | 172 | 35 | 101 | 162 | 49 | 0 | 0 | 12 | 8347.2 | 889 | 222 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 580 | 53 | 1406.65 | 0 | 48 | 0 | 113 | 0 | 81 | 0 | 35 | 0 | 0 | 30 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 327 | 0 | 0 | 205 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 267 | 11 | 110 | 220 | 0 | 300 | 1090 | 65 | 6587.65 | 14934.85 | 97.27
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 54 | 54 | 126 | 48 | 0 | 0 | 55 | 146 | 34 | 340 | 293 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 125 | 25 | 22 | 0 | 400 | 0 | 100 | 0 | 0 | 40 | 0 | 40 | 0 | 76 | 100 | 0 | 172 | 31 | 30 | 205 | 0 | 0 | 40 | 0 | 92 | 223 | 0 | 0 | 0 | 1155 | 0 | 51 | 0 | 185 | 0 | 300 | 340 | 49 | 0 | 20 | 17 | 0 | 199 | 9 | 20 | 95 | 46 | 52.2 | 0 | 29 | 290 | 320 | 323 | 0 | 0 | 134 | 8 | 0 | 80 | 30 | 0 | 16 | 172 | 35 | 101 | 162 | 54 | 0 | 0 | 12 | 7958.2 | 889 | 230 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 606 | 0 | 1424.44 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 4 | 0 | 373 | 0 | 0 | 205 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 10 | 100 | 220 | 0 | 300 | 1120 | 67 | 6440.44 | 14398.64 | 97.26
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 54 | 54 | 115 | 32 | 0 | 0 | 0 | 155 | 32 | 340 | 296 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 125 | 25 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 88 | 100 | 0 | 172 | 0 | 30 | 206 | 0 | 0 | 0 | 0 | 99 | 222 | 0 | 0 | 0 | 1160 | 0 | 51 | 0 | 185 | 0 | 300 | 340 | 49 | 0 | 20 | 17 | 0 | 199 | 9 | 20 | 95 | 44 | 52.2 | 0 | 37 | 295 | 320 | 321 | 0 | 0 | 142 | 8 | 0 | 80 | 30 | 0 | 16 | 172 | 17 | 101 | 162 | 69 | 0 | 0 | 12 | 7679.2 | 889 | 237 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 602 | 0 | 1418.7 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 3 | 0 | 370 | 0 | 0 | 200 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 10 | 100 | 220 | 0 | 301 | 1060 | 65 | 6349.7 | 14028.9 | 97.25
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 54 | 35 | 113 | 16 | 0 | 0 | 0 | 151 | 32 | 340 | 286 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 125 | 25 | 14 | 0 | 400 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 88 | 100 | 0 | 172 | 0 | 32 | 203 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1160 | 0 | 51 | 0 | 185 | 0 | 300 | 335 | 49 | 0 | 20 | 17 | 0 | 198 | 9 | 20 | 95 | 44 | 52.2 | 0 | 33 | 295 | 320 | 320 | 0 | 0 | 138 | 8 | 0 | 80 | 30 | 0 | 16 | 172 | 17 | 65 | 162 | 84 | 0 | 0 | 12 | 7488.2 | 889 | 245 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 592 | 0 | 1410.52 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 3 | 0 | 357 | 0 | 0 | 201 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 10 | 100 | 220 | 0 | 300 | 1106 | 0 | 6265.52 | 13753.72 | 97.24
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 29 | 35 | 113 | 16 | 0 | 0 | 0 | 90 | 33 | 340 | 282 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 108 | 0 | 14 | 0 | 400 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 24 | 100 | 0 | 172 | 0 | 32 | 207 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1150 | 0 | 51 | 0 | 185 | 0 | 300 | 340 | 49 | 0 | 20 | 17 | 0 | 198 | 9 | 20 | 95 | 42 | 52.2 | 0 | 38 | 290 | 320 | 304 | 0 | 0 | 140 | 8 | 0 | 80 | 30 | 0 | 16 | 172 | 17 | 45 | 152 | 77 | 0 | 0 | 12 | 7240.2 | 888 | 257 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 0 | 1408.99 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 41 | 0 | 348 | 0 | 0 | 203 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 9 | 100 | 220 | 0 | 300 | 1107 | 0 | 6204.99 | 13445.19 | 97.23
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 17 | 35 | 106 | 16 | 0 | 0 | 0 | 35 | 16 | 300 | 284 | 0 | 0 | 0 | 280 | 0 | 0 | 1 | 108 | 0 | 14 | 0 | 400 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 24 | 60 | 0 | 172 | 0 | 34 | 204 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1155 | 0 | 51 | 0 | 185 | 0 | 300 | 300 | 49 | 0 | 20 | 17 | 0 | 155 | 9 | 20 | 70 | 36 | 52.2 | 2 | 38 | 300 | 320 | 305 | 0 | 0 | 131 | 8 | 0 | 81 | 30 | 0 | 16 | 172 | 17 | 45 | 152 | 77 | 0 | 1.07 | 12 | 6936.27 | 889 | 260 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 592 | 0 | 1304.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1.59 | 0 | 0 | 185 | 0 | 93 | 0 | 348 | 0 | 0.16 | 201 | 48 | 70 | 2 | 70 | 0 | 0 | 0.4 | 5 | 0.03 | 0 | 201 | 9 | 100 | 220 | 0 | 300 | 1000 | 0 | 5942.7 | 12878.97 | 97.22
07:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 17 | 35 | 96 | 0 | 0 | 0 | 0 | 0 | 16 | 300 | 299 | 0 | 0 | 0 | 280 | 0 | 0 | 5 | 45 | 0 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 24 | 60 | 2 | 172 | 0 | 30 | 206 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1045 | 2 | 51 | 0 | 185 | 0 | 300 | 300 | 50 | 0 | 20 | 17 | 0 | 120 | 9 | 20 | 34 | 34 | 25 | 13 | 38 | 300 | 320 | 340 | 0 | 0 | 137 | 8 | 0 | 81 | 30 | 0 | 16 | 172 | 17 | 45 | 152 | 49 | 0 | 7.35 | 12 | 6710.35 | 889 | 265 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 22 | 565 | 0 | 1248.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 12.77 | 0 | 0 | 186 | 0 | 130 | 0 | 392 | 0 | 1.1 | 200 | 48 | 70 | 3 | 70 | 0 | 0 | 1 | 36 | 0.09 | 0 | 174 | 7 | 100 | 220 | 0 | 302 | 900 | 0 | 5905.91 | 12616.26 | 97.21
08:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 17 | 35 | 78 | 0 | 0 | 0 | 0 | 0 | 16 | 300 | 299 | 0 | 0 | 0 | 280 | 0 | 0 | 19 | 35 | 5 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 24 | 60 | 0 | 172 | 0 | 4 | 206 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1012 | 1 | 51 | 0 | 187 | 0 | 300 | 305 | 49 | 0 | 20 | 46 | 0 | 120 | 10 | 20 | 34 | 32 | 25 | 24 | 38 | 295 | 320 | 323 | 0 | 0 | 147 | 8 | 0 | 80 | 30 | 0 | 16 | 172 | 17 | 45 | 120 | 49 | 0 | 5.12 | 12 | 6615.12 | 889 | 265 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 45 | 519 | 0 | 1212.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8.55 | 0 | 0 | 190 | 0 | 180 | 0 | 375 | 0 | 1.07 | 198 | 46 | 70 | 18 | 70 | 0 | 0 | 1 | 70 | 0.44 | 0 | 173 | 7 | 100 | 220 | 0 | 301 | 900 | 0 | 5931.98 | 12547.1 | 97.2
09:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 35 | 78 | 0 | 0 | 0 | 9 | 0 | 0 | 300 | 299 | 0 | 0 | 0 | 335 | 0 | 0 | 17 | 85 | 14 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 24 | 60 | 0 | 172 | 0 | 2 | 205 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1014 | 7 | 51 | 0 | 185 | 0 | 344 | 305 | 49 | 0 | 20 | 51 | 0 | 120 | 9 | 20 | 33 | 32 | 25 | 18 | 38 | 295 | 320 | 320 | 0 | 0 | 148 | 8 | 0 | 77 | 30 | 0 | 16 | 172 | 17 | 45 | 120 | 49 | 1 | 7.22 | 12 | 6753.22 | 888 | 260 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 58 | 519 | 0 | 1156.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 23.89 | 0 | 0 | 194 | 0 | 194 | 0 | 385 | 0 | 1.71 | 202 | 48 | 35 | 25 | 0 | 0 | 0 | 2.9 | 100 | 0.61 | 0 | 173 | 7 | 100 | 220 | 0 | 302 | 900 | 0 | 5908.39 | 12661.61 | 97.19
10:00 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 35 | 82 | 0 | 0 | 0 | 35 | 45 | 0 | 400 | 288 | 0 | 0 | 0 | 335 | 0 | 0 | 29 | 90 | 20 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 24 | 60 | 2 | 172 | 0 | 2 | 203 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1097 | 6 | 51 | 0 | 185 | 0 | 338 | 340 | 44 | 0 | 20 | 35 | 0 | 123 | 9 | 20 | 33 | 32 | 25 | 47 | 38 | 290 | 320 | 385 | 0 | 0 | 156 | 8 | 0 | 76 | 30 | 0 | 16 | 171 | 17 | 45 | 120 | 49 | 1 | 25.67 | 12 | 7124.67 | 889 | 256 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 75.85 | 520 | 0 | 1092.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 12.49 | 0 | 0 | 200 | 0 | 195 | 0 | 414 | 0 | 1.12 | 205 | 46 | 0 | 11 | 0 | 0 | 0 | 0.6 | 94 | 0.51 | 0 | 212 | 6 | 120 | 220 | 0 | 302 | 950 | 0 | 5889.15 | 13013.82 | 97.18
11:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 4 | 35 | 118 | 0 | 15 | 0 | 35 | 90 | 0 | 400 | 288 | 0 | 0 | 17 | 334 | 0 | 0 | 25 | 90 | 24 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 24 | 60 | 3 | 172 | 0 | 2 | 204 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1090 | 11 | 51 | 32 | 185 | 0 | 340 | 335 | 42 | 0 | 20 | 16 | 0 | 136 | 9 | 20 | 60 | 34 | 25 | 39 | 29 | 290 | 320 | 374 | 0 | 0 | 147 | 8 | 0 | 78 | 30 | 0 | 16 | 171 | 17 | 45 | 100 | 45 | 1 | 26.75 | 12 | 7211.75 | 889 | 251 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 58.5 | 492 | 0 | 1114.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 55.37 | 0 | 0 | 198 | 0 | 181 | 0 | 347 | 0 | 5.66 | 202 | 46 | 0 | 6 | 0 | 0 | 0 | 6.7 | 95 | 0.95 | 0 | 245 | 6 | 120 | 180 | 0 | 302 | 1085 | 0 | 6049.99 | 13261.74 | 97.17
12:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 35 | 149 | 0 | 15 | 0 | 35 | 90 | 0 | 450 | 305 | 0 | 0 | 17 | 330 | 0 | 0 | 13 | 90 | 24 | 14 | 0 | 350 | 0 | 0 | 0 | 0 | 57 | 0 | 4 | 0 | 24 | 65 | 5 | 172 | 0 | 2 | 205 | 0 | 0 | 15 | 0 | 0 | 217 | 0 | 0 | 0 | 1158 | 11 | 51 | 60 | 195 | 0 | 336 | 340 | 42 | 0 | 20 | 16 | 0 | 155 | 9 | 20 | 64 | 36 | 25 | 69 | 29 | 290 | 320 | 380 | 0 | 0 | 148 | 8 | 0 | 78 | 30 | 0 | 16 | 170 | 17 | 45 | 100 | 45 | 1 | 37.55 | 12 | 7510.55 | 888 | 246 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 94 | 560 | 0 | 1220.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 42.2 | 0 | 0 | 198 | 0 | 160 | 0 | 414 | 0 | 3.09 | 203 | 48 | 0 | 21 | 0 | 0 | 0 | 5.2 | 195 | 0.65 | 0 | 265 | 6 | 120 | 220 | 0 | 302 | 1100 | 0 | 6378.11 | 13888.66 | 97.16
13:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 45 | 35 | 149 | 0 | 115 | 0 | 44 | 162 | 22 | 450 | 306 | 0 | 0 | 17 | 330 | 0 | 0 | 35 | 125 | 24 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 44 | 0 | 32 | 0 | 75 | 88 | 1 | 172 | 0 | 5 | 205 | 0 | 0 | 22 | 0 | 0 | 217 | 0 | 0 | 0 | 1123 | 8 | 51 | 70 | 195 | 0 | 342 | 340 | 43 | 0 | 20 | 21 | 0 | 148 | 9 | 20 | 83 | 38 | 28 | 31 | 29 | 295 | 320 | 345 | 0 | 0 | 149 | 8 | 0 | 78 | 30 | 0 | 16 | 170 | 17 | 71 | 105 | 45 | 1 | 55.99 | 12 | 7935.99 | 888 | 237 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 82.06 | 551 | 0 | 1308.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 59.49 | 0 | 0 | 196 | 0 | 160 | 0 | 376 | 0 | 6 | 202 | 48 | 0 | 26 | 0 | 0 | 0 | 1.5 | 145 | 0.21 | 0 | 258 | 4 | 100 | 220 | 0 | 302 | 1100 | 0 | 6397.83 | 14333.82 | 97.15
14:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 47 | 35 | 140 | 30 | 145 | 0 | 55 | 162 | 50 | 450 | 299 | 0 | 0 | 17 | 329 | 0 | 0 | 17 | 125 | 24 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 30 | 0 | 32 | 0 | 75 | 100 | 5 | 172 | 0 | 4 | 205 | 0 | 0 | 50 | 0 | 0 | 218 | 0 | 0 | 0 | 1078 | 3 | 51 | 10 | 195 | 0 | 300 | 335 | 46 | 0 | 20 | 82 | 0 | 145 | 9 | 20 | 95 | 40 | 16 | 68 | 37 | 290 | 320 | 315 | 0 | 0 | 135 | 8 | 0 | 77 | 30 | 0 | 16 | 170 | 17 | 71 | 120 | 45 | 1 | 48.71 | 12 | 7940.71 | 888 | 238 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 33 | 543 | 0 | 1304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 60.6 | 0 | 0 | 196 | 0 | 160 | 0 | 352 | 0 | 5.84 | 204 | 48 | 0 | 19 | 0 | 0 | 0 | 5.5 | 178 | 0.04 | 0 | 219 | 4 | 100 | 220 | 0 | 301 | 1090 | 0 | 6228.98 | 14169.69 | 97.14
15:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 35 | 114 | 32 | 145 | 0 | 55 | 162 | 52 | 450 | 307 | 0 | 0 | 17 | 329 | 0 | 0 | 30 | 125 | 24 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 14 | 0 | 32 | 0 | 75 | 100 | 4 | 172 | 0 | 4 | 203 | 0 | 0 | 50 | 0 | 0 | 217 | 0 | 0 | 0 | 1129 | 2 | 51 | 10 | 194 | 0 | 335 | 340 | 46 | 0 | 18 | 112 | 0 | 168 | 9 | 20 | 94 | 40 | 16 | 38 | 36 | 290 | 320 | 382 | 0 | 0 | 146 | 8 | 0 | 77 | 30 | 0 | 16 | 170 | 17 | 72 | 120 | 45 | 1 | 24.29 | 13 | 8095.29 | 889 | 227 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18.67 | 524 | 0 | 1348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22.03 | 0 | 0 | 194 | 0 | 160 | 0 | 398 | 0 | 1.77 | 153 | 49 | 22 | 19 | 0 | 0 | 0 | 7.6 | 164 | 0.32 | 0 | 225 | 3 | 104 | 220 | 0 | 303 | 1000 | 0 | 6106.39 | 14201.68 | 97.12
16:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 35 | 114 | 32 | 110 | 0 | 55 | 162 | 51 | 450 | 297 | 0 | 0 | 17 | 329 | 0 | 0 | 22 | 125 | 24 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 19 | 0 | 50 | 0 | 75 | 100 | 1 | 172 | 0 | 2 | 205 | 0 | 0 | 50 | 0 | 0 | 217 | 0 | 0 | 0 | 1145 | 3 | 51 | 10 | 195 | 0 | 343 | 340 | 46 | 0 | 20 | 110 | 0 | 163 | 9 | 20 | 94 | 38 | 16 | 22 | 36 | 290 | 320 | 377 | 0 | 0 | 153 | 8 | 0 | 77 | 30 | 0 | 16 | 170 | 17 | 72 | 120 | 47 | 1 | 29.56 | 13 | 8073.56 | 888 | 227 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 11.64 | 506 | 0 | 1313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 28.96 | 0 | 0 | 160 | 0 | 166 | 0 | 394 | 0 | 1.15 | 152 | 49 | 35 | 20 | 0 | 0 | 0 | 6.9 | 45 | 0.21 | 0 | 219 | 7 | 100 | 220 | 0 | 301 | 1000 | 0 | 5954.86 | 14028.42 | 97.1
17:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 35 | 115 | 32 | 110 | 0 | 55 | 162 | 51 | 380 | 298 | 0 | 0 | 17 | 328 | 0 | 0 | 3 | 125 | 24 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 21 | 0 | 67 | 0 | 90 | 100 | 0 | 172 | 0 | 8 | 204 | 0 | 0 | 50 | 0 | 0 | 217 | 0 | 0 | 0 | 1052 | 3 | 51 | 10 | 137 | 0 | 345 | 335 | 46 | 0 | 18 | 115 | 0 | 158 | 9 | 20 | 56 | 36 | 16 | 10 | 36 | 285 | 320 | 375 | 0 | 0 | 152 | 8 | 0 | 77 | 30 | 0 | 16 | 170 | 17 | 75 | 120 | 47 | 0 | 6.01 | 12 | 7785.01 | 889 | 228 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 10.32 | 495 | 0 | 1263 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 17 | 0 | 12.69 | 0 | 0 | 160 | 0 | 160 | 0 | 389 | 0 | 0.91 | 150 | 49 | 35 | 9 | 34 | 0 | 0 | 0.9 | 62 | 0.26 | 0 | 218 | 7 | 94 | 220 | 0 | 301 | 960 | 0 | 5810.08 | 13595.09 | 97.08
18:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17 | 46 | 138 | 32 | 110 | 0 | 55 | 90 | 51 | 300 | 291 | 0 | 0 | 17 | 330 | 0 | 0 | 2 | 108 | 24 | 22 | 0 | 400 | 0 | 15 | 0 | 0 | 26 | 0 | 70 | 0 | 60 | 70 | 0 | 172 | 0 | 13 | 204 | 0 | 0 | 33 | 0 | 6 | 218 | 0 | 0 | 0 | 1000 | 0 | 51 | 10 | 137 | 0 | 320 | 300 | 44 | 0 | 18 | 115 | 0 | 156 | 17 | 18 | 41 | 44 | 16 | 3 | 36 | 285 | 320 | 357 | 0 | 0 | 150 | 8 | 0 | 78 | 30 | 0 | 16 | 170 | 17 | 75 | 112 | 48 | 0 | 3.87 | 12 | 7415.87 | 889 | 227 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9.82 | 486 | 0 | 1262 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 8 | 0 | 2.21 | 0 | 0 | 160 | 0 | 160 | 0 | 337 | 0 | 0.24 | 180 | 49 | 35 | 2 | 34 | 0 | 0 | 0.4 | 13 | 0.04 | 0 | 212 | 5 | 94 | 180 | 0 | 301 | 940 | 0 | 5631.71 | 13047.58 | 97.06
19:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 45 | 54 | 132 | 80 | 110 | 4 | 55 | 79 | 50 | 300 | 307 | 0 | 0 | 17 | 305 | 0 | 0 | 0 | 142 | 24.5 | 22 | 0 | 400 | 3 | 15 | 0 | 0 | 36 | 58 | 70 | 0 | 83 | 100 | 0 | 172 | 6 | 11 | 204 | 0 | 0 | 33 | 0 | 19 | 219 | 0 | 0 | 0 | 1093 | 0 | 51 | 28 | 179 | 0 | 340 | 335 | 46 | 0 | 20 | 115 | 0 | 165 | 27 | 20 | 55 | 52 | 16 | 0 | 36 | 290 | 320 | 389 | 0 | 0 | 149 | 8 | 0 | 78 | 30 | 0 | 16 | 171 | 17 | 91 | 158 | 48 | 0 | 0 | 12 | 8015.5 | 889 | 227 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 508 | 24 | 1409 | 0 | 0 | 0 | 6 | 0 | 45 | 0 | 15 | 0 | 0 | 28 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 382 | 0 | 0 | 182 | 49 | 90 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 8 | 110 | 180 | 0 | 301 | 960 | 17 | 6114 | 14129.5 | 97.04
19:30 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 54 | 54 | 149 | 80 | 110 | 15 | 55 | 112 | 50 | 450 | 293 | 0 | 0 | 17 | 332 | 0 | 0 | 0 | 142 | 26 | 22 | 0 | 500 | 15 | 15 | 0 | 0 | 34 | 65 | 70 | 0 | 83 | 100 | 0 | 172 | 9 | 13 | 205 | 0 | 0 | 33 | 1 | 45 | 219 | 0 | 0 | 0 | 1113 | 0 | 51 | 70 | 189 | 0 | 347 | 335 | 47 | 0 | 20 | 115 | 0 | 166 | 29 | 20 | 71 | 50 | 16 | 0 | 37 | 290 | 320 | 366 | 0 | 0 | 152 | 8 | 0 | 78 | 30 | 0 | 16 | 171 | 17 | 92 | 158 | 48 | 0 | 0 | 12 | 8481 | 889 | 227 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 584 | 35 | 1456 | 0 | 0 | 0 | 30 | 0 | 57 | 0 | 25 | 0 | 0 | 28 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 395 | 0 | 0 | 183 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 10 | 116 | 220 | 0 | 301 | 1130 | 54 | 6610 | 15091
20:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 51.4 | 54 | 149 | 80 | 110 | 15 | 55 | 103 | 50 | 450 | 291 | 0 | 0 | 17 | 333 | 0 | 0 | 0 | 142 | 26 | 22 | 0 | 500 | 15 | 15 | 0 | 0 | 28 | 65 | 70 | 0 | 84 | 100 | 0 | 172 | 15 | 18 | 205 | 0 | 0 | 33 | 4 | 49 | 220 | 0 | 0 | 0 | 1131 | 0 | 51 | 60 | 190 | 0 | 348 | 335 | 47 | 0 | 20 | 115 | 0 | 181 | 28 | 20 | 78 | 32 | 16 | 0 | 37 | 290 | 320 | 363 | 0 | 0 | 155 | 8 | 0 | 79 | 30 | 0 | 18 | 171 | 17 | 100 | 159 | 48 | 0 | 0 | 12 | 8506.4 | 889 | 227 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 589 | 51 | 1460 | 0 | 42 | 0 | 61 | 0 | 57 | 0 | 37 | 0 | 0 | 28 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 394 | 0 | 0 | 180 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 10 | 120 | 220 | 0 | 301 | 1190 | 54 | 6780 | 15286.4 | 97.02
21:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 54 | 54 | 149 | 64 | 80 | 0 | 55 | 113 | 50 | 450 | 294 | 0 | 0 | 17 | 333 | 0 | 0 | 0 | 142 | 26 | 22 | 0 | 500 | 0 | 15 | 0 | 0 | 31 | 65 | 70 | 0 | 85 | 100 | 0 | 172 | 15 | 24 | 206 | 0 | 0 | 33 | 8 | 46 | 220 | 0 | 0 | 0 | 1133 | 0 | 51 | 80 | 194 | 0 | 349 | 340 | 48 | 0 | 20 | 115 | 0 | 173 | 28 | 20 | 78 | 42 | 16 | 0 | 37 | 285 | 320 | 387 | 0 | 0 | 153 | 8 | 0 | 79 | 30 | 0 | 18 | 172 | 17 | 91 | 180 | 49 | 0 | 0 | 12 | 8525 | 888 | 232 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 51 | 1455 | 0 | 42 | 0 | 35 | 0 | 57 | 0 | 37 | 0 | 0 | 28 | 0 | 0 | 0 | 195 | 0 | 195 | 0 | 401 | 0 | 0 | 178 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 10 | 120 | 220 | 0 | 301 | 1244 | 17 | 6869 | 15394 | 97
22:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 54 | 47 | 149 | 64 | 80 | 0 | 55 | 116 | 54 | 450 | 299 | 0 | 0 | 17 | 333 | 0 | 0 | 0 | 142 | 26 | 22 | 0 | 500 | 0 | 15 | 0 | 0 | 36 | 65 | 70 | 0 | 98 | 88 | 0 | 172 | 0 | 26 | 204 | 0 | 0 | 33 | 8 | 48 | 221 | 0 | 0 | 0 | 1126 | 0 | 51 | 80 | 195 | 0 | 353 | 335 | 48 | 0 | 20 | 109 | 0 | 178 | 29 | 20 | 78 | 42 | 30 | 0 | 38 | 285 | 320 | 365 | 0 | 0 | 155 | 8 | 0 | 79 | 30 | 0 | 18 | 172 | 17 | 91 | 190 | 49 | 0 | 0 | 12 | 8522 | 889 | 227 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 591 | 51 | 1444 | 0 | 42 | 0 | 35 | 0 | 57 | 0 | 37 | 0 | 0 | 28 | 0 | 0 | 0 | 197 | 0 | 196 | 0 | 398 | 0 | 0 | 178 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 11 | 120 | 220 | 0 | 301 | 1244 | 0 | 6842 | 15364 | 96.98
23:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 54 | 29 | 149 | 64 | 80 | 0 | 55 | 110 | 67 | 450 | 305 | 0 | 0 | 17 | 334 | 0 | 0 | 0 | 142 | 25.5 | 22 | 0 | 500 | 0 | 15 | 0 | 0 | 30 | 65 | 70 | 0 | 100 | 88 | 0 | 172 | 0 | 31 | 203 | 0 | 0 | 33 | 8 | 45 | 223 | 0 | 0 | 0 | 1138 | 0 | 51 | 80 | 195 | 0 | 354 | 335 | 48 | 0 | 20 | 66 | 0 | 199 | 28 | 20 | 78 | 44 | 52.2 | 0 | 38 | 290 | 320 | 387 | 0 | 0 | 151 | 8 | 0 | 79 | 30 | 0 | 18 | 173 | 17 | 90 | 190 | 49 | 0 | 0 | 12 | 8534.7 | 889 | 224 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 51 | 1419 | 0 | 42 | 0 | 35 | 0 | 57 | 0 | 37 | 0 | 0 | 28 | 0 | 0 | 0 | 197 | 0 | 196 | 0 | 408 | 0 | 0 | 178 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 11 | 120 | 220 | 0 | 300 | 1160 | 0 | 6737 | 15271.7 | 96.96
Total KWH | 0 | 1193280 | 381600 | 0 | 0 | 0 | 0 | 0 | 9817200 | 0 | 0 | 785880 | 983520 | 3008592 | 792480 | 1390538 | 22329 | 892146 | 2553120 | 892800 | 9106000 | 7115782 | 0 | 0 | 271828 | 7816867 | 0 | 0 | 188777 | 2754000 | 472800 | 486360 | 0 | 10429545.45 | 45164 | 398945 | 0 | 0 | 820800 | 412160 | 803566 | 27332 | 152256 | 2075520 | 17730 | 4118280 | 132980 | 401280 | 4967272.73 | 0 | 0 | 592800 | 38930.4 | 605527 | 5142839 | 0 | 0 | 0 | 26618178 | 62640 | 1187895 | 719272 | 4466128 | 0 | 8204500 | 8030000 | 1122720 | 0 | 483120 | 1386240 | 0 | 4044960 | 347760 | 453800 | 1753320 | 953280 | 797938 | 411282 | 852512 | 6977500 | 7663400 | 8813000 | 0 | 0 | 3517118 | 184680 | 0 | 1881600 | 711648 | 0 | 398000 | 4527740 | 483120 | 1731600 | 3374400 | 1198080 | 9800 | 238810 | 301200 | 186016067.58 | 21514181 | 5796864 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 130896 | 542160 | 13389090 | 377760 | 31867564 | 0 | 244981 | 0 | 765888 | 0 | 449024 | 25248 | 194944 | 0 | 577680 | 181040 | 356256 | 0 | 0 | 4660482 | 0 | 3432909 | 0 | 9121381 | 0 | 31320 | 4597000 | 1104000 | 1624240 | 203602 | 1393411 | 0 | 0 | 35041.8 | 1195200 | 3846 | 0 | 5695000 | 190156 | 2579000 | 5369980 | 0 | 7250909.09 | 26157090.91 | 300000 | 152270144.8 | 338286212.38

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 03-07-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13888.66 | MW | 12:00 Hr. | Energy Generated |  |  | 338.2862 |  | MKWHr.
| Day Peak Demand |  |  | 13888.66 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.736 |  | MKWHr.
| Evening Peak Generation |  |  | 15394 | MW | 21:00 Hr. | Energy Demand |  |  | 339.0222 |  | MKWHr.
| Evening Peak Demand |  |  | 15465 | MW | 21:00 Hr. | Maximum Temperature |  |  | 32.5 |  | °C
| Minimum Generation of the Day |  |  | 12547.1 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 1015.56 |  | MMCFD
| Maximum Generation of the Day |  |  | 15394 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.5399 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 45.2446 | 0 | 15.9221 | 0 | 0 | 0.18878 | 0 | 0 | 61.3554 | Gas | 141.7604 | Gas | 503953795.6265
| Chattogram Zone |  |  | 5.5441 | 31.5855 | 5.2852 | 0 | 4.1183 | 0.08037 | 0 | 0.8208 | 47.4342 | Coal | 89.7785 | Coal | 557698678.6255
| Cumilla Zone |  |  | 23.9482 | 0 | 9.902 | 0 | 0 | 0.41128 | 0.95328 | 0 | 35.2147 | HFO | 42.687 | HFO | 799140546.978
| Mymensingh Zone |  |  | 1.1981 | 0 | 5.8903 | 0 | 0 | 0.24861 | 0 | 0 | 7.337 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 34.6747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.6747 | Hydro | 4.1183 | Hydro | 411828
| Khulna Zone |  |  | 5.7969 | 13.3891 | 0.50866 | 0 | 0 | 0.54216 | 22.4262 | 0 | 42.663 | Solar | 3.8741 | Solar | 63008290.108
| Barishal Zone |  |  | 8.1391 | 39.103 | 0.3 | 0 | 0 | 0.003846 | 0 | 0 | 47.546 | Import | 55.247 | Import | 276136232.19
| Rajshahi Zone |  |  | 17.2148 | 0 | 1.8611 | 0 | 0 | 0.96526 | 31.8676 | 0 | 51.9087 | Wind | 0.8208 | Wind | 12016512
| Rangpur Zone |  |  | 0 | 5.701 | 3.0177 | 0 | 0 | 1.4338 | 0 | 0 | 10.1525
| Total |  |  | 141.7604 | 89.7785 | 42.687 | 0 | 4.1183 | 3.8741 | 55.247 | 0.8208 | 338.2862
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 503953795.6265 |  | Hydro | 411828
|  |  |  | Coal | 557698678.6255 |  | Solar | 63008290.108
|  |  |  | HFO | 799140546.978 |  | Import | 276136232.19
|  |  |  | HSD | 0 |  | Wind | 12016512
[5 empty] | Total: | 221,23,65,883 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5142 | Peak Hr Flow | 888.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 39655763.73 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 31.8676 | Peak Hr Flow | 1455.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 836 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.95328 | Peak Hr Flow | 42.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 998 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 54.335 | Peak Hr Flow | 2385.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 5 |  | 5192
|  |  |  | Chattogram |  | 0 |  | 1407
|  |  |  | Cumilla |  | 0 |  | 1418
|  |  |  | Mymensingh |  | 20 |  | 1242
|  |  |  | Sylhet |  | 0 |  | 632
|  |  |  | Khulna |  | 0 |  | 1818
|  |  |  | Barishal |  | 0 |  | 478
|  |  |  | Rajshahi |  | 0 |  | 1520
|  |  |  | Rangpur |  | 43 |  | 1086
|  |  |  | Total |  | 68 |  | 14793
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[7 empty] | 5 | Sirajgonj 225MW CCPP Unit-3 ST |  |  | 79
[5 empty] | Total | 300 |  |  |  | Total | 555
|  |  |  | Total Unavailable Capacity |  |  |  | 855
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 10:54 | 11:09 | Magura 132/33kV S/S T-3 (425T) LT Tripped showing Non directional earth fault & general | [7 empty] | 32.0MW load
|  |  | trip. relays Due to PBS Rawtara 33kV over current earth fault. | [7 empty] | interrup.
| 11:07 | 12:10 | Kurigram 132/33kV S/S Transformer T-1 (Tr-403T) HT Forced S/D Due to due to tempareture
high at 132kv CT PT and 33kv CT,PT,DS
| 12:00 |  | Day Peak Generation 13886 MW.
| 12:25 |  | Gopalganj 400/132kV S/S 400kV Rooppur Scheduled S/D Due to Equipment Testing at Rooppur
Power Station
| 13:28 | 13:56 | Sreepur 230/132/33kV S/S 132/33 kV T-1 LT Forced S/D Due to Jaek bus repair
| 13:29 | 13:55 | Sreepur 230/132/33kV S/S 132/33 kV T-1 HT Forced S/D Due to jaek bus Repair
| 14:14 | 14:32 | Barishal 132/33kV S/S T-1 (405T) LT Tripped showing O/C , E/F relays Due to Dopdopia 2 | [7 empty] | 45.0MW load
|  |  | 33kV feeder fault. | [7 empty] | interrup.
| 14:25 | 16:46 | Natore-Rajshahi 132kV Ckt-1 Scheduled S/D from Natore 132/33kV end Due to CB DC Cable
change work for earth fault and from Rajshahi 132/33kV end Due to shut down taken by
Natore end
| 14:25 |  | Laksham 132/33 kV T-2 (80/120 MVA) transformer was charged in no-load condition
for the first time.
| 14:25 |  | Laksham 132/33 kV T-2 (80/120 MVA) transformer was charged in no-load condition
for the first time.
| 14:29 | 15:59 | Bajitpur 132/33kV S/S Tr-1(404T) LT Scheduled S/D Due to Feeder Bus DS supporting | [7 empty] | 28.0MW load
|  |  | insulator change | [7 empty] | interrup.
| 14:43 | 16:57 | Mahasthangarh 132/33kV S/S 406T MTR1 HT Scheduled S/D Due to 33 kv Bpbs-2 Sukanpukur | [7 empty] | 30.0MW load
|  |  | Feeder Bus ds Damage | [7 empty] | interrup.
|  | 15:38 | Bhulta-Narsingdi 132 kV Ckt-1 is restored.
| 15:46 | 16:49 | Mongla 132/33kV S/S T-1 LT Forced S/D Due to T-1 TTB Change by BPDB. | [7 empty] | 7.5MW load
interrup.
| 15:47 | 16:48 | Mongla 132/33kV S/S T-1 HT Forced S/D Due to T-1 TTB change by BPDB. | [7 empty] | 7.5MW load
interrup.
| 15:51 | 16:17 | Baroaulia 132/33kV S/S T-1(405T) HT Scheduled S/D Due to T-1 circuit breaker change work
| 16:15 | 18:11 | Bajitpur 132/33kV S/S Tr-2(414T) LT Scheduled S/D | [7 empty] | 11.0MW load
interrup.
| 16:38 | 18:18 | Khulna(S)-PDB 330MW CCPP 230kV Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end Due to
DFDR Integration work
|  | 16:48 | Mongla 132/33kV S/S T-1 HT is restored.
| 16:52 | 17:35 | Cumilla(N) 230/132/33kV S/S 132KV T-03 HT Tripped showing Overcurrent Relay relays Due to | [7 empty] | 40.0MW load
|  |  | 33 KV Summit Jungalia Feeder DS loop blast | [7 empty] | interrup.
| 16:52 | 19:28 | Cumilla(N) 230/132/33kV S/S 132KV T-04 LT Tripped showing Overcurrent relay relays Due to | [7 empty] | 40.0MW load
|  |  | 33 KV Summit Jungalia Feeder DS loop blast | [7 empty] | interrup.
| 16:52 | 17:35 | Cumilla(N) 230/132/33kV S/S 132KV T-03 LT Tripped showing Overcurrent relay relays. | [7 empty] | 40.0MW load
interrup.
| 16:58 | 19:02 | Hasnabad 132/33kV S/S 33kv Reserve Bus Scheduled S/D
| 17:51 | 18:58 | Madunaghat 132/33kV S/S TR-2(517T) LT Forced S/D Due to Insolator Maintenance of Ononna | [7 empty] | 3.0MW load
|  |  | Feder. Shut Down by PDB. | [7 empty] | interrup.
| 19:21 |  | Raozan 25 MW PP Synchronized
| 22:01 | 23:46 | Jaldhaka 132/33kV S/S 406T-1 LT Forced S/D Due to 33KV BUS section-01 shutdown for PBS | [7 empty] | 40.0MW load
|  |  | Dimla 33KV Feeder Red hot maintenance work. | [7 empty] | interrup.
| 22:02 | 23:45 | Jaldhaka 132/33kV S/S 406T-1 HT Forced S/D Due to 33KV BUS section-01 shutdown for PBS | [7 empty] | 40.0MW load
|  |  | Dimla 33KV Feeder Red hot maintenance work. | [7 empty] | interrup.
| 00:40 |  | Raozan 25 MW PP Shutdown
| 01:32 |  | Sirajgonj 225MW CCPP Unit-3 ST Tripped with remarks:- Due to malfunction at HRSG Diverter
Damper Emergency Trip System
| 01:53 |  | Madaripur 132/33kV S/S T3-426T LT Tripped showing PRD relays Due to PRD trip
| 01:53 |  | Madaripur 132/33kV S/S T3-426T HT Tripped showing PRD relays Due to PRD trip
| 06:28 |  | Haripur-Meghnaghat 230kV Ckt-2 Scheduled S/D from Haripur 230/132kV end Due to Three Set
Isolator (3000amp) Replaced.
| 06:32 |  | Rahanpur 400/132kV S/S Rahanpur-Monakasha 400KV Line ckt-02 Scheduled S/D Due to
Maintenance work at Ahdani power plant side.
| 07:00 |  | Minimum Generation is 12012 MW
| 07:17 |  | Sylhet 132/33kV S/S T1 HT Scheduled S/D Due to T-1 33 KV bus "Y" phase conductor change. | [7 empty] | 24.0MW load
interrup.
| 07:17 |  | Kabirpur 132/33kV S/S XFR, T-3 HT Scheduled S/D Due to 33 BUS DS Change work | [7 empty] | 30.0MW load
interrup.
| 07:17 |  | Sylhet 132/33kV S/S T1 LT Scheduled S/D Due to T-1 33 KV bus "Y" phase conductor change. | [7 empty] | 24.0MW load
interrup.
| 07:39 |  | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Red hot Maintenance . | [7 empty] | 45.0MW load
interrup.
| 07:39 |  | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Red hot Maintenance. | [7 empty] | 45.0MW load
interrup.
| 07:52 |  | Chowmuhani-Feni 132 kV Ckt-1 Project Work S/D from Daganbhuiyan 132/33kV end Due to ফেনী
সার্কিট -1 ৪২ - ৪৩ নং টাওয়ারের মাঝে R ফেজ এর কাজের জন্য TB EA প্রজেক্ট শাটডাউন নেয়
| 07:55 |  | Mirpur 132/33kV S/S Main Bus Project Work S/D Due to 132kV T3 Main Bus DS Installation in
by G2G
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 03-07-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 403 | 9817200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9106000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 294 | 7115782 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 22329 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 333 | 7816867 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 785880 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 64 | 792480 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 892146 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 271828 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 26 | 472800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 486360 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 381600 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 80 | 1390538 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3008592 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1193280 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 50 | 892800 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 113 | 2553120 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 188777 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 983520 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 500 | 10429545.45 | None
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage instructed by DS(Gen)
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 142 | 2754000 | Dirty Fuel
Dhaka Area Total |  |  |  |  | 5939.724 | 2910 | 61355444.45
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 38930.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 62640 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 592800 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 172 | 4118280 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 5142839 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 46 | 605527 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 70 | 803566 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 412160 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 85 | 152256 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 24 | 401280 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 17730 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 398945 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 27332 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 15 | 132980 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2075520 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 45164 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1133 | 26618178 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 31 | 820800 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 206 | 4967272.73 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4895.72 | 2223 | 47434200.13
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 0 | 0 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 349 | 8204500 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 8030000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 20 | 483120 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 48 | 1122720 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 194 | 4466128 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1187895 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 80 | 719272 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 37 | 852512 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 173 | 4044960 | -
| Import (Tripura) |  | Import | 0 | 160 | 42 | 953280 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 16 | 797938 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 453800 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 78 | 1753320 | Engine Problem
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 347760 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1386240 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 411282 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1591 | 35214727
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 49 | 1198080 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9800 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 180 | 3374400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 91 | 1731600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 238810 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 301200 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 483120 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 349 | 7337010
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | Gas shortage instructed by DS(Gen)
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 153 | 3517118 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 711648 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 1881600 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 172 | 4527740 | Machine Problem
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 398000 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 184680 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 6977500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 387 | 8813000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7663400 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1452 | 34674686
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 888 | 21514181 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 232 | 5796864 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 51 | 377760 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 130896 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 542160 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 586 | 13389090 | U#2 under shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1795 | 42662951
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 301 | 7250909.09 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 10 | 190156 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2579000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 26157090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5369980 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 300000 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 277 | 5695000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3846 | -
Barishal Area Total |  |  |  |  | 2236 | 2189 | 47545982
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 42 | 244981 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 194944 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 195 | 4660482 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 195 | 3432909 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 401 | 9121381 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 181040 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 57 | 449024 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 765888 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 25248 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 31320 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1455 | 31867564 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 356256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 577680 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2445 | 51908717
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 49 | 1104000 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 178 | 4597000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 1393411 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 35041.8 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1624240 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 203602 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1195200 | -
Rangpur Area Total |  |  |  |  | 950 | 440 | 10152494.8
Eastern Grid Total |  |  |  |  | 16705.895 | 8525 | 186016067.58
Western Grid Total |  |  |  |  | 10378.16 | 6869 | 152270144.8
National Grid Total |  |  |  |  | 27084.055 | 15394 | 338286212.38
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 03-07-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9866.46 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4857.9 | MW
i) Dhaka area |  |  | 5187.18 |  | MW | i) Khulna area |  |  |  | 1817.6 | MW
ii) Chattogram area |  |  | 1407 |  | MW | ii) Barishal area |  |  |  | 477.7 | MW
iii) Cumilla area |  |  | 1418.28 |  | MW | iii) Rajshahi area |  |  |  | 1519.6 | MW
iv) Mymensingh area |  |  | 1222 |  | MW | iv) Rangpur area |  |  |  | 1043 | MW
v) Sylhet area |  |  | 632 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14724.36 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 80 | 00:00 | 133 | Pabna | 128 | 19:30
2 | AKSML | 133 | 09:00 | 68 | Ishurdi | 79 | 00:00 | 134 | Palashbari | 117 | 23:00
3 | Aftabnagar | 38 | 13:00 | 69 | Jaldhaka | 96 | 00:00 | 135 | Panchagarh | 69 | 20:00
4 | Agargaon | 131 | 13:00 | 70 | Jamalpur | 135 | 22:00 | 136 | Patuakhali | 79.5 | 22:00
5 | Agrabad | 92 | 15:00 | 71 | Jashore | 144 | 21:00 | 137 | Payra | 34 | 00:00
6 | Amnura | 44 | 00:00 | 72 | Jhenaidah | 133 | 19:30 | 138 | Postogola | 59 | 16:00
7 | Ashuganj | 94 | 13:00 | 73 | Joydebpur | 147 | 15:00 | 139 | Purbachal | 21 | 00:00
8 | BSRM | 198 | 09:00 | 74 | Joypurhat | 69 | 00:00 | 140 | Purbasadipur | 151 | 23:00
9 | Bagerhat | 86 | 00:00 | 75 | Juldah | 15 | 00:00 | 141 | Rahanpur | 32 | 00:00
10 | Bajitpur | 71 | 20:00 | 76 | KSRM | 22 | 18:00 | 142 | Rahim | 34 | 17:00
11 | Bakulia | 91 | 15:00 | 77 | Kabirpur | 227 | 10:00 | 143 | Rajbari | 82 | 23:00
12 | Banani | 40 | 12:00 | 78 | Kachua | 92 | 22:00 | 144 | Rajendrapur | 139 | 19:00
13 | Bangabhaban | 17 | 10:00 | 79 | Kallyanpur | 102 | 00:00 | 145 | Rajshahi | 120 | 00:00
14 | Barapukuria | 68 | 23:00 | 80 | Kalurghat | 40 | 11:00 | 146 | Rajshahi-230 | 90 | 00:00
15 | Barguna | 24 | 00:00 | 81 | Kamrangirchar | 70.3 | 13:00 | 147 | Ramganj | 114 | 22:00
16 | Barishal | 101 | 19:00 | 82 | Kaptai | N/A | N/A | 148 | Rampur | 38 | 02:00
17 | Barishal-230 | 110 | 21:00 | 83 | Kasba | 37 | 22:00 | 149 | Rangamati | 15 | 19:00
18 | Baroaulia | 68 | 10:00 | 84 | Kazla | 95 | 16:00 | 150 | Rangpur | 148 | 01:00
19 | Baroirhat | 60 | 19:00 | 85 | Keranigonj | 104 | 19:30 | 151 | Ruppur | 7.4 | 16:00
20 | Bashundhara | 193 | 16:00 | 86 | Khagrachori | 32 | 19:30 | 152 | SSM | 16 | 07:00
21 | BashundharaCement | 12 | 00:00 | 87 | Khulna | 69 | 00:00 | 153 | Saidpur | 106 | 19:30
22 | Beanibazar | 86 | 19:00 | 88 | Khulshi | 153 | 15:00 | 154 | Satkhira | 129 | 22:00
23 | Benapole | 70 | 22:00 | 89 | Kishoreganj | 142 | 00:00 | 155 | Satmasjid | 102 | 14:00
24 | Bhaluka | 157 | 19:30 | 90 | Kodda | 302 | 12:00 | 156 | Savar | 227 | 16:00
25 | Bhandaria | 57 | 00:00 | 91 | Kulaura | 56 | 00:00 | 157 | SevenRings | 17.74 | 18:00
26 | Bhangura | 38 | 19:30 | 92 | Kurigram | 74 | 23:00 | 158 | ShahCement | 21 | 18:00
27 | Bheramara(GK) | 69 | 21:00 | 93 | Kushtia | 161 | 19:30 | 159 | Shahjadpur | 86 | 19:30
28 | Bhulta | 245 | 22:00 | 94 | Lakshmipur | N/A | N/A | 160 | Shahjibazar | 132 | 21:00
29 | Bog-Sherpur | 68 | 00:00 | 95 | Lalbag | 58 | 13:00 | 161 | Shahmirpur | 62 | 00:00
30 | Bogura | 184 | 20:00 | 96 | Lalmonirhat | 70 | 02:00 | 162 | Shariatpur | 90 | 22:00
31 | Borhanuddin | 88 | 22:00 | 97 | MI_Cement | 13 | 10:00 | 163 | Sherpur | 160 | 00:00
32 | Brahmanbaria | 130 | 21:00 | 98 | Madanganj | 52 | 10:00 | 164 | Shikalbaha | 16 | 12:00
33 | Cantonment | 156 | 12:00 | 99 | Madaripur | 115 | 23:00 | 165 | Shitalakhya | 85.2 | 12:00
34 | Chandina | 15.17 | 22:00 | 100 | Madartek | 92 | 00:00 | 166 | Sholosohor | 47 | 19:00
35 | Chandpur | 78 | 00:00 | 101 | Madunaghat | 54 | 15:00 | 167 | Shyampur | 174 | 10:00
36 | Chandraghona | 36 | 21:00 | 102 | Magura | 67 | 19:30 | 168 | Siddhirganj | 118 | 16:00
37 | Chapai | 75 | 00:00 | 103 | Mahasthangarh | 90 | 23:00 | 169 | Sirajganj | 109 | 21:00
38 | Charsaidpur | 39 | 11:00 | 104 | Maijdee | 14 | 20:00 | 170 | Sonargaon | 95 | 00:00
39 | Chauddagram | 72 | 22:00 | 105 | Manikganj | 127 | 22:00 | 171 | Sreemongol | 82 | 22:00
40 | Chhatak | 45 | 23:00 | 106 | Maniknagar | 86 | 13:00 | 172 | Sreepur | 102 | 19:30
41 | Chowmuhani | 198 | 21:00 | 107 | Matarbari | 46 | 00:00 | 173 | Srinagar | 48.94 | 22:00
42 | Chuadanga | 113 | 00:00 | 108 | Matuail | 64 | 01:00 | 174 | Sunamganj | 65 | 19:30
43 | Coxsbazar | 131 | 00:00 | 109 | Millgate | 112 | 12:00 | 175 | Sylhet | 54 | 19:30
44 | Cumilla(N) | 153 | 22:00 | 110 | Mirpur | 122 | 16:00 | 176 | Sylhet-132 | 139 | 19:00
45 | Cumilla(S) | 177 | 19:30 | 111 | Mirsorai | 10 | 15:00 | 177 | TK | 33 | 22:00
46 | Daganbhuiyan | 0 | 14:00 | 112 | Mirzapur | 46 | 22:00 | 178 | Tangail | 186 | 22:00
47 | Daudkandi | 156 | 23:00 | 113 | Mithapukur | 75 | 20:00 | 179 | Taraganj | 25 | 23:00
48 | Dhaka | 78 | 13:00 | 114 | Modern | N/A | N/A | 180 | Thakurgaon | 119 | 22:00
49 | Dhamrai | 132 | 19:30 | 115 | Mogbazar | 147.6 | 16:00 | 181 | Tongi | 135 | 00:00
50 | Dhanmondi | 149 | 13:00 | 116 | Mongla | 43 | 11:00 | 182 | Ullahpara | 40 | 20:00
51 | Dohazari | 101 | 00:00 | 117 | Motijheel | 43 | 13:00 | 183 | Ullon | 41 | 00:00
52 | Faridpur | 160 | 00:00 | 118 | Muktagacha | 40 | 19:30 | 184 | Uttara | 87 | 13:00
53 | Fatullah | 99 | 16:00 | 119 | Munshiganj | 110 | 00:00 | 185 | UttaraNew | 61 | 00:00
54 | Fenchuganj | 49 | 00:00 | 120 | Muradnagar | 30 | 21:00 | 186 | Zigatola | 78 | 19:00
55 | Feni | 117 | 19:00 | 121 | Mymensingh | 210 | 23:00
56 | GPH | 84 | 19:00 | 122 | Naogaon | 139 | 00:00
57 | Ghatail | 82 | 19:30 | 123 | Narail | 57 | 21:00
58 | Ghorashal | 15 | 00:00 | 124 | Narinda | 78 | 13:00
59 | Ghorashal-230 | 87 | 21:00 | 125 | Narshingdi | 185 | 23:00
60 | Goalpara | 39 | 00:00 | 126 | Natore | 158 | 00:00
61 | Gollamari | 96 | 00:00 | 127 | Nawabganj | 61.4 | 22:00
62 | Gopalganj | 107 | 19:30 | 128 | Netrakona | 132 | 19:00
63 | Gulshan | 124 | 13:00 | 129 | New | 62.4 | 15:00
64 | Halishahar | 73 | 18:30 | 130 | Niamatpur | 82 | 00:00
65 | HaripurSBU | 167 | 01:00 | 131 | Noapara | 44 | 19:30
66 | Hasnabad | 61 | 16:00 | 132 | PHP | 7 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 03-07-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15367.84 | 137 |  | 15511.01
1:00 | 14934.85 | 130 |  | 15070.7
2:00 | 14398.64 | 117 |  | 14520.64
3:00 | 14028.9 | 88 |  | 14120.9
4:00 | 13753.72 | 35 |  | 13790.72
5:00 | 13445.19 | 0 |  | 13445.19
6:00 | 12878.97 | 0 |  | 12878.97
7:00 | 12616.26 | 0 |  | 12616.26
8:00 | 12547.1 | 0 |  | 12547.1
9:00 | 12661.61 | 0 |  | 12661.61
10:00 | 13013.82 | 0 |  | 13013.82
11:00 | 13261.74 | 0 |  | 13261.74
12:00 | 13888.66 | 0 |  | 13888.66
13:00 | 14333.82 | 0 |  | 14333.82
14:00 | 14169.69 | 0 |  | 14169.69
15:00 | 14201.68 | 0 |  | 14201.68
16:00 | 14028.42 | 0 |  | 14028.42
17:00 | 13595.09 | 0 |  | 13595.09
18:00 | 13047.58 | 0 |  | 13047.58
19:00 | 14129.5 | 0 |  | 14129.5
19:30 | 15091 | 37 |  | 15130
20:00 | 15286.4 | 61 |  | 15350.4
21:00 | 15394 | 68 |  | 15465
22:00 | 15364 | 53 |  | 15419.39
23:00 | 15271.7 | 47 |  | 15320.82
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 03-07-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8492.2 | 6875.64 | 15367.84 | DAILY GENERATION CURVE
00:30 | 8419.7 | 6731.645 | 15151.345
01:00 | 8347.2 | 6587.65 | 14934.85 | 03-07-2025
01:30 | 8152.7 | 6514.045 | 14666.745
02:00 | 7958.2 | 6440.44 | 14398.64
02:30 | 7818.7 | 6395.07 | 14213.77
03:00 | 7679.2 | 6349.7 | 14028.9
03:30 | 7583.7 | 6307.61 | 13891.31
04:00 | 7488.2 | 6265.52 | 13753.72
04:30 | 7364.2 | 6235.255 | 13599.455
05:00 | 7240.2 | 6204.99 | 13445.19
05:30 | 7088.235 | 6073.845 | 13162.08
06:00 | 6936.27 | 5942.7 | 12878.97
06:30 | 6823.31 | 5924.305 | 12747.615
07:00 | 6710.35 | 5905.91 | 12616.26
07:30 | 6662.735 | 5918.945 | 12581.68
08:00 | 6615.12 | 5931.98 | 12547.1
08:30 | 6684.17 | 5920.185 | 12604.355
09:00 | 6753.22 | 5908.39 | 12661.61
09:30 | 6938.945 | 5898.77 | 12837.715
10:00 | 7124.67 | 5889.15 | 13013.82
10:30 | 7168.21 | 5969.57 | 13137.78
11:00 | 7211.75 | 6049.99 | 13261.74
11:30 | 7361.15 | 6214.05 | 13575.2
12:00 | 7510.55 | 6378.11 | 13888.66
12:30 | 7723.27 | 6387.97 | 14111.24
13:00 | 7935.99 | 6397.83 | 14333.82
13:30 | 7938.35 | 6313.405 | 14251.755
14:00 | 7940.71 | 6228.98 | 14169.69
14:30 | 8018 | 6167.685 | 14185.685
15:00 | 8095.29 | 6106.39 | 14201.68
15:30 | 8084.425 | 6030.625 | 14115.05
16:00 | 8073.56 | 5954.86 | 14028.42
16:30 | 7929.285 | 5882.47 | 13811.755
17:00 | 7785.01 | 5810.08 | 13595.09
17:30 | 7600.44 | 5720.895 | 13321.335
18:00 | 7415.87 | 5631.71 | 13047.58
18:30 | 7715.685 | 5872.855 | 13588.54
19:00 | 8015.5 | 6114 | 14129.5
19:30 | 8481 | 6610 | 15091
20:00 | 8506.4 | 6780 | 15286.4
20:30 | 8515.7 | 6824.5 | 15340.2 |  | Executive Engineer
21:00 | 8525 | 6869 | 15394 |  | Network Operation Division
21:30 | 8523.5 | 6855.5 | 15379
22:00 | 8522 | 6842 | 15364
22:30 | 8528.35 | 6789.5 | 15317.85
23:00 | 8534.7 | 6737 | 15271.7

## En-Curve
QF-LDC-12
Date | 03-07-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3678 | 2235 | 889 | 38 | 50 | 1404.64 | 172 | 3902 | 0 | 678 | 2293.2 | 0 | 0 | 28 | 137 | DAILY ENERGY CURVE
00:30 | 3565.5 | 2227.5 | 889 | 38 | 49 | 1405.645 | 172 | 3853.5 | 0 | 662 | 2248.2 | 0 | 0 | 41 | 133.5 | 03-07-2025
01:00 | 3453 | 2220 | 889 | 38 | 48 | 1406.65 | 172 | 3805 | 0 | 646 | 2203.2 | 0 | 0 | 54 | 130
01:30 | 3442.5 | 2188.5 | 889 | 38 | 47 | 1415.545 | 172 | 3861.5 | 0 | 464 | 2101.7 | 0 | 0 | 47 | 123.5 | Energy Generated | 338.2862 |  | MKWHr
02:00 | 3432 | 2157 | 889 | 38 | 46 | 1424.44 | 172 | 3918 | 0 | 282 | 2000.2 | 0 | 0 | 40 | 117 | Energy not Served | 0.736 |  | MKWHr
02:30 | 3438.5 | 2165 | 889 | 38 | 45 | 1421.57 | 172 | 3886 | 0 | 250.5 | 1876.2 | 0 | 0 | 32 | 102.5 | Total Energy Requirement | 339.0222 |  | MKWHr
03:00 | 3445 | 2173 | 889 | 38 | 44 | 1418.7 | 172 | 3854 | 0 | 219 | 1752.2 | 0 | 0 | 24 | 88
03:30 | 3447.5 | 2163 | 889 | 38 | 44 | 1414.61 | 172 | 3871 | 0 | 209 | 1617.7 | 0 | 0 | 25.5 | 61.5
04:00 | 3450 | 2153 | 889 | 38 | 44 | 1410.52 | 172 | 3888 | 0 | 199 | 1483.2 | 0 | 0 | 27 | 35
04:30 | 3460 | 2136.5 | 888.5 | 38 | 43 | 1409.755 | 172 | 3853.5 | 0 | 193 | 1376.2 | 0 | 0 | 29 | 17.5
05:00 | 3470 | 2120 | 888 | 38 | 42 | 1408.99 | 172 | 3819 | 0 | 187 | 1269.2 | 0 | 0 | 31 | 0
05:30 | 3451.5 | 2103 | 888.5 | 38 | 39 | 1356.755 | 172 | 3760 | 9.125 | 187 | 1115.7 | 0 | 0 | 41.5 | 0
06:00 | 3433 | 2086 | 889 | 38 | 36 | 1304.52 | 172 | 3701 | 18.25 | 187 | 962.2 | 0 | 0 | 52 | 0
06:30 | 3479 | 2098 | 889 | 38 | 35 | 1276.735 | 172 | 3570.5 | 74.28 | 172.5 | 890.6 | 0 | 0 | 52 | 0
07:00 | 3525 | 2110 | 889 | 38 | 34 | 1248.95 | 172 | 3440 | 130.31 | 158 | 819 | 0 | 0 | 52 | 0
07:30 | 3537 | 2102 | 889 | 38 | 33 | 1230.935 | 172 | 3397.5 | 178.745 | 153 | 809 | 0 | 0 | 41.5 | 0
08:00 | 3549 | 2094 | 889 | 38 | 32 | 1212.92 | 172 | 3355 | 227.18 | 148 | 799 | 0 | 0 | 31 | 0
08:30 | 3608.5 | 2095.5 | 888.5 | 38 | 32 | 1184.6 | 172 | 3359 | 282.255 | 173 | 736 | 0 | 0 | 35 | 0
09:00 | 3668 | 2097 | 888 | 38 | 32 | 1156.28 | 172 | 3363 | 337.33 | 198 | 673 | 0 | 0 | 39 | 0
09:30 | 3739.5 | 2142.5 | 888.5 | 38 | 32 | 1124.43 | 172 | 3449 | 335.785 | 188.5 | 686.5 | 0 | 0 | 41 | 0
10:00 | 3811 | 2188 | 889 | 38 | 32 | 1092.58 | 172 | 3535 | 334.24 | 179 | 700 | 0 | 0 | 43 | 0
10:30 | 3758 | 2140.5 | 889 | 38 | 33 | 1103.695 | 172 | 3600.5 | 396.585 | 187 | 775 | 0 | 0 | 44.5 | 0
11:00 | 3705 | 2093 | 889 | 38 | 34 | 1114.81 | 172 | 3666 | 458.93 | 195 | 850 | 0 | 0 | 46 | 0
11:30 | 3724 | 2148 | 888.5 | 38 | 35 | 1167.89 | 172 | 3753.5 | 492.31 | 197 | 907.5 | 0 | 0 | 51.5 | 0
12:00 | 3743 | 2203 | 888 | 38 | 36 | 1220.97 | 172 | 3841 | 525.69 | 199 | 965 | 0 | 0 | 57 | 0
12:30 | 3694 | 2236.5 | 888 | 38 | 37 | 1264.77 | 172 | 3815 | 533.47 | 230.5 | 1151.5 | 0 | 0 | 50.5 | 0
13:00 | 3645 | 2270 | 888 | 38 | 38 | 1308.57 | 172 | 3789 | 541.25 | 262 | 1338 | 0 | 0 | 44 | 0
13:30 | 3595 | 2257.5 | 888 | 38 | 39 | 1306.285 | 172 | 3738.5 | 503.97 | 281 | 1395.5 | 0 | 0 | 37 | 0
14:00 | 3545 | 2245 | 888 | 38 | 40 | 1304 | 172 | 3688 | 466.69 | 300 | 1453 | 0 | 0 | 30 | 0
14:30 | 3615.5 | 2278.5 | 888.5 | 38 | 40 | 1326 | 172 | 3637 | 407.685 | 296.5 | 1464 | 0 | 0 | 22 | 0
15:00 | 3686 | 2312 | 889 | 38 | 40 | 1348 | 172 | 3586 | 348.68 | 293 | 1475 | 0 | 0 | 14 | 0
15:30 | 3671.5 | 2312 | 888.5 | 38 | 39 | 1330.5 | 172 | 3581.5 | 303.55 | 302 | 1460 | 0 | 0 | 16.5 | 0
16:00 | 3657 | 2312 | 888 | 38 | 38 | 1313 | 172 | 3577 | 258.42 | 311 | 1445 | 0 | 0 | 19 | 0
16:30 | 3645 | 2248.5 | 888.5 | 38 | 37 | 1288 | 172 | 3503 | 196.755 | 323 | 1452 | 0 | 0 | 20 | 0
17:00 | 3633 | 2185 | 889 | 38 | 36 | 1263 | 172 | 3429 | 135.09 | 335 | 1459 | 0 | 0 | 21 | 0
17:30 | 3570 | 2095.5 | 889 | 38 | 40 | 1262.5 | 172 | 3400.5 | 89.835 | 337 | 1403.5 | 0 | 0 | 23.5 | 0
18:00 | 3507 | 2006 | 889 | 38 | 44 | 1262 | 172 | 3372 | 44.58 | 339 | 1348 | 0 | 0 | 26 | 0
18:30 | 3550 | 2039.75 | 889 | 38 | 48 | 1335.5 | 172 | 3475 | 22.29 | 466 | 1522 | 0 | 0 | 31 | 0
19:00 | 3593 | 2073.5 | 889 | 38 | 52 | 1409 | 172 | 3578 | 0 | 593 | 1696 | 0 | 0 | 36 | 0
19:30 | 3625 | 2369 | 889 | 38 | 50 | 1456 | 172 | 3840 | 0 | 623 | 1995 | 0 | 0 | 34 | 37
20:00 | 3629 | 2377 | 889 | 38 | 32 | 1460 | 172 | 3920 | 0 | 677 | 2064.4 | 0 | 0 | 28 | 61
20:30 | 3706.5 | 2380.5 | 888.5 | 38 | 37 | 1457.5 | 172 | 3947 | 0 | 661.5 | 2022.2 | 0 | 0 | 29.5 | 64.5
21:00 | 3784 | 2384 | 888 | 38 | 42 | 1455 | 172 | 3974 | 0 | 646 | 1980 | 0 | 0 | 31 | 68
21:30 | 3770.5 | 2389.5 | 888.5 | 38 | 42 | 1449.5 | 172 | 3971.5 | 0 | 646.5 | 1977.5 | 0 | 0 | 33.5 | 60.5
22:00 | 3757 | 2395 | 889 | 38 | 42 | 1444 | 172 | 3969 | 0 | 647 | 1975 | 0 | 0 | 36 | 53
22:30 | 3773.5 | 2400.75 | 889 | 38 | 43 | 1431.5 | 172 | 3931 | 0 | 638 | 1968.1 | 0 | 0 | 33 | 50
23:00 | 3790 | 2406.5 | 889 | 38 | 44 | 1419 | 172 | 3893 | 0 | 629 | 1961.2 | 0 | 0 | 30 | 47
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 03-07-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 385 | 06:00 | 375 | 10:00 | Payra | 415 | 07:00 | 408 | 22:00
Ashuganj | 402 | 06:00 | 390 | 12:00 | Rahanpur | 403 | 11:00 | 390 | 22:00
Bhulta | 407 | 05:00 | 378 | 14:00 | Rampal | 401 | 06:00 | 387 | 21:00
Bibiana | 389 | 07:00 | 378 | 14:00
BIPTC | 402 | 06:00 | 390 | 12:00
Bogura | 388 | 11:00 | 373 | 21:00
Gopalganj | 398 | 08:00 | 386 | 21:00
Kaliakoir | 377 | 05:00 | 354 | 14:00
Madunaghat | 396 | 19:00 | 389 | 12:00
Meghnaghat | 388 | 05:00 | 380 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 226 | 06:00 | 217 | 12:00 | Keranigonj | 223 | 04:00 | 215 | 12:00
AKSML | 235 | 18:30 | 225 | 10:00 | Khulna(S) | 230 | 08:00 | 219 | 21:00
Aminbazar | 255 | 04:00 | 218 | 10:00 | Madunaghat | 235 | 18:00 | 230 | 09:00
Ashuganj | 235 | 05:00 | 223 | 15:00 | Madunaghat-400 | 235 | 00:00 | 229 | 12:00
Ashuganj-400 | 235 | 05:00 | 223 | 15:00 | Maniknagar | 221 | 06:00 | 214 | 12:00
Baghabari | 234 | 06:00 | 225 | 23:00 | Meghnaghat | 229 | 06:00 | 222 | 11:00
Barapukuria | 223 | 08:00 | 217 | 19:30 | Meghnaghat-400 | 225 | 04:00 | 219 | 12:00
Barapukuria-230 | 223 | 08:00 | 217 | 19:30 | Mirsorai | 229 | 18:30 | 222 | 10:00
Barishal | 229 | 08:00 | 221 | 21:00 | Rajshahi | 235 | 08:00 | 224 | 02:00
Bheramara | 234 | 08:00 | 223 | 23:00 | Rampal | 229 | 08:00 | 219 | 21:00
Bhulta | 233 | 06:00 | 215 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 230 | 06:00 | 221 | 14:00 | Rampura | 232 | 06:00 | 214 | 15:00
BIPTC | 236 | 08:00 | 224 | 22:00 | Shikalbaha | 233 | 00:00 | 228 | 09:00
Bogura | 234 | 08:00 | 225 | 21:00 | Shyampur | 223 | 04:00 | 216 | 12:00
Bogura-400 | 235 | 18:00 | 226 | 21:00 | Siddhirganj | 223 | 05:00 | 216 | 12:00
Borhanuddin | 235 | 08:00 | 228 | 23:00 | Sirajgonj | 268 | 18:30 | 234 | 01:00
BSRM | 228 | 18:00 | 221 | 12:00 | Sreepur | 229 | 06:00 | 222 | 00:00
Cumilla(N) | 224 | 05:00 | 218 | 12:00 | Tongi | 227 | 04:00 | 217 | 11:00
Faridpur | 226 | 06:00 | 218 | 22:00
Fenchuganj | 229 | 06:00 | 224 | 00:00
Ghorashal | 230 | 02:00 | 220 | 14:00
Ghorashal-230 | 230 | 06:00 | 216 | 15:00
Gopalganj | 227 | 06:00 | 219 | 23:00
GPH | 231 | 00:00 | 225 | 12:00
Haripur | 222 | 04:00 | 216 | 12:00
Hasnabad | 221 | 00:00 | 216 | 12:00
Hathazari | 235 | 00:00 | 225 | 23:00
Ishurdi | 237 | 08:00 | 226 | 21:00
Jhenaidah | 230 | 08:00 | 216 | 00:00
Kaliakoir | 232 | 05:00 | 219 | 16:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 141 | 06:00 | 127 | 15:00 | Madanganj | 129 | 18:30 | 124 | 05:00
Agargaon | 133 | 06:00 | 126 | 12:00 | Madaripur | 135 | 07:00 | 129 | 23:00
Agrabad | 133 | 00:00 | 128 | 09:00 | Madartek | 140 | 06:00 | 128 | 15:00
AKS | 131 | 00:00 | 127 | 11:00 | Madunaghat | 133 | 00:00 | 130 | 09:00
Aminbazar | 135 | 06:00 | 128 | 09:00 | Magura | 133 | 11:00 | 123 | 22:00
Amnura | 136 | 10:00 | 125 | 01:00 | Mahasthangarh | 135 | 08:00 | 126 | 22:00
Ashuganj | 140 | 06:00 | 134 | 15:00 | Maijdee | 121 | 18:00 | 109 | 23:00
Bagerhat | 132 | 09:00 | 122 | 23:00 | Manikganj | 130 | 05:00 | 120 | 16:00
Bajitpur | 131 | 05:00 | 125 | 00:00 | Maniknagar | 132 | 04:00 | 125 | 12:00
Bakulia | 135 | 01:00 | 130 | 15:00 | Matarbari | 126 | 17:00 | 116 | 15:00
Banani | 140 | 05:00 | 127 | 16:00 | Matuail | 129.3 | 04:00 | 125 | 12:00
Bangabhaban | 132 | 04:00 | 126 | 12:00 | Millgate | 133 | 08:00 | 124 | 15:00
Barapukuria | 136 | 04:00 | 128 | 10:00 | Mirpur | 133 | 18:00 | 127 | 09:00
Barguna | 135 | 00:00 | 130 | 23:00 | Mirzapur | 130 | 18:00 | 122 | 14:00
Barishal | 133 | 07:00 | 127 | 21:00 | Mithapukur | 132 | 18:00 | 119 | 22:00
Barishal-230 | 134 | 08:00 | 128 | 21:00 | MI_Cement | 130 | 05:00 | 125 | 12:00
Baroaulia | 134 | 00:00 | 130 | 09:00 | Modern | 0 | 00:00 | 0 | 00:00
Baroirhat | 126 | 18:00 | 119 | 00:00 | Mogbazar | 139 | 07:00 | 129 | 15:00
Bashundhara | 142 | 05:00 | 124 | 15:00 | Mongla | 133 | 08:00 | 121 | 23:00
BashundharaCement | 129 | 18:30 | 124 | 03:00 | Motijheel | 132 | 04:00 | 126 | 12:00
Beanibazar | 127 | 05:00 | 123 | 00:00 | Muktagacha | 134 | 09:00 | 126 | 19:30
Benapole | 132 | 09:00 | 121 | 21:00 | Munshiganj | 129 | 02:00 | 124 | 12:00
Bhaluka | 131 | 05:00 | 125 | 00:00 | Muradnagar | 128 | 18:00 | 121 | 00:00
Bhandaria | 129 | 08:00 | 119 | 22:00 | Mymensingh | 136 | 10:00 | 117 | 00:00
Bhangura | 133 | 05:00 | 127 | 23:00 | Naogaon | 134 | 18:00 | 124 | 23:00
Bheramara | 137 | 08:00 | 132 | 00:00 | Narail | 135 | 11:00 | 122 | 21:00
Bheramara(GK) | 137 | 08:00 | 132 | 00:00 | Narinda | 132 | 04:00 | 125 | 12:00
Bhulta | 122 | 18:00 | 117 | 07:00 | Narshingdi | 131 | 07:00 | 118 | 12:00
Bog-Sherpur | 136 | 09:00 | 128 | 22:00 | Natore | 135 | 08:00 | 129 | 00:00
Bogura | 138 | 09:00 | 131 | 22:00 | Nawabganj | 133 | 05:00 | 127 | 12:00
Bogura-230 | 138 | 08:00 | 131 | 22:00 | Netrakona | 126 | 06:00 | 117 | 00:00
Brahmanbaria | 133 | 05:00 | 126 | 21:00 | New | 134 | 06:00 | 125 | 15:00
Cantonment | 132 | 04:00 | 126 | 12:00 | Niamatpur | 137 | 18:00 | 130 | 00:00
Chandina | 129 | 18:00 | 122 | 12:00 | Noapara | 135 | 18:30 | 125 | 23:00
Chandpur | 131 | 18:30 | 12 | 19:30 | Pabna | 135 | 08:00 | 128 | 00:00
Chandraghona | 134 | 18:00 | 130 | 10:00 | Palashbari | 131 | 10:00 | 117 | 23:00
Chapai | 133 | 17:00 | 127 | 00:00 | Panchagarh | 135 | 19:00 | 121 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 05:00 | 125 | 12:00 | Patuakhali | 136 | 00:00 | 131 | 22:00
Chauddagram | 125 | 18:00 | 117 | 12:00 | Payra | 136 | 00:00 | 134 | 13:00
Chhatak | 126 | 05:00 | 119 | 19:30 | PHP | 125 | 18:30 | 117 | 22:00
Chowmuhani | 121 | 18:00 | 112 | 23:00 | Postogola | 132 | 06:00 | 127 | 12:00
Chuadanga | 132 | 09:00 | 119 | 21:00 | Purbachal | 141 | 06:00 | 124 | 15:00
Coxsbazar | 123 | 12:00 | 114 | 15:00 | Purbasadipur | 131 | 19:00 | 121 | 10:00
Cumilla(N) | 129 | 18:00 | 124 | 00:00 | Rahanpur | 137 | 08:00 | 132 | 19:30
Cumilla(S) | 133 | 06:00 | 120 | 12:00 | Rahanpur-400 | 138 | 18:00 | 133 | 00:00
Daganbhuiyan | 123 | 18:00 | 114 | 09:00 | Rahim | 130 | 05:00 | 125 | 12:00
Daudkandi | 126 | 18:00 | 120 | 00:00 | Rajbari | 133 | 08:00 | 126 | 21:00
Dhaka | 141 | 05:00 | 128 | 14:00 | Rajendrapur | 137 | 06:00 | 124 | 15:00
Dhamrai | 131 | 05:00 | 123 | 15:00 | Rajshahi | 135 | 07:00 | 129 | 23:00
Dhanmondi | 141 | 05:00 | 129 | 14:00 | Rajshahi-230 | 136 | 08:00 | 119 | 00:00
Dohazari | 131 | 13:00 | 127 | 06:00 | Ramganj | 120 | 14:00 | 112 | 23:00
Faridpur | 134 | 06:00 | 128 | 22:00 | Rampur | 134 | 19:00 | 128 | 11:00
Fatullah | 131 | 04:00 | 126 | 12:00 | Rampura | 141 | 06:00 | 128 | 15:00
Fenchuganj | 135 | 06:00 | 131 | 00:00 | Rangamati | 133 | 18:00 | 129 | 10:00
Feni | 123 | 18:00 | 119 | 12:00 | Rangpur | 131 | 05:00 | 122 | 14:00
Ghatail | 130 | 18:30 | 122 | 15:00 | Ruppur | 138 | 09:00 | 132 | 00:00
Ghorashal | 139 | 04:00 | 131 | 14:00 | Saidpur | 132 | 19:00 | 122 | 12:00
Goalpara | 136 | 08:00 | 128 | 22:00 | Satkhira | 134 | 09:00 | 122 | 21:00
Gollamari | 136 | 06:00 | 129 | 21:00 | Satmasjid | 131 | 03:00 | 125 | 12:00
Gopalganj | 135 | 08:00 | 128 | 21:00 | Savar | 132 | 00:00 | 126 | 08:00
Gopalganj-400 | 136 | 06:00 | 131 | 21:00 | SevenRings | 139 | 06:00 | 130 | 15:00
Gulshan | 140 | 06:00 | 128 | 15:00 | ShahCement | 130 | 05:00 | 125 | 12:00
Halishahar | 135 | 00:00 | 128 | 10:00 | Shahjadpur | 135 | 03:00 | 132 | 19:30
Haripur | 130 | 04:00 | 125 | 12:00 | Shahjibazar | 132 | 06:00 | 126 | 00:00
HaripurSBU | 130 | 04:00 | 125 | 12:00 | Shahmirpur | 135 | 00:00 | 131 | 10:00
Hasnabad | 132 | 05:00 | 127 | 10:00 | Shariatpur | 134 | 06:00 | 127 | 21:00
Hathazari | 135 | 18:00 | 132 | 07:00 | Sherpur | 136 | 10:00 | 127 | 19:30
Ishurdi | 139 | 08:00 | 133 | 00:00 | Shikalbaha | 124 | 00:00 | 119 | 11:00
Jaldhaka | 130 | 19:00 | 120 | 19:30 | Shikalbaha-230 | 136 | 18:30 | 131 | 10:00
Jamalpur | 138 | 10:00 | 131 | 19:30 | Shitalakhya | 130 | 05:00 | 125 | 12:00
Jashore | 131 | 18:30 | 119 | 22:00 | Sholosohor | 133 | 03:00 | 129 | 12:00
Jhenaidah | 135 | 10:00 | 122 | 22:00 | Shyampur | 130 | 01:00 | 125 | 10:00
Jhenaidah-230 | 136 | 08:00 | 126 | 21:00 | Shyampur-230 | 131 | 04:00 | 126 | 12:00
Joydebpur | 140 | 05:00 | 134 | 09:00 | Siddhirganj | 130 | 04:00 | 125 | 12:00
Joypurhat | 132 | 18:00 | 122 | 00:00 | Sirajganj | 134 | 08:00 | 126 | 22:00
Juldah | 136 | 00:00 | 131 | 10:00 | Sonargaon | 129 | 07:00 | 123 | 12:00
Kabirpur | 132 | 18:00 | 121 | 16:00 | Sreemongol | 132 | 07:00 | 125 | 00:00
Kachua | 129 | 18:00 | 117 | 12:00 | Sreepur | 133 | 06:00 | 128 | 00:00
Kaliakoir | 134 | 06:00 | 125 | 14:00 | Srinagar | 133 | 06:00 | 128 | 12:00
Kallyanpur | 132 | 01:00 | 128 | 12:00 | SSM | 138 | 18:30 | 131 | 11:00
Kalurghat | 133 | 00:00 | 129 | 12:00 | Sunamganj | 125 | 07:00 | 118 | 19:30
Kamrangirchar | 133 | 05:00 | 127 | 12:00 | Sylhet | 129 | 07:00 | 124 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet-132 | 128 | 06:00 | 125 | 23:00
Kasba | 127 | 18:00 | 120 | 00:00 | Tangail | 129 | 18:00 | 120 | 14:00
Kazla | 132 | 05:00 | 125 | 13:00 | Taraganj | 130 | 18:00 | 122 | 14:00
Keranigonj | 134 | 06:00 | 128 | 12:00 | Thakurgaon | 135 | 19:00 | 119 | 12:00
Khagrachori | 132 | 17:00 | 128 | 10:00 | TK | 133 | 01:00 | 129 | 10:00
Khulna | 135 | 09:00 | 126 | 23:00 | Tongi | 135 | 04:00 | 128 | 11:00
Khulna(S) | 137 | 08:00 | 129 | 21:00 | Ullahpara | 134 | 04:00 | 129 | 19:30
Khulshi | 132 | 00:00 | 127 | 11:00 | Ullon | 140 | 06:00 | 127 | 14:00
Kishoreganj | 128 | 05:00 | 123 | 00:00 | Uttara | 132 | 02:00 | 127 | 12:00
Kodda | 136 | 05:00 | 120 | 14:00 | UttaraNew | 132 | 01:00 | 127 | 12:00
KSRM | 134 | 18:00 | 128 | 11:00 | Zigatola | 134 | 06:00 | 127 | 12:00
Kulaura | 133 | 06:00 | 129 | 00:00
Kurigram | 130 | 05:00 | 120 | 21:00
Kushtia | 134 | 09:00 | 127 | 00:00
Lakshmipur | N/A | N/A | N/A | N/A
Lalbag | 133 | 04:00 | 127 | 12:00
Lalmonirhat | 128 | 06:00 | 121 | 21:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division