## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 05-07-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-07-2025 | during | 05-07-2025 | during | 05-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 401 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 420 | 450 | 450 | 450 | 450 | Allocation limit by Titas, instructed by DS(Gen)
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 300 | 303 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 330 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 15 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 16 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23 | 26 | 33 | 33 | 27 | 27 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 20 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 17 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 24 | 123 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 17 | 105 | 105 | 70 | 90 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 16 | 104 | 104 | 68 | 68 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 51 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 36 | 0 | 29 | 0 | 29 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 400 | 500 | 584 | 584 | 526 | 526 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage instructed by DS(Gen)
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 125 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2048 | 2452 | 5108.2 | 5173.2 | 3418.58 | 3503.58
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 6 | 0 | 4 | 0 | 4 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 32 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 172 | 172 | 165 | 165 | 165 | 165 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 220 | 220 | 213 | 213 | 213 | 213 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 33 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 39 | 56 | 72 | 48 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 65 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 48 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 21 | 35 | 2 | 25 | 2 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4 | 0 | 4.23 | 0 | 4.23 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 17 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 24 | 70 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 885 | 1220 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 22 | 36 | 26 | 36 | 26 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 203 | 204 | 575 | 575 | 200 | 200 | U2 S/D 06/06/25
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1548 | 2192 | 3573.95 | 3594.72 | 3160.95 | 3189.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 0 | 0 | 221 | 221 | 0 | 0 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 346 | 344 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 285 | 335 | 340 | 340 | 340 | 340 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 18 | 20 | 46.7 | 46.7 | 20 | 20 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 46 | 47 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 177 | 165 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 50 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 38 | 46 | 46 | 46 | 46 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 200 | 179 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 34 | 40 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 37 | 40 | 114 | 114 | 98 | 98 | Engine Problem
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 10 | 28 | 113 | 113 | 9 | 28 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 17 | 110 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 18 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1264 | 1459 | 2469.75 | 2399.75 | 1934.55 | 1883.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-07-2025 | during | 05-07-2025 | during | 05-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 83 | 88 | 157.5 | 157.5 | 80 | 80 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 75 | 170 | 200 | 200 | 160 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 48 | 57 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 20.35 | 0 | 39 | 0 | 39 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 256.35 | 344 | 590.1 | 549 | 462.6 | 421.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage instructed by DS(Gen)
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 146 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 81 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 171 | 171 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 18 | 18 | 18 | 18 | 18 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 8 | 8 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 290 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 378 | 387 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1453 | 1451 | 1520 | 1520 | 1425 | 1425
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 889 | 891 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 240 | 239 | 410 | 410 | 250 | 250 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 70 | 70 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 101 | 0 | 62 | 0 | 62 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 330 | 330
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 404 | 572 | 617.1 | 617.1 | 1204 | 1204 | U#2 under shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1672 | 1740 | 2991.1 | 2929.1 | 3383 | 3321
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 7 | 11 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 124 | 130 | 130 | 118 | 118 | Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 760 | 1111 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 169 | 282 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.62 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1473.62 | 1748 | 2172 | 2171 | 2100 | 2099
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 190 | 201 | 220 | 220 | 200 | 200 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 194 | 204 | 220 | 220 | 220 | 220
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 351 | 393 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 97 | 97 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.87 | 0 | 5.65 | 0 | 5.65 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 951.84 | 1199 | 1435.88 | 1435.88 | 1355 | 1355 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 36.92 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 60 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 1789.63 | 2032 | 2980.52 | 2813.87 | 2837.26 | 2670.61
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 49 | 49 | 50 | 50 | 50 | 50 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 202 | 200 | 200 | 200 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 27 | 98 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 1.4 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 114 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 22 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 180 | 0 | 150.46 | 0 | 150.46 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 516.4 | 461 | 699.06 | 512 | 699.06 | 512
System Total |  |  |  |  | 28565.2 | 27084.055 | 12021 | 13879 | 22104.68 | 21662.64 | 19421 | 19025.96
Forecast Scenario (05-07-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14082 |  | 0 |  | 14082
|  |  |  | 1:00 | 13823 |  | 0 |  | 13823
|  |  |  | 2:00 | 13427 |  | 0 |  | 13427
|  |  |  | 3:00 | 13092 |  | 0 |  | 13092
|  |  |  | 4:00 | 12815 |  | 0 |  | 12815
|  |  |  | 5:00 | 12579 |  | 0 |  | 12579
|  |  |  | 6:00 | 11785 |  | 0 |  | 11785
|  |  |  | 7:00 | 11611 |  | 0 |  | 11611
|  |  |  | 8:00 | 11078 |  | 0 |  | 11078
|  |  |  | 9:00 | 10802 |  | 0 |  | 10802
|  |  |  | 10:00 | 11423 |  | 0 |  | 11423
|  |  |  | 11:00 | 11792 |  | 0 |  | 11792
|  |  |  | 12:00 | 12251 |  | 0 |  | 12251
|  |  |  | 13:00 | 12563 |  | 0 |  | 12563
|  |  |  | 14:00 | 12732 |  | 0 |  | 12732
|  |  |  | 15:00 | 13042 |  | 0 |  | 13042
|  |  |  | 16:00 | 13029 |  | 0 |  | 13029
|  |  |  | 17:00 | 12819 |  | 0 |  | 12819
|  |  |  | 18:00 | 12937 |  | 0 |  | 12937
|  |  |  | 18:30 | 13500 |  | 0 |  | 13500
|  |  |  | 19:00 | 14181 |  | 0 |  | 14181
|  |  |  | 19:30 | 15310 |  | 0 |  | 15310
|  |  |  | 20:00 | 15421 |  | 0 |  | 15421
|  |  |  | 21:00 | 15310 |  | 0 |  | 15310
|  |  |  | 22:00 | 15230 |  | 0 |  | 15230
|  |  |  | 23:00 | 15330 |  | 0 |  | 15330
Probable Maximum Temperature: |  |  | 30.90°C
Probable Maximum Demand at Day Peak: |  |  | 12251.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15421.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13858.04 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 301.84128 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:12 hrs on 05-07-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 04-07-2025 | [28 empty] | Date: | 04-07-2025 | [28 empty] | Date: | 04-07-2025 | [28 empty] | Date: | 04-07-2025 | [28 empty] | Date: | 04-07-2025 | [12 empty] | Date: | 04-07-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [12 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 54 | 29 | 149 | 80 | 80 | 0 | 55 | 138 | 67 | 450 | 303 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 142 | 26.5 | 22 | 0 | 450 | 0 | 15 | 0 | 0 | 36 | 65 | 70 | 0 | 88 | 88 | 0 | 172 | 0 | 30 | 201 | 0 | 0 | 33 | 8 | 51 | 223 | 0 | 0 | 0 | 1145 | 0 | 51 | 80 | 195 | 0 | 354 | 335 | 48 | 0 | 20 | 21 | 0 | 200 | 29 | 20 | 78 | 42 | 52.2 | 0 | 38 | 280 | 320 | 375 | 0 | 0 | 159 | 8 | 0 | 80 | 30 | 0 | 18 | 173 | 17 | 91 | 190 | 49 | 0 | 0 | 12 | 8414.7 | 889 | 223 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 607 | 51 | 1418 | 0 | 42 | 0 | 53 | 0 | 57 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 197 | 0 | 196 | 0 | 414 | 0 | 0 | 174 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 11 | 120 | 220 | 0 | 301 | 1120 | 9 | 6736 | 15150.7 | 96.94
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 54 | 29 | 149 | 95 | 30 | 0 | 39 | 151 | 32 | 420 | 294 | 0 | 0 | 17 | 333 | 0 | 0 | 0 | 142 | 26.5 | 18 | 0 | 450 | 0 | 0 | 0 | 0 | 38 | 65 | 70 | 0 | 100 | 88 | 0 | 172 | 0 | 31 | 204 | 0 | 0 | 33 | 0 | 45 | 223 | 0 | 0 | 0 | 1152 | 0 | 51 | 10 | 195 | 0 | 349 | 340 | 48 | 0 | 20 | 16 | 0 | 200 | 17 | 20 | 78 | 44 | 52.2 | 0 | 39 | 280 | 320 | 380 | 0 | 0 | 156 | 8 | 0 | 80 | 30 | 0 | 18 | 173 | 17 | 91 | 180 | 49 | 0 | 0 | 12 | 8200.7 | 889 | 220 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 595 | 17 | 1419 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 196 | 0 | 414 | 0 | 0 | 173 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 10 | 120 | 220 | 0 | 302 | 1104 | 16 | 6521 | 14721.7 | 96.92
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 54 | 17 | 99 | 64 | 0 | 0 | 0 | 156 | 0 | 420 | 303 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 142 | 26.5 | 20 | 0 | 450 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 100 | 88 | 0 | 172 | 0 | 31 | 205 | 0 | 0 | 30 | 0 | 0 | 222 | 0 | 0 | 0 | 1145 | 0 | 51 | 0 | 195 | 0 | 352 | 340 | 49 | 0 | 20 | 17 | 0 | 200 | 9 | 20 | 78 | 42 | 52.2 | 0 | 39 | 285 | 320 | 375 | 0 | 0 | 158 | 8 | 0 | 80 | 30 | 0 | 18 | 173 | 17 | 91 | 180 | 49 | 0 | 0 | 12 | 7814.7 | 889 | 221 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 1413 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 164 | 0 | 414 | 0 | 0 | 175 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 10 | 120 | 220 | 0 | 301 | 1107 | 0 | 6449 | 14263.7 | 96.9
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 24 | 17 | 85 | 32 | 0 | 0 | 0 | 17 | 0 | 420 | 297 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 142 | 26.5 | 20 | 0 | 450 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 48 | 75 | 0 | 172 | 0 | 35 | 206 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1145 | 0 | 51 | 0 | 185 | 0 | 354 | 335 | 49 | 0 | 18 | 17 | 0 | 200 | 9 | 20 | 62 | 42 | 52.2 | 0 | 24 | 280 | 320 | 375 | 0 | 0 | 159 | 8 | 0 | 80 | 30 | 0 | 18 | 172 | 17 | 91 | 172 | 49 | 0 | 0 | 12 | 7442.7 | 889 | 220 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 605 | 0 | 1409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 123 | 0 | 407 | 0 | 0 | 173 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 10 | 120 | 220 | 0 | 302 | 1104 | 0 | 6357 | 13799.7 | 96.88
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 10 | 83 | 16 | 0 | 0 | 0 | 0 | 0 | 420 | 297 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 142 | 26.5 | 20 | 0 | 450 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 24 | 24 | 0 | 172 | 0 | 35 | 207 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1110 | 0 | 51 | 0 | 185 | 0 | 354 | 335 | 49 | 0 | 18 | 17 | 0 | 200 | 9 | 20 | 78 | 40 | 52.2 | 0 | 24 | 275 | 320 | 388 | 0 | 0 | 159 | 8 | 0 | 80 | 30 | 0 | 18 | 172 | 0 | 91 | 172 | 49 | 0 | 0 | 12 | 7243.7 | 889 | 220 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 604 | 0 | 1318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 130 | 0 | 414 | 0 | 0 | 180 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 221 | 10 | 120 | 220 | 0 | 302 | 1106 | 0 | 6230 | 13473.7 | 96.86
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 302 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 142 | 26.5 | 20 | 0 | 450 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 35 | 203 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1055 | 0 | 51 | 0 | 185 | 0 | 354 | 335 | 49 | 0 | 18 | 17 | 0 | 200 | 9 | 20 | 78 | 38 | 52.2 | 0 | 23 | 285 | 320 | 386 | 0 | 0 | 155 | 8 | 0 | 80 | 30 | 0 | 18 | 172 | 0 | 81 | 172 | 49 | 0 | 0 | 12 | 7080.7 | 889 | 221 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 587 | 0 | 1221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 131 | 0 | 407 | 0 | 0 | 178 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 7 | 120 | 220 | 0 | 304 | 1104 | 0 | 6053 | 13133.7 | 96.84
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 292 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 20 | 20 | 0 | 450 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 1 | 172 | 0 | 37 | 207 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 185 | 0 | 355 | 340 | 50 | 0 | 18 | 17 | 0 | 160 | 9 | 20 | 58 | 36 | 25 | 1 | 23 | 285 | 320 | 345 | 0 | 0 | 152 | 8 | 0 | 80 | 30 | 0 | 18 | 172 | 0 | 45 | 153 | 56 | 0 | 1.52 | 12 | 6800.52 | 889 | 222 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 546 | 0 | 1004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 191 | 0 | 122 | 0 | 389 | 0 | 0 | 178 | 48 | 35 | 2 | 49 | 0 | 0 | 0.2 | 9 | 0.02 | 0 | 166 | 6 | 114 | 220 | 0 | 304 | 1050 | 0 | 5589.22 | 12389.74 | 96.82
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 298 | 0 | 0 | 0 | 335 | 0 | 0 | 6 | 35 | 20 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 1 | 172 | 0 | 38 | 204 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 949 | 0 | 51 | 0 | 185 | 0 | 354 | 340 | 50 | 0 | 18 | 17 | 0 | 146 | 9 | 20 | 52 | 34 | 8 | 8 | 0 | 285 | 320 | 385 | 0 | 0 | 156 | 8 | 0 | 80 | 30 | 0 | 18 | 172 | 0 | 45 | 135 | 81 | 0 | 7.57 | 12 | 6508.57 | 889 | 225 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7 | 514 | 0 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 191 | 0 | 80 | 0 | 414 | 0 | 0.03 | 176 | 48 | 35 | 6 | 34 | 0 | 0 | 2.7 | 66 | 0 | 0 | 201 | 5 | 120 | 220 | 0 | 304 | 1000 | 0 | 5505.73 | 12014.3 | 96.8
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 298 | 0 | 0 | 0 | 335 | 0 | 0 | 5 | 35 | 20 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 172 | 0 | 38 | 205 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 867 | 2 | 51 | 0 | 147 | 0 | 352 | 335 | 50 | 0 | 20 | 17 | 0 | 158 | 9 | 20 | 0 | 32 | 8 | 9 | 0 | 290 | 320 | 382 | 0 | 0 | 152 | 8 | 0 | 80 | 30 | 0 | 18 | 172 | 0 | 45 | 85 | 103 | 1 | 3.62 | 12 | 6261.62 | 889 | 227 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 8 | 467 | 0 | 862.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 5.79 | 0 | 0 | 191 | 0 | 76 | 0 | 372 | 0 | 0.45 | 176 | 48 | 35 | 15 | 0 | 0 | 0 | 5.1 | 43 | 0 | 0 | 219 | 4 | 120 | 220 | 0 | 304 | 960 | 0 | 5301.38 | 11563 | 96.78
09:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 296 | 0 | 0 | 0 | 335 | 0 | 0 | 14 | 17 | 25 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 1 | 172 | 0 | 20 | 206 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 800 | 2 | 51 | 0 | 147 | 0 | 353 | 340 | 50 | 0 | 20 | 16 | 0 | 200 | 9 | 20 | 0 | 32 | 8 | 32 | 0 | 290 | 320 | 358 | 0 | 0 | 135 | 8 | 0 | 74 | 30 | 0 | 18 | 173 | 0 | 45 | 65 | 82 | 0 | 19.25 | 12 | 6221.25 | 889 | 231 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 391 | 0 | 853.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 8.87 | 0 | 0 | 191 | 0 | 98 | 0 | 341 | 0 | 1.04 | 174 | 49 | 35 | 9 | 0 | 0 | 0 | 4.7 | 73 | 0.19 | 0 | 175 | 4 | 120 | 220 | 0 | 304 | 920 | 0 | 5145.09 | 11366.34 | 96.77
10:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 308 | 0 | 0 | 0 | 280 | 0 | 0 | 17 | 17 | 23 | 14 | 0 | 350 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 2 | 172 | 0 | 20 | 204 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 846 | 2 | 51 | 0 | 145 | 0 | 300 | 285 | 49 | 0 | 16 | 17 | 0 | 200 | 9 | 17 | 0 | 30 | 8 | 19 | 0 | 290 | 320 | 360 | 0 | 0 | 138 | 8 | 0 | 74 | 30 | 0 | 18 | 173 | 0 | 45 | 55 | 83 | 0 | 20.31 | 12 | 5998.31 | 889 | 235 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 29 | 397 | 0 | 833.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 22.36 | 0 | 0 | 197 | 0 | 170 | 0 | 384 | 0 | 1.4 | 173 | 48 | 35 | 6 | 34 | 0 | 0 | 5.7 | 109 | 0.4 | 0 | 172 | 4 | 100 | 180 | 0 | 283 | 720 | 0 | 5107.18 | 11105.49 | 96.76
11:00 | 0 | 3 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 306 | 0 | 0 | 0 | 327 | 0 | 0 | 32 | 17 | 23 | 14 | 0 | 350 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 3 | 172 | 0 | 21 | 205 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 855 | 3 | 51 | 0 | 140 | 0 | 300 | 285 | 47 | 0 | 18 | 17 | 0 | 200 | 13 | 17 | 1 | 31 | 8 | 57 | 0 | 285 | 320 | 360 | 0 | 0 | 152 | 8 | 0 | 77 | 30 | 0 | 16 | 173 | 17 | 45 | 55 | 83 | 1 | 40.57 | 12 | 6208.57 | 889 | 239 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 66 | 401 | 0 | 836.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 16.97 | 0 | 0 | 190 | 0 | 194 | 0 | 392 | 0 | 2.55 | 172 | 49 | 35 | 20 | 34 | 0 | 0 | 6.7 | 80 | 0.6 | 0 | 174 | 4 | 100 | 220 | 0 | 217 | 700 | 0 | 5113.81 | 11322.38 | 96.75
12:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 15 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 300 | 0 | 0 | 0 | 330 | 0 | 0 | 36 | 52 | 23 | 14 | 0 | 400 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 12 | 24 | 4 | 172 | 0 | 21 | 203 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 885 | 6 | 51 | 0 | 177 | 0 | 346 | 285 | 46 | 0 | 18 | 17 | 0 | 200 | 10 | 17 | 37 | 34 | 8 | 18 | 0 | 295 | 320 | 378 | 0 | 0 | 156 | 8 | 0 | 79 | 30 | 0 | 16 | 171 | 17 | 48 | 75 | 83 | 1 | 20.35 | 12 | 6569.35 | 889 | 240 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 101 | 404 | 0 | 951.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 36.92 | 0 | 0 | 190 | 0 | 194 | 0 | 351 | 0 | 5.87 | 202 | 49 | 35 | 22 | 27 | 0 | 0 | 1.4 | 180 | 0.62 | 0 | 169 | 7 | 120 | 220 | 0 | 197 | 760 | 0 | 5451.65 | 12021 | 96.74
13:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 35 | 51 | 0 | 0 | 0 | 0 | 0 | 12 | 420 | 305 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 52 | 23 | 10 | 0 | 500 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 48 | 2 | 172 | 0 | 28 | 206 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 946 | 2 | 51 | 0 | 182 | 0 | 336 | 330 | 46 | 0 | 17 | 17 | 0 | 185 | 9 | 12 | 48 | 38 | 8 | 34 | 7 | 295 | 320 | 384 | 0 | 0 | 156 | 8 | 0 | 77 | 30 | 0 | 16 | 171 | 17 | 70 | 77 | 71 | 2 | 18.95 | 12 | 6883.95 | 890 | 239 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 73 | 481 | 0 | 999.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 61.07 | 0 | 0 | 190 | 0 | 194 | 0 | 405 | 0 | 5.91 | 197 | 48 | 0 | 36 | 34 | 0 | 0 | 5.3 | 103 | 0.76 | 0 | 228 | 7 | 120 | 220 | 0 | 135 | 955 | 0 | 5695.91 | 12579.86 | 96.73
14:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 32 | 17 | 51 | 0 | 0 | 0 | 0 | 0 | 16 | 420 | 295 | 0 | 0 | 0 | 326 | 0 | 0 | 27 | 52 | 23 | 10 | 0 | 400 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 12 | 4 | 172 | 0 | 27 | 206 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1000 | 2 | 51 | 0 | 185 | 0 | 342 | 340 | 47 | 0 | 20 | 17 | 0 | 175 | 10 | 17 | 47 | 37 | 0 | 58 | 42 | 290 | 320 | 355 | 0 | 0 | 143 | 8 | 0 | 77 | 30 | 0 | 18 | 171 | 17 | 71 | 95 | 71 | 2 | 36.19 | 12 | 6885.19 | 891 | 239 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 485 | 0 | 968.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 8.89 | 0 | 0 | 188 | 0 | 192 | 0 | 355 | 0 | 0.07 | 199 | 48 | 0 | 9 | 34 | 0 | 0 | 7.8 | 192 | 0.4 | 0 | 178 | 7 | 120 | 220 | 0 | 0 | 1045 | 0 | 5438.2 | 12323.39 | 96.72
15:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 38 | 0 | 0 | 0 | 0 | 0 | 16 | 420 | 304 | 0 | 0 | 0 | 326 | 0 | 0 | 22 | 52 | 23 | 10 | 0 | 400 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 12 | 4 | 172 | 0 | 23 | 203 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1007 | 2 | 43 | 0 | 185 | 0 | 343 | 340 | 45 | 0 | 20 | 16 | 0 | 151 | 9 | 17 | 47 | 36 | 0 | 51 | 36 | 300 | 320 | 334 | 0 | 0 | 144 | 0 | 0 | 75 | 30 | 0 | 18 | 171 | 17 | 45 | 65 | 72 | 1 | 30.25 | 12 | 6720.25 | 890 | 239 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7 | 459 | 0 | 972.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 14.56 | 0 | 0 | 192 | 0 | 202 | 0 | 369 | 0 | 1.8 | 200 | 49 | 0 | 19 | 0 | 0 | 0 | 3.9 | 152 | 0.16 | 0 | 181 | 7 | 120 | 220 | 0 | 0 | 1050 | 0 | 5421.24 | 12141.49 | 96.71
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 300 | 0 | 0 | 0 | 328 | 0 | 0 | 5 | 52 | 23 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 12 | 1 | 172 | 0 | 22 | 204 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 935 | 4 | 43 | 0 | 185 | 0 | 339 | 335 | 46 | 0 | 20 | 17 | 0 | 155 | 8 | 19 | 30 | 31 | 0 | 16 | 36 | 295 | 320 | 333 | 0 | 0 | 137 | 0 | 0 | 77 | 30 | 0 | 18 | 170 | 17 | 45 | 45 | 72 | 1 | 14.38 | 12 | 6445.38 | 890 | 239 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 15 | 445 | 0 | 868.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 17.29 | 0 | 0 | 192 | 0 | 205 | 0 | 378 | 0 | 1.76 | 196 | 49 | 0 | 20 | 0 | 0 | 0 | 2.1 | 118 | 0.14 | 0 | 171 | 6 | 120 | 220 | 0 | 0 | 950 | 0 | 5189.51 | 11634.89 | 96.7
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 288 | 0 | 0 | 0 | 330 | 0 | 0 | 1 | 52 | 23 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 12 | 1 | 172 | 0 | 26 | 204 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 905 | 3 | 43 | 0 | 185 | 0 | 351 | 340 | 45 | 0 | 20 | 34 | 0 | 144 | 9 | 20 | 29 | 32 | 0 | 10 | 36 | 295 | 320 | 328 | 0 | 0 | 137 | 8 | 0 | 80 | 30 | 0 | 18 | 170 | 17 | 45 | 45 | 88 | 0 | 4.28 | 12 | 6403.28 | 890 | 240 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6 | 441 | 0 | 875.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 5.76 | 0 | 0 | 199 | 0 | 206 | 0 | 355 | 0 | 0.54 | 200 | 49 | 0 | 6 | 0 | 0 | 0 | 3.6 | 53 | 0.09 | 0 | 171 | 7 | 120 | 220 | 0 | 0 | 850 | 0 | 4954.82 | 11358.1 | 96.69
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 295 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 52 | 26 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 12 | 0 | 172 | 0 | 26 | 204 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 908 | 0 | 43 | 0 | 185 | 0 | 300 | 280 | 47 | 0 | 20 | 34 | 0 | 142 | 21 | 20 | 30 | 30 | 0 | 3 | 37 | 290 | 320 | 333 | 0 | 0 | 134 | 8 | 0 | 80 | 30 | 0 | 18 | 171 | 17 | 45 | 45 | 87 | 0 | 3.18 | 12 | 6189.18 | 890 | 240 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 400 | 0 | 878.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 2.74 | 0 | 0 | 201 | 0 | 206 | 0 | 366 | 0 | 0.26 | 197 | 49 | 0 | 3 | 6 | 0 | 0 | 1.5 | 8 | 0.05 | 0 | 172 | 5 | 120 | 220 | 0 | 0 | 845 | 0 | 4853.2 | 11042.38 | 96.68
19:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 13 | 27 | 16 | 0 | 0 | 8 | 7 | 13 | 420 | 306 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 102 | 26 | 0 | 0 | 350 | 0 | 15 | 0 | 0 | 13 | 65 | 37 | 0 | 24 | 50 | 0 | 172 | 2 | 35 | 203 | 0 | 0 | 5 | 0 | 17 | 221 | 0 | 0 | 0 | 1113 | 0 | 43 | 15 | 185 | 0 | 335 | 325 | 46 | 0 | 20 | 51 | 0 | 144 | 27 | 20 | 32 | 40 | 0 | 0 | 37 | 295 | 320 | 370 | 0 | 0 | 139 | 8 | 0 | 81 | 30 | 0 | 18 | 171 | 17 | 45 | 142 | 85 | 0 | 0 | 8 | 7041 | 891 | 240 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 1033.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 206 | 0 | 385 | 0 | 0 | 195 | 49 | 95 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 10 | 120 | 220 | 0 | 0 | 878 | 0 | 5300.62 | 12341.62 | 96.67
19:30 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 17 | 123 | 16 | 0 | 0 | 17 | 48 | 16 | 420 | 291 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 125 | 26 | 0 | 0 | 500 | 0 | 15 | 0 | 0 | 14 | 65 | 39 | 0 | 48 | 65 | 0 | 172 | 17 | 33 | 203 | 0 | 0 | 30 | 0 | 30 | 220 | 0 | 0 | 0 | 1185 | 0 | 43 | 40 | 185 | 0 | 347 | 335 | 46 | 0 | 20 | 99 | 0 | 153 | 29 | 20 | 34 | 38 | 0 | 0 | 37 | 290 | 320 | 354 | 0 | 0 | 147 | 8 | 0 | 81 | 30 | 0 | 18 | 171 | 17 | 45 | 160 | 88 | 0 | 0 | 12 | 7702 | 890 | 240 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 535 | 0 | 1118.91 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 206 | 0 | 352 | 0 | 0 | 198 | 49 | 108 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 10 | 120 | 220 | 0 | 0 | 1110 | 0 | 5781.91 | 13483.91
20:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 25 | 26 | 113 | 16 | 0 | 0 | 17 | 48 | 16 | 420 | 296 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 125 | 26 | 14 | 0 | 500 | 0 | 15 | 0 | 0 | 16 | 65 | 39 | 0 | 48 | 65 | 0 | 172 | 17 | 35 | 204 | 0 | 0 | 31 | 0 | 33 | 220 | 0 | 0 | 0 | 1224 | 0 | 43 | 41 | 170 | 0 | 346 | 335 | 44 | 0 | 20 | 105 | 0 | 156 | 28 | 20 | 32 | 38 | 0 | 0 | 38 | 290 | 320 | 392 | 0 | 0 | 150 | 8 | 0 | 80 | 30 | 0 | 18 | 171 | 17 | 45 | 168 | 87 | 0 | 0 | 12 | 7795 | 890 | 239 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 602 | 0 | 1174.89 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 205 | 0 | 370 | 0 | 0 | 194 | 49 | 114 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 10 | 120 | 220 | 0 | 0 | 1120 | 0 | 5932.89 | 13727.89 | 96.66
21:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 35 | 123 | 16 | 0 | 0 | 17 | 51 | 16 | 420 | 303 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 125 | 26 | 20 | 0 | 500 | 0 | 15 | 0 | 0 | 22 | 65 | 39 | 0 | 48 | 70 | 0 | 172 | 17 | 35 | 204 | 0 | 0 | 32 | 0 | 33 | 220 | 0 | 0 | 0 | 1220 | 0 | 43 | 50 | 165 | 0 | 344 | 335 | 47 | 0 | 20 | 110 | 0 | 179 | 28 | 20 | 40 | 40 | 0 | 0 | 38 | 290 | 320 | 387 | 0 | 0 | 146 | 8 | 0 | 81 | 30 | 0 | 18 | 171 | 17 | 57 | 170 | 88 | 0 | 0 | 12 | 7898 | 891 | 239 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 572 | 0 | 1199 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 204 | 0 | 393 | 0 | 0 | 200 | 49 | 114 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 11 | 124 | 220 | 0 | 0 | 1111 | 0 | 5981 | 13879 | 96.65
22:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 35 | 123 | 16 | 0 | 0 | 17 | 53 | 16 | 420 | 300 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 125 | 20 | 20 | 0 | 584 | 0 | 15 | 0 | 0 | 33 | 65 | 39 | 0 | 48 | 70 | 0 | 172 | 17 | 10 | 204 | 0 | 0 | 0 | 0 | 34 | 221 | 0 | 0 | 0 | 1224 | 0 | 51 | 50 | 165 | 0 | 351 | 335 | 48 | 30 | 20 | 114 | 0 | 194 | 29 | 20 | 64 | 42 | 0 | 0 | 38 | 285 | 320 | 373 | 0 | 0 | 153 | 8 | 0 | 80 | 30 | 0 | 18 | 171 | 29 | 84 | 182 | 82 | 0 | 0 | 12 | 8064 | 890 | 233 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 593 | 0 | 1176 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 203 | 0 | 414 | 0 | 0 | 203 | 49 | 114 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 11 | 120 | 220 | 0 | 0 | 1125 | 0 | 6001 | 14065 | 96.64
23:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 35 | 127 | 16 | 0 | 0 | 17 | 50 | 16 | 420 | 311 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 125 | 20 | 20 | 0 | 584 | 0 | 15 | 0 | 0 | 31 | 65 | 39 | 0 | 48 | 70 | 0 | 172 | 17 | 36 | 204 | 0 | 0 | 14 | 0 | 30 | 221 | 0 | 0 | 0 | 1224 | 0 | 51 | 50 | 168 | 0 | 348 | 340 | 48 | 27 | 20 | 73 | 0 | 174 | 29 | 20 | 97 | 42 | 3 | 0 | 38 | 290 | 320 | 373 | 0 | 0 | 154 | 8 | 0 | 80 | 30 | 0 | 18 | 171 | 35 | 84 | 182 | 82 | 0 | 0 | 12 | 8098 | 891 | 233 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 591 | 0 | 1172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 202 | 0 | 373 | 0 | 0 | 202 | 48 | 114.5 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 11 | 120 | 220 | 0 | 0 | 1230 | 0 | 6021.5 | 14119.5 | 96.63
Total KWH | 0 | 317760 | 263520 | 0 | 0 | 0 | 0 | 0 | 9658800 | 0 | 0 | 478440 | 348840 | 1639152 | 312960 | 69753 | 0 | 150003 | 678240 | 211200 | 9500000 | 7216815 | 0 | 0 | 25830 | 7824185 | 0 | 0 | 150954 | 2050800 | 567000 | 342000 | 0 | 10646818.18 | 0 | 97855 | 0 | 0 | 560640 | 445688 | 336096 | 0 | 607680 | 827520 | 20520 | 4122080 | 92800 | 681600 | 4967272.73 | 0 | 0 | 206880 | 4617 | 272654 | 5202142 | 0 | 0 | 0 | 24774543 | 25380 | 1110256 | 331200 | 4248727 | 0 | 8561000 | 7970000 | 1142400 | 82000 | 471528 | 836160 | 0 | 4273440 | 348600 | 453840 | 1129740 | 881280 | 417576 | 301300 | 576704 | 6987000 | 7672200 | 9172000 | 0 | 0 | 3594273 | 164808 | 0 | 1886400 | 716928 | 0 | 426000 | 4531740 | 356040 | 1513200 | 2882400 | 1692480 | 9300 | 224720 | 288480 | 170952757.91 | 21538909 | 5609088 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 317520 | 12254550 | 50880 | 25664187.74 | 0 | 0 | 0 | 285024 | 0 | 49808 | 0 | 16969 | 0 | 343250 | 27662 | 230248 | 77364 | 0 | 4914782 | 0 | 4327336 | 0 | 9275272 | 0 | 20640 | 4602000 | 1134109 | 1509778 | 193748 | 1370140 | 0 | 0 | 50229.12 | 1211760 | 2904 | 0 | 5258000 | 189750 | 2850000 | 5410180 | 0 | 3687272.73 | 24942545.45 | 50400 | 138378306.04 | 309331063.95

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 04-07-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12021 | MW | 12:00 Hr. | Energy Generated |  |  | 309.3311 |  | MKWHr.
| Day Peak Demand |  |  | 12021 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.347 |  | MKWHr.
| Evening Peak Generation |  |  | 13879 | MW | 21:00 Hr. | Energy Demand |  |  | 309.6781 |  | MKWHr.
| Evening Peak Demand |  |  | 13879 | MW | 21:00 Hr. | Maximum Temperature |  |  | 30.7 |  | °C
| Minimum Generation of the Day |  |  | 11105.49 | MW | 10:00 Hr. | Total Gas Supplied |  |  | 1014.81 |  | MMCFD
| Maximum Generation of the Day |  |  | 15150.7 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.8871 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 45.7556 | 0 | 6.5465 | 0 | 0 | 0.15095 | 0 | 0 | 52.4531 | Gas | 145.1767 | Gas | 517403295.6706
| Chattogram Zone |  |  | 5.8837 | 29.7418 | 2.8918 | 0 | 4.1221 | 0.0459 | 0 | 0.56064 | 43.246 | Coal | 81.6203 | Coal | 526142719.5925
| Cumilla Zone |  |  | 24.0398 | 0 | 7.9134 | 0 | 0 | 0.3013 | 0.88128 | 0 | 33.1358 | HFO | 25.7525 | HFO | 482991608.18
| Mymensingh Zone |  |  | 1.6925 | 0 | 5.0401 | 0 | 0 | 0.23402 | 0 | 0 | 6.9666 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 35.1513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.1513 | Hydro | 4.1221 | Hydro | 412208
| Khulna Zone |  |  | 5.6091 | 12.2546 | 0.05088 | 0 | 0 | 0.31752 | 22.4509 | 0 | 40.6829 | Solar | 3.1025 | Solar | 51715389.8832
| Barishal Zone |  |  | 8.4499 | 33.8878 | 0.0504 | 0 | 0 | 0.002904 | 0 | 0 | 42.3911 | Import | 48.9964 | Import | 234202242.6984
| Rajshahi Zone |  |  | 18.5948 | 0 | 0.37946 | 0 | 0 | 0.59414 | 25.6642 | 0 | 45.2325 | Wind | 0.56064 | Wind | 8207769.6
| Rangpur Zone |  |  | 0 | 5.7361 | 2.8799 | 0 | 0 | 1.4557 | 0 | 0 | 10.0718
| Total |  |  | 145.1767 | 81.6203 | 25.7525 | 0 | 4.1221 | 3.1025 | 48.9964 | 0.56064 | 309.3311
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 517403295.6706 |  | Hydro | 412208
|  |  |  | Coal | 526142719.5925 |  | Solar | 51715389.8832
|  |  |  | HFO | 482991608.18 |  | Import | 234202242.6984
|  |  |  | HSD | 0 |  | Wind | 8207769.6
[5 empty] | Total: | 182,10,75,233 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5389 | Peak Hr Flow | 891.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 33249563.72 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 25.6642 | Peak Hr Flow | 1199.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 836 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.88128 | Peak Hr Flow | 40.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 998 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 48.0844 | Peak Hr Flow | 2130.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4606
|  |  |  | Chattogram |  | 0 |  | 1247
|  |  |  | Cumilla |  | 0 |  | 1404
|  |  |  | Mymensingh |  | 0 |  | 1163
|  |  |  | Sylhet |  | 0 |  | 643
|  |  |  | Khulna |  | 0 |  | 1514
|  |  |  | Barishal |  | 0 |  | 462
|  |  |  | Rajshahi |  | 0 |  | 1401
|  |  |  | Rangpur |  | 0 |  | 959
|  |  |  | Total |  | 0 |  | 13399
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[5 empty] | Total | 300 |  |  |  | Total | 476
|  |  |  | Total Unavailable Capacity |  |  |  | 776
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:08 |  | Sirajgonj 225MW CCPP Unit-3 Synchronized with remarks:- ST
| 08:08 |  | Sirajgonj 225MW CCPP Unit-3 ST Synchronized with remarks:- As instructed by NLDC.
| 08:29 | 13:03 | Chapai 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to 33 kv barendra feeder bus loop | [7 empty] | 25.0MW load
|  |  | change maintenance work | [7 empty] | interrup.
| 08:30 | 13:03 | Chapai 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to 33 kv barendra feeder bus loop | [7 empty] | 25.0MW load
|  |  | change maintenance work | [7 empty] | interrup.
|  | 08:51 | Madaripur 132/33kV S/S T3-426T HT is restored.
|  | 08:52 | Madaripur 132/33kV S/S T3-426T LT is restored.
| 09:10 | 11:04 | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to 33kv Jhalokathi feeder maintenance | [7 empty] | 30.0MW load
interrup.
| 09:11 | 11:02 | Barishal 230/132kV S/S T-5 HT Scheduled S/D | [7 empty] | 30.0MW load
interrup.
|  | 09:26 | Faridpur 132/33kV S/S Transformer-1 HT is restored.
|  | 09:27 | Faridpur 132/33kV S/S Transformer-1 LT is restored.
| 09:29 | 11:45 | Chapai 132/33kV S/S T-3 (425T) LT Scheduled S/D Due to T-2 & T-03 broken bus section DS
insulator change.
| 09:30 | 11:42 | Chapai 132/33kV S/S T-3 (425T) HT Scheduled S/D Due to T-2 & T-03 broken bus section DS
insulator change.
| 09:38 | 15:21 | Baghabari-Ishurdi 230 kV Ckt-1 Project Work S/D from Ishurdi 230/132kV end.
| 09:39 | 15:25 | Baghabari-Ishurdi 230 kV Ckt-2 Project Work S/D from Ishurdi 230/132kV end.
| 09:40 | 12:28 | Madunaghat-Sikalbaha 132kV Ckt-2 Scheduled S/D from Madunaghat 132/33kV end Due to For
Army project work.
| 09:46 | 12:29 | Madunaghat-TKCL 132kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end Due to For Army
project work
| 09:54 | 16:54 | Cumilla(S) 132/33kV S/S Tripura Ckt-1 Scheduled S/D Due to Work for Tripura end
|  | 10:23 | Chowmuhani-Feni 132 kV Ckt-1 is restored.
|  | 11:20 | Sylhet 132/33kV S/S T1 HT is restored.
|  | 11:22 | Sylhet 132/33kV S/S T1 LT is restored.
| 12:00 |  | Day Peak Generation: 12017 MW.
| 13:28 |  | Patuakhali 1320 MW (RNPL) Unit-2 was shutdown due to generator cooling issue
| 14:18 |  | GPH 230/33kV S/S Transformer-01(D05) HT Forced S/D Due to routine maintenance work
|  | 15:23 | Kabirpur 132/33kV S/S XFR, T-3 HT is restored.
|  | 17:14 | Mirpur 132/33kV S/S Main Bus is restored.
| 19:09 |  | Adani–Rohanpur CKT-2 tripped at 19:09 hrs while being switched on after a scheduled
shutdown taken by Adani for maintenance purposes. Relay indicated SOTF and Distance (51.3
KM from Rohanpur) on Rohanpur SS.
| 20:30 | 20:55 | Faridpur 132/33kV S/S Transformer-2 LT Tripped showing 33kV Over current relays Due to | [7 empty] | 66.0MW load
|  |  | 33kV khalil Mondol hat & Vanga-2 PBS Feeder fault. | [7 empty] | interrup.
| 20:30 | 20:53 | Faridpur 132/33kV S/S Transformer-1 LT Tripped showing 33kV Over current relays Due to | [7 empty] | 66.0MW load
|  |  | 33kV khalil Mondol hat & Vanga-2 PBS Feeder fault. | [7 empty] | interrup.
| 21:00 |  | Evening Peak Generation 13879 MW.
| 21:40 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- GT
| 21:40 |  | Ashuganj CCPP 225 MW GT was sync. at 21:40 hrs.
| 21:43 | 22:57 | Gopalganj 400/132kV S/S ATR-04 LT Project Work S/D
| 21:43 | 22:57 | Gopalganj 400/132kV S/S ATR-04 LT Project Work S/D
| 21:45 | 22:56 | Gopalganj 400/132kV S/S ATR-04 HT Project Work S/D
| 22:30 | 23:45 | Chowmuhani 132/33kV S/S TR3-435T HT Forced S/D Due to 33 KV Dotterhat feeder Red Hot | [7 empty] | 50.0MW load
|  |  | Maintenance | [7 empty] | interrup.
| 22:30 | 23:45 | Chowmuhani 132/33kV S/S TR3-435T LT Forced S/D Due to 33 KV Dotterhat Feeder Red Hot | [7 empty] | 560.0MW load
|  |  | Maintenence | [7 empty] | interrup.
| 02:52 |  | Goalpara 132/33kV S/S T1 HT Tripped showing differential relays Due to Rain
| 02:52 |  | Goalpara 132/33kV S/S T1 LT Tripped showing Differential relays Due to Rainfall
| 02:52 |  | Goalpara 132/33kV S/S T1 HT Tripped showing Differential relay relays Due to Rainfall
| 02:53 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- ST
| 07:00 |  | Minimum Generation is 11588 MW
| 07:03 |  | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) LT Scheduled S/D Due to Red Hot Maintenance | [7 empty] | 35.0MW load
interrup.
| 07:04 |  | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) HT Scheduled S/D Due to Red Hot Maintenance | [7 empty] | 35.0MW load
interrup.
| 07:10 |  | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) LT Scheduled S/D Due to Red Hot Maintenance | [7 empty] | 35.0MW load
interrup.
| 07:10 |  | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) HT Scheduled S/D Due to Red Hot Maintenance | [7 empty] | 35.0MW load
interrup.
| 07:50 |  | Magura 132/33kV S/S T-3 (425T) LT Tripped showing 51/51N relays Due to Pbs 33kV Rawtara | [7 empty] | 30.0MW load
|  |  | feeder trip. | [7 empty] | interrup.
| 07:52 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT Scheduled S/D
| 07:53 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) HT Scheduled S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 04-07-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 401 | 9658800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9500000 | Allocation limit by Titas, instructed by DS(Gen)
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 303 | 7216815 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 7824185 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 478440 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 16 | 312960 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 150003 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 25830 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 26 | 567000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 342000 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 17 | 263520 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 69753 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 123 | 1639152 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 317760 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 211200 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 51 | 678240 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 150954 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 348840 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 500 | 10646818.18 | FGMO
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage instructed by DS(Gen)
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 125 | 2050800 | Engine Problem
Dhaka Area Total |  |  |  |  | 5939.724 | 2452 | 52453070.18
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 4617 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 25380 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 32 | 206880 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 172 | 4122080 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 5202142 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 33 | 272654 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 39 | 336096 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 445688 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 48 | 607680 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 35 | 681600 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20520 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 97855 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 92800 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 70 | 827520 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1220 | 24774543 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 22 | 560640 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 204 | 4967272.73 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4895.72 | 2192 | 43245967.73
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 0 | 82000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 344 | 8561000 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 335 | 7970000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 20 | 471528 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 47 | 1142400 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 165 | 4248727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 43 | 1110256 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 50 | 331200 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 38 | 576704 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 179 | 4273440 | -
| Import (Tripura) |  | Import | 0 | 160 | 40 | 881280 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 417576 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 453840 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 40 | 1129740 | Engine Problem
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 348600 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 110 | 836160 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 301300 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1459 | 33135751
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 88 | 1692480 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9300 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 170 | 2882400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 57 | 1513200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 224720 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 288480 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 356040 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 344 | 6966620
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | Gas shortage instructed by DS(Gen)
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 146 | 3594273 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 716928 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1886400 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 171 | 4531740 | Machine Problem
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 426000 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 164808 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 6987000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 387 | 9172000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7672200 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1451 | 35151349
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 891 | 21538909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 239 | 5609088 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 50880 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 317520 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 572 | 12254550 | U#2 under shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1740 | 40682947
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 0 | 3687272.73 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 11 | 189750 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 124 | 2850000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1111 | 24942545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5410180 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 50400 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 282 | 5258000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2904 | -
Barishal Area Total |  |  |  |  | 2236 | 1748 | 42391052.18
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 16969 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 77364 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 201 | 4914782 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 204 | 4327336 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 393 | 9275272 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 27662 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 49808 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 285024 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 20640 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1199 | 25664187.74 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 230248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 343250 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2032 | 45232542.74
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 49 | 1134109 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4602000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 1370140 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 50229.12 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 114 | 1509778 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 193748 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1211760 | -
Rangpur Area Total |  |  |  |  | 950 | 461 | 10071764.12
Eastern Grid Total |  |  |  |  | 16705.895 | 7898 | 170952757.91
Western Grid Total |  |  |  |  | 10378.16 | 5981 | 138378306.04
National Grid Total |  |  |  |  | 27084.055 | 13879 | 309331063.95
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 04-07-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9063.09 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4335.8 | MW
i) Dhaka area |  |  | 4606.27 |  | MW | i) Khulna area |  |  |  | 1514.2 | MW
ii) Chattogram area |  |  | 1247 |  | MW | ii) Barishal area |  |  |  | 462 | MW
iii) Cumilla area |  |  | 1403.82 |  | MW | iii) Rajshahi area |  |  |  | 1400.6 | MW
iv) Mymensingh area |  |  | 1163 |  | MW | iv) Rangpur area |  |  |  | 959 | MW
v) Sylhet area |  |  | 643 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13398.89 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 77 | 00:00 | 133 | Pabna | 119 | 00:00
2 | AKSML | 118 | 13:00 | 68 | Ishurdi | 75 | 00:00 | 134 | Palashbari | 118 | 00:00
3 | Aftabnagar | 36 | 00:00 | 69 | Jaldhaka | 88 | 02:00 | 135 | Panchagarh | 64 | 19:30
4 | Agargaon | 116 | 00:00 | 70 | Jamalpur | 134 | 00:00 | 136 | Patuakhali | 79.5 | 00:00
5 | Agrabad | 76 | 19:00 | 71 | Jashore | 136 | 00:00 | 137 | Payra | 32 | 01:00
6 | Amnura | 40 | 22:00 | 72 | Jhenaidah | 124 | 00:00 | 138 | Postogola | 55 | 00:00
7 | Ashuganj | 108 | 23:00 | 73 | Joydebpur | 124 | 00:00 | 139 | Purbachal | 21 | 00:00
8 | BSRM | 194 | 09:00 | 74 | Joypurhat | 69 | 21:00 | 140 | Purbasadipur | 145 | 00:00
9 | Bagerhat | 83 | 00:00 | 75 | Juldah | 15 | 00:00 | 141 | Rahanpur | 31 | 22:00
10 | Bajitpur | 68 | 00:00 | 76 | KSRM | 20 | 02:00 | 142 | Rahim | 28 | 09:00
11 | Bakulia | 78 | 01:00 | 77 | Kabirpur | 180 | 00:00 | 143 | Rajbari | 80 | 00:00
12 | Banani | 25.6 | 19:00 | 78 | Kachua | 90 | 22:00 | 144 | Rajendrapur | 136 | 00:00
13 | Bangabhaban | 4 | 00:00 | 79 | Kallyanpur | 105 | 00:00 | 145 | Rajshahi | 119 | 23:00
14 | Barapukuria | 66 | 00:00 | 80 | Kalurghat | 30 | 00:00 | 146 | Rajshahi-230 | 86 | 13:00
15 | Barguna | 22 | 00:00 | 81 | Kamrangirchar | 62.8 | 00:00 | 147 | Ramganj | 114 | 13:00
16 | Barishal | 94 | 22:00 | 82 | Kaptai | N/A | N/A | 148 | Rampur | 38 | 00:00
17 | Barishal-230 | 104 | 19:30 | 83 | Kasba | 37 | 21:00 | 149 | Rangamati | 16 | 19:30
18 | Baroaulia | 58 | 23:00 | 84 | Kazla | 89 | 01:00 | 150 | Rangpur | 157 | 01:00
19 | Baroirhat | 57 | 00:00 | 85 | Keranigonj | 100 | 00:00 | 151 | Ruppur | 5.8 | 09:00
20 | Bashundhara | 166 | 00:00 | 86 | Khagrachori | 30 | 21:00 | 152 | SSM | 15 | 06:00
21 | BashundharaCement | 7 | 00:00 | 87 | Khulna | 62 | 13:00 | 153 | Saidpur | 96 | 00:00
22 | Beanibazar | 82 | 19:00 | 88 | Khulshi | 135 | 19:00 | 154 | Satkhira | 126 | 00:00
23 | Benapole | 68 | 00:00 | 89 | Kishoreganj | 144 | 23:00 | 155 | Satmasjid | 90 | 00:00
24 | Bhaluka | 152 | 00:00 | 90 | Kodda | 282 | 00:00 | 156 | Savar | 189 | 00:00
25 | Bhandaria | 56 | 22:00 | 91 | Kulaura | 59 | 23:00 | 157 | SevenRings | 18.52 | 23:00
26 | Bhangura | 35 | 00:00 | 92 | Kurigram | 68 | 20:00 | 158 | ShahCement | 26 | 21:00
27 | Bheramara(GK) | 64 | 01:00 | 93 | Kushtia | 158 | 00:00 | 159 | Shahjadpur | 75 | 00:00
28 | Bhulta | 243 | 00:00 | 94 | Lakshmipur | 21.07 | 23:00 | 160 | Shahjibazar | 130 | 00:00
29 | Bog-Sherpur | 68 | 00:00 | 95 | Lalbag | 53 | 00:00 | 161 | Shahmirpur | 58 | 02:00
30 | Bogura | 172 | 01:00 | 96 | Lalmonirhat | 66 | 00:00 | 162 | Shariatpur | 88 | 00:00
31 | Borhanuddin | 86 | 00:00 | 97 | MI_Cement | 12 | 00:00 | 163 | Sherpur | 160 | 01:00
32 | Brahmanbaria | 130 | 22:00 | 98 | Madanganj | 48 | 00:00 | 164 | Shikalbaha | 18 | 00:00
33 | Cantonment | 134 | 12:00 | 99 | Madaripur | 111 | 00:00 | 165 | Shitalakhya | 62.5 | 00:00
34 | Chandina | 15.1 | 23:00 | 100 | Madartek | 91.73 | 00:00 | 166 | Sholosohor | 39 | 00:00
35 | Chandpur | 78 | 22:00 | 101 | Madunaghat | 53 | 01:00 | 167 | Shyampur | 162 | 02:00
36 | Chandraghona | 34 | 23:00 | 102 | Magura | 64 | 00:00 | 168 | Siddhirganj | 106 | 00:00
37 | Chapai | 69 | 22:00 | 103 | Mahasthangarh | 92 | 00:00 | 169 | Sirajganj | 104 | 00:00
38 | Charsaidpur | 37 | 01:00 | 104 | Maijdee | 14 | 01:00 | 170 | Sonargaon | 87 | 07:00
39 | Chauddagram | 70 | 23:00 | 105 | Manikganj | 120 | 00:00 | 171 | Sreemongol | 81 | 00:00
40 | Chhatak | 45 | 00:00 | 106 | Maniknagar | 72 | 00:00 | 172 | Sreepur | 91 | 00:00
41 | Chowmuhani | 191 | 21:00 | 107 | Matarbari | 44 | 00:00 | 173 | Srinagar | 47.26 | 22:00
42 | Chuadanga | 109 | 00:00 | 108 | Matuail | 64 | 00:00 | 174 | Sunamganj | 64 | 23:00
43 | Coxsbazar | 127 | 19:00 | 109 | Millgate | 90 | 00:00 | 175 | Sylhet | 52 | 01:00
44 | Cumilla(N) | 152 | 00:00 | 110 | Mirpur | 111 | 00:00 | 176 | Sylhet-132 | 138 | 23:00
45 | Cumilla(S) | 163 | 01:00 | 111 | Mirsorai | 8 | 00:00 | 177 | TK | 34.5 | 13:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirzapur | 44 | 00:00 | 178 | Tangail | 176 | 00:00
47 | Daudkandi | 150 | 21:00 | 113 | Mithapukur | 73 | 00:00 | 179 | Taraganj | 24 | 00:00
48 | Dhaka | 34 | 13:00 | 114 | Modern | N/A | N/A | 180 | Thakurgaon | 114 | 20:00
49 | Dhamrai | 130 | 00:00 | 115 | Mogbazar | 116.9 | 15:00 | 181 | Tongi | 121 | 00:00
50 | Dhanmondi | 114 | 19:00 | 116 | Mongla | 44 | 00:00 | 182 | Ullahpara | 37 | 00:00
51 | Dohazari | 100 | 19:00 | 117 | Motijheel | 35 | 00:00 | 183 | Ullon | 41 | 00:00
52 | Faridpur | 160 | 00:00 | 118 | Muktagacha | 38 | 00:00 | 184 | Uttara | 73 | 16:00
53 | Fatullah | 84 | 00:00 | 119 | Munshiganj | 114 | 00:00 | 185 | UttaraNew | 59 | 00:00
54 | Fenchuganj | 42 | 01:00 | 120 | Muradnagar | 28 | 00:00 | 186 | Zigatola | 74 | 00:00
55 | Feni | 109 | 23:00 | 121 | Mymensingh | 208 | 00:00
56 | GPH | 96 | 06:00 | 122 | Naogaon | 137 | 00:00
57 | Ghatail | 82 | 20:00 | 123 | Narail | 57 | 00:00
58 | Ghorashal | 15 | 01:00 | 124 | Narinda | 54 | 00:00
59 | Ghorashal-230 | 88 | 00:00 | 125 | Narshingdi | 182 | 23:00
60 | Goalpara | 36 | 00:00 | 126 | Natore | 146 | 00:00
61 | Gollamari | 94 | 00:00 | 127 | Nawabganj | 60 | 23:00
62 | Gopalganj | 100.8 | 00:00 | 128 | Netrakona | 130 | 23:00
63 | Gulshan | 94 | 14:00 | 129 | New | 54.8 | 00:00
64 | Halishahar | 45.5 | 10:00 | 130 | Niamatpur | 76 | 22:00
65 | HaripurSBU | 152 | 01:00 | 131 | Noapara | 39 | 00:00
66 | Hasnabad | 61 | 00:00 | 132 | PHP | 6 | 14:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 04-07-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15150.7 | 67 |  | 15220.72
1:00 | 14721.7 | 75 |  | 14800.08
2:00 | 14263.7 | 74 |  | 14341.03
3:00 | 13799.7 | 63 |  | 13865.54
4:00 | 13473.7 | 40 |  | 13515.5
5:00 | 13133.7 | 0 |  | 13133.7
6:00 | 12389.74 | 0 |  | 12389.74
7:00 | 12014.3 | 0 |  | 12014.3
8:00 | 11563 | 28 |  | 11592.26
9:00 | 11366.34 | 0 |  | 11366.34
10:00 | 11105.49 | 0 |  | 11105.49
11:00 | 11322.38 | 0 |  | 11322.38
12:00 | 12021 | 0 |  | 12021
13:00 | 12579.86 | 0 |  | 12579.86
14:00 | 12323.39 | 0 |  | 12323.39
15:00 | 12141.49 | 0 |  | 12141.49
16:00 | 11634.89 | 0 |  | 11634.89
17:00 | 11358.1 | 0 |  | 11358.1
18:00 | 11042.38 | 0 |  | 11042.38
19:00 | 12341.62 | 0 |  | 12341.62
19:30 | 13483.91 | 0 |  | 13483.91
20:00 | 13727.89 | 0 |  | 13727.89
21:00 | 13879 | 0 |  | 13879
22:00 | 14065 | 0 |  | 14065
23:00 | 14119.5 | 0 |  | 14119.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 04-07-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8414.7 | 6736 | 15150.7 | DAILY GENERATION CURVE
00:30 | 8307.7 | 6628.5 | 14936.2
01:00 | 8200.7 | 6521 | 14721.7 | 04-07-2025
01:30 | 8007.7 | 6485 | 14492.7
02:00 | 7814.7 | 6449 | 14263.7
02:30 | 7628.7 | 6403 | 14031.7
03:00 | 7442.7 | 6357 | 13799.7
03:30 | 7343.2 | 6293.5 | 13636.7
04:00 | 7243.7 | 6230 | 13473.7
04:30 | 7162.2 | 6141.5 | 13303.7
05:00 | 7080.7 | 6053 | 13133.7
05:30 | 6940.61 | 5821.11 | 12761.72
06:00 | 6800.52 | 5589.22 | 12389.74
06:30 | 6654.545 | 5547.475 | 12202.02
07:00 | 6508.57 | 5505.73 | 12014.3
07:30 | 6385.095 | 5403.555 | 11788.65
08:00 | 6261.62 | 5301.38 | 11563
08:30 | 6241.435 | 5223.235 | 11464.67
09:00 | 6221.25 | 5145.09 | 11366.34
09:30 | 6109.78 | 5126.135 | 11235.915
10:00 | 5998.31 | 5107.18 | 11105.49
10:30 | 6103.44 | 5110.495 | 11213.935
11:00 | 6208.57 | 5113.81 | 11322.38
11:30 | 6388.96 | 5282.73 | 11671.69
12:00 | 6569.35 | 5451.65 | 12021
12:30 | 6726.65 | 5573.78 | 12300.43
13:00 | 6883.95 | 5695.91 | 12579.86
13:30 | 6884.57 | 5567.055 | 12451.625
14:00 | 6885.19 | 5438.2 | 12323.39
14:30 | 6802.72 | 5429.72 | 12232.44
15:00 | 6720.25 | 5421.24 | 12141.49
15:30 | 6582.815 | 5305.375 | 11888.19
16:00 | 6445.38 | 5189.51 | 11634.89
16:30 | 6424.33 | 5072.165 | 11496.495
17:00 | 6403.28 | 4954.82 | 11358.1
17:30 | 6296.23 | 4904.01 | 11200.24
18:00 | 6189.18 | 4853.2 | 11042.38
18:30 | 6615.09 | 5076.91 | 11692
19:00 | 7041 | 5300.62 | 12341.62
19:30 | 7702 | 5781.91 | 13483.91
20:00 | 7795 | 5932.89 | 13727.89
20:30 | 7846.5 | 5956.945 | 13803.445 |  | Executive Engineer
21:00 | 7898 | 5981 | 13879 |  | Network Operation Division
21:30 | 7981 | 5991 | 13972
22:00 | 8064 | 6001 | 14065
22:30 | 8081 | 6011.25 | 14092.25
23:00 | 8098 | 6021.5 | 14119.5

## En-Curve
QF-LDC-12
Date | 04-07-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3784 | 2353.5 | 889 | 38 | 42 | 1418 | 172 | 3875 | 0 | 575 | 1968.2 | 0 | 0 | 36 | 67 | DAILY ENERGY CURVE
00:30 | 3784 | 2330.5 | 889 | 38 | 43 | 1418.5 | 172 | 3866.5 | 0 | 505.5 | 1852.2 | 0 | 0 | 37 | 71 | 04-07-2025
01:00 | 3784 | 2307.5 | 889 | 38 | 44 | 1419 | 172 | 3858 | 0 | 436 | 1736.2 | 0 | 0 | 38 | 75
01:30 | 3768 | 2317 | 889 | 38 | 43 | 1416 | 172 | 3859 | 0 | 353 | 1594.7 | 0 | 0 | 43 | 74.5 | Energy Generated | 309.3311 |  | MKWHr
02:00 | 3752 | 2326.5 | 889 | 38 | 42 | 1413 | 172 | 3860 | 0 | 270 | 1453.2 | 0 | 0 | 48 | 74 | Energy not Served | 0.347 |  | MKWHr
02:30 | 3724.5 | 2318.5 | 889 | 38 | 42 | 1411 | 172 | 3861 | 0 | 246.5 | 1282.2 | 0 | 0 | 47 | 68.5 | Total Energy Requirement | 309.6781 |  | MKWHr
03:00 | 3697 | 2310.5 | 889 | 38 | 42 | 1409 | 172 | 3862 | 0 | 223 | 1111.2 | 0 | 0 | 46 | 63
03:30 | 3710.5 | 2308 | 889 | 38 | 41 | 1363.5 | 172 | 3820 | 0 | 215 | 1048.2 | 0 | 0 | 31.5 | 51.5
04:00 | 3724 | 2305.5 | 889 | 38 | 40 | 1318 | 172 | 3778 | 0 | 207 | 985.2 | 0 | 0 | 17 | 40
04:30 | 3722 | 2309.5 | 889 | 38 | 39 | 1269.5 | 172 | 3713.5 | 0 | 198.5 | 943.7 | 0 | 0 | 9 | 20
05:00 | 3720 | 2313.5 | 889 | 38 | 38 | 1221 | 172 | 3649 | 0 | 190 | 902.2 | 0 | 0 | 1 | 0
05:30 | 3689 | 2304.75 | 889 | 38 | 37 | 1112.5 | 172 | 3574 | 10.87 | 164 | 766.6 | 0 | 0 | 4 | 0
06:00 | 3658 | 2296 | 889 | 38 | 36 | 1004 | 172 | 3499 | 21.74 | 138 | 631 | 0 | 0 | 7 | 0
06:30 | 3660.5 | 2216.5 | 889 | 38 | 35 | 962.5 | 172 | 3447.5 | 67.52 | 99 | 596 | 0 | 0 | 18.5 | 0
07:00 | 3663 | 2137 | 889 | 38 | 34 | 921 | 172 | 3396 | 113.3 | 60 | 561 | 0 | 0 | 30 | 0
07:30 | 3646 | 2118 | 889 | 38 | 33 | 891.52 | 172 | 3321 | 114.63 | 60 | 490.5 | 0 | 0 | 15 | 14
08:00 | 3629 | 2099 | 889 | 38 | 32 | 862.04 | 172 | 3246 | 115.96 | 60 | 420 | 0 | 0 | 0 | 28
08:30 | 3634 | 2080 | 889 | 38 | 32 | 857.665 | 172 | 3132.5 | 148.005 | 46.5 | 422 | 0 | 0 | 13 | 14
09:00 | 3639 | 2061 | 889 | 38 | 32 | 853.29 | 172 | 3019 | 180.05 | 33 | 424 | 0 | 0 | 26 | 0
09:30 | 3606.5 | 2016 | 889 | 38 | 31 | 843.305 | 172 | 2931 | 227.61 | 33 | 428 | 0 | 0 | 20.5 | 0
10:00 | 3574 | 1971 | 889 | 38 | 30 | 833.32 | 172 | 2843 | 275.17 | 33 | 432 | 0 | 0 | 15 | 0
10:30 | 3612 | 2018 | 889 | 38 | 30.5 | 835.155 | 172 | 2808 | 320.28 | 34.5 | 443 | 0 | 0 | 13.5 | 0
11:00 | 3650 | 2065 | 889 | 38 | 31 | 836.99 | 172 | 2773 | 365.39 | 36 | 454 | 0 | 0 | 12 | 0
11:30 | 3671.5 | 2149.5 | 889 | 38 | 32.5 | 894.415 | 172 | 2821 | 429.275 | 60.5 | 507.5 | 0 | 0 | 6.5 | 0
12:00 | 3693 | 2234 | 889 | 38 | 34 | 951.84 | 172 | 2869 | 493.16 | 85 | 561 | 0 | 0 | 1 | 0
12:30 | 3730 | 2287 | 889.5 | 38 | 36 | 975.855 | 172 | 3032.5 | 433.575 | 88.5 | 609.5 | 0 | 0 | 8 | 0
13:00 | 3767 | 2340 | 890 | 38 | 38 | 999.87 | 172 | 3196 | 373.99 | 92 | 658 | 0 | 0 | 15 | 0
13:30 | 3736.5 | 2280 | 890.5 | 38 | 37.5 | 983.955 | 172 | 3178.5 | 367.17 | 109.5 | 632 | 0 | 0 | 26 | 0
14:00 | 3706 | 2220 | 891 | 38 | 37 | 968.04 | 172 | 3161 | 360.35 | 127 | 606 | 0 | 0 | 37 | 0
14:30 | 3710.5 | 2218 | 890.5 | 38 | 36.5 | 970.43 | 172 | 3155 | 351.51 | 116 | 534 | 0 | 0 | 40 | 0
15:00 | 3715 | 2216 | 890 | 38 | 36 | 972.82 | 172 | 3149 | 342.67 | 105 | 462 | 0 | 0 | 43 | 0
15:30 | 3716.5 | 2204.5 | 890 | 38 | 33.5 | 920.52 | 172 | 3049.5 | 303.17 | 96.5 | 418.5 | 0 | 0 | 45.5 | 0
16:00 | 3718 | 2193 | 890 | 38 | 31 | 868.22 | 172 | 2950 | 263.67 | 88 | 375 | 0 | 0 | 48 | 0
16:30 | 3726 | 2195 | 890 | 38 | 31.5 | 872.025 | 172 | 2885 | 187.97 | 88 | 378 | 0 | 0 | 33 | 0
17:00 | 3734 | 2197 | 890 | 38 | 32 | 875.83 | 172 | 2820 | 112.27 | 88 | 381 | 0 | 0 | 18 | 0
17:30 | 3662.5 | 2173 | 890 | 38 | 31 | 877.24 | 172 | 2797.5 | 69 | 88.5 | 389.5 | 0 | 0 | 12 | 0
18:00 | 3591 | 2149 | 890 | 38 | 30 | 878.65 | 172 | 2775 | 25.73 | 89 | 398 | 0 | 0 | 6 | 0
18:30 | 3659.5 | 2166.5 | 890.5 | 38 | 35 | 956.135 | 172 | 2936 | 12.865 | 190 | 626 | 0 | 0 | 9.5 | 0
19:00 | 3728 | 2184 | 891 | 38 | 40 | 1033.62 | 172 | 3097 | 0 | 291 | 854 | 0 | 0 | 13 | 0
19:30 | 3753 | 2320 | 890 | 38 | 38 | 1118.91 | 172 | 3557 | 0 | 316 | 1267 | 0 | 0 | 14 | 0
20:00 | 3805 | 2326 | 890 | 38 | 38 | 1174.89 | 172 | 3673 | 0 | 317 | 1278 | 0 | 0 | 16 | 0
20:30 | 3815 | 2330.5 | 890.5 | 38 | 39 | 1186.945 | 172 | 3655.5 | 0 | 317 | 1340 | 0 | 0 | 19 | 0
21:00 | 3825 | 2335 | 891 | 38 | 40 | 1199 | 172 | 3638 | 0 | 317 | 1402 | 0 | 0 | 22 | 0
21:30 | 3841.5 | 2365 | 890.5 | 38 | 41 | 1187.5 | 172 | 3657 | 0 | 317 | 1435 | 0 | 0 | 27.5 | 0
22:00 | 3858 | 2395 | 890 | 38 | 42 | 1176 | 172 | 3676 | 0 | 317 | 1468 | 0 | 0 | 33 | 0
22:30 | 3834.5 | 2418 | 890.5 | 38 | 42 | 1174 | 172 | 3727.5 | 0 | 317 | 1446.75 | 0 | 0 | 32 | 0
23:00 | 3811 | 2441 | 891 | 38 | 42 | 1172 | 172 | 3779 | 0 | 317 | 1425.5 | 0 | 0 | 31 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 04-07-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 388 | 17:00 | 283 | 12:00 | Payra | 417 | 10:00 | 407 | 22:00
Ashuganj | 401 | 4:00 | 385 | 21:00 | Rahanpur | 404 | 06:00 | 377 | 22:00
Bhulta | 399 | 04:00 | 381 | 12:00 | Rampal | 405 | 17:00 | 388 | 22:00
Bibiana | 390 | 18:00 | 384 | 00:00
BIPTC | 402 | 06:00 | 392 | 00:00
Bogura | 388 | 06:00 | 366 | 21:00
Gopalganj | 402 | 18:00 | 386 | 00:00
Kaliakoir | 379 | 18:00 | 368 | 22:00
Madunaghat | 397 | 10:00 | 392 | 00:00
Meghnaghat | 393 | 18:30 | 383 | 01:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 227 | 18:00 | 221 | 00:00 | Keranigonj | 226 | 18:00 | 219 | 00:00
AKSML | 235 | 18:30 | 227 | 02:00 | Khulna(S) | 233 | 10:00 | 218 | 01:00
Aminbazar | 227 | 05:00 | 222 | 21:00 | Madunaghat | 234 | 18:30 | 230 | 03:00
Ashuganj | 233 | 18:00 | 224 | 21:00 | Madunaghat-400 | 234 | 09:00 | 231 | 04:00
Ashuganj-400 | 232 | 4:00 | 222 | 21:00 | Maniknagar | 223 | 06:00 | 217 | 00:00
Baghabari | 235 | 16:00 | 225 | 20:00 | Meghnaghat | 232 | 18:30 | 222 | 00:00
Barapukuria | 223 | 10:00 | 215 | 23:00 | Meghnaghat-400 | 228 | 18:00 | 222 | 00:00
Barapukuria-230 | 223 | 10:00 | 216 | 22:00 | Mirsorai | 230 | 18:00 | 224 | 00:00
Barishal | 231 | 16:00 | 222 | 00:00 | Rajshahi | 235 | 09:00 | 220 | 21:00
Bheramara | 233 | 09:00 | 221 | 21:00 | Rampal | 232 | 17:00 | 219 | 01:00
Bhulta | 230 | 04:00 | 217 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 232 | 18:30 | 223 | 21:00 | Rampura | 229 | 04:00 | 215 | 12:00
BIPTC | 236 | 09:00 | 221 | 21:00 | Shikalbaha | 232 | 00:00 | 228 | 04:00
Bogura | 234 | 06:00 | 222 | 23:00 | Shyampur | 226 | 18:00 | 218 | 01:00
Bogura-400 | 235 | 06:00 | 223 | 21:00 | Siddhirganj | 225 | 18:00 | 220 | 00:00
Borhanuddin | 237 | 18:00 | 228 | 00:00 | Sirajgonj | 239 | 17:00 | 232 | 21:00
BSRM | 229 | 18:00 | 224 | 01:00 | Sreepur | 229 | 18:00 | 220 | 22:00
Cumilla(N) | 226 | 17:00 | 219 | 00:00 | Tongi | 227 | 06:00 | 220 | 21:00
Faridpur | 229 | 17:00 | 218 | 00:00
Fenchuganj | 231 | 18:00 | 224 | 02:00
Ghorashal | 235 | 17:00 | 230 | 00:00
Ghorashal-230 | 228 | 18:30 | 219 | 22:00
Gopalganj | 230 | 18:00 | 220 | 00:00
GPH | 232 | 18:30 | 227 | 02:00
Haripur | 225 | 18:00 | 219 | 00:00
Hasnabad | 226 | 17:00 | 219 | 00:00
Hathazari | 232 | 18:30 | 225 | 00:00
Ishurdi | 236 | 09:00 | 224 | 21:00
Jhenaidah | 233 | 17:00 | 217 | 00:00
Kaliakoir | 233 | 18:00 | 225 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 03:00 | 127 | 11:00 | Madanganj | 132 | 18:00 | 124 | 10:00
Agargaon | 133 | 06:00 | 129 | 00:00 | Madaripur | 137 | 09:00 | 130 | 00:00
Agrabad | 133 | 00:00 | 129 | 04:00 | Madartek | 138 | 04:00 | 127 | 12:00
AKS | 130 | 00:00 | 128 | 03:00 | Madunaghat | 134 | 18:30 | 130 | 04:00
Aminbazar | 134 | 05:00 | 130 | 11:00 | Magura | 137 | 17:00 | 123 | 01:00
Amnura | 137 | 09:00 | 122 | 21:00 | Mahasthangarh | 135 | 09:00 | 126 | 01:00
Ashuganj | 140 | 09:00 | 134 | 23:00 | Maijdee | 119 | 18:00 | 108 | 00:00
Bagerhat | 136 | 10:00 | 121 | 02:00 | Manikganj | 130 | 08:00 | 123 | 00:00
Bajitpur | 134 | 18:00 | 124 | 21:00 | Maniknagar | 133 | 06:00 | 129 | 00:00
Bakulia | 134 | 18:30 | 131 | 04:00 | Matarbari | 126 | 09:00 | 117 | 04:00
Banani | 138 | 03:00 | 127 | 12:00 | Matuail | 132 | 18:00 | 127 | 00:00
Bangabhaban | 133 | 06:00 | 128 | 00:00 | Millgate | 133 | 05:00 | 128 | 21:00
Barapukuria | 136 | 11:00 | 129 | 08:00 | Mirpur | 133 | 06:00 | 127 | 13:00
Barguna | 135 | 08:00 | 130 | 22:00 | Mirzapur | 131 | 18:30 | 125 | 13:00
Barishal | 136 | 18:00 | 128 | 00:00 | Mithapukur | 132 | 10:00 | 119 | 00:00
Barishal-230 | 136 | 18:00 | 128 | 00:00 | MI_Cement | 132 | 18:00 | 128 | 00:00
Baroaulia | 132 | 00:00 | 130 | 13:00 | Modern | N/A | N/A | N/A | N/A
Baroirhat | 125 | 18:00 | 119 | 00:00 | Mogbazar | 138 | 01:00 | 130 | 11:00
Bashundhara | 138 | 04:00 | 128 | 01:00 | Mongla | 137 | 17:00 | 120 | 01:00
BashundharaCement | 132 | 18:00 | 124 | 10:00 | Motijheel | 133 | 06:00 | 128 | 00:00
Beanibazar | 129 | 10:00 | 123 | 21:00 | Muktagacha | 135 | 09:00 | 128 | 00:00
Benapole | 135 | 17:00 | 121 | 00:00 | Munshiganj | 132 | 18:00 | 127 | 00:00
Bhaluka | 132 | 17:00 | 124 | 22:00 | Muradnagar | 128 | 18:00 | 121 | 00:00
Bhandaria | 132 | 17:00 | 120 | 00:00 | Mymensingh | 136 | 14:00 | 116 | 21:00
Bhangura | 134 | 10:00 | 128 | 01:00 | Naogaon | 133 | 17:00 | 122 | 21:00
Bheramara | 137 | 08:00 | 132 | 01:00 | Narail | 137 | 17:00 | 121 | 00:00
Bheramara(GK) | 137 | 06:00 | 132 | 00:00 | Narinda | 133 | 6:00 | 129 | 0:00
Bhulta | 125 | 16:00 | 118 | 11:00 | Narshingdi | 132 | 17:00 | 117 | 21:00
Bog-Sherpur | 136 | 09:00 | 128 | 21:00 | Natore | 136 | 17:00 | 127 | 21:00
Bogura | 138 | 10:00 | 130 | 21:00 | Nawabganj | 135 | 18:00 | 128 | 00:00
Bogura-230 | 138 | 06:00 | 130 | 21:00 | Netrakona | 127 | 17:00 | 113 | 21:00
Brahmanbaria | 135 | 18:30 | 125 | 23:00 | New | 134 | 08:00 | 129 | 12:00
Cantonment | 133 | 06:00 | 129 | 00:00 | Niamatpur | 136 | 06:00 | 126 | 21:00
Chandina | 129 | 18:00 | 123 | 00:00 | Noapara | 138 | 17:00 | 126 | 00:00
Chandpur | 126 | 09:00 | 117 | 00:00 | Pabna | 135 | 06:00 | 129 | 00:00
Chandraghona | 133 | 09:00 | 131 | 15:00 | Palashbari | 132 | 10:00 | 119 | 20:00
Chapai | 132 | 04:00 | 125 | 20:00 | Panchagarh | 136 | 05:00 | 123 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 132 | 18:00 | 127 | 01:00 | Patuakhali | 135 | 09:00 | 131 | 23:00
Chauddagram | 124 | 18:00 | 117 | 00:00 | Payra | 137 | 18:00 | 133 | 22:00
Chhatak | 130 | 10:00 | 120 | 23:00 | PHP | 124 | 18:00 | 117 | 00:00
Chowmuhani | 121 | 18:00 | 109 | 22:00 | Postogola | 134 | 17:00 | 129 | 00:00
Chuadanga | 136 | 04:00 | 120 | 00:00 | Purbachal | 139 | 05:00 | 128 | 12:00
Coxsbazar | 125 | 09:00 | 118 | 19:00 | Purbasadipur | 131 | 05:00 | 122 | 07:00
Cumilla(N) | 129 | 17:00 | 123 | 00:00 | Rahanpur | 138 | 06:00 | 127 | 23:00
Cumilla(S) | 134 | 06:00 | 121 | 00:00 | Rahanpur-400 | 138 | 06:00 | 128 | 22:00
Daganbhuiyan | 121 | 18:00 | 112 | 22:00 | Rahim | 132 | 18:00 | 128 | 00:00
Daudkandi | 126 | 18:00 | 120 | 00:00 | Rajbari | 135 | 17:00 | 126 | 00:00
Dhaka | 138 | 03:00 | 130 | 11:00 | Rajendrapur | 135 | 01:00 | 125 | 00:00
Dhamrai | 133 | 18:00 | 126 | 00:00 | Rajshahi | 136 | 09:00 | 127 | 21:00
Dhanmondi | 138 | 04:00 | 129 | 12:00 | Rajshahi-230 | 136 | 09:00 | 118 | 21:00
Dohazari | 131 | 10:00 | 127 | 04:00 | Ramganj | 120 | 07:00 | 111 | 00:00
Faridpur | 136 | 18:00 | 128 | 00:00 | Rampur | 133 | 00:00 | 130 | 05:00
Fatullah | 134 | 17:00 | 128 | 00:00 | Rampura | 139 | 04:00 | 128 | 12:00
Fenchuganj | 136 | 09:00 | 132 | 00:00 | Rangamati | 132 | 00:00 | 130 | 05:00
Feni | 123 | 08:00 | 115 | 21:00 | Rangpur | 131 | 10:00 | 125 | 09:00
Ghatail | 130 | 07:00 | 124 | 13:00 | Ruppur | 138 | 08:00 | 131 | 21:00
Ghorashal | 137 | 06:00 | 132 | 12:00 | Saidpur | 130 | 05:00 | 122 | 23:00
Goalpara | 140 | 18:00 | 127 | 01:00 | Satkhira | 138 | 17:00 | 122 | 00:00
Gollamari | 140 | 17:00 | 126 | 02:00 | Satmasjid | 133 | 08:00 | 128 | 13:00
Gopalganj | 137 | 10:00 | 128 | 00:00 | Savar | 132 | 00:00 | 127 | 02:00
Gopalganj-400 | 138 | 17:00 | 132 | 00:00 | SevenRings | 139 | 06:00 | 130 | 13:00
Gulshan | 137 | 18:00 | 129 | 12:00 | ShahCement | 132 | 18:00 | 127 | 01:00
Halishahar | 134 | 00:00 | 129 | 05:00 | Shahjadpur | 137 | 09:00 | 132 | 21:00
Haripur | 132 | 18:00 | 127 | 01:00 | Shahjibazar | 135 | 18:30 | 126 | 23:00
HaripurSBU | 132 | 18:00 | 128 | 00:00 | Shahmirpur | 134 | 00:00 | 128 | 06:00
Hasnabad | 134 | 18:00 | 131 | 00:00 | Shariatpur | 136 | 09:00 | 127 | 00:00
Hathazari | 135 | 08:00 | 132 | 06:00 | Sherpur | 134 | 06:00 | 124 | 18:00
Ishurdi | 139 | 09:00 | 132 | 01:00 | Shikalbaha | 123 | 00:00 | 121 | 04:00
Jaldhaka | 130 | 19:00 | 120 | 23:00 | Shikalbaha-230 | 135 | 00:00 | 131 | 06:00
Jamalpur | 136 | 06:00 | 127 | 18:00 | Shitalakhya | 132 | 18:00 | 128 | 00:00
Jashore | 134 | 17:00 | 119 | 00:00 | Sholosohor | 132 | 00:00 | 130 | 04:00
Jhenaidah | 137 | 17:00 | 123 | 00:00 | Shyampur | 133 | 18:00 | 127 | 00:00
Jhenaidah-230 | 138 | 17:00 | 126 | 00:00 | Shyampur-230 | 133 | 18:00 | 128 | 00:00
Joydebpur | 140 | 00:00 | 128 | 12:00 | Siddhirganj | 132 | 18:00 | 127 | 00:00
Joypurhat | 131 | 06:00 | 120 | 21:00 | Sirajganj | 134 | 08:00 | 126 | 23:00
Juldah | 135 | 00:00 | 130 | 05:00 | Sonargaon | 131 | 18:30 | 127 | 00:00
Kabirpur | 132 | 18:30 | 125 | 23:00 | Sreemongol | 134 | 18:30 | 126 | 00:00
Kachua | 126 | 18:00 | 117 | 00:00 | Sreepur | 133 | 06:00 | 127 | 22:00
Kaliakoir | 135 | 18:30 | 129 | 22:00 | Srinagar | 136 | 18:00 | 129 | 00:00
Kallyanpur | 134 | 05:00 | 130 | 11:00 | SSM | 136 | 00:00 | 132 | 14:00
Kalurghat | 132 | 00:00 | 130 | 04:00 | Sunamganj | 128 | 10:00 | 118 | 23:00
Kamrangirchar | 136 | 06:00 | 129 | 00:00 | Sylhet | 130 | 09:00 | 125 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet-132 | 130 | 08:00 | 125 | 00:00
Kasba | 127 | 18:00 | 120 | 00:00 | Tangail | 130 | 03:00 | 123 | 00:00
Kazla | 133 | 07:00 | 129 | 00:00 | Taraganj | 131 | 10:00 | 124 | 20:00
Keranigonj | 139 | 18:30 | 130 | 00:00 | Thakurgaon | 135 | 05:00 | 120 | 13:00
Khagrachori | 132 | 17:00 | 129 | 13:00 | TK | 132 | 00:00 | 130 | 06:00
Khulna | 138 | 09:00 | 125 | 01:00 | Tongi | 135 | 13:00 | 130 | 12:00
Khulna(S) | 140 | 10:00 | 128 | 01:00 | Ullahpara | 136 | 09:00 | 128 | 21:00
Khulshi | 132 | 00:00 | 129 | 13:00 | Ullon | 139 | 04:00 | 128 | 12:00
Kishoreganj | 129 | 18:00 | 120 | 21:00 | Uttara | 132 | 06:00 | 127 | 13:00
Kodda | 136 | 00:00 | 123 | 13:00 | UttaraNew | 132 | 08:00 | 128 | 13:00
KSRM | 134 | 10:00 | 130 | 08:00 | Zigatola | 135 | 06:00 | 130 | 00:00
Kulaura | 135 | 18:30 | 129 | 23:00
Kurigram | 131 | 10:00 | 122 | 07:00
Kushtia | 135 | 11:00 | 127 | 00:00
Lakshmipur | 121 | 18:00 | 118 | 23:00
Lalbag | 135 | 06:00 | 129 | 00:00
Lalmonirhat | 129 | 11:00 | 121 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division