## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 06-07-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-07-2025 | during | 06-07-2025 | during | 06-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 401 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 420 | 450 | 450 | 450 | 450 | Allocation limit by Titas, instructed by DS(Gen)
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 300 | 292 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 334 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 32 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23.5 | 26.5 | 33 | 33 | 27 | 27 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 52 | 69 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 88 | 105 | 105 | 70 | 90 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 51 | 104 | 104 | 68 | 68 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 145 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 4 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 54 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 450 | 450 | 584 | 584 | 526 | 526 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage instructed by DS(Gen)
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 108 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2086.5 | 2690.5 | 5126.4 | 5126.4 | 3421.58 | 3441.58
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 1 | 0 | 1 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 172 | 172 | 165 | 165 | 165 | 165 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 221 | 220 | 213 | 213 | 213 | 213 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 93 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 71 | 56 | 72 | 48 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 65 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 88 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 3 | 27 | 2 | 25 | 2 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0 | 0 | 5.22 | 0 | 5.22 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 17 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 15 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 36 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 17 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1088 | 1117 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 12 | 19 | 35 | 33 | 35 | 33 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 204 | 203 | 575 | 575 | 575 | 575 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1760 | 2283 | 3570.94 | 3601.72 | 3562.94 | 3601.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 195 | 196 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 330 | 352 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 340 | 340 | 340 | 340 | 340 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 20 | 20 | 46.7 | 46.7 | 20 | 20 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 20 | 52 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 120 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 137 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 37 | 46 | 46 | 46 | 46 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 146 | 171 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 36 | 40 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 14 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 78 | 96 | 114 | 114 | 98 | 98 | Engine Problem
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 13 | 29 | 113 | 113 | 9 | 28 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 16 | 115 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 70 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1337 | 1786 | 2469.75 | 2399.75 | 2139.55 | 2088.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-07-2025 | during | 06-07-2025 | during | 06-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 68 | 71 | 157.5 | 157.5 | 90 | 90 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 3 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 65 | 163 | 200 | 200 | 160 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 82 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 15.31 | 0 | 39 | 0 | 39 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 35 | 35 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 237.31 | 363 | 590.1 | 549 | 472.6 | 431.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage instructed by DS(Gen)
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 132 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 78 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 171 | 172 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 18 | 18 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 8 | 8 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 290 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 360 | 374 | 380 | 380 | 352 | 352 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 360 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1468 | 1422 | 1522 | 1522 | 1425 | 1425
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 891 | 891 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 260 | 240 | 410 | 410 | 250 | 250 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 70 | 70 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 103 | 0 | 55 | 0 | 55 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 545 | 603 | 617.1 | 617.1 | 617.1 | 617.1 | U#2 under shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1837 | 1787 | 2654.1 | 2599.1 | 2459.1 | 2404.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 5 | 11 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 100 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 980 | 1244 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 110 | 110 | 110 | 110 | GT-12 Under shutdown for Offline water wash
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 201 | 278 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.95 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1526.95 | 1870 | 2062 | 2061 | 2000 | 1999
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 49 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 5 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 171 | 200 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 207 | 204 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 353 | 344 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 6.36 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1013.52 | 1248.22 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 34.04 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 129 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 1913.92 | 2292.22 | 2979.47 | 2812.87 | 2938.09 | 2771.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 49 | 48 | 48 | 48 | 48 | 48 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 202 | 170 | 200 | 200 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.1 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 114 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 40 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 194 | 0 | 151.54 | 0 | 151.54 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 489.1 | 445 | 697.54 | 510 | 697.54 | 510
System Total |  |  |  |  | 28565.2 | 27084.055 | 12655.78 | 14938.72 | 21672.3 | 21181.84 | 19116.4 | 18672.94
Forecast Scenario (06-07-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14572 |  | 0 |  | 14572
|  |  |  | 1:00 | 14157 |  | 0 |  | 14157
|  |  |  | 2:00 | 13626 |  | 0 |  | 13626
|  |  |  | 3:00 | 13227 |  | 0 |  | 13227
|  |  |  | 4:00 | 12806 |  | 0 |  | 12806
|  |  |  | 5:00 | 12530 |  | 0 |  | 12530
|  |  |  | 6:00 | 12182 |  | 0 |  | 12182
|  |  |  | 7:00 | 11991 |  | 0 |  | 11991
|  |  |  | 8:00 | 12053 |  | 0 |  | 12053
|  |  |  | 9:00 | 12147 |  | 0 |  | 12147
|  |  |  | 10:00 | 12261 |  | 0 |  | 12261
|  |  |  | 11:00 | 12593 |  | 0 |  | 12593
|  |  |  | 12:00 | 13056 |  | 0 |  | 13056
|  |  |  | 13:00 | 13324 |  | 0 |  | 13324
|  |  |  | 14:00 | 13291 |  | 0 |  | 13291
|  |  |  | 15:00 | 13661 |  | 0 |  | 13661
|  |  |  | 16:00 | 13479 |  | 0 |  | 13479
|  |  |  | 17:00 | 12962 |  | 0 |  | 12962
|  |  |  | 18:00 | 12632 |  | 0 |  | 12632
|  |  |  | 18:30 | 13200 |  | 0 |  | 13200
|  |  |  | 19:00 | 13871 |  | 0 |  | 13871
|  |  |  | 19:30 | 15125 |  | 0 |  | 15125
|  |  |  | 20:00 | 15172 |  | 0 |  | 15172
|  |  |  | 21:00 | 15366 |  | 0 |  | 15366
|  |  |  | 22:00 | 15200 |  | 0 |  | 15200
|  |  |  | 23:00 | 15100 |  | 0 |  | 15100
Probable Maximum Temperature: |  |  | 31.10°C
Probable Maximum Demand at Day Peak: |  |  | 13056.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15366.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15366.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 318.87388 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:38 hrs on 06-07-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 05-07-2025 | [28 empty] | Date: | 05-07-2025 | [28 empty] | Date: | 05-07-2025 | [28 empty] | Date: | 05-07-2025 | [28 empty] | Date: | 05-07-2025 | [12 empty] | Date: | 05-07-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [12 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 35 | 132 | 16 | 0 | 0 | 17 | 51 | 16 | 420 | 314 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 125 | 20 | 20 | 0 | 584 | 0 | 15 | 0 | 0 | 29 | 65 | 39 | 0 | 48 | 70 | 0 | 172 | 17 | 40 | 205 | 0 | 0 | 31 | 0 | 33 | 222 | 0 | 0 | 0 | 1224 | 0 | 51 | 50 | 184 | 0 | 350 | 340 | 48 | 37 | 20 | 37 | 0 | 183 | 12 | 20 | 97 | 40 | 45 | 0 | 38 | 285 | 320 | 373 | 0 | 0 | 159 | 8 | 0 | 81 | 30 | 0 | 18 | 171 | 35 | 84 | 182 | 84 | 0 | 0 | 8 | 8146 | 890 | 232 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 0 | 1170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 196 | 0 | 364 | 0 | 0 | 202 | 48 | 114 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 11 | 120 | 220 | 0 | 0 | 1244 | 0 | 6026 | 14172 | 96.62
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 35 | 35 | 132 | 16 | 0 | 0 | 17 | 53 | 16 | 420 | 294 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 125 | 20 | 21 | 0 | 500 | 0 | 15 | 0 | 0 | 22 | 65 | 39 | 0 | 48 | 70 | 0 | 172 | 17 | 42 | 203 | 0 | 0 | 0 | 0 | 33 | 223 | 0 | 0 | 0 | 1160 | 0 | 51 | 50 | 86 | 0 | 325 | 320 | 49 | 42 | 20 | 17 | 0 | 183 | 12 | 20 | 97 | 40 | 52.2 | 0 | 38 | 280 | 320 | 373 | 0 | 0 | 158 | 8 | 0 | 81 | 30 | 0 | 18 | 171 | 17 | 70 | 173 | 86 | 0 | 0 | 12 | 7744.2 | 890 | 232 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 608 | 0 | 1165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 196 | 0 | 352 | 0 | 0 | 203 | 49 | 114 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 11 | 120 | 220 | 0 | 0 | 1244 | 0 | 6013 | 13757.2 | 96.61
02:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 35 | 17 | 82 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 309 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 20 | 21 | 0 | 500 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 48 | 70 | 0 | 172 | 0 | 40 | 205 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1160 | 0 | 51 | 0 | 86 | 0 | 352 | 315 | 49 | 42 | 20 | 17 | 0 | 178 | 6 | 20 | 97 | 36 | 52.2 | 0 | 16 | 285 | 320 | 373 | 0 | 0 | 157 | 8 | 0 | 81 | 30 | 0 | 18 | 171 | 0 | 45 | 173 | 86 | 0 | 0 | 12 | 7307.2 | 890 | 235 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 597 | 0 | 1169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 196 | 0 | 362 | 0 | 0 | 201 | 49 | 90 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 10 | 120 | 220 | 0 | 0 | 1200 | 0 | 5919 | 13226.2 | 96.6
03:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 298 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 90 | 20 | 21 | 0 | 500 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 24 | 36 | 0 | 172 | 0 | 40 | 205 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1160 | 0 | 51 | 0 | 86 | 0 | 355 | 320 | 50 | 63 | 20 | 17 | 0 | 179 | 7 | 20 | 97 | 38 | 52.2 | 0 | 0 | 285 | 320 | 370 | 0 | 0 | 158 | 8 | 0 | 81 | 30 | 0 | 18 | 171 | 7 | 45 | 135 | 89 | 0 | 0 | 12 | 7075.2 | 890 | 240 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 583 | 0 | 1168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 196 | 0 | 362 | 0 | 0 | 204 | 50 | 70 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 239 | 10 | 120 | 220 | 0 | 0 | 1120 | 0 | 5752 | 12827.2 | 96.59
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 304 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 20 | 21 | 0 | 500 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 40 | 205 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 16 | 0 | 352 | 320 | 50 | 120 | 20 | 16 | 0 | 183 | 9 | 20 | 79 | 36 | 52.2 | 0 | 0 | 290 | 320 | 373 | 0 | 0 | 160 | 8 | 0 | 81 | 30 | 0 | 18 | 171 | 0 | 45 | 95 | 89 | 0 | 0 | 12 | 6852.2 | 890 | 243 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 518 | 0 | 1121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 197 | 0 | 372 | 0 | 0 | 205 | 48 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 10 | 120 | 220 | 0 | 0 | 1108 | 0 | 5554 | 12406.2 | 96.58
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 298 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 20 | 21 | 0 | 500 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 40 | 200 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1025 | 0 | 51 | 0 | 16 | 0 | 355 | 325 | 50 | 202 | 20 | 16 | 0 | 183 | 9 | 20 | 79 | 30 | 52.2 | 0 | 0 | 285 | 320 | 360 | 0 | 0 | 159 | 8 | 0 | 81 | 30 | 0 | 18 | 171 | 1 | 45 | 95 | 89 | 0 | 0 | 12 | 6762.2 | 891 | 248 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 0 | 1057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 197 | 0 | 353 | 0 | 0 | 202 | 48 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 8 | 120 | 220 | 0 | 0 | 1048 | 0 | 5368 | 12130.2 | 96.57
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 304 | 0 | 0 | 0 | 335 | 0 | 0 | 1 | 52 | 20 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 40 | 205 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 950 | 0 | 51 | 0 | 16 | 0 | 356 | 340 | 50 | 197 | 20 | 17 | 0 | 173 | 9 | 20 | 79 | 32 | 16 | 2 | 0 | 285 | 320 | 360 | 0 | 0 | 153 | 8 | 0 | 81 | 30 | 0 | 18 | 171 | 17 | 45 | 95 | 90 | 0 | 3.64 | 12 | 6619.64 | 890 | 251 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4 | 483 | 0 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0.96 | 0 | 0 | 194 | 0 | 197 | 0 | 344 | 0 | 0.11 | 203 | 48 | 35 | 2 | 0 | 0 | 0 | 0 | 3.39 | 0.03 | 0 | 200 | 8 | 120 | 220 | 0 | 0 | 1000 | 0 | 5162.49 | 11782.13 | 96.56
07:00 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 303 | 0 | 0 | 0 | 335 | 0 | 0 | 3 | 35 | 20 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 36 | 204 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 945 | 0 | 51 | 0 | 16 | 0 | 300 | 335 | 50 | 194 | 20 | 17 | 0 | 168 | 9 | 20 | 79 | 32 | 16 | 6 | 0 | 290 | 320 | 350 | 0 | 0 | 150 | 8 | 0 | 81 | 30 | 0 | 18 | 171 | 17 | 55 | 98 | 89 | 0 | 9.68 | 12 | 6528.68 | 890 | 255 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 13.2 | 437 | 0 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 12.57 | 0 | 0 | 199 | 0 | 160 | 0 | 339 | 0 | 1.38 | 202 | 48 | 35 | 5 | 0 | 0 | 0 | 1 | 33.62 | 0.12 | 0 | 198 | 6 | 120 | 180 | 0 | 0 | 970 | 0 | 5061.89 | 11590.57 | 96.55
08:00 | 0 | 4 | 16 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 310 | 0 | 0 | 0 | 335 | 0 | 0 | 9 | 17 | 26.5 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 8 | 205 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 956 | 0 | 51 | 0 | 8 | 0 | 300 | 335 | 20 | 198 | 20 | 17 | 0 | 140 | 9 | 20 | 79 | 30 | 0 | 37 | 0 | 295 | 320 | 373 | 0 | 0 | 151 | 8 | 0 | 81 | 30 | 0 | 18 | 171 | 17 | 55 | 114 | 89 | 1 | 5.55 | 12 | 6539.05 | 891 | 256 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12.52 | 435 | 0 | 929.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 30.56 | 0 | 0 | 191 | 0 | 160 | 0 | 363 | 0 | 1.63 | 200 | 49 | 35 | 1 | 0 | 0 | 0 | 2.5 | 44 | 0.11 | 0 | 202 | 6 | 120 | 180 | 0 | 0 | 940 | 0 | 5114.38 | 11653.43 | 96.54
09:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 6 | 0 | 0 | 340 | 310 | 0 | 0 | 0 | 331 | 0 | 0 | 21 | 17 | 22.5 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 3 | 203 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 958 | 0 | 51 | 0 | 8 | 0 | 300 | 340 | 20 | 204 | 20 | 17 | 0 | 150 | 9 | 20 | 78 | 30 | 0 | 51 | 0 | 290 | 320 | 375 | 0 | 0 | 159 | 8 | 0 | 78 | 30 | 0 | 18 | 171 | 17 | 45 | 65 | 72 | 1 | 37.62 | 12 | 6583.12 | 890 | 259 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6.95 | 463 | 0 | 933.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 28.22 | 0 | 0 | 179 | 0 | 160 | 0 | 382 | 0 | 4.23 | 202 | 49 | 35 | 10 | 0 | 0 | 0 | 1.9 | 55 | 0.42 | 0 | 201 | 3 | 120 | 180 | 0 | 0 | 900 | 0 | 5164.02 | 11747.14 | 96.53
10:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 17 | 0 | 0 | 340 | 309 | 0 | 0 | 0 | 330 | 0 | 0 | 17 | 17 | 23.5 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 24 | 25 | 0 | 172 | 0 | 3 | 206 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 955 | 0 | 51 | 0 | 8 | 0 | 300 | 340 | 20 | 201 | 20 | 17 | 0 | 150 | 9 | 20 | 78 | 32 | 0 | 39 | 0 | 300 | 320 | 375 | 0 | 0 | 160 | 8 | 0 | 75 | 30 | 0 | 18 | 171 | 17 | 45 | 65 | 70 | 1 | 39.51 | 6 | 6647.01 | 891 | 259 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 105 | 448 | 0 | 930.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 34.35 | 0 | 0 | 179 | 0 | 160 | 0 | 375 | 0 | 3.54 | 201 | 50 | 0 | 32 | 0 | 0 | 0 | 2 | 64 | 0.65 | 0 | 202 | 5 | 120 | 180 | 0 | 0 | 900 | 0 | 5213.69 | 11860.7 | 96.52
11:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 17 | 0 | 0 | 420 | 308 | 0 | 0 | 0 | 326 | 0 | 0 | 27 | 17 | 23.5 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 24 | 36 | 0 | 172 | 0 | 3 | 206 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 975 | 0 | 51 | 0 | 8 | 0 | 330 | 340 | 20 | 209 | 20 | 17 | 0 | 154 | 9 | 14 | 78 | 32 | 0 | 53 | 0 | 295 | 320 | 375 | 0 | 0 | 157 | 8 | 0 | 77 | 30 | 0 | 18 | 171 | 20 | 45 | 65 | 68 | 1 | 53.19 | 6 | 6803.69 | 891 | 259 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 42 | 470 | 0 | 1002.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 18.84 | 0 | 0 | 181 | 0 | 190 | 0 | 393 | 0 | 1.6 | 201 | 51 | 0 | 21 | 0 | 0 | 0 | 1.2 | 65 | 0.82 | 0 | 204 | 5 | 120 | 220 | 0 | 0 | 910 | 0 | 5388.96 | 12192.65 | 96.51
12:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 17 | 0 | 0 | 420 | 300 | 0 | 0 | 0 | 330 | 0 | 0 | 4 | 17 | 23.5 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 24 | 36 | 0 | 172 | 0 | 3 | 204 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1088 | 0 | 51 | 0 | 8 | 0 | 330 | 340 | 20 | 195 | 20 | 16 | 0 | 146 | 13 | 14 | 78 | 36 | 0 | 70 | 0 | 290 | 360 | 360 | 0 | 0 | 155 | 8 | 0 | 76 | 30 | 0 | 18 | 171 | 35 | 45 | 65 | 68 | 3 | 15.31 | 6 | 6888.81 | 891 | 260 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 103 | 545 | 0 | 1013.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 0 | 34.04 | 0 | 0 | 171 | 0 | 207 | 0 | 353 | 0 | 6.36 | 202 | 49 | 0 | 40 | 0 | 0 | 0 | 4.1 | 194 | 0.95 | 0 | 201 | 5 | 120 | 220 | 0 | 0 | 980 | 0 | 5766.97 | 12655.78 | 96.5
13:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 22 | 62 | 0 | 420 | 300 | 0 | 0 | 0 | 328 | 0 | 0 | 16 | 17 | 23.5 | 22 | 0 | 500 | 0 | 3 | 0 | 0 | 24 | 0 | 0 | 0 | 48 | 48 | 0 | 172 | 0 | 10 | 204 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1155 | 1 | 51 | 0 | 8 | 0 | 343 | 340 | 20 | 193 | 20 | 17 | 0 | 149 | 9 | 14 | 78 | 38 | 0 | 14 | 0 | 290 | 320 | 350 | 0 | 0 | 155 | 8 | 0 | 75 | 30 | 0 | 16 | 172 | 35 | 45 | 95 | 68 | 3 | 19.49 | 6 | 7081.99 | 890 | 256 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14 | 610 | 0 | 1011.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 39.82 | 0 | 0 | 171 | 0 | 207 | 0 | 414 | 0 | 4.19 | 201 | 50 | 0 | 9 | 0 | 0 | 0 | 6.8 | 143 | 0.65 | 0 | 276 | 5 | 120 | 220 | 0 | 0 | 1055 | 0 | 5842.04 | 12924.03 | 96.49
14:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 81 | 0 | 0 | 0 | 35 | 65 | 0 | 370 | 303 | 0 | 0 | 0 | 325 | 0 | 0 | 3 | 35 | 23.5 | 22 | 0 | 450 | 0 | 30 | 0 | 0 | 23 | 0 | 0 | 0 | 48 | 48 | 0 | 172 | 0 | 4 | 202 | 0 | 0 | 0 | 0 | 13 | 220 | 0 | 0 | 0 | 1162 | 2 | 51 | 0 | 8 | 0 | 342 | 305 | 20 | 198 | 20 | 17 | 0 | 144 | 9 | 14 | 78 | 40 | 0 | 11 | 0 | 285 | 320 | 380 | 0 | 0 | 153 | 8 | 0 | 75 | 30 | 0 | 16 | 172 | 35 | 45 | 95 | 67 | 3 | 15.55 | 6 | 7067.05 | 890 | 254 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 15 | 608 | 0 | 1036.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 26.25 | 0 | 0 | 170 | 0 | 209 | 0 | 370 | 0 | 5.19 | 198 | 50 | 0 | 13 | 0 | 0 | 0 | 8 | 106 | 0.32 | 0 | 278 | 5 | 120 | 220 | 0 | 0 | 1120 | 0 | 5824.15 | 12891.2 | 96.48
15:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 45 | 0 | 87 | 0 | 0 | 0 | 35 | 68 | 0 | 420 | 305 | 0 | 0 | 0 | 325 | 0 | 0 | 27 | 52 | 25.5 | 22 | 0 | 450 | 0 | 30 | 0 | 0 | 22 | 0 | 0 | 0 | 88 | 82 | 1 | 172 | 0 | 4 | 204 | 0 | 0 | 0 | 0 | 16 | 219 | 0 | 0 | 0 | 1155 | 4 | 51 | 0 | 8 | 0 | 339 | 340 | 23 | 199 | 20 | 17 | 0 | 149 | 9 | 14 | 78 | 36 | 0 | 13 | 0 | 290 | 320 | 354 | 0 | 0 | 154 | 8 | 0 | 77 | 30 | 0 | 16 | 170 | 35 | 45 | 139 | 67 | 2 | 27.86 | 6 | 7346.36 | 890 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12 | 608 | 0 | 1069.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 19.56 | 0 | 0 | 188 | 0 | 206 | 0 | 401 | 0 | 1.53 | 195 | 49 | 0 | 22 | 0 | 0 | 0 | 5 | 164 | 0.13 | 0 | 307 | 5 | 120 | 220 | 0 | 0 | 1110 | 0 | 5914.5 | 13260.86 | 96.47
16:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 0 | 87 | 0 | 0 | 0 | 35 | 66 | 14 | 420 | 293 | 0 | 0 | 0 | 326 | 0 | 0 | 22 | 52 | 25.5 | 21 | 0 | 400 | 0 | 30 | 0 | 0 | 24 | 0 | 32 | 0 | 100 | 95 | 0 | 172 | 0 | 4 | 201 | 0 | 0 | 0 | 0 | 15 | 219 | 0 | 0 | 0 | 1137 | 0 | 51 | 38 | 43 | 0 | 342 | 340 | 35 | 192 | 20 | 17 | 0 | 170 | 9 | 14 | 78 | 36 | 15 | 19 | 0 | 285 | 320 | 330 | 0 | 0 | 137 | 8 | 0 | 76 | 30 | 0 | 16 | 168 | 35 | 45 | 150 | 67 | 1 | 28.72 | 6 | 7417.22 | 891 | 245 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 551 | 0 | 1053.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 20.32 | 0 | 0 | 201 | 0 | 209 | 0 | 360 | 0 | 1.42 | 200 | 49 | 0 | 12 | 0 | 0 | 0 | 4.2 | 82 | 0.18 | 0 | 273 | 5 | 100 | 220 | 0 | 0 | 1090 | 0 | 5661.39 | 13078.61 | 96.46
17:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 10 | 87 | 0 | 0 | 0 | 35 | 71 | 28 | 420 | 290 | 0 | 0 | 0 | 332 | 0 | 0 | 4 | 52 | 25.5 | 21 | 0 | 400 | 0 | 30 | 0 | 0 | 20 | 0 | 32 | 0 | 100 | 100 | 0 | 172 | 0 | 4 | 202 | 0 | 0 | 0 | 0 | 15 | 221 | 0 | 0 | 0 | 1017 | 2 | 51 | 50 | 45 | 0 | 343 | 340 | 37 | 190 | 20 | 25 | 0 | 173 | 9 | 14 | 78 | 40 | 52.2 | 7 | 25 | 290 | 320 | 308 | 0 | 0 | 135 | 8 | 0 | 77 | 30 | 0 | 16 | 168 | 35 | 45 | 152 | 67 | 0 | 10.51 | 11 | 7367.21 | 891 | 240 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 19 | 533 | 0 | 866.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 8.36 | 0 | 0 | 200 | 0 | 208 | 0 | 332 | 0 | 0.73 | 186 | 49 | 0 | 9 | 0 | 0 | 0 | 3 | 69 | 0 | 0 | 191 | 5 | 100 | 180 | 0 | 0 | 1060 | 0 | 5194.7 | 12561.91 | 96.45
18:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 17 | 87 | 0 | 0 | 0 | 35 | 62 | 42 | 320 | 296 | 0 | 0 | 0 | 280 | 0 | 0 | 1 | 52 | 25.5 | 21 | 0 | 400 | 0 | 30 | 0 | 0 | 18 | 0 | 48 | 0 | 100 | 100 | 0 | 172 | 0 | 9 | 202 | 0 | 0 | 0 | 0 | 15 | 220 | 0 | 0 | 0 | 960 | 0 | 51 | 50 | 45 | 0 | 300 | 340 | 39 | 197 | 20 | 34 | 0 | 171 | 19 | 14 | 78 | 42 | 16 | 2 | 37 | 290 | 320 | 329 | 0 | 0 | 133 | 8 | 0 | 77 | 30 | 0 | 16 | 172 | 35 | 45 | 162 | 67 | 0 | 3.52 | 12 | 7172.02 | 891 | 240 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 445 | 0 | 868.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.54 | 0 | 0 | 200 | 0 | 205 | 0 | 344 | 0 | 0.42 | 168 | 49 | 0 | 1 | 0 | 0 | 0 | 1 | 18 | 0.02 | 0 | 201 | 5 | 100 | 180 | 0 | 0 | 1100 | 0 | 5060.29 | 12232.31 | 96.44
19:00 | 0 | 45 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 50 | 87 | 48 | 90 | 4 | 40 | 89 | 54 | 320 | 293 | 0 | 0 | 25 | 280 | 0 | 0 | 0 | 85 | 25.5 | 21 | 0 | 400 | 0 | 60 | 0 | 0 | 19 | 64 | 54 | 3 | 100 | 100 | 0 | 172 | 4 | 16 | 203 | 9 | 0 | 9 | 3 | 30 | 220 | 0 | 0 | 0 | 1109 | 0 | 51 | 63 | 72 | 0 | 300 | 340 | 47 | 196 | 20 | 57 | 0 | 177 | 27 | 14 | 78 | 48 | 18 | 0 | 37 | 295 | 320 | 329 | 0 | 0 | 138 | 8 | 0 | 78 | 30 | 0 | 16 | 172 | 35 | 81 | 162 | 68 | 0 | 0 | 12 | 7900.5 | 891 | 240 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 16 | 0 | 475 | 0 | 976.6 | 0 | 0 | 0 | 12 | 4 | 55 | 20 | 8 | 0 | 0 | 12 | 0 | 0 | 0 | 200 | 0 | 204 | 0 | 343 | 0 | 0 | 165 | 48 | 95 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 9 | 100 | 180 | 0 | 0 | 1120 | 10 | 5570.6 | 13471.1 | 96.43
19:30 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 54 | 55 | 80 | 48 | 145 | 15 | 55 | 146 | 60 | 420 | 290 | 0 | 0 | 35 | 332 | 0 | 0 | 0 | 108 | 25.5 | 21 | 0 | 400 | 17 | 100 | 0 | 0 | 19 | 65 | 62 | 17 | 100 | 100 | 0 | 172 | 14 | 19 | 203 | 17 | 0 | 19 | 10 | 91 | 220 | 0 | 0 | 0 | 1045 | 0 | 51 | 110 | 82 | 0 | 352 | 325 | 47 | 193 | 20 | 115 | 0 | 174 | 29 | 14 | 78 | 48 | 52.2 | 0 | 37 | 290 | 320 | 350 | 0 | 0 | 140 | 8 | 0 | 78 | 30 | 0 | 18 | 172 | 35 | 82 | 162 | 71 | 0 | 0 | 12 | 8590.7 | 890 | 240 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 540 | 0 | 1089.32 | 0 | 0 | 0 | 90 | 5 | 90 | 35 | 8 | 0 | 0 | 30 | 0 | 0 | 0 | 200 | 0 | 203 | 0 | 349 | 0 | 0 | 166 | 48 | 109 | 0 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 10 | 100 | 220 | 0 | 0 | 1210 | 35 | 6134.32 | 14725.02
20:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 54 | 78 | 32 | 145 | 15 | 55 | 147 | 66 | 420 | 291 | 0 | 0 | 35 | 333 | 0 | 0 | 0 | 108 | 25.5 | 21 | 0 | 400 | 15 | 100 | 0 | 0 | 11 | 65 | 64 | 17 | 100 | 100 | 0 | 172 | 18 | 24 | 202 | 17 | 0 | 19 | 15 | 97 | 220 | 0 | 0 | 0 | 1070 | 0 | 51 | 103 | 120 | 0 | 352 | 320 | 51 | 193 | 20 | 111 | 0 | 177 | 29 | 14 | 96 | 40 | 52.2 | 0 | 37 | 290 | 320 | 361 | 0 | 0 | 142 | 8 | 0 | 78 | 30 | 0 | 18 | 172 | 35 | 82 | 162 | 70 | 0 | 0 | 12 | 8665.7 | 891 | 240 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 541 | 0 | 1095.74 | 0 | 0 | 0 | 50 | 6 | 90 | 35 | 28 | 0 | 0 | 30 | 0 | 0 | 0 | 200 | 0 | 203 | 0 | 340 | 0 | 0 | 168 | 48 | 111 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 10 | 120 | 220 | 0 | 0 | 1210 | 35 | 6106.74 | 14772.44 | 96.42
21:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 54 | 69 | 32 | 15 | 15 | 55 | 145 | 51 | 420 | 292 | 0 | 0 | 35 | 334 | 0 | 0 | 0 | 108 | 26.5 | 21 | 0 | 450 | 17 | 15 | 0 | 0 | 19 | 65 | 71 | 17 | 88 | 100 | 0 | 172 | 15 | 27 | 203 | 17 | 0 | 19 | 8 | 93 | 220 | 0 | 0 | 0 | 1117 | 0 | 51 | 137 | 120 | 0 | 352 | 340 | 52 | 196 | 20 | 115 | 0 | 171 | 29 | 14 | 96 | 40 | 16 | 0 | 37 | 290 | 320 | 374 | 0 | 0 | 132 | 8 | 0 | 78 | 30 | 0 | 18 | 172 | 35 | 82 | 163 | 71 | 0 | 0 | 12 | 8544.5 | 891 | 240 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 603 | 0 | 1248.22 | 0 | 49 | 0 | 50 | 5 | 90 | 35 | 37 | 0 | 0 | 30 | 0 | 0 | 0 | 200 | 0 | 204 | 0 | 344 | 0 | 0 | 170 | 48 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 11 | 100 | 220 | 0 | 0 | 1244 | 17 | 6394.22 | 14938.72 | 96.41
22:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 54 | 68 | 32 | 15 | 15 | 55 | 151 | 65 | 420 | 296 | 0 | 0 | 35 | 334 | 0 | 0 | 0 | 108 | 26.5 | 21 | 0 | 450 | 17 | 15 | 0 | 0 | 19 | 65 | 71 | 17 | 88 | 100 | 0 | 172 | 16 | 30 | 203 | 17 | 0 | 19 | 8 | 96 | 220 | 0 | 0 | 0 | 1150 | 0 | 51 | 142 | 8 | 0 | 353 | 340 | 36 | 186 | 20 | 106 | 0 | 176 | 28 | 20 | 96 | 40 | 16 | 0 | 30 | 285 | 320 | 386 | 0 | 0 | 136 | 8 | 0 | 78 | 30 | 0 | 18 | 172 | 35 | 92 | 163 | 71 | 0 | 0 | 12 | 8490.5 | 890 | 240 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 609 | 0 | 1248.22 | 0 | 49 | 0 | 50 | 5 | 90 | 35 | 37 | 0 | 0 | 30 | 0 | 0 | 0 | 200 | 0 | 203 | 0 | 346 | 0 | 0 | 172 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 11 | 100 | 220 | 0 | 0 | 1244 | 17 | 6402.22 | 14892.72 | 96.4
23:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 54 | 35 | 68 | 32 | 15 | 15 | 40 | 149 | 65 | 420 | 298 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 108 | 26.5 | 21 | 0 | 450 | 17 | 15 | 0 | 0 | 25 | 65 | 68 | 17 | 76 | 100 | 0 | 172 | 15 | 32 | 203 | 17 | 0 | 19 | 8 | 92 | 220 | 0 | 0 | 0 | 1150 | 0 | 51 | 143 | 8 | 0 | 353 | 340 | 20 | 215 | 20 | 68 | 0 | 178 | 29 | 20 | 96 | 42 | 16 | 0 | 30 | 285 | 320 | 388 | 0 | 0 | 137 | 8 | 0 | 78 | 30 | 0 | 18 | 172 | 35 | 92 | 163 | 71 | 0 | 0 | 12 | 8396.5 | 890 | 241 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 607 | 0 | 1284.99 | 0 | 49 | 0 | 50 | 0 | 90 | 35 | 36 | 0 | 0 | 28 | 0 | 0 | 0 | 198 | 0 | 200 | 0 | 352 | 0 | 0 | 171 | 48 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 11 | 100 | 220 | 0 | 0 | 1244 | 17 | 6430.99 | 14827.49 | 96.39
Total KWH | 0 | 797760 | 349838 | 0 | 0 | 0 | 0 | 0 | 9720000 | 0 | 0 | 596880 | 393840 | 1366992 | 195360 | 254673 | 80041 | 567526 | 1296000 | 465600 | 9454500 | 7242240 | 0 | 0 | 191391 | 7912422 | 0 | 0 | 142770 | 1503600 | 557400 | 504360 | 0 | 11120000 | 86564 | 449127 | 0 | 0 | 540960 | 435925 | 518016 | 88805 | 1178880 | 1333440 | 3359 | 4129780 | 110400 | 538080 | 4945454.55 | 75273 | 0 | 120960 | 55155.6 | 650690 | 5228240 | 0 | 0 | 0 | 25832725 | 13095 | 1195477 | 958472 | 920000 | 0 | 8360900 | 8062000 | 855360 | 4241000 | 491544 | 838080 | 0 | 4028160 | 334320 | 415090 | 2021220 | 892800 | 557520 | 294818 | 320368 | 6980500 | 7680900 | 9134000 | 0 | 0 | 3584864 | 179112 | 0 | 1876800 | 718464 | 0 | 421000 | 3523250 | 639720 | 1393200 | 2978400 | 1741440 | 14600 | 317720 | 252480 | 177271701.15 | 21564364 | 5994432 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 110304 | 336240 | 12974550 | 6720 | 25412430 | 0 | 175311 | 0 | 323328 | 19200 | 436544 | 189312 | 134887 | 0 | 579970 | 132838 | 306000 | 0 | 0 | 4818673 | 0 | 4962273 | 0 | 8811927 | 0 | 27840 | 4649000 | 1134109 | 1152658 | 155625 | 895891 | 0 | 0 | 39678.24 | 969840 | 3586 | 0 | 5825000 | 189360 | 2721000 | 5259460 | 0 | 0 | 26754909.09 | 120000 | 138099259.33 | 315370960.48

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 05-07-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12655.78 | MW | 12:00 Hr. | Energy Generated |  |  | 315.371 |  | MKWHr.
| Day Peak Demand |  |  | 12655.78 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.085 |  | MKWHr.
| Evening Peak Generation |  |  | 14938.72 | MW | 21:00 Hr. | Energy Demand |  |  | 315.456 |  | MKWHr.
| Evening Peak Demand |  |  | 14965.72 | MW | 21:00 Hr. | Maximum Temperature |  |  | 33 |  | °C
| Minimum Generation of the Day |  |  | 11590.57 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 1016.9 |  | MMCFD
| Maximum Generation of the Day |  |  | 14938.72 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.1683 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 46.5109 | 0 | 8.0595 | 0 | 0 | 0.14277 | 0 | 0 | 54.7132 | Gas | 145.4161 | Gas | 515360377.27
| Chattogram Zone |  |  | 5.7663 | 30.7782 | 5.1032 | 0 | 4.1298 | 0.016454 | 0 | 0.54096 | 46.3349 | Coal | 82.1157 | Coal | 554686989.9445
| Cumilla Zone |  |  | 24.5414 | 0 | 9.0581 | 0 | 0 | 0.29482 | 0.8928 | 0 | 34.7871 | HFO | 31.1817 | HFO | 581656618.982
| Mymensingh Zone |  |  | 1.7414 | 0 | 5.2638 | 0 | 0 | 0.33232 | 0 | 0 | 7.3376 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 34.0989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.0989 | Hydro | 4.1298 | Hydro | 412978
| Khulna Zone |  |  | 5.9944 | 12.9746 | 0.11702 | 0 | 0 | 0.33624 | 22.4764 | 0 | 41.8986 | Solar | 3.2051 | Solar | 52568398.3564
| Barishal Zone |  |  | 8.1698 | 32.5799 | 0.12 | 0 | 0 | 0.003586 | 0 | 0 | 40.8733 | Import | 48.7816 | Import | 232699656
| Rajshahi Zone |  |  | 18.5929 | 0 | 1.4114 | 0 | 0 | 0.91381 | 25.4124 | 0 | 46.3305 | Wind | 0.54096 | Wind | 7919654.4
| Rangpur Zone |  |  | 0 | 5.7831 | 2.0485 | 0 | 0 | 1.1651 | 0 | 0 | 8.9968
| Total |  |  | 145.4161 | 82.1157 | 31.1817 | 0 | 4.1298 | 3.2051 | 48.7816 | 0.54096 | 315.371
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 515360377.27 |  | Hydro | 412978
|  |  |  | Coal | 554686989.9445 |  | Solar | 52568398.3564
|  |  |  | HFO | 581656618.982 |  | Import | 232699656
|  |  |  | HSD | 0 |  | Wind | 7919654.4
[5 empty] | Total: | 194,53,04,672 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5644 | Peak Hr Flow | 891.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 26755000 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 25.4124 | Peak Hr Flow | 1248.22 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 634 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.8928 | Peak Hr Flow | 40.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 960 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 47.8696 | Peak Hr Flow | 2179.22 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5058
|  |  |  | Chattogram |  | 0 |  | 1238
|  |  |  | Cumilla |  | 0 |  | 1407
|  |  |  | Mymensingh |  | 0 |  | 1252
|  |  |  | Sylhet |  | 0 |  | 660
|  |  |  | Khulna |  | 0 |  | 1745
|  |  |  | Barishal |  | 0 |  | 461
|  |  |  | Rajshahi |  | 0 |  | 1479
|  |  |  | Rangpur |  | 26 |  | 1051
|  |  |  | Total |  | 26 |  | 14351
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[5 empty] | Total | 300 |  |  |  | Total | 476
|  |  |  | Total Unavailable Capacity |  |  |  | 776
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:01 | 17:58 | Mirpur 132/33kV S/S Reserve Bus Project Work S/D
|  | 08:19 | Magura 132/33kV S/S T-3 (425T) LT is restored.
| 08:33 | 20:37 | Sreepur 230/132/33kV S/S 132/33 kV T-1 HT Scheduled S/D Due to Changing jack bus | [7 empty] | 20.0MW load
|  |  | conductor | [7 empty] | interrup.
| 08:33 | 20:41 | Sreepur 230/132/33kV S/S 132/33 kV T-1 LT Scheduled S/D Due to Changing Jack bus | [7 empty] | 20.0MW load
|  |  | conductor | [7 empty] | interrup.
| 09:01 |  | Haripur 230/132kV S/S Bus-1 Scheduled S/D Due to Meghnaghat 2 DS replacement
| 09:07 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is ON with remarks:- FGMO Minimum @07:49 hrs by
shawkat, SDE
| 09:32 | 10:13 | Cumilla(N)-Daudkandi 132 kV Ckt-1 Tripped from Daudkandi 132/33kV end showing distance | [7 empty] | 10.0MW load
|  |  | relay relays Due to Total substation dead because main busbar fault . | [7 empty] | interrup. Daudkandi
132/33kV end
| 09:32 | 10:14 | Cumilla(N)-Daudkandi 132 kV Ckt-2 Tripped from Daudkandi 132/33kV end showing distance | [7 empty] | 10.0MW load
|  |  | relay relays Due to Total substation dead because main busbar fault . | [7 empty] | interrup. Daudkandi
132/33kV end
| 09:32 | 09:57 | Daudkandi 132/33kV S/S Transformer-1 HT Tripped showing differential protection relay | [7 empty] | 25.0MW load
|  |  | relays Due to Total substation dead because main busbar fault . | [7 empty] | interrup.
| 09:32 | 09:57 | Daudkandi 132/33kV S/S Transformer-1 LT Tripped showing differential protection relay | [7 empty] | 25.0MW load
|  |  | relays Due to Total substation dead because main busbar fault . | [7 empty] | interrup.
| 09:32 | 09:57 | Daudkandi 132/33kV S/S Transformer-2 HT Tripped showing differential protection relay | [7 empty] | 25.0MW load
|  |  | relays Due to Total substation dead because main busbar fault . | [7 empty] | interrup.
| 09:32 | 09:57 | Daudkandi 132/33kV S/S Transformer-2 LT Tripped showing differential protection relay | [7 empty] | 25.0MW load
|  |  | relays Due to Total substation dead because main busbar fault . | [7 empty] | interrup.
| 09:32 | 09:57 | Daudkandi 132/33kV S/S Transformer-3 HT Tripped showing differential protection relay | [7 empty] | 20.0MW load
|  |  | relays Due to Total substation dead because main busbar fault . | [7 empty] | interrup.
| 09:32 | 09:58 | Daudkandi 132/33kV S/S Transformer-3 LT Tripped showing differential protection relay | [7 empty] | 20.0MW load
|  |  | relays Due to Total substation dead because main busbar fault . | [7 empty] | interrup.
| 09:32 | 09:58 | Daudkandi 132/33kV S/S Titas 50 MW Power Plant Line Tripped showing distance relay relays
Due to Total substation dead because main busbar fault .
| 09:32 | 09:58 | Daudkandi-Sonargaon 132 kV Ckt-1 Tripped from Sonargaon 132/33kV end showing General | [7 empty] | and 25.0MW load
|  |  | Trip zone 2 Trip RYB phase fault relays Due to Due to Daudkandi end trip and their bus | [7 empty] | interrup. Daudkandi
|  |  | fault. simultaneously sonargaon end trip. and from Daudkandi 132/33kV end showing | [7 empty] | 132/33kV end
distance relay relays Due to Total substation dead because main busbar fault .
| 09:32 | 10:02 | Daudkandi-Sonargaon 132 kV Ckt-2 Tripped from Sonargaon 132/33kV end showing General Trip | [7 empty] | and 25.0MW load
|  |  | zone 2 Trip RYB phase fault relays Due to Due to Daudkandi end trip and their bus | [7 empty] | interrup. Daudkandi
|  |  | fault. simultaneously sonargaon end trip. and from Daudkandi 132/33kV end showing | [7 empty] | 132/33kV end
distance relay relays Due to Total substation dead because main busbar fault .
| 09:41 | 14:39 | Madunaghat-TKCL 132kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end.
| 09:44 | 23:30 | Khulna(S)-PDB 330MW CCPP 230kV Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end Due to
DFDR Integration Work
| 10:09 | 14:32 | Madunaghat-Sikalbaha 132kV Ckt-2 Scheduled S/D from Madunaghat 132/33kV end.
| 10:24 | 11:47 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) LT Project Work S/D Due to For installation | [7 empty] | 8.0MW load
|  |  | of Transformer-3 | [7 empty] | interrup.
| 10:25 | 11:46 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) HT Project Work S/D Due to For installation | [7 empty] | 8.0MW load
|  |  | of Transformer-3 | [7 empty] | interrup.
|  | 10:32 | Goalpara 132/33kV S/S T1 HT is restored.
|  | 10:33 | Goalpara 132/33kV S/S T1 LT is restored.
| 12:00 |  | Day peak generation 12653MW
| 13:20 | 13:51 | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to Bus balance checking by Energy Audit | [7 empty] | 50.0MW load
|  |  | Barishal. | [7 empty] | interrup.
|  | 14:24 | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) HT is restored.
|  | 14:25 | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) HT is restored.
|  | 14:26 | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) LT is restored.
|  | 14:27 | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) LT is restored.
|  | 14:32 | Rangpur-Rangpur Confidence(100MW) 132kV Ckt-2 is restored.
|  | 14:38 | GPH 230/33kV S/S Transformer-01(D05) HT is restored.
| 14:38 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is OFF with remarks:-
| 15:56 | 16:09 | Cumilla(S) 132/33kV S/S TR-2 LT Tripped showing RET 650 REF 615 relays Due to 33KV Laksam | [7 empty] | 40.0MW load
|  |  | REB Feeder Fault | [7 empty] | interrup.
|  | 17:32 | Sylhet (South) S/S Trafo-2 HT is restored.
|  | 17:34 | Sylhet (South) S/S Trafo-2 LT is restored.
| 18:35 |  | Raozan 25 MW PP Synchronized
|  | 18:50 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) HT is restored.
|  | 18:55 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT is restored.
| 19:48 |  | Adani–Rohanpur 400kV ckt-2 tripped while being switched on from Rohanpur side, showing
SOTF and distance (zone-1, R-phase, 51.3km) relay.
| 21:00 |  | Evening Peak Generation: 14938 MW.
| 00:28 |  | Bhola Nutan Biddut BD LTD Shutdown with remarks:- GT-12
| 00:28 |  | Bhola Nutan Biddut BD LTD Shutdown
| 00:29 |  | Bhola Nutan Biddut BD LTD Synchronized with remarks:- GT-11 (FALSE)
| 00:29 |  | Bhola Nutan Biddut BD LTD Synchronized with remarks:- GT-11
| 01:34 |  | Raozan 25 MW PP Shutdown
| 06:55 |  | Mahasthangar-Palashbari 132kV Ckt-1 Project Work S/D from Mahasthangarh 132/33kV end Due
to Line Project Work. and from Palashbari 132/33kV end Due to Project Work
| 07:00 |  | Minimum Generation is 11983 MW
| 07:36 |  | Faridpur 132/33kV S/S Transformer-2 LT Scheduled S/D Due to 33 Kv Bus-section-3 Hotspot | [7 empty] | 50.0MW load
|  |  | Maintenance. | [7 empty] | interrup.
| 07:37 |  | Faridpur 132/33kV S/S Transformer-2 HT Scheduled S/D Due to 33 Kv Bus-section-3 Hotspot | [7 empty] | 50.0MW load
|  |  | Maintenance. | [7 empty] | interrup.
| 07:42 |  | Bhulta-Narsingdi 132 kV Ckt-1 Project Work S/D from Bhulta 132/33kV end Due to PG clamp
connection
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 05-07-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 401 | 9720000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9454500 | Allocation limit by Titas, instructed by DS(Gen)
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 292 | 7242240 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 80041 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 334 | 7912422 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 596880 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 32 | 195360 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 567526 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 191391 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 26.5 | 557400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 504360 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 349838 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 15 | 254673 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 69 | 1366992 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 797760 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 51 | 465600 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 145 | 1296000 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 142770 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 393840 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 450 | 11120000 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage instructed by DS(Gen)
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 1503600 | Engine Problem
Dhaka Area Total |  |  |  |  | 5939.724 | 2690.5 | 54713193
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 55155.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 13095 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 120960 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 172 | 4129780 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 5228240 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 93 | 650690 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 71 | 518016 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 435925 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 88 | 1178880 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 27 | 538080 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 3359 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 449127 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 17 | 88805 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 15 | 110400 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1333440 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 86564 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 17 | 75273 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1117 | 25832725 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 19 | 540960 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 203 | 4945454.55 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4895.72 | 2283 | 46334929.15
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 196 | 4241000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 352 | 8360900 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 8062000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 20 | 491544 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 52 | 855360 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 120 | 920000 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1195477 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 137 | 958472 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 37 | 320368 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 171 | 4028160 | -
| Import (Tripura) |  | Import | 0 | 160 | 40 | 892800 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 16 | 557520 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 415090 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 96 | 2021220 | Engine Problem
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 29 | 334320 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 838080 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 294818 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1786 | 34787129
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 71 | 1741440 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 163 | 2978400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 82 | 1393200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 317720 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 252480 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 639720 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 363 | 7337560
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | Gas shortage instructed by DS(Gen)
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 132 | 3584864 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 718464 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1876800 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 172 | 3523250 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 421000 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 179112 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 6980500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 374 | 9134000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7680900 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1422 | 34098890
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 891 | 21564364 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 240 | 5994432 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 6720 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 110304 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 336240 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 603 | 12974550 | U#2 under shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1787 | 41898610
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 11 | 189360 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 100 | 2721000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 26754909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5259460 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 120000 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 278 | 5825000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3586 | -
Barishal Area Total |  |  |  |  | 2236 | 1870 | 40873315.09
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 49 | 175311 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 5 | 19200 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 134887 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 200 | 4818673 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 204 | 4962273 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 344 | 8811927 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 132838 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 436544 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 323328 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 189312 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 27840 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1248.22 | 25412430 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 306000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 579970 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2292.22 | 46330533
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 48 | 1134109 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4649000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 895891 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 39678.24 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 114 | 1152658 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 155625 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 969840 | -
Rangpur Area Total |  |  |  |  | 950 | 445 | 8996801.24
Eastern Grid Total |  |  |  |  | 16705.895 | 8544.5 | 177271701.15
Western Grid Total |  |  |  |  | 10378.16 | 6394.22 | 138099259.33
National Grid Total |  |  |  |  | 27084.055 | 14938.72 | 315370960.48
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 05-07-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9614.95 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4709.8 | MW
i) Dhaka area |  |  | 5057.69 |  | MW | i) Khulna area |  |  |  | 1745 | MW
ii) Chattogram area |  |  | 1238.5 |  | MW | ii) Barishal area |  |  |  | 461 | MW
iii) Cumilla area |  |  | 1406.76 |  | MW | iii) Rajshahi area |  |  |  | 1478.8 | MW
iv) Mymensingh area |  |  | 1252 |  | MW | iv) Rangpur area |  |  |  | 1025 | MW
v) Sylhet area |  |  | 660 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14324.75 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 76 | 21:00 | 133 | Pabna | 124 | 21:00
2 | AKSML | 108 | 00:00 | 68 | Ishurdi | 79 | 19:30 | 134 | Palashbari | 110 | 00:00
3 | Aftabnagar | 36 | 19:00 | 69 | Jaldhaka | 90 | 22:00 | 135 | Panchagarh | 64 | 19:30
4 | Agargaon | 123 | 12:00 | 70 | Jamalpur | 121 | 20:00 | 136 | Patuakhali | 77.3 | 22:00
5 | Agrabad | 84 | 20:00 | 71 | Jashore | 130 | 19:30 | 137 | Payra | 32 | 00:00
6 | Amnura | 38 | 00:00 | 72 | Jhenaidah | 119 | 19:30 | 138 | Postogola | 58 | 17:00
7 | Ashuganj | 108 | 00:00 | 73 | Joydebpur | 143 | 12:00 | 139 | Purbachal | 21 | 19:00
8 | BSRM | 191 | 06:00 | 74 | Joypurhat | 68 | 22:00 | 140 | Purbasadipur | 137 | 23:00
9 | Bagerhat | 83 | 00:00 | 75 | Juldah | 14 | 00:00 | 141 | Rahanpur | 31 | 22:00
10 | Bajitpur | 68 | 00:00 | 76 | KSRM | 20 | 05:00 | 142 | Rahim | 22 | 00:00
11 | Bakulia | 86 | 19:00 | 77 | Kabirpur | 193 | 21:00 | 143 | Rajbari | 80 | 19:30
12 | Banani | 32 | 13:00 | 78 | Kachua | 96 | 22:00 | 144 | Rajendrapur | 134 | 19:30
13 | Bangabhaban | 6 | 10:00 | 79 | Kallyanpur | 102 | 19:00 | 145 | Rajshahi | 115 | 00:00
14 | Barapukuria | 64 | 22:00 | 80 | Kalurghat | 36 | 12:00 | 146 | Rajshahi-230 | 87 | 13:00
15 | Barguna | 20 | 00:00 | 81 | Kamrangirchar | 67 | 13:00 | 147 | Ramganj | 114 | 00:00
16 | Barishal | 99 | 22:00 | 82 | Kaptai | N/A | N/A | 148 | Rampur | 38 | 23:00
17 | Barishal-230 | 108 | 19:30 | 83 | Kasba | 37 | 22:00 | 149 | Rangamati | 16 | 19:00
18 | Baroaulia | 71 | 11:00 | 84 | Kazla | 96 | 13:00 | 150 | Rangpur | 151 | 20:00
19 | Baroirhat | 67 | 19:30 | 85 | Keranigonj | 95 | 19:30 | 151 | Ruppur | 4.6 | 11:00
20 | Bashundhara | 178 | 15:00 | 86 | Khagrachori | 30 | 19:00 | 152 | SSM | 3 | 22:00
21 | BashundharaCement | 8 | 15:00 | 87 | Khulna | 62 | 13:00 | 153 | Saidpur | 112 | 20:00
22 | Beanibazar | 86 | 21:00 | 88 | Khulshi | 143 | 19:00 | 154 | Satkhira | 126 | 21:00
23 | Benapole | 66 | 21:00 | 89 | Kishoreganj | 144 | 21:00 | 155 | Satmasjid | 98 | 14:00
24 | Bhaluka | 153 | 20:00 | 90 | Kodda | 304 | 19:30 | 156 | Savar | 226 | 15:00
25 | Bhandaria | 70 | 05:00 | 91 | Kulaura | 59 | 00:00 | 157 | SevenRings | 17.91 | 00:00
26 | Bhangura | 36 | 19:30 | 92 | Kurigram | 66 | 20:00 | 158 | ShahCement | 23 | 00:00
27 | Bheramara(GK) | 67 | 22:00 | 93 | Kushtia | 153 | 19:30 | 159 | Shahjadpur | 79 | 19:30
28 | Bhulta | 239 | 21:00 | 94 | Lakshmipur | 20.42 | 00:00 | 160 | Shahjibazar | 125 | 22:00
29 | Bog-Sherpur | 62 | 19:30 | 95 | Lalbag | 56 | 18:30 | 161 | Shahmirpur | 62 | 12:00
30 | Bogura | 165 | 23:00 | 96 | Lalmonirhat | 66 | 19:30 | 162 | Shariatpur | 90 | 22:00
31 | Borhanuddin | 87 | 00:00 | 97 | MI_Cement | 13.2 | 09:00 | 163 | Sherpur | 160 | 22:00
32 | Brahmanbaria | 125 | 00:00 | 98 | Madanganj | 48 | 00:00 | 164 | Shikalbaha | 22 | 18:00
33 | Cantonment | 146 | 19:00 | 99 | Madaripur | 110 | 22:00 | 165 | Shitalakhya | 80.9 | 16:00
34 | Chandina | 19.56 | 21:00 | 100 | Madartek | 86.66 | 19:00 | 166 | Sholosohor | 43 | 15:00
35 | Chandpur | 76 | 21:00 | 101 | Madunaghat | 59 | 20:00 | 167 | Shyampur | 168 | 12:00
36 | Chandraghona | 35 | 19:30 | 102 | Magura | 62 | 19:30 | 168 | Siddhirganj | 123 | 16:00
37 | Chapai | 67 | 01:00 | 103 | Mahasthangarh | 80 | 20:00 | 169 | Sirajganj | 104 | 20:00
38 | Charsaidpur | 25 | 13:00 | 104 | Maijdee | 15 | 21:00 | 170 | Sonargaon | 87 | 21:00
39 | Chauddagram | 68 | 22:00 | 105 | Manikganj | 117 | 23:00 | 171 | Sreemongol | 80 | 00:00
40 | Chhatak | 43 | 23:00 | 106 | Maniknagar | 72 | 13:00 | 172 | Sreepur | 84 | 23:00
41 | Chowmuhani | 194 | 19:00 | 107 | Matarbari | 47 | 19:00 | 173 | Srinagar | 48.73 | 22:00
42 | Chuadanga | 116 | 21:00 | 108 | Matuail | 65 | 16:00 | 174 | Sunamganj | 65 | 23:00
43 | Coxsbazar | 119 | 00:00 | 109 | Millgate | 112 | 15:00 | 175 | Sylhet | 52 | 20:00
44 | Cumilla(N) | 148 | 00:00 | 110 | Mirpur | 125 | 19:00 | 176 | Sylhet-132 | 151 | 14:00
45 | Cumilla(S) | 159 | 14:00 | 111 | Mirsorai | 10 | 12:00 | 177 | TK | 34 | 15:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirzapur | 50 | 21:00 | 178 | Tangail | 178 | 21:00
47 | Daudkandi | 145 | 21:00 | 113 | Mithapukur | 65 | 20:00 | 179 | Taraganj | 22 | 00:00
48 | Dhaka | 62 | 13:00 | 114 | Modern | N/A | N/A | 180 | Thakurgaon | 112 | 21:00
49 | Dhamrai | 126 | 20:00 | 115 | Mogbazar | 136 | 17:00 | 181 | Tongi | 137 | 10:00
50 | Dhanmondi | 129.3 | 13:00 | 116 | Mongla | 39 | 16:00 | 182 | Ullahpara | 38 | 19:30
51 | Dohazari | 98 | 00:00 | 117 | Motijheel | 39 | 13:00 | 183 | Ullon | 38 | 00:00
52 | Faridpur | 159 | 22:00 | 118 | Muktagacha | 40 | 22:00 | 184 | Uttara | 77 | 12:00
53 | Fatullah | 100 | 12:00 | 119 | Munshiganj | 113 | 00:00 | 185 | UttaraNew | 59 | 19:30
54 | Fenchuganj | 45 | 14:00 | 120 | Muradnagar | 28 | 20:00 | 186 | Zigatola | 78 | 19:30
55 | Feni | 102 | 20:00 | 121 | Mymensingh | 204 | 00:00
56 | GPH | 18 | 20:00 | 122 | Naogaon | 123 | 21:00
57 | Ghatail | 84 | 21:00 | 123 | Narail | 56.5 | 20:00
58 | Ghorashal | 14 | 09:00 | 124 | Narinda | 71 | 13:00
59 | Ghorashal-230 | 91 | 20:00 | 125 | Narshingdi | 195 | 20:00
60 | Goalpara | 36 | 13:00 | 126 | Natore | 156 | 23:00
61 | Gollamari | 92 | 21:00 | 127 | Nawabganj | 60 | 22:00
62 | Gopalganj | 103.6 | 22:00 | 128 | Netrakona | 136 | 22:00
63 | Gulshan | 112 | 15:00 | 129 | New | 61 | 15:00
64 | Halishahar | 64 | 16:00 | 130 | Niamatpur | 72 | 00:00
65 | HaripurSBU | 182 | 12:00 | 131 | Noapara | 46 | 20:00
66 | Hasnabad | 67 | 19:00 | 132 | PHP | 8 | 11:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 05-07-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14172 | 0 |  | 14172
1:00 | 13757.2 | 0 |  | 13757.2
2:00 | 13226.2 | 0 |  | 13226.2
3:00 | 12827.2 | 0 |  | 12827.2
4:00 | 12406.2 | 0 |  | 12406.2
5:00 | 12130.2 | 0 |  | 12130.2
6:00 | 11782.13 | 0 |  | 11782.13
7:00 | 11590.57 | 0 |  | 11590.57
8:00 | 11653.43 | 0 |  | 11653.43
9:00 | 11747.14 | 0 |  | 11747.14
10:00 | 11860.7 | 0 |  | 11860.7
11:00 | 12192.65 | 0 |  | 12192.65
12:00 | 12655.78 | 0 |  | 12655.78
13:00 | 12924.03 | 0 |  | 12924.03
14:00 | 12891.2 | 0 |  | 12891.2
15:00 | 13260.86 | 0 |  | 13260.86
16:00 | 13078.61 | 0 |  | 13078.61
17:00 | 12561.91 | 0 |  | 12561.91
18:00 | 12232.31 | 0 |  | 12232.31
19:00 | 13471.1 | 0 |  | 13471.1
19:30 | 14725.02 | 0 |  | 14725.02
20:00 | 14772.44 | 0 |  | 14772.44
21:00 | 14938.72 | 26 |  | 14965.72
22:00 | 14892.72 | 27 |  | 14920.72
23:00 | 14827.49 | 32 |  | 14860.93
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 05-07-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8146 | 6026 | 14172 | DAILY GENERATION CURVE
00:30 | 7945.1 | 6019.5 | 13964.6
01:00 | 7744.2 | 6013 | 13757.2 | 05-07-2025
01:30 | 7525.7 | 5966 | 13491.7
02:00 | 7307.2 | 5919 | 13226.2
02:30 | 7191.2 | 5835.5 | 13026.7
03:00 | 7075.2 | 5752 | 12827.2
03:30 | 6963.7 | 5653 | 12616.7
04:00 | 6852.2 | 5554 | 12406.2
04:30 | 6807.2 | 5461 | 12268.2
05:00 | 6762.2 | 5368 | 12130.2
05:30 | 6690.92 | 5265.245 | 11956.165
06:00 | 6619.64 | 5162.49 | 11782.13
06:30 | 6574.16 | 5112.19 | 11686.35
07:00 | 6528.68 | 5061.89 | 11590.57
07:30 | 6533.865 | 5088.135 | 11622
08:00 | 6539.05 | 5114.38 | 11653.43
08:30 | 6561.085 | 5139.2 | 11700.285
09:00 | 6583.12 | 5164.02 | 11747.14
09:30 | 6615.065 | 5188.855 | 11803.92
10:00 | 6647.01 | 5213.69 | 11860.7
10:30 | 6725.35 | 5301.325 | 12026.675
11:00 | 6803.69 | 5388.96 | 12192.65
11:30 | 6846.25 | 5577.965 | 12424.215
12:00 | 6888.81 | 5766.97 | 12655.78
12:30 | 6985.4 | 5804.505 | 12789.905
13:00 | 7081.99 | 5842.04 | 12924.03
13:30 | 7074.52 | 5833.095 | 12907.615
14:00 | 7067.05 | 5824.15 | 12891.2
14:30 | 7206.705 | 5869.325 | 13076.03
15:00 | 7346.36 | 5914.5 | 13260.86
15:30 | 7381.79 | 5787.945 | 13169.735
16:00 | 7417.22 | 5661.39 | 13078.61
16:30 | 7392.215 | 5428.045 | 12820.26
17:00 | 7367.21 | 5194.7 | 12561.91
17:30 | 7269.615 | 5127.495 | 12397.11
18:00 | 7172.02 | 5060.29 | 12232.31
18:30 | 7536.26 | 5315.445 | 12851.705
19:00 | 7900.5 | 5570.6 | 13471.1
19:30 | 8590.7 | 6134.32 | 14725.02
20:00 | 8665.7 | 6106.74 | 14772.44
20:30 | 8605.1 | 6250.48 | 14855.58 |  | Executive Engineer
21:00 | 8544.5 | 6394.22 | 14938.72 |  | Network Operation Division
21:30 | 8517.5 | 6398.22 | 14915.72
22:00 | 8490.5 | 6402.22 | 14892.72
22:30 | 8443.5 | 6416.605 | 14860.105
23:00 | 8396.5 | 6430.99 | 14827.49

## En-Curve
QF-LDC-12
Date | 05-07-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3808 | 2465 | 890 | 38 | 40 | 1170 | 172 | 3807 | 0 | 308 | 1445 | 0 | 0 | 29 | 0 | DAILY ENERGY CURVE
00:30 | 3779 | 2363 | 890 | 38 | 40 | 1167.5 | 172 | 3776 | 0 | 308 | 1405.6 | 0 | 0 | 25.5 | 0 | 05-07-2025
01:00 | 3750 | 2261 | 890 | 38 | 40 | 1165 | 172 | 3745 | 0 | 308 | 1366.2 | 0 | 0 | 22 | 0
01:30 | 3769.5 | 2269 | 890 | 38 | 38 | 1167 | 172 | 3718 | 0 | 211 | 1187.7 | 0 | 0 | 31.5 | 0 | Energy Generated | 315.371 |  | MKWHr
02:00 | 3789 | 2277 | 890 | 38 | 36 | 1169 | 172 | 3691 | 0 | 114 | 1009.2 | 0 | 0 | 41 | 0 | Energy not Served | 0.085 |  | MKWHr
02:30 | 3807.5 | 2272.5 | 890 | 38 | 37 | 1168.5 | 172 | 3626 | 0 | 106 | 878.2 | 0 | 0 | 31 | 0 | Total Energy Requirement | 315.456 |  | MKWHr
03:00 | 3826 | 2268 | 890 | 38 | 38 | 1168 | 172 | 3561 | 0 | 98 | 747.2 | 0 | 0 | 21 | 0
03:30 | 3861.5 | 2239.5 | 890 | 38 | 37 | 1144.5 | 172 | 3473 | 0 | 84 | 653.7 | 0 | 0 | 23.5 | 0
04:00 | 3897 | 2211 | 890 | 38 | 36 | 1121 | 172 | 3385 | 0 | 70 | 560.2 | 0 | 0 | 26 | 0
04:30 | 3929 | 2184 | 890.5 | 38 | 33 | 1089 | 172 | 3308.5 | 0 | 61 | 543.7 | 0 | 0 | 19.5 | 0
05:00 | 3961 | 2157 | 891 | 38 | 30 | 1057 | 172 | 3232 | 0 | 52 | 527.2 | 0 | 0 | 13 | 0
05:30 | 3963.5 | 2132 | 890.5 | 38 | 31 | 988 | 172 | 3160.5 | 9.565 | 52 | 512.6 | 0 | 0 | 6.5 | 0
06:00 | 3966 | 2107 | 890 | 38 | 32 | 919 | 172 | 3089 | 19.13 | 52 | 498 | 0 | 0 | 0 | 0
06:30 | 3914 | 2064.5 | 890 | 38 | 32 | 914.5 | 172 | 3046.5 | 56.35 | 45 | 502 | 0 | 0 | 11.5 | 0
07:00 | 3862 | 2022 | 890 | 38 | 32 | 910 | 172 | 3004 | 93.57 | 38 | 506 | 0 | 0 | 23 | 0
07:30 | 3884.5 | 1998.75 | 890.5 | 38 | 31 | 919.53 | 172 | 2995.5 | 132.72 | 37.5 | 496.5 | 0 | 0 | 25.5 | 0
08:00 | 3907 | 1975.5 | 891 | 38 | 30 | 929.06 | 172 | 2987 | 171.87 | 37 | 487 | 0 | 0 | 28 | 0
08:30 | 3905.5 | 1969.5 | 890.5 | 38 | 30 | 931.18 | 172 | 2981.5 | 226.105 | 52 | 470 | 0 | 0 | 34 | 0
09:00 | 3904 | 1963.5 | 890 | 38 | 30 | 933.3 | 172 | 2976 | 280.34 | 67 | 453 | 0 | 0 | 40 | 0
09:30 | 3897.5 | 1965 | 890.5 | 38 | 31 | 931.725 | 172 | 2969 | 326.195 | 67 | 475 | 0 | 0 | 41 | 0
10:00 | 3891 | 1966.5 | 891 | 38 | 32 | 930.15 | 172 | 2962 | 372.05 | 67 | 497 | 0 | 0 | 42 | 0
10:30 | 3931.5 | 2020 | 891 | 38 | 32 | 966.325 | 172 | 2989.5 | 379.85 | 67 | 510 | 0 | 0 | 29.5 | 0
11:00 | 3972 | 2073.5 | 891 | 38 | 32 | 1002.5 | 172 | 3017 | 387.65 | 67 | 523 | 0 | 0 | 17 | 0
11:30 | 3963.5 | 2069.5 | 891 | 38 | 34 | 1008.01 | 172 | 3143 | 495.705 | 67 | 528 | 0 | 0 | 14.5 | 0
12:00 | 3955 | 2065.5 | 891 | 38 | 36 | 1013.52 | 172 | 3269 | 603.76 | 67 | 533 | 0 | 0 | 12 | 0
12:30 | 3962.5 | 2093.5 | 890.5 | 38 | 37 | 1012.55 | 172 | 3410 | 487.355 | 67 | 601.5 | 0 | 0 | 18 | 0
13:00 | 3970 | 2121.5 | 890 | 38 | 38 | 1011.58 | 172 | 3551 | 370.95 | 67 | 670 | 0 | 0 | 24 | 0
13:30 | 3944.5 | 2066.5 | 890 | 38 | 39 | 1023.985 | 172 | 3584.5 | 331.63 | 76 | 718 | 0 | 0 | 23.5 | 0
14:00 | 3919 | 2011.5 | 890 | 38 | 40 | 1036.39 | 172 | 3618 | 292.31 | 85 | 766 | 0 | 0 | 23 | 0
14:30 | 3942 | 2044 | 890 | 38 | 38 | 1052.835 | 172 | 3623 | 312.695 | 93.5 | 847.5 | 0 | 0 | 22.5 | 0
15:00 | 3965 | 2076.5 | 890 | 38 | 36 | 1069.28 | 172 | 3628 | 333.08 | 102 | 929 | 0 | 0 | 22 | 0
15:30 | 3925.5 | 2057 | 890.5 | 38 | 36 | 1061.275 | 172 | 3564.5 | 289.96 | 118 | 994 | 0 | 0 | 23 | 0
16:00 | 3886 | 2037.5 | 891 | 38 | 36 | 1053.27 | 172 | 3501 | 246.84 | 134 | 1059 | 0 | 0 | 24 | 0
16:30 | 3861 | 2020 | 891 | 38 | 38 | 959.94 | 172 | 3369.5 | 192.72 | 146.5 | 1109.6 | 0 | 0 | 22 | 0
17:00 | 3836 | 2002.5 | 891 | 38 | 40 | 866.61 | 172 | 3238 | 138.6 | 159 | 1160.2 | 0 | 0 | 20 | 0
17:30 | 3808.5 | 1958 | 891 | 38 | 41 | 867.46 | 172 | 3181.5 | 85.55 | 173 | 1162.1 | 0 | 0 | 19 | 0
18:00 | 3781 | 1913.5 | 891 | 38 | 42 | 868.31 | 172 | 3125 | 32.5 | 187 | 1164 | 0 | 0 | 18 | 0
18:30 | 3780 | 1940.5 | 891 | 38 | 45 | 922.455 | 172 | 3259 | 16.25 | 320 | 1449 | 0 | 0 | 18.5 | 0
19:00 | 3779 | 1967.5 | 891 | 38 | 48 | 976.6 | 172 | 3393 | 0 | 453 | 1734 | 0 | 0 | 19 | 0
19:30 | 3898 | 2115.5 | 890 | 38 | 48 | 1089.32 | 172 | 3490 | 0 | 616 | 2349.2 | 0 | 0 | 19 | 0
20:00 | 3913 | 2165.5 | 891 | 38 | 40 | 1095.74 | 172 | 3517 | 0 | 588 | 2341.2 | 0 | 0 | 11 | 0
20:30 | 3924.5 | 2189 | 891 | 38 | 40 | 1171.98 | 172 | 3590 | 0 | 620 | 2204.1 | 0 | 0 | 15 | 13
21:00 | 3936 | 2212.5 | 891 | 38 | 40 | 1248.22 | 172 | 3663 | 0 | 652 | 2067 | 0 | 0 | 19 | 26
21:30 | 3938 | 2154.5 | 890.5 | 38 | 40 | 1248.22 | 172 | 3683 | 0 | 648.5 | 2084 | 0 | 0 | 19 | 26.5
22:00 | 3940 | 2096.5 | 890 | 38 | 40 | 1248.22 | 172 | 3703 | 0 | 645 | 2101 | 0 | 0 | 19 | 27
22:30 | 3958.5 | 2091 | 890 | 38 | 41 | 1266.605 | 172 | 3702.5 | 0 | 621.5 | 2057 | 0 | 0 | 22 | 29.5
23:00 | 3977 | 2085.5 | 890 | 38 | 42 | 1284.99 | 172 | 3702 | 0 | 598 | 2013 | 0 | 0 | 25 | 32
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 05-07-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 388 | 07:00 | 376 | 12:00 | Payra | 416 | 07:00 | 408 | 00:00
Ashuganj | 400 | 5:00 | 368 | 13:00 | Rahanpur | 394 | 07:00 | 374 | 23:00
Bhulta | 395 | 06:00 | 366 | 12:00 | Rampal | 405 | 07:00 | 386 | 22:00
Bibiana | 390 | 07:00 | 383 | 13:00
BIPTC | 402 | 06:00 | 394 | 23:00
Bogura | 384 | 19:00 | 363 | 23:00
Gopalganj | 400 | 06:00 | 386 | 23:00
Kaliakoir | 378 | 06:00 | 364 | 15:00
Madunaghat | 398 | 20:00 | 391 | 13:00
Meghnaghat | 392 | 07:00 | 381 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 227 | 07:00 | 217 | 12:00 | Keranigonj | 226 | 07:00 | 216 | 12:00
AKSML | 234 | 19:00 | 227 | 02:00 | Khulna(S) | 233 | 08:00 | 215 | 22:00
Aminbazar | 228 | 06:00 | 218 | 12:00 | Madunaghat | 237 | 19:00 | 230 | 04:00
Ashuganj | 231 | 07:00 | 218 | 14:00 | Madunaghat-400 | 238 | 20:00 | 231 | 03:00
Ashuganj-400 | 231 | 07:00 | 218 | 14:00 | Maniknagar | 224 | 06:00 | 216 | 12:00
Baghabari | 235 | 06:00 | 225 | 21:00 | Meghnaghat | 232 | 18:30 | 222 | 14:00
Barapukuria | 224 | 19:00 | 214 | 22:00 | Meghnaghat-400 | 228 | 07:00 | 221 | 12:00
Barapukuria-230 | 224 | 19:00 | 214 | 22:00 | Mirsorai | 232 | 17:00 | 224 | 02:00
Barishal | 230 | 05:00 | 221 | 23:00 | Rajshahi | 235 | 07:00 | 222 | 21:00
Bheramara | 233 | 06:00 | 221 | 21:00 | Rampal | 232 | 08:00 | 215 | 23:00
Bhulta | 227 | 06:00 | 208 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 229 | 18:00 | 222 | 22:00 | Rampura | 226 | 06:00 | 206 | 15:00
BIPTC | 237 | 06:00 | 221 | 23:00 | Shikalbaha | 236 | 18:30 | 227 | 04:00
Bogura | 233 | 07:00 | 222 | 00:00 | Shyampur | 230 | 18:00 | 217 | 12:00
Bogura-400 | 233 | 19:00 | 221 | 23:00 | Siddhirganj | 225 | 05:00 | 218 | 14:00
Borhanuddin | 236 | 07:00 | 230 | 00:00 | Sirajgonj | 238 | 06:00 | 231 | 23:00
BSRM | 231 | 18:00 | 224 | 00:00 | Sreepur | 228 | 07:00 | 216 | 23:00
Cumilla(N) | 225 | 07:00 | 217 | 13:00 | Tongi | 227 | 04:00 | 210 | 15:00
Faridpur | 228 | 07:00 | 218 | 22:00
Fenchuganj | 231 | 18:30 | 224 | 21:00
Ghorashal | 232 | 02:00 | 220 | 01:00
Ghorashal-230 | 226 | 06:00 | 210 | 15:00
Gopalganj | 230 | 16:00 | 220 | 21:00
GPH | 235 | 19:30 | 228 | 00:00
Haripur | 224 | 06:00 | 217 | 12:00
Hasnabad | 226 | 06:00 | 217 | 15:00
Hathazari | 233 | 17:00 | 227 | 12:00
Ishurdi | 236 | 06:00 | 223 | 21:00
Jhenaidah | 234 | 08:00 | 215 | 21:00
Kaliakoir | 232 | 06:00 | 221 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 05:00 | 123 | 14:00 | Madanganj | 131 | 05:00 | 126 | 11:00
Agargaon | 134 | 07:00 | 126 | 12:00 | Madaripur | 136 | 09:00 | 130 | 00:00
Agrabad | 135 | 19:30 | 129 | 12:00 | Madartek | 137 | 06:00 | 123 | 14:00
AKS | 134 | 18:00 | 126 | 12:00 | Madunaghat | 135 | 18:30 | 130 | 04:00
Aminbazar | 132 | 00:00 | 126 | 12:00 | Magura | 138 | 07:00 | 122 | 19:30
Amnura | 136 | 06:00 | 120 | 21:00 | Mahasthangarh | 134 | 06:00 | 126 | 00:00
Ashuganj | 139 | 18:00 | 132 | 22:00 | Maijdee | 122 | 18:30 | 108 | 01:00
Bagerhat | 134 | 07:00 | 118 | 22:00 | Manikganj | 129 | 06:00 | 117 | 12:00
Bajitpur | 132 | 18:00 | 124 | 12:00 | Maniknagar | 133 | 03:00 | 127 | 13:00
Bakulia | 137 | 19:30 | 131 | 02:00 | Matarbari | 129 | 21:00 | 118 | 06:00
Banani | 138 | 06:00 | 123 | 15:00 | Matuail | 131 | 07:00 | 126 | 12:00
Bangabhaban | 133 | 04:00 | 127 | 13:00 | Millgate | 133 | 05:00 | 121 | 12:00
Barapukuria | 137 | 19:00 | 126 | 23:00 | Mirpur | 132 | 05:00 | 124 | 12:00
Barguna | 134 | 06:00 | 131 | 00:00 | Mirzapur | 130 | 06:00 | 124 | 21:00
Barishal | 135 | 09:00 | 128 | 00:00 | Mithapukur | 132 | 19:00 | 120 | 00:00
Barishal-230 | 135 | 07:00 | 128 | 23:00 | MI_Cement | 132 | 06:00 | 126 | 12:00
Baroaulia | 135 | 18:00 | 130 | 12:00 | Modern | N/A | N/A | N/A | N/A
Baroirhat | 124 | 08:00 | 118 | 15:00 | Mogbazar | 139 | 07:00 | 123 | 15:00
Bashundhara | 137 | 06:00 | 121 | 16:00 | Mongla | 136 | 08:00 | 120 | 22:00
BashundharaCement | 131 | 05:00 | 126 | 11:00 | Motijheel | 133 | 04:00 | 127 | 13:00
Beanibazar | 130 | 18:00 | 122 | 22:00 | Muktagacha | 134 | 08:00 | 127 | 21:00
Benapole | 133 | 05:00 | 118 | 22:00 | Munshiganj | 131 | 06:00 | 125 | 12:00
Bhaluka | 131 | 08:00 | 121 | 22:00 | Muradnagar | 128 | 18:00 | 120 | 13:00
Bhandaria | 132 | 18:00 | 120 | 22:00 | Mymensingh | 136 | 08:00 | 112 | 23:00
Bhangura | 133 | 01:00 | 127 | 21:00 | Naogaon | 132 | 06:00 | 123 | 00:00
Bheramara | 137 | 06:00 | 131 | 23:00 | Narail | 138 | 08:00 | 119 | 19:30
Bheramara(GK) | 137 | 06:00 | 132 | 00:00 | Narinda | 133 | 03:00 | 127 | 13:00
Bhulta | 122 | 06:00 | 111 | 15:00 | Narshingdi | 133 | 18:00 | 112 | 15:00
Bog-Sherpur | 135 | 07:00 | 128 | 00:00 | Natore | 135 | 06:00 | 128 | 00:00
Bogura | 138 | 19:00 | 130 | 00:00 | Nawabganj | 135 | 06:00 | 128 | 12:00
Bogura-230 | 138 | 19:00 | 130 | 00:00 | Netrakona | 129 | 07:00 | 110 | 22:00
Brahmanbaria | 133 | 18:00 | 122 | 23:00 | New | 134 | 06:00 | 122 | 12:00
Cantonment | 134 | 06:00 | 126 | 12:00 | Niamatpur | 134 | 17:00 | 124 | 23:00
Chandina | 130 | 18:30 | 122 | 13:00 | Noapara | 137 | 08:00 | 123 | 22:00
Chandpur | 131 | 18:30 | 116 | 15:00 | Pabna | 135 | 06:00 | 128 | 21:00
Chandraghona | 135 | 18:30 | 131 | 02:00 | Palashbari | 130 | 19:00 | 121 | 00:00
Chapai | 132 | 18:00 | 121 | 23:00 | Panchagarh | 138 | 19:00 | 122 | 04:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 131 | 05:00 | 126 | 12:00 | Patuakhali | 135 | 09:00 | 131 | 00:00
Chauddagram | 126 | 18:00 | 117 | 15:00 | Payra | 136 | 05:00 | 133 | 14:00
Chhatak | 128 | 18:00 | 119 | 23:00 | PHP | 126 | 18:30 | 117 | 01:00
Chowmuhani | 121 | 18:00 | 111 | 00:00 | Postogola | 134 | 03:00 | 128 | 12:00
Chuadanga | 137 | 08:00 | 117 | 23:00 | Purbachal | 137 | 06:00 | 121 | 15:00
Coxsbazar | 128 | 19:30 | 119 | 03:00 | Purbasadipur | 129 | 19:00 | 120 | 12:00
Cumilla(N) | 130 | 18:00 | 123 | 13:00 | Rahanpur | 135 | 18:00 | 126 | 23:00
Cumilla(S) | 133 | 05:00 | 120 | 13:00 | Rahanpur-400 | 135 | 07:00 | 127 | 23:00
Daganbhuiyan | 122 | 18:00 | 111 | 23:00 | Rahim | 131 | 05:00 | 127 | 11:00
Daudkandi | 129 | 10:00 | 119 | 12:00 | Rajbari | 134 | 07:00 | 126 | 23:00
Dhaka | 138 | 06:00 | 125 | 13:00 | Rajendrapur | 134 | 00:00 | 120 | 12:00
Dhamrai | 132 | 07:00 | 123 | 15:00 | Rajshahi | 136 | 07:00 | 128 | 00:00
Dhanmondi | 138 | 06:00 | 123.6 | 15:00 | Rajshahi-230 | 136 | 06:00 | 114 | 23:00
Dohazari | 135 | 21:00 | 127 | 06:00 | Ramganj | 124 | 18:30 | 111 | 00:00
Faridpur | 135 | 06:00 | 129 | 22:00 | Rampur | 135 | 19:30 | 129 | 01:00
Fatullah | 133 | 06:00 | 127 | 12:00 | Rampura | 137 | 06:00 | 123 | 15:00
Fenchuganj | 136 | 17:00 | 131 | 21:00 | Rangamati | 134 | 18:30 | 130 | 01:00
Feni | 124 | 18:30 | 114 | 23:00 | Rangpur | 128 | 01:00 | 121 | 23:00
Ghatail | 132 | 18:30 | 122 | 21:00 | Ruppur | 138 | 07:00 | 131 | 21:00
Ghorashal | 135 | 01:00 | 128 | 12:00 | Saidpur | 132 | 19:00 | 121 | 23:00
Goalpara | 138 | 08:00 | 125 | 22:00 | Satkhira | 137 | 09:00 | 120 | 21:00
Gollamari | 138 | 06:00 | 127 | 22:00 | Satmasjid | 134 | 06:00 | 126 | 12:00
Gopalganj | 136 | 06:00 | 128 | 22:00 | Savar | 132 | 20:00 | 122 | 12:00
Gopalganj-400 | 137 | 05:00 | 131 | 23:00 | SevenRings | 137 | 07:00 | 127 | 12:00
Gulshan | 137 | 04:00 | 123 | 15:00 | ShahCement | 131 | 05:00 | 126 | 12:00
Halishahar | 138 | 19:30 | 124 | 23:00 | Shahjadpur | 136 | 08:00 | 132 | 00:00
Haripur | 132 | 06:00 | 127 | 12:00 | Shahjibazar | 133 | 07:00 | 123 | 23:00
HaripurSBU | 132 | 06:00 | 127 | 12:00 | Shahmirpur | 137 | 18:00 | 130 | 04:00
Hasnabad | 133 | 04:00 | 128 | 13:00 | Shariatpur | 135 | 08:00 | 127 | 23:00
Hathazari | 136 | 20:00 | 132 | 00:00 | Sherpur | 136 | 18:30 | 125 | 12:00
Ishurdi | 138 | 06:00 | 131 | 23:00 | Shikalbaha | 126 | 18:30 | 120 | 03:00
Jaldhaka | 126 | 04:00 | 118 | 23:00 | Shikalbaha-230 | 138 | 19:30 | 132 | 12:00
Jamalpur | 139 | 18:30 | 130 | 14:00 | Shitalakhya | 132 | 06:00 | 126 | 12:00
Jashore | 133 | 06:00 | 119 | 19:30 | Sholosohor | 134 | 18:30 | 130 | 01:00
Jhenaidah | 137 | 07:00 | 122 | 23:00 | Shyampur | 132 | 04:00 | 127 | 10:00
Jhenaidah-230 | 139 | 08:00 | 125 | 21:00 | Shyampur-230 | 132 | 05:00 | 127 | 12:00
Joydebpur | 134 | 02:00 | 122 | 12:00 | Siddhirganj | 132 | 05:00 | 126 | 12:00
Joypurhat | 130 | 06:00 | 120 | 00:00 | Sirajganj | 133 | 08:00 | 126 | 22:00
Juldah | 137 | 18:30 | 130 | 04:00 | Sonargaon | 130 | 05:00 | 125 | 11:00
Kabirpur | 133 | 19:00 | 118 | 15:00 | Sreemongol | 133 | 18:00 | 124 | 22:00
Kachua | 128 | 18:00 | 116 | 23:00 | Sreepur | 133 | 07:00 | 124 | 22:00
Kaliakoir | 135 | 06:00 | 126 | 12:00 | Srinagar | 135 | 06:00 | 128 | 12:00
Kallyanpur | 132 | 18:00 | 126 | 12:00 | SSM | 139 | 18:00 | 132 | 02:00
Kalurghat | 135 | 20:00 | 130 | 02:00 | Sunamganj | 125 | 18:00 | 117 | 23:00
Kamrangirchar | 136 | 04:00 | 127 | 12:00 | Sylhet | 131 | 18:00 | 124 | 22:00
Kaptai | 134 | 6:00 | 124 | 13:00 | Sylhet-132 | 129 | 05:00 | 125 | 21:00
Kasba | 128 | 18:00 | 119 | 13:00 | Tangail | 129 | 08:00 | 122 | 21:00
Kazla | 133 | 06:00 | 127 | 13:00 | Taraganj | 132 | 19:00 | 122 | 13:00
Keranigonj | 139 | 06:00 | 129 | 12:00 | Thakurgaon | 138 | 19:00 | 120 | 13:00
Khagrachori | 133 | 17:00 | 129 | 02:00 | TK | 135 | 19:30 | 130 | 04:00
Khulna | 137 | 07:00 | 124 | 22:00 | Tongi | 135 | 04:00 | 125 | 12:00
Khulna(S) | 139 | 06:00 | 127 | 21:00 | Ullahpara | 135 | 07:00 | 128 | 21:00
Khulshi | 134 | 19:00 | 128 | 12:00 | Ullon | 136 | 07:00 | 123 | 15:00
Kishoreganj | 130 | 18:00 | 117 | 23:00 | Uttara | 132 | 06:00 | 124 | 12:00
Kodda | 134 | 00:00 | 120 | 12:00 | UttaraNew | 132 | 05:00 | 124 | 12:00
KSRM | 136 | 19:30 | 130 | 12:00 | Zigatola | 135 | 05:00 | 127 | 13:00
Kulaura | 135 | 18:00 | 128 | 22:00
Kurigram | 128 | 19:00 | 118 | 20:00
Kushtia | 135 | 07:00 | 126 | 23:00
Lakshmipur | 122 | 18:30 | 110 | 01:00
Lalbag | 135 | 05:00 | 128 | 12:00
Lalmonirhat | 128 | 18:00 | 120 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division