## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 07-07-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-07-2025 | during | 07-07-2025 | during | 07-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 404 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 370 | 420 | 450 | 450 | 450 | 450 | Allocation limit by Titas, instructed by DS(Gen)
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 304 | 313 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 253 | 331 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 29 | 48.24 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 62 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 27.5 | 28 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 125 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 95 | 95 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 70 | 105 | 105 | 70 | 90 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 16 | 68 | 104 | 104 | 68 | 68 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 153 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 16 | 0 | 29 | 0 | 29 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 500 | 480 | 584 | 584 | 526 | 526 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage instructed by DS(Gen)
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 0 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2134.5 | 2724.24 | 5123.4 | 5188.4 | 3424.58 | 3509.58
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 1 | 0 | 1 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 172 | 172 | 167 | 167 | 167 | 167 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 220 | 213 | 213 | 213 | 213 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 98 | 105 | 105 | 105 | 105 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 48 | 48 | 72 | 48 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 65 | 66 | 66 | 66 | 66 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 36 | 60 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 10 | 34 | 2 | 20 | 2 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3 | 0 | 4.42 | 0 | 4.42 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 150 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 49 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 60 | 93 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1065 | 1142 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 26 | 37 | 41 | 45 | 41 | 45 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 206 | 195 | 575 | 575 | 575 | 575 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1797 | 2382 | 3570.14 | 3610.72 | 3570.14 | 3610.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 205 | 205 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 334 | 347 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 340 | 340 | 340 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 19 | 20 | 46.7 | 46.7 | 20 | 20 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 49 | 52 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 8 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 143 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 29 | 37 | 46 | 46 | 46 | 46 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 136 | 155 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 34 | 40 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20.83 | 20.83 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 38 | 97 | 114 | 114 | 98 | 98 | Engine Problem
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 29 | 113 | 113 | 9 | 28 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 17 | 107 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 28 | 0 | 68 | 0 | 68 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1317 | 1676 | 2464.08 | 2396.08 | 2137.55 | 2088.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-07-2025 | during | 07-07-2025 | during | 07-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 68 | 72 | 157.5 | 157.5 | 90 | 90 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 3 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 55 | 164 | 200 | 200 | 160 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 82 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 47.52 | 0 | 48.8 | 0 | 48.8 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 18 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 35 | 35 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 265.52 | 371 | 599.9 | 549 | 482.4 | 431.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage instructed by DS(Gen)
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 147 | 156 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 75 | 78 | 80 | 80 | 80 | 80 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 170 | 172 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 8 | 8 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 285 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 384 | 389 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 350 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1477 | 1456 | 1517 | 1517 | 1422 | 1422
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 890 | 891 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 253 | 247 | 410 | 410 | 250 | 250 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 70 | 70 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 23.39 | 0 | 60 | 0 | 60 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 462 | 597 | 617.1 | 617.1 | 617 | 617 | U#2 under shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1666.39 | 1805 | 2659.1 | 2599.1 | 2464 | 2404
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 6 | 0 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1050 | 1220 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 112 | 110 | 110 | 110 | 110 | 110 | Partial Shutdown due to maintenance
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 213 | 279 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.17 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1501.17 | 1729 | 2062 | 2061 | 2050 | 2049
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 205 | 208 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 208 | 209 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 405 | 410 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 63 | 98 | 98 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 111 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.51 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1141 | 1025 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 43.53 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 75 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 2081.04 | 2128 | 2970.47 | 2814.87 | 2927.09 | 2771.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 49 | 49 | 48 | 48 | 50 | 50 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 178 | 195 | 200 | 200 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.1 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 95 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 27 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 131 | 0 | 164.61 | 0 | 164.61 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 391.1 | 452 | 697.21 | 496 | 699.21 | 498
System Total |  |  |  |  | 28565.2 | 27084.055 | 12630.72 | 14723.24 | 21663.3 | 21232.17 | 19176.97 | 18784.84
Forecast Scenario (07-07-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14700 |  | 0 |  | 14700
|  |  |  | 1:00 | 14420 |  | 0 |  | 14420
|  |  |  | 2:00 | 13910 |  | 0 |  | 13910
|  |  |  | 3:00 | 13600 |  | 0 |  | 13600
|  |  |  | 4:00 | 13290 |  | 0 |  | 13290
|  |  |  | 5:00 | 12950 |  | 0 |  | 12950
|  |  |  | 6:00 | 12050 |  | 0 |  | 12050
|  |  |  | 7:00 | 11770 |  | 0 |  | 11770
|  |  |  | 8:00 | 11800 |  | 0 |  | 11800
|  |  |  | 9:00 | 11910 |  | 0 |  | 11910
|  |  |  | 10:00 | 12070 |  | 0 |  | 12070
|  |  |  | 11:00 | 12340 |  | 0 |  | 12340
|  |  |  | 12:00 | 12860 |  | 0 |  | 12860
|  |  |  | 13:00 | 13310 |  | 0 |  | 13310
|  |  |  | 14:00 | 13370 |  | 0 |  | 13370
|  |  |  | 15:00 | 13360 |  | 0 |  | 13360
|  |  |  | 16:00 | 13240 |  | 0 |  | 13240
|  |  |  | 17:00 | 12850 |  | 0 |  | 12850
|  |  |  | 18:00 | 12310 |  | 0 |  | 12310
|  |  |  | 18:30 | 13000 |  | 0 |  | 13000
|  |  |  | 19:00 | 13770 |  | 0 |  | 13770
|  |  |  | 19:30 | 14690 |  | 0 |  | 14690
|  |  |  | 20:00 | 14590 |  | 0 |  | 14590
|  |  |  | 21:00 | 14590 |  | 0 |  | 14590
|  |  |  | 22:00 | 14560 |  | 0 |  | 14560
|  |  |  | 23:00 | 14460 |  | 0 |  | 14460
Probable Maximum Temperature: |  |  | 30.00°C
Probable Maximum Demand at Day Peak: |  |  | 12860.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14690.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14690.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 316.79254 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:16 hrs on 07-07-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 06-07-2025 | [28 empty] | Date: | 06-07-2025 | [28 empty] | Date: | 06-07-2025 | [28 empty] | Date: | 06-07-2025 | [28 empty] | Date: | 06-07-2025 | [12 empty] | Date: | 06-07-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [12 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 54 | 35 | 68 | 64 | 14 | 15 | 37 | 159 | 65 | 420 | 303 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 108 | 23 | 21 | 0 | 450 | 17 | 15 | 0 | 0 | 21 | 65 | 55 | 17 | 85 | 100 | 0 | 172 | 15 | 34 | 204 | 17 | 0 | 19 | 8 | 102 | 220 | 0 | 0 | 0 | 1145 | 0 | 51 | 143 | 8 | 0 | 351 | 340 | 20 | 215 | 20 | 46 | 0 | 194 | 10 | 20 | 96 | 40 | 16 | 0 | 30 | 290 | 320 | 388 | 0 | 0 | 142 | 0 | 0 | 78 | 30 | 0 | 18 | 172 | 35 | 92 | 163 | 72 | 0 | 0 | 12 | 8366 | 891 | 241 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 608 | 17 | 1276.96 | 0 | 49 | 0 | 50 | 0 | 90 | 35 | 35 | 0 | 0 | 28 | 0 | 0 | 0 | 196 | 0 | 197 | 0 | 364 | 0 | 0 | 171 | 49 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 11 | 100 | 220 | 0 | 0 | 1244 | 17 | 6448.96 | 14814.96 | 96.38
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 54 | 35 | 68 | 80 | 12 | 0 | 37 | 152 | 67 | 420 | 291 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 0 | 23 | 21 | 0 | 450 | 17 | 15 | 0 | 0 | 28 | 65 | 40 | 17 | 100 | 100 | 0 | 172 | 16 | 34 | 203 | 9 | 0 | 19 | 8 | 94 | 223 | 0 | 0 | 0 | 1140 | 0 | 51 | 143 | 8 | 0 | 354 | 335 | 20 | 216 | 18 | 17 | 0 | 200 | 9 | 20 | 96 | 44 | 16 | 0 | 30 | 280 | 320 | 360 | 0 | 0 | 136 | 8 | 0 | 79 | 30 | 0 | 18 | 172 | 35 | 92 | 163 | 72 | 0 | 0 | 8 | 8159 | 890 | 242 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 584 | 17 | 1286.04 | 0 | 49 | 0 | 50 | 0 | 90 | 35 | 36 | 0 | 0 | 28 | 0 | 0 | 0 | 195 | 0 | 197 | 0 | 338 | 0 | 0 | 171 | 48 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 11 | 96 | 111 | 0 | 0 | 1120 | 17 | 6166.04 | 14325.04 | 96.37
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 54 | 35 | 56 | 48 | 0 | 0 | 17 | 142 | 42 | 420 | 289 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 22 | 21 | 0 | 450 | 15 | 15 | 0 | 0 | 14 | 16 | 40 | 0 | 89 | 100 | 0 | 172 | 15 | 34 | 204 | 0 | 0 | 19 | 0 | 95 | 221 | 0 | 0 | 0 | 1138 | 0 | 51 | 142 | 8 | 0 | 355 | 340 | 23 | 216 | 18 | 17 | 0 | 200 | 9 | 20 | 96 | 42 | 16 | 0 | 30 | 285 | 320 | 358 | 0 | 0 | 131 | 8 | 0 | 76 | 30 | 0 | 18 | 172 | 35 | 92 | 163 | 72 | 0 | 0 | 12 | 7919 | 891 | 245 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 578 | 17 | 1259.86 | 0 | 49 | 0 | 50 | 0 | 90 | 0 | 30 | 0 | 0 | 28 | 0 | 0 | 0 | 196 | 0 | 197 | 0 | 328 | 0 | 0 | 170 | 48 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 10 | 96 | 111 | 0 | 0 | 1104 | 16 | 6048.86 | 13967.86 | 96.36
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 48 | 35 | 32 | 16 | 0 | 0 | 0 | 108 | 16 | 420 | 291 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 22 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 70 | 100 | 0 | 172 | 0 | 35 | 205 | 0 | 0 | 0 | 0 | 17 | 221 | 0 | 0 | 0 | 1145 | 0 | 51 | 120 | 8 | 0 | 355 | 340 | 34 | 215 | 18 | 17 | 0 | 200 | 9 | 20 | 96 | 42 | 16 | 0 | 30 | 290 | 320 | 358 | 0 | 0 | 145 | 8 | 0 | 76 | 30 | 0 | 18 | 172 | 35 | 93 | 163 | 72 | 0 | 0 | 12 | 7576 | 890 | 249 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 579 | 0 | 1263.99 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 198 | 0 | 398 | 0 | 0 | 168 | 48 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 10 | 120 | 111 | 0 | 0 | 1100 | 16 | 5919.99 | 13495.99 | 96.35
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 27 | 35 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 290 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 22 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 36 | 45 | 0 | 172 | 0 | 35 | 205 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1132 | 0 | 51 | 50 | 25 | 0 | 353 | 340 | 51 | 216 | 18 | 17 | 0 | 200 | 9 | 20 | 96 | 40 | 0 | 0 | 30 | 285 | 320 | 377 | 0 | 0 | 156 | 8 | 0 | 76 | 30 | 0 | 18 | 172 | 35 | 94 | 163 | 72 | 0 | 0 | 12 | 7237 | 890 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 585 | 0 | 1266.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 206 | 0 | 402 | 0 | 0 | 169 | 48 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 9 | 120 | 111 | 0 | 0 | 1108 | 0 | 5865.58 | 13102.58 | 96.34
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 35 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 287 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 22 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 36 | 36 | 0 | 172 | 0 | 37 | 205 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1016 | 0 | 51 | 50 | 26 | 0 | 354 | 335 | 52 | 217 | 18 | 17 | 0 | 155 | 9 | 20 | 96 | 40 | 0 | 0 | 30 | 285 | 320 | 347 | 0 | 0 | 152 | 8 | 0 | 76 | 30 | 0 | 18 | 172 | 35 | 45 | 153 | 72 | 0 | 0 | 12 | 6983 | 890 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 578 | 0 | 1257.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 206 | 0 | 382 | 0 | 0 | 170 | 48 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 267 | 9 | 120 | 111 | 0 | 0 | 1095 | 0 | 5806.65 | 12789.65 | 96.33
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 35 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 291 | 0 | 0 | 0 | 335 | 0 | 0 | 4 | 0 | 21 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 36 | 24 | 0 | 172 | 0 | 38 | 201 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 946 | 0 | 51 | 20 | 26 | 0 | 354 | 340 | 53 | 195 | 16 | 17 | 0 | 155 | 9 | 20 | 52 | 38 | 0 | 5 | 29 | 290 | 320 | 365 | 0 | 0 | 152 | 8 | 0 | 76 | 30 | 0 | 18 | 172 | 35 | 45 | 110 | 88 | 0 | 1.5 | 12 | 6767.5 | 891 | 254 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 526 | 0 | 1080.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 2.5 | 0 | 0 | 204 | 0 | 206 | 0 | 398 | 0 | 0.2 | 172 | 48 | 70 | 1 | 113 | 0 | 0 | 0 | 6 | 0.02 | 0 | 173 | 8 | 120 | 110 | 0 | 0 | 1050 | 0 | 5477.71 | 12245.21 | 96.32
07:00 | 0 | 17 | 10 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 17 | 35 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 293 | 0 | 0 | 0 | 335 | 0 | 0 | 5 | 0 | 21 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 36 | 24 | 0 | 172 | 0 | 36 | 204 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 901 | 1 | 51 | 20 | 26 | 0 | 353 | 340 | 53 | 188 | 16 | 17 | 0 | 120 | 9 | 20 | 52 | 36 | 0 | 17 | 29 | 290 | 320 | 370 | 0 | 0 | 156 | 8 | 0 | 78 | 30 | 0 | 18 | 172 | 35 | 45 | 110 | 88 | 1 | 6.82 | 12 | 6714.82 | 890 | 253 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 24 | 430 | 0 | 952.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 9.77 | 0 | 0 | 204 | 0 | 206 | 0 | 403 | 0 | 0.65 | 168 | 48 | 70 | 4 | 113 | 0 | 0 | 2 | 36 | 0.06 | 0 | 171 | 7 | 120 | 111 | 0 | 0 | 997 | 0 | 5271.04 | 11985.86 | 96.31
08:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 17 | 35 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 309 | 0 | 0 | 0 | 332 | 0 | 0 | 9 | 0 | 26 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 2 | 172 | 0 | 10 | 205 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 842 | 1 | 51 | 10 | 8 | 0 | 344 | 340 | 52 | 184 | 20 | 17 | 0 | 100 | 9 | 20 | 32 | 34 | 0 | 21 | 29 | 285 | 320 | 390 | 0 | 0 | 153 | 8 | 0 | 78 | 30 | 0 | 18 | 172 | 35 | 45 | 75 | 83 | 1 | 22.81 | 12 | 6513.81 | 890 | 258 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4 | 403 | 0 | 945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 13.26 | 0 | 0 | 208 | 0 | 212 | 0 | 411 | 0 | 1.48 | 170 | 50 | 52 | 15 | 70 | 0 | 0 | 1.5 | 60 | 0.21 | 0 | 176 | 6 | 126 | 111 | 0 | 0 | 970 | 0 | 5204.45 | 11718.26 | 96.3
09:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 35 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 293 | 0 | 0 | 0 | 335 | 0 | 0 | 12 | 0 | 27 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 10 | 0 | 1 | 172 | 0 | 12 | 203 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 898 | 0 | 51 | 0 | 8 | 0 | 349 | 340 | 51 | 197 | 20 | 16 | 0 | 100 | 9 | 20 | 32 | 30 | 0 | 30 | 29 | 290 | 320 | 363 | 0 | 0 | 154 | 8 | 0 | 77 | 30 | 0 | 18 | 171 | 35 | 45 | 75 | 83 | 2 | 37.52 | 12 | 6676.52 | 890 | 258 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7 | 440 | 0 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 16.4 | 0 | 0 | 209 | 0 | 212 | 0 | 402 | 0 | 1.35 | 168 | 50 | 52 | 21 | 70 | 0 | 0 | 2.2 | 70 | 0.08 | 0 | 202 | 6 | 120 | 112 | 0 | 0 | 990 | 0 | 5268.03 | 11944.55 | 96.29
10:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 17 | 35 | 95 | 0 | 0 | 0 | 0 | 0 | 12 | 370 | 284 | 0 | 0 | 0 | 319 | 0 | 0 | 21 | 0 | 27.5 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 24 | 36 | 2 | 172 | 0 | 3 | 205 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 8 | 0 | 349 | 340 | 51 | 197 | 20 | 17 | 0 | 96 | 9 | 20 | 32 | 30 | 0 | 14 | 29 | 285 | 320 | 330 | 0 | 0 | 149 | 8 | 0 | 76 | 30 | 0 | 18 | 171 | 35 | 45 | 75 | 68 | 0 | 48.54 | 12 | 6600.04 | 890 | 258 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 45 | 432 | 0 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 41.91 | 0 | 0 | 209 | 0 | 212 | 0 | 335 | 0 | 2.35 | 207 | 50 | 35 | 36 | 0 | 0 | 0 | 2 | 181 | 0.13 | 0 | 191 | 5 | 120 | 112 | 0 | 0 | 980 | 0 | 5359.39 | 11959.43 | 96.28
11:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 35 | 95 | 0 | 0 | 0 | 4 | 12 | 16 | 370 | 301 | 0 | 0 | 0 | 280 | 0 | 0 | 21 | 0 | 26.5 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 24 | 36 | 1 | 172 | 0 | 5 | 203 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 958 | 0 | 51 | 0 | 8 | 0 | 336 | 340 | 50 | 212 | 20 | 17 | 0 | 131 | 8 | 17 | 34 | 32 | 0 | 38 | 29 | 295 | 320 | 335 | 0 | 0 | 144 | 8 | 0 | 74 | 30 | 0 | 18 | 170 | 35 | 45 | 55 | 68 | 0 | 39.62 | 12 | 6714.12 | 891 | 258 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 11 | 468 | 0 | 1024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 36.83 | 0 | 0 | 207 | 0 | 210 | 0 | 409 | 0 | 3.6 | 181 | 50 | 0 | 10 | 0 | 0 | 0 | 4 | 141 | 0.11 | 0 | 203 | 6 | 120 | 112 | 0 | 0 | 1000 | 0 | 5452.54 | 12166.66 | 96.27
12:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 29 | 35 | 95 | 0 | 0 | 0 | 17 | 17 | 16 | 370 | 304 | 0 | 0 | 0 | 253 | 0 | 0 | 16 | 0 | 27.5 | 21 | 0 | 500 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 36 | 60 | 3 | 172 | 0 | 10 | 206 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1065 | 0 | 51 | 0 | 8 | 0 | 334 | 340 | 49 | 205 | 19 | 17 | 0 | 136 | 9 | 20 | 38 | 34 | 0 | 28 | 29 | 295 | 350 | 384 | 0 | 0 | 147 | 8 | 0 | 75 | 30 | 0 | 18 | 170 | 35 | 45 | 55 | 68 | 3 | 47.52 | 12 | 6991.02 | 890 | 253 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 23.39 | 462 | 0 | 1141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 43.53 | 0 | 0 | 205 | 0 | 208 | 0 | 405 | 0 | 3.51 | 178 | 49 | 0 | 27 | 0 | 0 | 0 | 6.1 | 131 | 0.17 | 0 | 213 | 6 | 120 | 112 | 0 | 0 | 1050 | 0 | 5639.7 | 12630.72 | 96.26
13:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 35 | 95 | 0 | 0 | 0 | 17 | 37 | 16 | 420 | 286 | 0 | 0 | 0 | 240 | 0 | 0 | 36 | 0 | 27.5 | 21 | 0 | 520 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 90 | 74 | 1 | 172 | 0 | 13 | 204 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1105 | 1 | 51 | 18 | 8 | 0 | 347 | 340 | 48 | 200 | 19 | 17 | 0 | 143 | 9 | 20 | 59 | 38 | 0 | 8 | 28 | 290 | 320 | 338 | 0 | 0 | 154 | 8 | 0 | 74 | 30 | 0 | 18 | 170 | 35 | 65 | 75 | 67 | 2 | 44.62 | 12 | 7174.12 | 890 | 253 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 42.44 | 568 | 0 | 1200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 47.25 | 0 | 0 | 205 | 0 | 207 | 0 | 344 | 0 | 4.98 | 182 | 49 | 68 | 31 | 30 | 0 | 0 | 6.6 | 202 | 0.25 | 0 | 259 | 6 | 120 | 112 | 0 | 0 | 1070 | 0 | 6000.52 | 13174.64 | 96.25
14:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 35 | 91 | 0 | 0 | 0 | 17 | 88 | 16 | 420 | 300 | 0 | 0 | 0 | 220 | 0 | 0 | 17 | 0 | 22.5 | 14 | 0 | 470 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 100 | 88 | 3 | 172 | 0 | 13 | 203 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1145 | 1 | 51 | 24 | 8 | 0 | 300 | 340 | 48 | 210 | 19 | 17 | 0 | 145 | 9 | 20 | 62 | 38 | 0 | 32 | 28 | 285 | 320 | 316 | 0 | 0 | 154 | 8 | 0 | 74 | 30 | 0 | 16 | 171 | 35 | 74 | 103 | 69 | 2 | 43.97 | 12 | 7224.47 | 890 | 248 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 30 | 585 | 0 | 1151.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 21.67 | 0 | 0 | 205 | 0 | 206 | 0 | 348 | 0 | 5.25 | 178 | 50 | 70 | 33 | 34 | 0 | 0 | 4.4 | 201 | 0.29 | 0 | 274 | 6 | 120 | 112 | 0 | 0 | 1070 | 0 | 5956.3 | 13180.77 | 96.24
15:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 35 | 62 | 0 | 0 | 0 | 17 | 83 | 32 | 420 | 301 | 0 | 0 | 0 | 327 | 0 | 0 | 3 | 0 | 27.9 | 21 | 0 | 470 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 24 | 70 | 0 | 172 | 0 | 4 | 203 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1149 | 1 | 51 | 0 | 8 | 0 | 300 | 335 | 48 | 210 | 19 | 17 | 0 | 145 | 9 | 20 | 62 | 32 | 0 | 30 | 28 | 300 | 320 | 335 | 0 | 0 | 154 | 8 | 0 | 73 | 30 | 0 | 16 | 171 | 35 | 74 | 96 | 68 | 2 | 49.91 | 14 | 7222.81 | 891 | 245 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 10 | 592 | 0 | 1172.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 33.53 | 0 | 0 | 204 | 0 | 205 | 0 | 362 | 0 | 2.16 | 198 | 49 | 70 | 15 | 34 | 0 | 0 | 0.9 | 132 | 0.43 | 0 | 278 | 6 | 120 | 110 | 0 | 0 | 1070 | 0 | 5881.32 | 13104.13 | 96.23
16:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 31 | 35 | 60 | 0 | 0 | 0 | 17 | 82 | 32 | 420 | 299 | 0 | 0 | 0 | 330 | 0 | 0 | 14 | 0 | 27.9 | 21 | 0 | 470 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 24 | 24 | 1 | 172 | 0 | 4 | 204 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1146 | 2 | 51 | 0 | 8 | 0 | 300 | 335 | 48 | 212 | 17 | 17 | 0 | 145 | 8 | 20 | 49 | 32 | 0 | 9 | 28 | 295 | 320 | 323 | 0 | 0 | 154 | 5 | 0 | 75 | 30 | 0 | 16 | 171 | 35 | 65 | 103 | 70 | 1 | 21.84 | 14 | 7093.74 | 891 | 248 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 29 | 578 | 0 | 1011.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 23.97 | 0 | 0 | 204 | 0 | 205 | 0 | 346 | 0 | 2.02 | 202 | 49 | 70 | 12 | 34 | 0 | 0 | 4.8 | 135 | 0.16 | 0 | 272 | 6 | 120 | 110 | 0 | 0 | 1070 | 0 | 5677.84 | 12771.58 | 96.22
17:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 21 | 35 | 60 | 0 | 0 | 0 | 17 | 49 | 32 | 420 | 302 | 0 | 0 | 0 | 330 | 0 | 0 | 11 | 0 | 27.5 | 21 | 0 | 470 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 0 | 12 | 12 | 0 | 172 | 0 | 4 | 203 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1066 | 0 | 51 | 0 | 8 | 0 | 300 | 340 | 50 | 213 | 18 | 25 | 0 | 136 | 9 | 20 | 60 | 32 | 3 | 2 | 34 | 290 | 320 | 318 | 0 | 0 | 153 | 0 | 0 | 76 | 30 | 0 | 16 | 167 | 35 | 55 | 103 | 70 | 0 | 6.68 | 12 | 6923.18 | 891 | 248 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 17.72 | 560 | 0 | 1009.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 5.85 | 0 | 0 | 204 | 0 | 206 | 0 | 353 | 0 | 0.53 | 137 | 48 | 50 | 2 | 34 | 0 | 0 | 3 | 29 | 0.01 | 0 | 223 | 5 | 120 | 110 | 0 | 0 | 1150 | 0 | 5458.16 | 12381.34 | 96.21
18:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 35 | 60 | 16 | 30 | 0 | 17 | 49 | 32 | 370 | 308 | 0 | 0 | 0 | 328 | 0 | 0 | 3 | 0 | 27.5 | 21 | 0 | 400 | 0 | 20 | 0 | 0 | 27 | 15 | 0 | 0 | 12 | 12 | 0 | 172 | 1 | 10 | 200 | 0 | 0 | 0 | 0 | 5 | 218 | 0 | 0 | 0 | 1020 | 0 | 51 | 4 | 8 | 0 | 300 | 280 | 41 | 212 | 20 | 34 | 0 | 114 | 19 | 20 | 70 | 32 | 8 | 1 | 34 | 295 | 320 | 351 | 0 | 0 | 147 | 8 | 0 | 54 | 30 | 0 | 16 | 167 | 35 | 55 | 114 | 71 | 0 | 0.58 | 12 | 6800.08 | 890 | 248 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4 | 519 | 0 | 930.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.11 | 0 | 0 | 170 | 0 | 170 | 0 | 394 | 0 | 0.24 | 198 | 49 | 50 | 3 | 70 | 0 | 0 | 1.1 | 27 | 0.01 | 0 | 176 | 4 | 120 | 110 | 0 | 0 | 1120 | 0 | 5294.54 | 12094.62 | 96.2
19:00 | 0 | 51 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 19.08 | 35 | 68 | 36 | 120 | 0 | 19 | 66 | 62 | 370 | 309 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 27 | 21 | 0 | 480 | 0 | 65 | 0 | 0 | 22 | 65 | 32 | 0 | 60 | 88 | 0 | 172 | 16 | 10 | 195 | 0 | 0 | 23 | 0 | 39 | 219 | 0 | 0 | 0 | 1162 | 0 | 51 | 50 | 8 | 0 | 300 | 280 | 26 | 208 | 20 | 47 | 0 | 125 | 28 | 20 | 70 | 40 | 16 | 0 | 34 | 295 | 320 | 385 | 0 | 0 | 143 | 8 | 0 | 51 | 30 | 0 | 16 | 170 | 35 | 55 | 125 | 72 | 0 | 0.15 | 16 | 7642.23 | 891 | 247 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 480 | 7 | 1027.11 | 0 | 0 | 0 | 8 | 0 | 60 | 5 | 10 | 0 | 0 | 20 | 0 | 0 | 0 | 190 | 0 | 191 | 0 | 398 | 0 | 0 | 200 | 50 | 81 | 0 | 90 | 0 | 0 | 0 | 1 | 0 | 0 | 244 | 7 | 120 | 110 | 0 | 0 | 1105 | 0 | 5595.11 | 13237.34 | 96.19
19:30 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 50 | 35 | 95 | 62 | 125 | 0 | 55 | 155 | 68 | 420 | 305 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 28 | 21 | 0 | 480 | 0 | 150 | 0 | 0 | 27 | 65 | 33 | 0 | 60 | 90 | 0 | 172 | 25 | 25 | 195 | 0 | 0 | 40 | 0 | 92 | 219 | 0 | 0 | 0 | 1160 | 0 | 51 | 125 | 8 | 0 | 348 | 340 | 26 | 203 | 20 | 91 | 0 | 168 | 28 | 20 | 97 | 38 | 25 | 0 | 34 | 290 | 320 | 388 | 0 | 0 | 156 | 8 | 0 | 78 | 30 | 0 | 16 | 170 | 35 | 82 | 151 | 72 | 0 | 0 | 18 | 8507 | 891 | 251 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 550 | 17 | 1022.56 | 0 | 0 | 0 | 103 | 0 | 63 | 35 | 25 | 0 | 0 | 30 | 0 | 0 | 0 | 203 | 0 | 208 | 0 | 414 | 0 | 0 | 200 | 50 | 93 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 0 | 120 | 110 | 0 | 0 | 1170 | 0 | 6000.56 | 14507.56 | 96.19
20:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 50.04 | 35 | 95 | 62 | 125 | 0 | 55 | 155 | 68 | 420 | 303 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 24 | 21 | 0 | 480 | 0 | 150 | 0 | 0 | 32 | 65 | 36 | 0 | 60 | 91 | 0 | 172 | 38 | 28 | 194 | 0 | 0 | 39 | 0 | 100 | 220 | 0 | 0 | 0 | 1160 | 0 | 51 | 123 | 8 | 0 | 349 | 340 | 42 | 200 | 20 | 80 | 0 | 160 | 28 | 20 | 97 | 38 | 25 | 0 | 34 | 290 | 320 | 389 | 0 | 0 | 158 | 8 | 0 | 78 | 30 | 0 | 18 | 171 | 35 | 82 | 151 | 72 | 0 | 0 | 18 | 8534.04 | 891 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 588 | 17 | 1048.41 | 0 | 0 | 0 | 80 | 0 | 63 | 35 | 37 | 0 | 0 | 30 | 0 | 0 | 0 | 205 | 0 | 206 | 0 | 409 | 0 | 0 | 200 | 50 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 120 | 110 | 0 | 0 | 1185 | 0 | 6065.41 | 14599.45 | 96.18
21:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 48.24 | 35 | 95 | 62 | 125 | 0 | 55 | 153 | 68 | 420 | 313 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 28 | 21 | 0 | 480 | 0 | 150 | 0 | 0 | 37 | 65 | 48 | 0 | 60 | 93 | 0 | 172 | 49 | 34 | 195 | 0 | 0 | 19 | 0 | 98 | 220 | 0 | 0 | 0 | 1142 | 0 | 51 | 143 | 8 | 0 | 347 | 340 | 52 | 205 | 20 | 107 | 0 | 155 | 29 | 20 | 97 | 40 | 25 | 0 | 37 | 285 | 320 | 389 | 0 | 0 | 156 | 8 | 0 | 78 | 30 | 0 | 18 | 172 | 35 | 82 | 164 | 72 | 0 | 0 | 18 | 8609.24 | 891 | 247 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 597 | 17 | 1025 | 0 | 0 | 0 | 111 | 0 | 63 | 35 | 37 | 0 | 0 | 30 | 0 | 0 | 0 | 208 | 0 | 209 | 0 | 410 | 0 | 0 | 195 | 49 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 0 | 120 | 110 | 0 | 0 | 1220 | 0 | 6114 | 14723.24 | 96.17
22:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 48.24 | 35 | 95 | 62 | 125 | 0 | 55 | 154 | 68 | 420 | 306 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 28 | 21 | 0 | 480 | 0 | 150 | 0 | 0 | 36 | 65 | 55 | 0 | 60 | 96 | 0 | 172 | 49 | 37 | 197 | 0 | 0 | 19 | 0 | 97 | 220 | 0 | 0 | 0 | 1148 | 0 | 51 | 143 | 8 | 0 | 352 | 340 | 52 | 200 | 20 | 115 | 0 | 169 | 29 | 20 | 97 | 44 | 25 | 0 | 37 | 290 | 320 | 388 | 0 | 0 | 157 | 8 | 0 | 78 | 30 | 0 | 16 | 172 | 35 | 94 | 153 | 72 | 0 | 0 | 18 | 8655.24 | 891 | 248 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 585 | 17 | 1025.69 | 0 | 0 | 0 | 113 | 0 | 63 | 35 | 35 | 0 | 0 | 30 | 0 | 0 | 0 | 205 | 0 | 207 | 0 | 414 | 0 | 0 | 199 | 49 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 0 | 120 | 110 | 0 | 0 | 1244 | 0 | 6130.69 | 14785.93 | 96.16
23:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 47.16 | 35 | 86 | 62 | 45 | 0 | 55 | 148 | 68 | 420 | 309 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 28 | 21 | 0 | 440 | 0 | 150 | 0 | 0 | 26 | 65 | 55 | 0 | 72 | 98 | 0 | 172 | 48 | 30 | 196 | 0 | 0 | 19 | 0 | 100 | 220 | 0 | 0 | 0 | 1155 | 0 | 51 | 50 | 8 | 0 | 349 | 340 | 52 | 207 | 20 | 106 | 0 | 162 | 29 | 20 | 97 | 48 | 25 | 0 | 37 | 285 | 320 | 345 | 0 | 0 | 148 | 8 | 0 | 78 | 30 | 0 | 16 | 172 | 35 | 94 | 153 | 72 | 0 | 0 | 12 | 8362.16 | 891 | 245 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 594 | 17 | 1215.97 | 0 | 0 | 0 | 113 | 0 | 63 | 35 | 35 | 0 | 0 | 30 | 0 | 0 | 0 | 176 | 0 | 180 | 0 | 388 | 0 | 0 | 203 | 49 | 95 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 120 | 110 | 0 | 0 | 1244 | 0 | 6246.97 | 14609.13 | 96.15
Total KWH | 0 | 723840 | 344640 | 0 | 0 | 0 | 0 | 0 | 9853200 | 0 | 0 | 778320 | 864000 | 1575936 | 514560 | 617738 | 14729 | 490886 | 1730880 | 722880 | 9772500 | 7226851 | 0 | 0 | 73960 | 7708767 | 0 | 0 | 155090 | 48000 | 601200 | 513000 | 0 | 10997272.73 | 35127 | 800400 | 0 | 0 | 585600 | 482889 | 344928 | 23937 | 1198080 | 1464960 | 13848 | 4151200 | 294400 | 533280 | 4894545.45 | 11709 | 0 | 203520 | 11143.8 | 809600 | 5233730 | 0 | 0 | 0 | 25750906 | 8775 | 1196409 | 1368290 | 284364 | 0 | 8474300 | 8132000 | 1099680 | 5006000 | 464760 | 836160 | 0 | 3639840 | 330960 | 460220 | 1663260 | 907200 | 213610 | 215782 | 745792 | 6986500 | 7687700 | 9006000 | 0 | 0 | 3609327 | 165096 | 0 | 1795200 | 718752 | 0 | 422000 | 4529690 | 856080 | 1633200 | 2851200 | 1688640 | 11000 | 313000 | 321360 | 179814199.98 | 21563636 | 6052320 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 111888 | 242640 | 12945450 | 137280 | 26505812 | 0 | 110581 | 0 | 715392 | 0 | 574176 | 218592 | 226430 | 0 | 468690 | 206529 | 285000 | 0 | 0 | 5033200 | 0 | 5108609 | 0 | 9250181 | 0 | 26160 | 4412000 | 1124072 | 1767197 | 201942 | 1824480 | 0 | 0 | 40945.44 | 1159200 | 1750 | 0 | 5913000 | 148726 | 2814000 | 2712990 | 0 | 0 | 26772363.64 | 51600 | 139638832.08 | 319453032.06

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 06-07-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12630.72 | MW | 12:00 Hr. | Energy Generated |  |  | 319.453 |  | MKWHr.
| Day Peak Demand |  |  | 12640.72 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.106 |  | MKWHr.
| Evening Peak Generation |  |  | 14723.24 | MW | 21:00 Hr. | Energy Demand |  |  | 320.559 |  | MKWHr.
| Evening Peak Demand |  |  | 14810.24 | MW | 21:00 Hr. | Maximum Temperature |  |  | 31.6 |  | °C
| Minimum Generation of the Day |  |  | 11718.26 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 1012.96 |  | MMCFD
| Maximum Generation of the Day |  |  | 14814.96 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.297 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 46.6728 | 0 | 8.5004 | 0 | 0 | 0.15509 | 0 | 0 | 55.3282 | Gas | 145.2865 | Gas | 515182373.3641
| Chattogram Zone |  |  | 5.767 | 30.6455 | 5.6807 | 0 | 4.1512 | 0.022623 | 0 | 0.5856 | 46.8526 | Coal | 81.8123 | Coal | 552890453.847
| Cumilla Zone |  |  | 25.1177 | 0 | 8.7979 | 0 | 0 | 0.21578 | 0.9072 | 0 | 35.0386 | HFO | 34.585 | HFO | 641690033.166
| Mymensingh Zone |  |  | 1.6886 | 0 | 5.6618 | 0 | 0 | 0.324 | 0 | 0 | 7.6745 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 34.9203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.9203 | Hydro | 4.1512 | Hydro | 415120
| Khulna Zone |  |  | 6.0523 | 12.9454 | 0.24917 | 0 | 0 | 0.24264 | 22.4756 | 0 | 41.9652 | Solar | 3.1438 | Solar | 52740091.9384
| Barishal Zone |  |  | 5.6757 | 32.6854 | 0.0516 | 0 | 0 | 0.00175 | 0 | 0 | 38.4144 | Import | 49.8886 | Import | 240116235.72
| Rajshahi Zone |  |  | 19.392 | 0 | 2.0517 | 0 | 0 | 0.77985 | 26.5058 | 0 | 48.7294 | Wind | 0.5856 | Wind | 8573184
| Rangpur Zone |  |  | 0 | 5.5361 | 3.5917 | 0 | 0 | 1.4021 | 0 | 0 | 10.5298
| Total |  |  | 145.2865 | 81.8123 | 34.585 | 0 | 4.1512 | 3.1438 | 49.8886 | 0.5856 | 319.453
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 515182373.3641 |  | Hydro | 415120
|  |  |  | Coal | 552890453.847 |  | Solar | 52740091.9384
|  |  |  | HFO | 641690033.166 |  | Import | 240116235.72
|  |  |  | HSD | 0 |  | Wind | 8573184
[5 empty] | Total: | 201,16,07,492 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5636 | Peak Hr Flow | 891.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 31910272.82 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.5058 | Peak Hr Flow | 1025.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 740 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.9072 | Peak Hr Flow | 40.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 974 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 48.9766 | Peak Hr Flow | 1956.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5017
|  |  |  | Chattogram |  | 0 |  | 1256
|  |  |  | Cumilla |  | 0 |  | 1367
|  |  |  | Mymensingh |  | 50 |  | 1230
|  |  |  | Sylhet |  | 0 |  | 662
|  |  |  | Khulna |  | 0 |  | 1738
|  |  |  | Barishal |  | 0 |  | 418
|  |  |  | Rajshahi |  | 0 |  | 1557
|  |  |  | Rangpur |  | 33 |  | 1076
|  |  |  | Total |  | 83 |  | 14321
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[5 empty] | Total | 300 |  |  |  | Total | 476
|  |  |  | Total Unavailable Capacity |  |  |  | 776
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:20 | 08:35 | Shahjibazar 132/33kV S/S TR-02 HT Tripped showing SRT in Micom relay, lockout relay
relays Due to N/A
| 08:20 | 08:47 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing lockout relay relays Due to N/A
| 09:29 | 14:33 | Madunaghat-TKCL 132kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end.
| 09:35 | 14:25 | Madunaghat-Sikalbaha 132kV Ckt-2 Scheduled S/D from Madunaghat 132/33kV end.
| 09:50 | 12:36 | Kodda 132/33kV S/S Tr-3 (426T) LT Scheduled S/D Due to None | [7 empty] | 20.0MW load
interrup.
| 09:51 | 12:34 | Kodda 132/33kV S/S Tr-3 (426T) HT Scheduled S/D Due to Redhot maintenance
| 10:25 | 12:40 | Mirpur 132/33kV S/S Reserve Bus Project Work S/D Due to 132 KV Reserve bus DS of T-3 XFr
installation and alligenment adjustment.
|  | 10:30 | Faridpur 132/33kV S/S Transformer-2 HT is restored.
|  | 10:31 | Faridpur 132/33kV S/S Transformer-2 LT is restored.
| 12:37 | 13:13 | Narshingdi 132/33kV S/S T-4 LT Tripped showing Lockout operated relays Due to 33 kV | [7 empty] | 23.0MW load
|  |  | Shibpur feeder fault | [7 empty] | interrup.
|  | 17:00 | Haripur 230/132kV S/S Bus-1 is restored.
|  | 17:34 | Haripur-Meghnaghat 230kV Ckt-2 is restored.
|  | 17:47 | Haripur-Meghnaghat 230kV Ckt-2 is restored.
|  | 19:19 | Mahasthangar-Palashbari 132kV Ckt-1 is restored.
| 21:00 |  | Peak generation 14723 MW
|  | 21:38 | Rahanpur 400/132kV S/S Rahanpur-Monakasha 400KV Line ckt-02 is restored.
| 22:30 | 00:27 | Chowmuhani 132/33kV S/S TR2 Scheduled S/D Due to TR2 33 KV Side incoming L- Bus incoming | [7 empty] | 40.0MW load
|  |  | Loop Red Hot. | [7 empty] | interrup.
| 22:45 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is ON with remarks:- FGMO Minimum @22:44 by Mr. Fahad
Mahmud, Xen
| 05:46 |  | Bogura-Rahanpur 400kV Ckt-2 Tripped from Rahanpur 400/132kV end showing Protection Relay
relays Due to Connected with Busbar-2
| 05:46 |  | Rahanpur 400/132kV S/S HV 400 KV BUS Tripped showing Bus Protection Relay relays Due to
Bus Zone 2 Trip.Fault Distance 0.3km
| 05:46 |  | Rahanpur 400/132kV S/S AT-02 HT Tripped showing Protection Relay relays Due to Connected
with Busbar-2
| 05:46 |  | Rahanpur 400/132kV S/S Rahanpur-Monakasha 400KV Line ckt-02 Tripped showing Protection
Relay relays Due to Connected with Busbar-2
| 06:00 |  | Minimum Generation: 12090 MW.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 06-07-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 404 | 9853200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9772500 | Allocation limit by Titas, instructed by DS(Gen)
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 313 | 7226851 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 14729 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 331 | 7708767 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 48.24 | 778320 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 62 | 514560 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 490886 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 73960 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 28 | 601200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 513000 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 344640 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 125 | 617738 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 95 | 1575936 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 723840 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 68 | 722880 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 153 | 1730880 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 155090 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 864000 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 480 | 10997272.73 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage instructed by DS(Gen)
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 0 | 48000 | Engine Problem
Dhaka Area Total |  |  |  |  | 5939.724 | 2724.24 | 55328249.73
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 11143.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 8775 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 203520 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 172 | 4151200 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 5233730 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 98 | 809600 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 48 | 344928 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 482889 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 60 | 1198080 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 34 | 533280 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 13848 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 150 | 800400 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 23937 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 49 | 294400 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 93 | 1464960 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 35127 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 11709 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1142 | 25750906 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 37 | 585600 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 195 | 4894545.45 | U2 S/D 06/06/25(NLDC request)
Chattogram Area Total |  |  |  |  | 4895.72 | 2382 | 46852578.25
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 205 | 5006000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 347 | 8474300 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 8132000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 20 | 464760 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 52 | 1099680 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 284364 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1196409 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 143 | 1368290 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 37 | 745792 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 155 | 3639840 | -
| Import (Tripura) |  | Import | 0 | 160 | 40 | 907200 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 25 | 213610 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 460220 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 97 | 1663260 | Engine Problem
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 29 | 330960 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 107 | 836160 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 215782 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1676 | 35038627
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 72 | 1688640 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 164 | 2851200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 82 | 1633200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 313000 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 321360 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 856080 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 371 | 7674480
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | Gas shortage instructed by DS(Gen)
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 156 | 3609327 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 718752 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1795200 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 172 | 4529690 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 422000 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 165096 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 6986500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 389 | 9006000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7687700 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1456 | 34920265
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 891 | 21563636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 247 | 6052320 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 137280 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 111888 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 242640 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 597 | 12945450 | U#2 under shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1805 | 41965214
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 148726 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2814000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1220 | 26772363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 110 | 2712990 | GT-12 Under shutdown for Offline water wash
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 51600 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 279 | 5913000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1750 | -
Barishal Area Total |  |  |  |  | 2236 | 1729 | 38414429.64
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 110581 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 226430 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 208 | 5033200 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 209 | 5108609 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 410 | 9250181 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 206529 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 63 | 574176 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 111 | 715392 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 218592 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 26160 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1025 | 26505812 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 285000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 468690 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2128 | 48729352
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 49 | 1124072 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 195 | 4412000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1824480 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 40945.44 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 1767197 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 201942 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1159200 | -
Rangpur Area Total |  |  |  |  | 950 | 452 | 10529836.44
Eastern Grid Total |  |  |  |  | 16705.895 | 8609.24 | 179814199.98
Western Grid Total |  |  |  |  | 10378.16 | 6114 | 139638832.08
National Grid Total |  |  |  |  | 27084.055 | 14723.24 | 319453032.06
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 06-07-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9482.22 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4756.9 | MW
i) Dhaka area |  |  | 5016.73 |  | MW | i) Khulna area |  |  |  | 1738 | MW
ii) Chattogram area |  |  | 1256 |  | MW | ii) Barishal area |  |  |  | 418.5 | MW
iii) Cumilla area |  |  | 1367.49 |  | MW | iii) Rajshahi area |  |  |  | 1557.4 | MW
iv) Mymensingh area |  |  | 1180 |  | MW | iv) Rangpur area |  |  |  | 1043 | MW
v) Sylhet area |  |  | 662 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14239.12 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 77 | 19:30 | 133 | Pabna | 123 | 21:00
2 | AKSML | 110 | 04:00 | 68 | Ishurdi | 79 | 21:00 | 134 | Palashbari | 120 | 03:00
3 | Aftabnagar | 36 | 19:30 | 69 | Jaldhaka | 93 | 23:00 | 135 | Panchagarh | 67 | 23:00
4 | Agargaon | 113 | 00:00 | 70 | Jamalpur | 135 | 00:00 | 136 | Patuakhali | 74.8 | 00:00
5 | Agrabad | 76 | 19:00 | 71 | Jashore | 136 | 19:30 | 137 | Payra | 30 | 20:00
6 | Amnura | 41 | 22:00 | 72 | Jhenaidah | 123 | 19:30 | 138 | Postogola | 53 | 00:00
7 | Ashuganj | 102 | 00:00 | 73 | Joydebpur | 135 | 19:30 | 139 | Purbachal | 20 | 00:00
8 | BSRM | 195 | 17:00 | 74 | Joypurhat | 68 | 00:00 | 140 | Purbasadipur | 143 | 22:00
9 | Bagerhat | 83 | 20:00 | 75 | Juldah | 15 | 00:00 | 141 | Rahanpur | 34 | 22:00
10 | Bajitpur | 54 | 20:00 | 76 | KSRM | 14 | 10:00 | 142 | Rahim | 9 | 11:00
11 | Bakulia | 78 | 19:30 | 77 | Kabirpur | 210 | 11:00 | 143 | Rajbari | 78 | 22:00
12 | Banani | 26.2 | 13:00 | 78 | Kachua | 88 | 23:00 | 144 | Rajendrapur | 133 | 20:00
13 | Bangabhaban | 4 | 00:00 | 79 | Kallyanpur | 102 | 00:00 | 145 | Rajshahi | 116 | 22:00
14 | Barapukuria | 67 | 21:00 | 80 | Kalurghat | 32 | 11:00 | 146 | Rajshahi-230 | 84 | 13:00
15 | Barguna | 20 | 00:00 | 81 | Kamrangirchar | 62 | 13:00 | 147 | Ramganj | 110 | 00:00
16 | Barishal | 94 | 00:00 | 82 | Kaptai | N/A | N/A | 148 | Rampur | 37 | 00:00
17 | Barishal-230 | 106 | 00:00 | 83 | Kasba | 36 | 21:00 | 149 | Rangamati | 15 | 19:30
18 | Baroaulia | 62 | 13:00 | 84 | Kazla | 91 | 00:00 | 150 | Rangpur | 142 | 00:00
19 | Baroirhat | 62 | 00:00 | 85 | Keranigonj | 90 | 00:00 | 151 | Ruppur | 7.6 | 10:00
20 | Bashundhara | 176 | 19:30 | 86 | Khagrachori | 32 | 19:30 | 152 | SSM | 12 | 10:00
21 | BashundharaCement | 7 | 00:00 | 87 | Khulna | 64 | 23:00 | 153 | Saidpur | 104 | 00:00
22 | Beanibazar | 87 | 21:00 | 88 | Khulshi | 130 | 22:00 | 154 | Satkhira | 122 | 00:00
23 | Benapole | 66 | 22:00 | 89 | Kishoreganj | 151 | 22:00 | 155 | Satmasjid | 90 | 20:00
24 | Bhaluka | 141 | 00:00 | 90 | Kodda | 294 | 19:00 | 156 | Savar | 214 | 15:00
25 | Bhandaria | 54 | 22:00 | 91 | Kulaura | 57 | 00:00 | 157 | SevenRings | 16.25 | 12:00
26 | Bhangura | 36 | 20:00 | 92 | Kurigram | 72 | 20:00 | 158 | ShahCement | 24 | 11:00
27 | Bheramara(GK) | 66 | 21:00 | 93 | Kushtia | 146 | 00:00 | 159 | Shahjadpur | 83 | 21:00
28 | Bhulta | 246 | 00:00 | 94 | Lakshmipur | 25 | 23:00 | 160 | Shahjibazar | 124 | 22:00
29 | Bog-Sherpur | 66 | 19:30 | 95 | Lalbag | 50 | 00:00 | 161 | Shahmirpur | 52.5 | 02:00
30 | Bogura | 173 | 23:00 | 96 | Lalmonirhat | 64 | 00:00 | 162 | Shariatpur | 88 | 00:00
31 | Borhanuddin | 82 | 00:00 | 97 | MI_Cement | 16.4 | 15:00 | 163 | Sherpur | 156 | 00:00
32 | Brahmanbaria | 128 | 19:30 | 98 | Madanganj | 48 | 00:00 | 164 | Shikalbaha | 13 | 10:00
33 | Cantonment | 132 | 19:00 | 99 | Madaripur | 105 | 00:00 | 165 | Shitalakhya | 77.5 | 13:00
34 | Chandina | 19.17 | 23:00 | 100 | Madartek | 87 | 21:00 | 166 | Sholosohor | 39 | 09:00
35 | Chandpur | 78 | 22:00 | 101 | Madunaghat | 51 | 02:00 | 167 | Shyampur | 156 | 13:00
36 | Chandraghona | 35 | 21:00 | 102 | Magura | 65 | 20:00 | 168 | Siddhirganj | 113 | 12:00
37 | Chapai | 73 | 22:00 | 103 | Mahasthangarh | 86 | 22:00 | 169 | Sirajganj | 116 | 21:00
38 | Charsaidpur | 41 | 02:00 | 104 | Maijdee | 15 | 22:00 | 170 | Sonargaon | 99 | 19:00
39 | Chauddagram | 67 | 22:00 | 105 | Manikganj | 124 | 21:00 | 171 | Sreemongol | 79 | 22:00
40 | Chhatak | 44 | 21:00 | 106 | Maniknagar | 68 | 13:00 | 172 | Sreepur | 97 | 21:00
41 | Chowmuhani | 191 | 19:30 | 107 | Matarbari | 44 | 00:00 | 173 | Srinagar | 46.7 | 22:00
42 | Chuadanga | 111 | 21:00 | 108 | Matuail | 64 | 12:00 | 174 | Sunamganj | 65 | 22:00
43 | Coxsbazar | 121 | 19:30 | 109 | Millgate | 107 | 15:00 | 175 | Sylhet | 53 | 19:30
44 | Cumilla(N) | 149 | 00:00 | 110 | Mirpur | 117.5 | 19:30 | 176 | Sylhet-132 | 131 | 19:00
45 | Cumilla(S) | 166 | 23:00 | 111 | Mirsorai | 9 | 10:00 | 177 | TK | 36 | 15:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirzapur | 44 | 21:00 | 178 | Tangail | 186 | 22:00
47 | Daudkandi | 149 | 22:00 | 113 | Mithapukur | 74 | 19:30 | 179 | Taraganj | 23 | 00:00
48 | Dhaka | 44 | 13:00 | 114 | Modern | N/A | N/A | 180 | Thakurgaon | 115 | 21:00
49 | Dhamrai | 118 | 21:00 | 115 | Mogbazar | 119.1 | 19:00 | 181 | Tongi | 127 | 00:00
50 | Dhanmondi | 103 | 13:00 | 116 | Mongla | 39 | 00:00 | 182 | Ullahpara | 40 | 20:00
51 | Dohazari | 94 | 00:00 | 117 | Motijheel | 36 | 19:00 | 183 | Ullon | 40 | 22:00
52 | Faridpur | 161 | 20:00 | 118 | Muktagacha | 38 | 23:00 | 184 | Uttara | 77 | 19:30
53 | Fatullah | 93 | 12:00 | 119 | Munshiganj | 114 | 00:00 | 185 | UttaraNew | 59 | 00:00
54 | Fenchuganj | 43 | 19:30 | 120 | Muradnagar | 28 | 19:30 | 186 | Zigatola | 74 | 00:00
55 | Feni | 108 | 21:00 | 121 | Mymensingh | 206 | 22:00
56 | GPH | 19 | 11:00 | 122 | Naogaon | 142 | 23:00
57 | Ghatail | 88 | 20:00 | 123 | Narail | 56 | 20:00
58 | Ghorashal | 16 | 14:00 | 124 | Narinda | 53 | 00:00
59 | Ghorashal-230 | 96 | 22:00 | 125 | Narshingdi | 186 | 00:00
60 | Goalpara | 30 | 00:00 | 126 | Natore | 154 | 22:00
61 | Gollamari | 90 | 00:00 | 127 | Nawabganj | 58.4 | 22:00
62 | Gopalganj | 104 | 20:00 | 128 | Netrakona | 138 | 00:00
63 | Gulshan | 88 | 13:00 | 129 | New | 56 | 15:00
64 | Halishahar | 58 | 12:00 | 130 | Niamatpur | 86 | 22:00
65 | HaripurSBU | 154 | 18:00 | 131 | Noapara | 47 | 19:30
66 | Hasnabad | 65 | 00:00 | 132 | PHP | 7 | 01:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 06-07-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14814.96 | 39 |  | 14855.72
1:00 | 14325.04 | 110 |  | 14439.99
2:00 | 13967.86 | 108 |  | 14080.72
3:00 | 13495.99 | 91 |  | 13591.09
4:00 | 13102.58 | 65 |  | 13170.51
5:00 | 12789.65 | 63 |  | 12855.49
6:00 | 12245.21 | 31 |  | 12277.61
7:00 | 11985.86 | 0 |  | 11985.86
8:00 | 11718.26 | 13 |  | 11731.85
9:00 | 11944.55 | 11 |  | 11956.05
10:00 | 11959.43 | 10 |  | 11969.43
11:00 | 12166.66 | 10 |  | 12176.66
12:00 | 12630.72 | 10 |  | 12640.72
13:00 | 13174.64 | 23 |  | 13198.64
14:00 | 13180.77 | 22 |  | 13203.76
15:00 | 13104.13 | 29 |  | 13134.44
16:00 | 12771.58 | 32 |  | 12805.02
17:00 | 12381.34 | 31 |  | 12413.74
18:00 | 12094.62 | 0 |  | 12094.62
19:00 | 13237.34 | 41 |  | 13280.19
19:30 | 14507.56 | 89 |  | 14600.56
20:00 | 14599.45 | 96 |  | 14699.45
21:00 | 14723.24 | 83 |  | 14810.24
22:00 | 14785.93 | 91 |  | 14881.03
23:00 | 14609.13 | 97 |  | 14710.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 06-07-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8366 | 6448.96 | 14814.96 | DAILY GENERATION CURVE
00:30 | 8262.5 | 6307.5 | 14570
01:00 | 8159 | 6166.04 | 14325.04 | 06-07-2025
01:30 | 8039 | 6107.45 | 14146.45
02:00 | 7919 | 6048.86 | 13967.86
02:30 | 7747.5 | 5984.425 | 13731.925
03:00 | 7576 | 5919.99 | 13495.99
03:30 | 7406.5 | 5892.785 | 13299.285
04:00 | 7237 | 5865.58 | 13102.58
04:30 | 7110 | 5836.115 | 12946.115
05:00 | 6983 | 5806.65 | 12789.65
05:30 | 6875.25 | 5642.18 | 12517.43
06:00 | 6767.5 | 5477.71 | 12245.21
06:30 | 6741.16 | 5374.375 | 12115.535
07:00 | 6714.82 | 5271.04 | 11985.86
07:30 | 6614.315 | 5237.745 | 11852.06
08:00 | 6513.81 | 5204.45 | 11718.26
08:30 | 6595.165 | 5236.24 | 11831.405
09:00 | 6676.52 | 5268.03 | 11944.55
09:30 | 6638.28 | 5313.71 | 11951.99
10:00 | 6600.04 | 5359.39 | 11959.43
10:30 | 6657.08 | 5405.965 | 12063.045
11:00 | 6714.12 | 5452.54 | 12166.66
11:30 | 6852.57 | 5546.12 | 12398.69
12:00 | 6991.02 | 5639.7 | 12630.72
12:30 | 7082.57 | 5820.11 | 12902.68
13:00 | 7174.12 | 6000.52 | 13174.64
13:30 | 7199.295 | 5978.41 | 13177.705
14:00 | 7224.47 | 5956.3 | 13180.77
14:30 | 7223.64 | 5918.81 | 13142.45
15:00 | 7222.81 | 5881.32 | 13104.13
15:30 | 7158.275 | 5779.58 | 12937.855
16:00 | 7093.74 | 5677.84 | 12771.58
16:30 | 7008.46 | 5568 | 12576.46
17:00 | 6923.18 | 5458.16 | 12381.34
17:30 | 6861.63 | 5376.35 | 12237.98
18:00 | 6800.08 | 5294.54 | 12094.62
18:30 | 7221.155 | 5444.825 | 12665.98
19:00 | 7642.23 | 5595.11 | 13237.34
19:30 | 8507 | 6000.56 | 14507.56
20:00 | 8534.04 | 6065.41 | 14599.45
20:30 | 8571.64 | 6089.705 | 14661.345 |  | Executive Engineer
21:00 | 8609.24 | 6114 | 14723.24 |  | Network Operation Division
21:30 | 8632.24 | 6122.345 | 14754.585
22:00 | 8655.24 | 6130.69 | 14785.93
22:30 | 8508.7 | 6188.83 | 14697.53
23:00 | 8362.16 | 6246.97 | 14609.13

## En-Curve
QF-LDC-12
Date | 06-07-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3983 | 2091 | 891 | 38 | 40 | 1276.96 | 172 | 3700 | 0 | 572 | 2030 | 0 | 0 | 21 | 39 | DAILY ENERGY CURVE
00:30 | 3954 | 2027 | 890.5 | 38 | 42 | 1281.5 | 172 | 3620.5 | 0 | 515 | 2005 | 0 | 0 | 24.5 | 74.5 | 06-07-2025
01:00 | 3925 | 1963 | 890 | 38 | 44 | 1286.04 | 172 | 3541 | 0 | 458 | 1980 | 0 | 0 | 28 | 110
01:30 | 3923 | 1961 | 890.5 | 38 | 43 | 1272.95 | 172 | 3526.5 | 0 | 407 | 1891.5 | 0 | 0 | 21 | 109 | Energy Generated | 319.453 |  | MKWHr
02:00 | 3921 | 1959 | 891 | 38 | 42 | 1259.86 | 172 | 3512 | 0 | 356 | 1803 | 0 | 0 | 14 | 108 | Energy not Served | 1.106 |  | MKWHr
02:30 | 3970.5 | 1975.5 | 890.5 | 38 | 42 | 1261.925 | 172 | 3517 | 0 | 228.5 | 1616.5 | 0 | 0 | 19.5 | 99.5 | Total Energy Requirement | 320.559 |  | MKWHr
03:00 | 4020 | 1992 | 890 | 38 | 42 | 1263.99 | 172 | 3522 | 0 | 101 | 1430 | 0 | 0 | 25 | 91
03:30 | 4038 | 2011 | 890 | 38 | 41 | 1265.285 | 172 | 3523.5 | 0 | 78 | 1223.5 | 0 | 0 | 19 | 78
04:00 | 4056 | 2030 | 890 | 38 | 40 | 1266.58 | 172 | 3525 | 0 | 55 | 1017 | 0 | 0 | 13 | 65
04:30 | 4030 | 2028.5 | 890 | 38 | 40 | 1262.115 | 172 | 3452 | 0 | 55 | 955.5 | 0 | 0 | 23 | 64
05:00 | 4004 | 2027 | 890 | 38 | 40 | 1257.65 | 172 | 3379 | 0 | 55 | 894 | 0 | 0 | 33 | 63
05:30 | 4022 | 2011 | 890.5 | 38 | 39 | 1169.32 | 172 | 3247.5 | 13.11 | 54.5 | 829.5 | 0 | 0 | 31 | 47
06:00 | 4040 | 1995 | 891 | 38 | 38 | 1080.99 | 172 | 3116 | 26.22 | 54 | 765 | 0 | 0 | 29 | 31
06:30 | 4042 | 1998 | 890.5 | 38 | 37 | 1016.775 | 172 | 3017.5 | 73.26 | 55 | 747.5 | 0 | 0 | 28 | 15.5
07:00 | 4044 | 2001 | 890 | 38 | 36 | 952.56 | 172 | 2919 | 120.3 | 56 | 730 | 0 | 0 | 27 | 0
07:30 | 4059.5 | 1984.5 | 890 | 38 | 35 | 948.78 | 172 | 2867.5 | 142.78 | 59 | 633.5 | 0 | 0 | 21.5 | 6.5
08:00 | 4075 | 1968 | 890 | 38 | 34 | 945 | 172 | 2816 | 165.26 | 62 | 537 | 0 | 0 | 16 | 13
08:30 | 4064 | 1984 | 890 | 38 | 32 | 927 | 172 | 2883.5 | 193.905 | 62 | 566.5 | 0 | 0 | 18.5 | 12
09:00 | 4053 | 2000 | 890 | 38 | 30 | 909 | 172 | 2951 | 222.55 | 62 | 596 | 0 | 0 | 21 | 11
09:30 | 3988.5 | 1960.25 | 890 | 38 | 30 | 911.5 | 172 | 2958 | 339.74 | 62 | 585.5 | 0 | 0 | 16.5 | 10.5
10:00 | 3924 | 1920.5 | 890 | 38 | 30 | 914 | 172 | 2965 | 456.93 | 62 | 575 | 0 | 0 | 12 | 10
10:30 | 3940 | 1929.5 | 890.5 | 38 | 31 | 969 | 172 | 3014 | 416.045 | 62 | 575.5 | 0 | 0 | 25.5 | 10
11:00 | 3956 | 1938.5 | 891 | 38 | 32 | 1024 | 172 | 3063 | 375.16 | 62 | 576 | 0 | 0 | 39 | 10
11:30 | 3969 | 1971 | 890.5 | 38 | 33 | 1082.5 | 172 | 3143 | 391.19 | 62 | 614 | 0 | 0 | 32.5 | 10
12:00 | 3982 | 2003.5 | 890 | 38 | 34 | 1141 | 172 | 3223 | 407.22 | 62 | 652 | 0 | 0 | 26 | 10
12:30 | 3911 | 2031 | 890 | 38 | 36 | 1170.5 | 172 | 3330 | 449.68 | 61.5 | 791 | 0 | 0 | 22 | 16.5
13:00 | 3840 | 2058.5 | 890 | 38 | 38 | 1200 | 172 | 3437 | 492.14 | 61 | 930 | 0 | 0 | 18 | 23
13:30 | 3800 | 2032 | 890 | 38 | 38 | 1175.845 | 172 | 3471 | 480.86 | 69.5 | 992.5 | 0 | 0 | 18 | 22.5
14:00 | 3760 | 2005.5 | 890 | 38 | 38 | 1151.69 | 172 | 3505 | 469.58 | 78 | 1055 | 0 | 0 | 18 | 22
14:30 | 3824 | 2013.7 | 890.5 | 38 | 35 | 1161.995 | 172 | 3522 | 396.255 | 78 | 984.5 | 0 | 0 | 26.5 | 25.5
15:00 | 3888 | 2021.9 | 891 | 38 | 32 | 1172.3 | 172 | 3539 | 322.93 | 78 | 914 | 0 | 0 | 35 | 29
15:30 | 3877.5 | 2017.9 | 891 | 38 | 32 | 1092.095 | 172 | 3530 | 297.36 | 69.5 | 879.5 | 0 | 0 | 41 | 30.5
16:00 | 3867 | 2013.9 | 891 | 38 | 32 | 1011.89 | 172 | 3521 | 271.79 | 61 | 845 | 0 | 0 | 47 | 32
16:30 | 3870.5 | 2010.7 | 891 | 38 | 32 | 1010.47 | 172 | 3454 | 181.79 | 72.5 | 802.5 | 0 | 0 | 41 | 31.5
17:00 | 3874 | 2007.5 | 891 | 38 | 32 | 1009.05 | 172 | 3387 | 91.79 | 84 | 760 | 0 | 0 | 35 | 31
17:30 | 3845 | 1941 | 890.5 | 38 | 32 | 969.565 | 172 | 3334.5 | 67.415 | 99.5 | 817.5 | 0 | 0 | 31 | 15.5
18:00 | 3816 | 1874.5 | 890 | 38 | 32 | 930.08 | 172 | 3282 | 43.04 | 115 | 875 | 0 | 0 | 27 | 0
18:30 | 3856.5 | 1905.25 | 890.5 | 38 | 36 | 978.595 | 172 | 3359 | 22.095 | 227 | 1156.54 | 0 | 0 | 24.5 | 20.5
19:00 | 3897 | 1936 | 891 | 38 | 40 | 1027.11 | 172 | 3436 | 1.15 | 339 | 1438.08 | 0 | 0 | 22 | 41
19:30 | 4055 | 2026 | 891 | 38 | 38 | 1022.56 | 172 | 3604 | 0 | 413 | 2221 | 0 | 0 | 27 | 89
20:00 | 4054 | 2041 | 891 | 38 | 38 | 1048.41 | 172 | 3657 | 0 | 428 | 2200.04 | 0 | 0 | 32 | 96
20:30 | 4058 | 2052.5 | 891 | 38 | 39 | 1036.705 | 172 | 3667 | 0 | 435.5 | 2237.14 | 0 | 0 | 34.5 | 89.5
21:00 | 4062 | 2064 | 891 | 38 | 40 | 1025 | 172 | 3677 | 0 | 443 | 2274.24 | 0 | 0 | 37 | 83
21:30 | 4062 | 2065 | 891 | 38 | 42 | 1025.345 | 172 | 3689 | 0 | 445.5 | 2288.24 | 0 | 0 | 36.5 | 87
22:00 | 4062 | 2066 | 891 | 38 | 44 | 1025.69 | 172 | 3701 | 0 | 448 | 2302.24 | 0 | 0 | 36 | 91
22:30 | 3999.5 | 2037 | 891 | 38 | 46 | 1120.83 | 172 | 3711.5 | 0 | 448 | 2202.7 | 0 | 0 | 31 | 94
23:00 | 3937 | 2008 | 891 | 38 | 48 | 1215.97 | 172 | 3722 | 0 | 448 | 2103.16 | 0 | 0 | 26 | 97
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 06-07-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 388 | 07:00 | 378 | 00:00 | Payra | 415 | 07:00 | 409 | 00:00
Ashuganj | 402 | 6:00 | 371 | 14:00 | Rahanpur | 399 | 22:00 | 376 | 00:00
Bhulta | 394 | 07:00 | 369 | 15:00 | Rampal | 402 | 06:00 | 389 | 00:00
Bibiana | 389 | 10:00 | 382 | 00:00
BIPTC | 405 | 18:30 | 394 | 23:00
Bogura | 385 | 07:00 | 364 | 00:00
Gopalganj | 400 | 08:00 | 388 | 00:00
Kaliakoir | 377 | 07:00 | 366 | 15:00
Madunaghat | 398 | 22:00 | 392 | 13:00
Meghnaghat | 392 | 07:00 | 385 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 227 | 07:00 | 220 | 15:00 | Keranigonj | 225 | 07:00 | 219 | 12:00
AKSML | 233 | 19:30 | 221 | 15:00 | Khulna(S) | 232 | 09:00 | 220 | 00:00
Aminbazar | 227 | 06:00 | 221 | 14:00 | Madunaghat | 237 | 22:00 | 230 | 17:00
Ashuganj | 229 | 20:00 | 220 | 00:00 | Madunaghat-400 | 238 | 20:00 | 231 | 16:00
Ashuganj-400 | 229 | 20:00 | 220 | 00:00 | Maniknagar | 222 | 05:00 | 219 | 00:00
Baghabari | 234 | 07:00 | 225 | 15:00 | Meghnaghat | 231 | 06:00 | 227 | 15:00
Barapukuria | 225 | 06:00 | 214 | 00:00 | Meghnaghat-400 | 233 | 16:00 | 222 | 15:00
Barapukuria-230 | 225 | 06:00 | 214 | 00:00 | Mirsorai | 230 | 18:30 | 224 | 16:00
Barishal | 230 | 07:00 | 222 | 00:00 | Rajshahi | 235 | 07:00 | 224 | 15:00
Bheramara | 234 | 06:00 | 221 | 12:00 | Rampal | 230 | 07:00 | 219 | 00:00
Bhulta | 227 | 07:00 | 211 | 15:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 229 | 06:00 | 222 | 00:00 | Rampura | 227 | 07:00 | 209 | 15:00
BIPTC | 237 | 07:00 | 222 | 23:00 | Shikalbaha | 236 | 20:00 | 227 | 15:00
Bogura | 234 | 07:00 | 223 | 00:00 | Shyampur | 226 | 07:00 | 220 | 12:00
Bogura-400 | 234 | 07:00 | 222 | 00:00 | Siddhirganj | 225 | 05:00 | 221 | 12:00
Borhanuddin | 234 | 07:00 | 229 | 01:00 | Sirajgonj | 238 | 06:00 | 232 | 00:00
BSRM | 230 | 18:30 | 223 | 16:00 | Sreepur | 225 | 07:00 | 216 | 15:00
Cumilla(N) | 224 | 06:00 | 218 | 00:00 | Tongi | 225 | 04:00 | 213 | 00:00
Faridpur | 229 | 09:00 | 218 | 00:00
Fenchuganj | 231 | 08:00 | 223 | 01:00
Ghorashal | 230 | 02:00 | 220 | 00:00
Ghorashal-230 | 228 | 07:00 | 214 | 00:00
Gopalganj | 229 | 09:00 | 221 | 00:00
GPH | 233 | 18:30 | 227 | 16:00
Haripur | 225 | 07:00 | 220 | 00:00
Hasnabad | 224 | 07:00 | 220 | 12:00
Hathazari | 231 | 00:00 | 228 | 12:00
Ishurdi | 236 | 06:00 | 225 | 21:00
Jhenaidah | 231 | 07:00 | 216 | 21:00
Kaliakoir | 232 | 18:30 | 222 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 22:00 | 127 | 15:00 | Madanganj | 130 | 04:00 | 128 | 11:00
Agargaon | 133 | 06:00 | 128 | 15:00 | Madaripur | 136 | 07:00 | 130 | 00:00
Agrabad | 134 | 00:00 | 129 | 15:00 | Madartek | 136 | 08:00 | 127 | 16:00
AKS | 132 | 01:00 | 126 | 16:00 | Madunaghat | 135 | 22:00 | 131 | 12:00
Aminbazar | 134 | 20:00 | 129 | 12:00 | Magura | 136 | 09:00 | 124 | 21:00
Amnura | 136 | 01:00 | 122 | 00:00 | Mahasthangarh | 136 | 07:00 | 127 | 00:00
Ashuganj | 139 | 09:00 | 130 | 21:00 | Maijdee | 119 | 21:00 | 109 | 00:00
Bagerhat | 134 | 10:00 | 120 | 23:00 | Manikganj | 128 | 06:00 | 120 | 00:00
Bajitpur | 130 | 05:00 | 122 | 00:00 | Maniknagar | 133 | 05:00 | 130 | 12:00
Bakulia | 136 | 03:00 | 131 | 15:00 | Matarbari | 132 | 19:00 | 121 | 08:00
Banani | 137 | 22:00 | 126 | 15:00 | Matuail | 131 | 06:00 | 129 | 00:00
Bangabhaban | 133 | 06:00 | 130 | 00:00 | Millgate | 132 | 18:00 | 123 | 15:00
Barapukuria | 138 | 06:00 | 127 | 00:00 | Mirpur | 132 | 19:00 | 127 | 15:00
Barguna | 135 | 09:00 | 130 | 20:00 | Mirzapur | 131 | 18:30 | 124 | 00:00
Barishal | 135 | 06:00 | 129 | 00:00 | Mithapukur | 135 | 07:00 | 123 | 00:00
Barishal-230 | 135 | 07:00 | 129 | 00:00 | MI_Cement | 131 | 06:00 | 128 | 12:00
Baroaulia | 135 | 03:00 | 130 | 15:00 | Modern | N/A | N/A | N/A | N/A
Baroirhat | 125 | 21:00 | 118 | 16:00 | Mogbazar | 138 | 07:00 | 125 | 15:00
Bashundhara | 137 | 22:00 | 122 | 15:00 | Mongla | 134 | 09:00 | 123 | 00:00
BashundharaCement | 130 | 04:00 | 128 | 11:00 | Motijheel | 133 | 06:00 | 130 | 00:00
Beanibazar | 127 | 07:00 | 122 | 00:00 | Muktagacha | 135 | 18:30 | 127 | 01:00
Benapole | 133 | 10:00 | 121 | 00:00 | Munshiganj | 130 | 01:00 | 127 | 12:00
Bhaluka | 126 | 08:00 | 120 | 15:00 | Muradnagar | 127 | 18:00 | 122 | 00:00
Bhandaria | 131 | 10:00 | 121 | 00:00 | Mymensingh | 136 | 18:30 | 116 | 16:00
Bhangura | 133 | 04:00 | 127 | 21:00 | Naogaon | 132 | 07:00 | 125 | 00:00
Bheramara | 138 | 07:00 | 131 | 12:00 | Narail | 136 | 09:00 | 122 | 23:00
Bheramara(GK) | 138 | 07:00 | 132 | 23:00 | Narinda | 0 | 00:00 | N/A | N/A
Bhulta | 126 | 18:30 | 116 | 00:00 | Narshingdi | 136 | 07:00 | 125 | 0:00
Bog-Sherpur | 136 | 09:00 | 128 | 00:00 | Natore | 135 | 06:00 | 129 | 00:00
Bogura | 138 | 09:00 | 131 | 00:00 | Nawabganj | 134 | 06:00 | 130 | 00:00
Bogura-230 | 138 | 07:00 | 131 | 00:00 | Netrakona | 124 | 17:00 | 110 | 00:00
Brahmanbaria | 132 | 07:00 | 123 | 00:00 | New | 132 | 05:00 | 124 | 15:00
Cantonment | 133 | 07:00 | 128 | 14:00 | Niamatpur | 135 | 08:00 | 127 | 00:00
Chandina | 129 | 18:30 | 123 | 00:00 | Noapara | 136 | 09:00 | 126 | 00:00
Chandpur | 128 | 21:00 | 117 | 00:00 | Pabna | 135 | 07:00 | 128 | 21:00
Chandraghona | 138 | 21:00 | 132 | 03:00 | Palashbari | 131 | 06:00 | 121 | 00:00
Chapai | 131 | 08:00 | 121 | 00:00 | Panchagarh | 136 | 07:00 | 120 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 132 | 06:00 | 128 | 12:00 | Patuakhali | 135 | 08:00 | 131 | 00:00
Chauddagram | 124 | 18:00 | 117 | 00:00 | Payra | 136 | 06:00 | 133 | 00:00
Chhatak | 126 | 07:00 | 119 | 00:00 | PHP | 124 | 18:30 | 118 | 00:00
Chowmuhani | 120 | 18:30 | 109 | 00:00 | Postogola | 133 | 06:00 | 130 | 12:00
Chuadanga | 132 | 06:00 | 121 | 00:00 | Purbachal | 138 | 07:00 | 123 | 15:00
Coxsbazar | 127 | 00:00 | 121 | 07:00 | Purbasadipur | 133 | 07:00 | 118 | 12:00
Cumilla(N) | 128 | 07:00 | 124 | 00:00 | Rahanpur | 136 | 22:00 | 126 | 00:00
Cumilla(S) | 132 | 06:00 | 120 | 00:00 | Rahanpur-400 | 136 | 22:00 | 128 | 00:00
Daganbhuiyan | 122 | 22:00 | 113 | 00:00 | Rahim | 131 | 06:00 | 129 | 00:00
Daudkandi | 126 | 18:00 | 120 | 00:00 | Rajbari | 134 | 07:00 | 127 | 00:00
Dhaka | 137 | 22:00 | 125 | 15:00 | Rajendrapur | 132 | 20:00 | 121 | 15:00
Dhamrai | 138 | 21:00 | 125 | 15:00 | Rajshahi | 136 | 09:00 | 128 | 00:00
Dhanmondi | 137 | 07:00 | 129 | 00:00 | Rajshahi-230 | 136 | 08:00 | 116 | 00:00
Dohazari | 133 | 00:00 | 128 | 05:00 | Ramganj | 121 | 21:00 | 110 | 00:00
Faridpur | 136 | 09:00 | 129 | 00:00 | Rampur | 135 | 20:00 | 129 | 16:00
Fatullah | 132 | 06:00 | 129 | 12:00 | Rampura | 137 | 07:00 | 126 | 15:00
Fenchuganj | 136 | 08:00 | 130 | 00:00 | Rangamati | 133 | 18:30 | 130 | 12:00
Feni | 124 | 18:30 | 116 | 00:00 | Rangpur | 133 | 06:00 | 121 | 00:00
Ghatail | 132 | 18:30 | 124 | 00:00 | Ruppur | 138 | 08:00 | 131 | 23:00
Ghorashal | 136 | 19:00 | 128 | 15:00 | Saidpur | 131 | 07:00 | 121 | 00:00
Goalpara | 138 | 09:00 | 127 | 00:00 | Satkhira | 136 | 10:00 | 122 | 00:00
Gollamari | 137 | 06:00 | 130 | 00:00 | Satmasjid | 133 | 06:00 | 128 | 16:00
Gopalganj | 136 | 07:00 | 129 | 00:00 | Savar | 133 | 19:30 | 126 | 16:00
Gopalganj-400 | 137 | 06:00 | 132 | 00:00 | SevenRings | 136 | 19:30 | 128 | 15:00
Gulshan | 137 | 07:00 | 126 | 15:00 | ShahCement | 131 | 01:00 | 128 | 12:00
Halishahar | 136 | 00:00 | 129 | 16:00 | Shahjadpur | 136 | 07:00 | 132 | 14:00
Haripur | 131 | 02:00 | 129 | 10:00 | Shahjibazar | 133 | 09:00 | 124 | 00:00
HaripurSBU | 132 | 19:00 | 124 | 21:00 | Shahmirpur | 136 | 00:00 | 131 | 08:00
Hasnabad | 132 | 01:00 | 130 | 13:00 | Shariatpur | 136 | 09:00 | 128 | 00:00
Hathazari | 135 | 00:00 | 131 | 15:00 | Sherpur | 135 | 18:30 | 125 | 12:00
Ishurdi | 139 | 07:00 | 132 | 23:00 | Shikalbaha | 126 | 01:00 | 120 | 15:00
Jaldhaka | 130 | 06:00 | 118 | 00:00 | Shikalbaha-230 | 137 | 20:00 | 132 | 15:00
Jamalpur | 138 | 18:30 | 127 | 12:00 | Shitalakhya | 131 | 06:00 | 128 | 12:00
Jashore | 132 | 06:00 | 120 | 23:00 | Sholosohor | 134 | 00:00 | 130 | 12:00
Jhenaidah | 136 | 06:00 | 123 | 23:00 | Shyampur | 132 | 18:30 | 127 | 00:00
Jhenaidah-230 | 137 | 09:00 | 125 | 21:00 | Shyampur-230 | 132 | 07:00 | 129 | 12:00
Joydebpur | 134 | 19:30 | 124 | 14:00 | Siddhirganj | 131 | 03:00 | 129 | 12:00
Joypurhat | 131 | 07:00 | 121 | 00:00 | Sirajganj | 133 | 06:00 | 126 | 21:00
Juldah | 137 | 00:00 | 131 | 07:00 | Sonargaon | 130 | 18:30 | 125 | 04:00
Kabirpur | 133 | 20:00 | 120 | 15:00 | Sreemongol | 132 | 07:00 | 124 | 00:00
Kachua | 127 | 21:00 | 116 | 00:00 | Sreepur | 130 | 07:00 | 123 | 15:00
Kaliakoir | 134 | 18:30 | 128 | 15:00 | Srinagar | 135 | 07:00 | 130 | 12:00
Kallyanpur | 134 | 22:00 | 128 | 12:00 | SSM | 138 | 18:00 | 131 | 16:00
Kalurghat | 134 | 19:30 | 130 | 12:00 | Sunamganj | 124 | 09:00 | 117 | 00:00
Kamrangirchar | 134 | 06:00 | 130 | 00:00 | Sylhet | 129 | 08:00 | 123 | 00:00
Kaptai | 136 | 1:00 | 133 | 12:00 | Sylhet-132 | 129 | 07:00 | 125 | 00:00
Kasba | 126 | 18:00 | 120 | 00:00 | Tangail | 129 | 18:00 | 122 | 00:00
Kazla | 133 | 06:00 | 130 | 00:00 | Taraganj | 133 | 07:00 | 122 | 00:00
Keranigonj | 135 | 06:00 | 131 | 00:00 | Thakurgaon | 134 | 06:00 | 117 | 12:00
Khagrachori | 133 | 22:00 | 129 | 12:00 | TK | 134 | 20:00 | 130 | 15:00
Khulna | 136 | 10:00 | 124 | 00:00 | Tongi | 135 | 04:00 | 126 | 15:00
Khulna(S) | 138 | 07:00 | 129 | 00:00 | Ullahpara | 135 | 07:00 | 128 | 21:00
Khulshi | 134 | 21:00 | 129 | 08:00 | Ullon | 137 | 07:00 | 125 | 15:00
Kishoreganj | 127 | 17:00 | 118 | 00:00 | Uttara | 132 | 01:00 | 127 | 12:00
Kodda | 132 | 20:00 | 122 | 13:00 | UttaraNew | 132 | 01:00 | 127 | 12:00
KSRM | 135 | 21:00 | 130 | 14:00 | Zigatola | 135 | 07:00 | 130 | 00:00
Kulaura | 134 | 09:00 | 128 | 00:00
Kurigram | 132 | 07:00 | 118 | 00:00
Kushtia | 134 | 03:00 | 127 | 23:00
Lakshmipur | 121 | 18:30 | 110.63 | 00:00
Lalbag | 134 | 05:00 | 130 | 15:00
Lalmonirhat | 132 | 08:00 | 118 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division