## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 10-07-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 09-07-2025 | during | 10-07-2025 | during | 10-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 324 | 406 | 400.75 | 400.75 | 320 | 320 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 400 | 450 | 450 | 450 | 450 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 306 | 296 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 18 | 48 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 17 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 28.5 | 25 | 4.4 | 4.4 | 4.4 | 4.4 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 52 | 34 | 52.19 | 52.19 | 42 | 42 | Engine Problem
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 68 | 51 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 70 | 105 | 105 | 70 | 90 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 68 | 68 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 16 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 5 | 0 | 29 | 0 | 29 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 25 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 350 | 400 | 584 | 584 | 425 | 425 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | Gas shortage instructed by DS(Gen)
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 52 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 1984.5 | 2253 | 5094.8 | 5159.8 | 3211.23 | 3296.23
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 16 | 0 | 11 | 0 | 11 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 202 | 172 | 167 | 167 | 167 | 167 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 224 | 219 | 219 | 219 | 219 | 219 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 56 | 72 | 56 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 33 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 24 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 10 | 2 | 20 | 2 | 5 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1 | 0 | 1.27 | 0 | 1.27 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 48 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 950 | 890 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 63 | 22 | 42 | 38 | 42 | 38 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 201 | 752 | 875 | 875 | 195 | 195 | Machine Problem
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1659 | 2170 | 3890.99 | 3908.72 | 3210.99 | 3213.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 207 | 197 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 300 | 357 | 353.35 | 353.35 | 353.35 | 353.35
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 330 | 340 | 340 | 340 | 340 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 18 | 20 | 46.7 | 46.7 | 10 | 10 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 48 | 52 | 55 | 55 | 40 | 40 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 91 | 63 | 195 | 195 | 195 | 195
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 10 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 136 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 30 | 30 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 20 | 24.5 | 24.5 | 15 | 15 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 46 | 114 | 114 | 98 | 98 | Engine Problem
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 38 | 113 | 113 | 9 | 28 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 31 | 21 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 19 | 0 | 15 | 0 | 15 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1188 | 1387 | 2415.75 | 2400.75 | 2055.55 | 2059.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 09-07-2025 | during | 10-07-2025 | during | 10-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 30 | 34 | 157.5 | 157.5 | 30 | 30 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 0 | 110 | 200 | 200 | 160 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 86 | 75 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 9.47 | 0 | 34.35 | 0 | 34.35 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 35 | 35 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 138.47 | 231 | 585.25 | 549 | 388.25 | 352
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage instructed by DS(Gen)
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 143 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 20 | 20 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 79 | 83 | 83 | 72 | 72 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 172 | 172 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 18 | 18 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 6 | 6 | 25 | 25 | 6 | 6 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 388 | 345 | 380 | 380 | 332 | 332 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 350 | 350 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1476 | 1418 | 1552 | 1552 | 1382 | 1382
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 902 | 902 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 213 | 200 | 410 | 410 | 190 | 190 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 70 | 70 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 50.02 | 0 | 30 | 0 | 30 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 812 | 896 | 1234.2 | 1234.2 | 1150 | 1150 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2015.02 | 2053 | 3578.2 | 3548.2 | 2679 | 2649
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 4 | 9 | 10 | 10 | 2 | 2 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 100 | 120 | 120 | 120 | 101 | 101 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 867 | 900 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 173 | 248 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.24 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1364.24 | 1497 | 2162 | 2161 | 2135 | 2134
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 150 | 140 | 220 | 220 | 200 | 200 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 130 | 220 | 220 | 203 | 203 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 342 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0.85 | 0 | 3.6 | 0 | 3.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 971.82 | 1009 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 4.35 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 12 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 1693.02 | 1621 | 2959.47 | 2805.87 | 2881.09 | 2727.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 50 | 0 | 0 | 50 | 50 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 170 | 204 | 200 | 200 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 98 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.7 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 110 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 15 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 181 | 0 | 122.69 | 0 | 122.69 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 457.7 | 462 | 621.29 | 462 | 671.29 | 512
System Total |  |  |  |  | 28565.2 | 27084.055 | 11975.95 | 13092 | 22859.75 | 22547.34 | 18614.4 | 18325.99
Forecast Scenario (10-07-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12730 |  | 0 |  | 12730
|  |  |  | 1:00 | 12290 |  | 0 |  | 12290
|  |  |  | 2:00 | 11780 |  | 0 |  | 11780
|  |  |  | 3:00 | 11220 |  | 0 |  | 11220
|  |  |  | 4:00 | 10740 |  | 0 |  | 10740
|  |  |  | 5:00 | 10550 |  | 0 |  | 10550
|  |  |  | 6:00 | 10160 |  | 0 |  | 10160
|  |  |  | 7:00 | 10320 |  | 0 |  | 10320
|  |  |  | 8:00 | 10610 |  | 0 |  | 10610
|  |  |  | 9:00 | 10880 |  | 0 |  | 10880
|  |  |  | 10:00 | 10970 |  | 0 |  | 10970
|  |  |  | 11:00 | 11230 |  | 0 |  | 11230
|  |  |  | 12:00 | 11770 |  | 0 |  | 11770
|  |  |  | 13:00 | 11820 |  | 0 |  | 11820
|  |  |  | 14:00 | 11560 |  | 0 |  | 11560
|  |  |  | 15:00 | 11460 |  | 0 |  | 11460
|  |  |  | 16:00 | 11290 |  | 0 |  | 11290
|  |  |  | 17:00 | 10920 |  | 0 |  | 10920
|  |  |  | 18:00 | 10990 |  | 0 |  | 10990
|  |  |  | 18:30 | 11500 |  | 0 |  | 11500
|  |  |  | 19:00 | 11970 |  | 0 |  | 11970
|  |  |  | 19:30 | 12890 |  | 0 |  | 12890
|  |  |  | 20:00 | 12830 |  | 0 |  | 12830
|  |  |  | 21:00 | 12620 |  | 0 |  | 12620
|  |  |  | 22:00 | 12620 |  | 0 |  | 12620
|  |  |  | 23:00 | 12500 |  | 0 |  | 12500
Probable Maximum Temperature: |  |  | 31.40°C
Probable Maximum Demand at Day Peak: |  |  | 11770.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12890.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12890.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 275.83 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:10 hrs on 10-07-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 09-07-2025 | [28 empty] | Date: | 09-07-2025 | [28 empty] | Date: | 09-07-2025 | [28 empty] | Date: | 09-07-2025 | [28 empty] | Date: | 09-07-2025 | [12 empty] | Date: | 09-07-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [12 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 302 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 24 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 31 | 191 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1125 | 0 | 51 | 0 | 137 | 0 | 356 | 340 | 52 | 202 | 16 | 51 | 0 | 80 | 13 | 21 | 27 | 34 | 8 | 0 | 30 | 285 | 320 | 330 | 0 | 0 | 146 | 6 | 0 | 78 | 30 | 0 | 18 | 172 | 17 | 75 | 135 | 49 | 0 | 0 | 0 | 6885 | 876 | 196 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1011 | 0 | 1061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 140 | 0 | 360 | 0 | 0 | 199 | 52 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 7 | 120 | 220 | 0 | 0 | 1180 | 0 | 6051 | 12936 | 95.66
01:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 304 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 23 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 31 | 195 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1053 | 0 | 51 | 0 | 137 | 0 | 356 | 340 | 52 | 199 | 18 | 51 | 0 | 80 | 9 | 21 | 34 | 32 | 0 | 0 | 16 | 285 | 320 | 332 | 0 | 0 | 156 | 6 | 0 | 78 | 30 | 0 | 18 | 172 | 17 | 75 | 135 | 51 | 0 | 0 | 5 | 6787 | 875 | 196 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 914 | 0 | 961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 140 | 0 | 353 | 0 | 0 | 202 | 52 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 8 | 120 | 220 | 0 | 0 | 1080 | 0 | 5706 | 12493 | 95.68
02:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 300 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 23 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 31 | 190 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 950 | 0 | 51 | 0 | 137 | 0 | 356 | 340 | 52 | 205 | 18 | 51 | 0 | 79 | 9 | 21 | 29 | 32 | 0 | 0 | 0 | 290 | 320 | 334 | 0 | 0 | 141 | 6 | 0 | 78 | 30 | 0 | 18 | 172 | 17 | 75 | 135 | 51 | 0 | 0 | 12 | 6606 | 875 | 196 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 845 | 0 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 140 | 0 | 375 | 0 | 0 | 200 | 52 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 7 | 120 | 220 | 0 | 0 | 900 | 0 | 5381 | 11987 | 95.7
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 291 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 23 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 33 | 190 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 867 | 0 | 51 | 0 | 130 | 0 | 356 | 340 | 52 | 197 | 18 | 51 | 0 | 51 | 9 | 18 | 17 | 30 | 0 | 0 | 0 | 285 | 320 | 334 | 0 | 0 | 138 | 6 | 0 | 78 | 30 | 0 | 18 | 172 | 17 | 45 | 55 | 51 | 0 | 0 | 12 | 6306 | 875 | 196 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 789 | 0 | 861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 140 | 0 | 350 | 0 | 0 | 200 | 52 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 7 | 120 | 220 | 0 | 0 | 820 | 0 | 5118 | 11424 | 95.73
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 306 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 33 | 188 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 854 | 0 | 51 | 0 | 86 | 0 | 300 | 340 | 52 | 209 | 18 | 51 | 0 | 0 | 5 | 18 | 0 | 30 | 0 | 0 | 0 | 280 | 320 | 325 | 0 | 0 | 143 | 0 | 0 | 78 | 30 | 0 | 18 | 172 | 0 | 16 | 55 | 51 | 0 | 0 | 0 | 5936 | 875 | 196 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 827 | 0 | 872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 140 | 0 | 387 | 0 | 0 | 201 | 53 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 6 | 120 | 180 | 0 | 0 | 700 | 0 | 5013 | 10949 | 95.76
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 296 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 33 | 188 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 86 | 0 | 300 | 335 | 52 | 200 | 18 | 53 | 0 | 0 | 0 | 18 | 0 | 28 | 0 | 0 | 0 | 290 | 320 | 335 | 0 | 0 | 140 | 6 | 0 | 78 | 30 | 0 | 18 | 172 | 0 | 16 | 55 | 51 | 0 | 0 | 0 | 5927 | 877 | 205 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 0 | 865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 140 | 0 | 358 | 0 | 0 | 202 | 53 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 5 | 120 | 180 | 0 | 0 | 600 | 0 | 4829 | 10756 | 95.79
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 36 | 190 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 840 | 1 | 51 | 0 | 86 | 0 | 280 | 285 | 52 | 205 | 16 | 0 | 0 | 0 | 0 | 18 | 0 | 28 | 0 | 0 | 0 | 290 | 320 | 335 | 0 | 0 | 139 | 6 | 0 | 78 | 30 | 0 | 18 | 172 | 0 | 16 | 55 | 51 | 0 | 1.2 | 0 | 5556.2 | 877 | 210 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0.5 | 748 | 0 | 869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28 | 0 | 0 | 150 | 0 | 140 | 0 | 372 | 0 | 0.07 | 202 | 51 | 35 | 2 | 49 | 0 | 0 | 0.2 | 8 | 0 | 0 | 173 | 5 | 100 | 180 | 0 | 0 | 600 | 0 | 4810.05 | 10366.25 | 95.83
07:00 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 308 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 31 | 190 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 855 | 2 | 51 | 0 | 86 | 0 | 280 | 285 | 52 | 210 | 16 | 0 | 0 | 0 | 0 | 18 | 0 | 28 | 0 | 1 | 0 | 285 | 320 | 350 | 0 | 0 | 145 | 6 | 0 | 78 | 30 | 0 | 18 | 172 | 0 | 35 | 65 | 51 | 0 | 5.36 | 0 | 5638.36 | 877 | 215 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0.6 | 754 | 0 | 893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 1.28 | 0 | 0 | 150 | 0 | 140 | 0 | 392 | 0 | 0.14 | 200 | 51 | 35 | 4 | 49 | 0 | 0 | 1.4 | 19 | 0.01 | 0 | 173 | 4 | 100 | 180 | 0 | 0 | 600 | 0 | 4883.43 | 10521.79 | 95.87
08:00 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 306 | 0 | 0 | 0 | 335 | 0 | 0 | 1 | 0 | 20 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 7 | 196 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 860 | 8 | 51 | 0 | 86 | 0 | 356 | 280 | 52 | 209 | 16 | 0 | 0 | 0 | 0 | 18 | 0 | 26 | 0 | 2 | 0 | 290 | 320 | 349 | 0 | 0 | 148 | 6 | 0 | 76 | 30 | 0 | 18 | 172 | 0 | 35 | 85 | 50 | 1 | 5.13 | 0 | 5899.13 | 886 | 218 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4 | 767 | 0 | 868.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1.54 | 0 | 0 | 150 | 0 | 140 | 0 | 387 | 0 | 0.18 | 202 | 51 | 35 | 8 | 49 | 0 | 0 | 1.9 | 40 | 0.01 | 0 | 173 | 3 | 100 | 180 | 0 | 0 | 600 | 0 | 4918.36 | 10817.49 | 95.91
09:00 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 297 | 0 | 0 | 0 | 335 | 0 | 0 | 1 | 0 | 30 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 2 | 192 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 845 | 11 | 51 | 0 | 86 | 0 | 356 | 340 | 51 | 206 | 12 | 1 | 0 | 1 | 0 | 18 | 0 | 26 | 0 | 1 | 0 | 285 | 320 | 333 | 0 | 0 | 159 | 6 | 0 | 76 | 30 | 0 | 18 | 172 | 0 | 45 | 85 | 50 | 0 | 15.45 | 0 | 6105.45 | 892 | 218 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7.96 | 763 | 0 | 874.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 1.79 | 0 | 0 | 150 | 0 | 140 | 0 | 373 | 0 | 0.23 | 203 | 51 | 0 | 10 | 34 | 0 | 0 | 4.6 | 80 | 0.02 | 0 | 173 | 4 | 100 | 220 | 0 | 0 | 635 | 0 | 4981.04 | 11086.49 | 95.95
10:00 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 17 | 34 | 0 | 0 | 0 | 13 | 0 | 0 | 400 | 300 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 23 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 2 | 188 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 842 | 8 | 51 | 0 | 86 | 0 | 356 | 340 | 52 | 201 | 14 | 29 | 0 | 31 | 0 | 18 | 0 | 28 | 0 | 3 | 0 | 285 | 320 | 334 | 0 | 0 | 158 | 6 | 0 | 76 | 30 | 0 | 18 | 172 | 0 | 45 | 85 | 46 | 1 | 14.73 | 0 | 6195.73 | 892 | 218 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14 | 742 | 0 | 873.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 7.99 | 0 | 0 | 150 | 0 | 140 | 0 | 362 | 0 | 0.57 | 204 | 51 | 0 | 26 | 34 | 0 | 0 | 2.8 | 20 | 0.13 | 0 | 172 | 3 | 100 | 220 | 0 | 0 | 700 | 0 | 4980.51 | 11176.24 | 95.99
11:00 | 0 | 2 | 42 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 17 | 50 | 0 | 0 | 0 | 17 | 0 | 0 | 400 | 306 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 30 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0.37 | 172 | 0 | 2 | 188 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 855 | 12 | 51 | 0 | 86 | 0 | 356 | 340 | 50 | 203 | 18 | 34 | 0 | 27 | 0 | 18 | 0 | 28 | 0 | 10 | 0 | 290 | 320 | 386 | 0 | 0 | 152 | 6 | 0 | 76 | 30 | 0 | 18 | 172 | 0 | 52 | 85 | 46 | 0 | 7.66 | 2 | 6272.03 | 901 | 215 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 54 | 747 | 0 | 870.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 4.15 | 0 | 0 | 150 | 0 | 140 | 0 | 370 | 0 | 0.47 | 200 | 52 | 0 | 17 | 34 | 0 | 0 | 1.4 | 96 | 0.24 | 0 | 172 | 4 | 100 | 220 | 0 | 0 | 740 | 0 | 5161.05 | 11433.08 | 96.03
12:00 | 0 | 34 | 52 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 25 | 68 | 18 | 0 | 0 | 17 | 0 | 0 | 400 | 306 | 0 | 0 | 0 | 335 | 0 | 0 | 5 | 0 | 28.5 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 1 | 202 | 0 | 2 | 201 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 950 | 16 | 51 | 0 | 91 | 0 | 300 | 340 | 48 | 207 | 18 | 31 | 0 | 34 | 0 | 19 | 0 | 30 | 0 | 19 | 0 | 310 | 320 | 388 | 0 | 0 | 156 | 6 | 0 | 76 | 30 | 0 | 18 | 172 | 0 | 86 | 0 | 30 | 1 | 9.47 | 12 | 6445.97 | 902 | 213 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 50.02 | 812 | 0 | 971.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 4.35 | 0 | 0 | 150 | 0 | 140 | 0 | 414 | 0 | 0.85 | 170 | 50 | 0 | 15 | 34 | 0 | 0 | 7.7 | 181 | 0.24 | 0 | 173 | 4 | 100 | 220 | 0 | 0 | 867 | 0 | 5529.98 | 11975.95 | 96.07
13:00 | 0 | 50 | 52 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 35 | 68 | 16 | 0 | 0 | 17 | 0 | 0 | 400 | 296 | 0 | 0 | 0 | 335 | 0 | 0 | 4 | 0 | 27 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 12 | 24 | 0 | 202 | 0 | 9 | 208 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 980 | 11 | 51 | 0 | 96 | 0 | 300 | 340 | 46 | 198 | 20 | 34 | 0 | 34 | 0 | 19 | 0 | 30 | 0 | 24 | 0 | 305 | 320 | 371 | 0 | 0 | 157 | 6 | 0 | 77 | 30 | 0 | 18 | 172 | 0 | 65 | 38 | 31 | 0 | 10.91 | 12 | 6505.91 | 902 | 210 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2.52 | 844 | 0 | 951.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 3.47 | 0 | 0 | 150 | 0 | 140 | 0 | 414 | 0 | 0.3 | 160 | 50 | 0 | 8 | 34 | 0 | 0 | 4.7 | 180 | 0.11 | 0 | 172 | 3 | 100 | 220 | 0 | 0 | 895 | 0 | 5520.5 | 12026.41 | 96.11
14:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 37 | 0 | 0 | 0 | 17 | 35 | 0 | 300 | 294 | 0 | 0 | 0 | 280 | 0 | 0 | 6 | 0 | 29 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 12 | 24 | 0.11 | 202 | 0 | 5 | 365 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 955 | 8 | 51 | 0 | 86 | 0 | 300 | 330 | 46 | 195 | 20 | 34 | 0 | 34 | 0 | 20 | 0 | 30 | 0 | 15 | 0 | 300 | 320 | 319 | 0 | 0 | 138 | 6 | 0 | 77 | 20 | 0 | 18 | 172 | 0 | 45 | 82 | 34 | 0 | 8.79 | 6 | 6366.9 | 902 | 201 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3.8 | 802 | 0 | 985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 12.52 | 0 | 0 | 140 | 0 | 130 | 0 | 343 | 0 | 1.29 | 204 | 49 | 0 | 17 | 34 | 0 | 0 | 2.8 | 183 | 0.14 | 0 | 169 | 5 | 120 | 220 | 0 | 0 | 803 | 0 | 5397.55 | 11764.45 | 96.16
15:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 35 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 350 | 305 | 0 | 0 | 0 | 335 | 0 | 0 | 7 | 0 | 26 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0.26 | 202 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 860 | 13 | 51 | 0 | 53 | 0 | 354 | 305 | 49 | 204 | 20 | 34 | 0 | 34 | 7 | 20 | 0 | 28 | 0 | 9 | 0 | 305 | 320 | 322 | 0 | 0 | 144 | 6 | 0 | 77 | 20 | 0 | 18 | 172 | 0 | 45 | 82 | 33 | 0 | 9.87 | 12 | 6425.13 | 902 | 200 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3.65 | 770 | 0 | 978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 8.96 | 0 | 0 | 140 | 0 | 130 | 0 | 373 | 0 | 0.89 | 204 | 50 | 0 | 10 | 34 | 0 | 0 | 7.7 | 55 | 0.08 | 0 | 172 | 7 | 120 | 220 | 0 | 0 | 800 | 0 | 5239.28 | 11664.41 | 96.21
16:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 6 | 0 | 35 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 350 | 294 | 0 | 0 | 0 | 335 | 0 | 0 | 7 | 0 | 23 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0.24 | 172 | 0 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 855 | 1 | 51 | 0 | 53 | 0 | 354 | 305 | 52 | 196 | 20 | 34 | 0 | 34 | 9 | 20 | 0 | 26 | 0 | 8 | 0 | 305 | 320 | 319 | 0 | 0 | 137 | 6 | 0 | 77 | 20 | 0 | 18 | 172 | 0 | 45 | 65 | 33 | 0 | 7.12 | 12 | 6385.36 | 901 | 200 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4.45 | 745 | 0 | 978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 4.35 | 0 | 0 | 140 | 0 | 130 | 0 | 346 | 0 | 0.45 | 202 | 51 | 0 | 9 | 34 | 0 | 0 | 2.5 | 54 | 0.03 | 0 | 170 | 6 | 120 | 220 | 0 | 0 | 740 | 0 | 5109.78 | 11495.14 | 96.25
17:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 3 | 0 | 35 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 300 | 297 | 0 | 0 | 0 | 335 | 0 | 0 | 1 | 0 | 24 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0.22 | 172 | 0 | 2 | 525 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 850 | 2 | 51 | 0 | 53 | 0 | 300 | 305 | 52 | 199 | 20 | 34 | 0 | 34 | 25 | 20 | 0 | 28 | 0 | 1 | 0 | 300 | 320 | 321 | 0 | 0 | 133 | 6 | 0 | 53 | 20 | 0 | 18 | 172 | 0 | 45 | 65 | 33 | 0 | 1.49 | 12 | 6292.71 | 902 | 200 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7.67 | 735 | 0 | 877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2.46 | 0 | 0 | 140 | 0 | 130 | 0 | 346 | 0 | 0.28 | 182 | 49 | 0 | 3 | 34 | 0 | 0 | 1.5 | 17 | 0.02 | 0 | 171 | 0 | 120 | 220 | 0 | 0 | 650 | 0 | 4827.93 | 11120.64 | 96.29
18:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 7 | 0 | 35 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 300 | 310 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 24 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0.03 | 172 | 0 | 8 | 568 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 905 | 0 | 51 | 0 | 26 | 0 | 280 | 305 | 52 | 208 | 20 | 34 | 0 | 34 | 28 | 20 | 0 | 26 | 0 | 0 | 0 | 305 | 320 | 337 | 0 | 0 | 139 | 6 | 0 | 22 | 20 | 0 | 18 | 172 | 0 | 45 | 68 | 33 | 0 | 0.83 | 13 | 6319.86 | 902 | 200 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 750 | 0 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.99 | 0 | 0 | 140 | 0 | 130 | 0 | 346 | 0 | 0.18 | 201 | 51 | 0 | 3 | 34 | 0 | 0 | 0.5 | 5 | 0.01 | 0 | 175 | 0 | 120 | 220 | 0 | 0 | 667 | 0 | 4877.68 | 11197.54 | 96.33
19:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 48 | 0 | 35 | 25 | 64 | 0 | 0 | 17 | 32 | 0 | 300 | 299 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 52 | 25 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 16 | 33 | 0 | 0 | 24 | 48 | 0 | 172 | 0 | 7 | 631 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 36 | 0 | 280 | 305 | 52 | 199 | 20 | 31 | 0 | 55 | 38 | 20 | 40 | 32 | 16 | 0 | 0 | 310 | 320 | 319 | 0 | 0 | 141 | 6 | 0 | 79 | 20 | 0 | 18 | 172 | 0 | 75 | 125 | 33 | 0 | 0 | 12 | 6914 | 902 | 200 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 776 | 10 | 956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 130 | 0 | 348 | 0 | 0 | 204 | 50 | 85 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 8 | 120 | 220 | 0 | 0 | 760 | 0 | 5265 | 12179 | 96.37
19:30 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 46 | 0 | 35 | 51 | 48 | 0 | 0 | 17 | 16 | 0 | 400 | 296 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 25 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 22 | 33 | 0 | 0 | 24 | 48 | 0 | 172 | 0 | 10 | 752 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 890 | 0 | 51 | 0 | 63 | 0 | 357 | 330 | 52 | 197 | 20 | 21 | 0 | 136 | 38 | 20 | 46 | 30 | 16 | 0 | 10 | 305 | 320 | 345 | 0 | 0 | 143 | 6 | 0 | 79 | 30 | 0 | 18 | 172 | 0 | 75 | 110 | 34 | 0 | 0 | 12 | 7459 | 902 | 200 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 896 | 17 | 1009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 130 | 0 | 342 | 0 | 0 | 204 | 50 | 110 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 9 | 120 | 220 | 0 | 0 | 900 | 0 | 5633 | 13092 | 96.37
20:00 | 0 | 52 | 34 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 77 | 0 | 35 | 51 | 48 | 0 | 0 | 0 | 16 | 0 | 400 | 293 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 26 | 22 | 0 | 430 | 0 | 0 | 0 | 0 | 30 | 33 | 0 | 0 | 24 | 48 | 0 | 212 | 0 | 15 | 707 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 868 | 0 | 51 | 0 | 70 | 0 | 356 | 335 | 52 | 191 | 20 | 24 | 0 | 134 | 38 | 21 | 44 | 32 | 16 | 0 | 21 | 300 | 320 | 345 | 0 | 0 | 152 | 6 | 0 | 78 | 30 | 0 | 18 | 172 | 0 | 65 | 110 | 34 | 0 | 0 | 12 | 7482 | 902 | 200 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 874 | 17 | 1010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 130 | 0 | 332 | 0 | 0 | 203 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 8 | 120 | 220 | 0 | 0 | 900 | 0 | 5549 | 13031 | 96.41
21:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 188 | 0 | 35 | 36 | 32 | 0 | 0 | 0 | 0 | 0 | 350 | 306 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 26 | 22 | 0 | 380 | 0 | 0 | 0 | 0 | 26 | 17 | 0 | 0 | 12 | 12 | 0 | 212 | 0 | 25 | 713 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 853 | 0 | 51 | 0 | 63 | 0 | 355 | 340 | 52 | 203 | 20 | 17 | 0 | 136 | 38 | 18 | 44 | 36 | 16 | 0 | 23 | 305 | 320 | 385 | 0 | 0 | 134 | 6 | 0 | 81 | 30 | 0 | 18 | 172 | 0 | 65 | 95 | 34 | 0 | 0 | 12 | 7336 | 902 | 200 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 834 | 0 | 984.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 130 | 0 | 351 | 0 | 0 | 202 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 120 | 220 | 0 | 0 | 895 | 0 | 5488.02 | 12824.02 | 96.45
22:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 266 | 0 | 35 | 33 | 32 | 0 | 0 | 0 | 0 | 0 | 300 | 302 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 25.5 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 21 | 17 | 0 | 0 | 12 | 12 | 0 | 212 | 0 | 28 | 704 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 855 | 0 | 51 | 0 | 63 | 0 | 355 | 340 | 52 | 200 | 20 | 17 | 0 | 136 | 26 | 14 | 48 | 34 | 16 | 0 | 23 | 305 | 320 | 387 | 0 | 0 | 141 | 6 | 0 | 81 | 30 | 0 | 18 | 172 | 0 | 65 | 95 | 33 | 0 | 0 | 12 | 7304.5 | 902 | 204 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 860 | 0 | 979.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 130 | 0 | 351 | 0 | 0 | 202 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 9 | 120 | 220 | 0 | 0 | 897 | 0 | 5516.86 | 12821.36 | 96.49
23:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 307 | 0 | 35 | 33 | 32 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 17 | 23 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 15 | 17 | 0 | 0 | 12 | 12 | 0 | 212 | 0 | 28 | 712 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 63 | 0 | 356 | 340 | 52 | 200 | 20 | 17 | 0 | 136 | 28 | 18 | 47 | 34 | 16 | 0 | 23 | 290 | 320 | 384 | 0 | 0 | 136 | 6 | 0 | 81 | 30 | 0 | 18 | 171 | 0 | 65 | 95 | 33 | 0 | 0 | 12 | 7221 | 902 | 203 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 841 | 0 | 975.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 130 | 0 | 346 | 0 | 0 | 201 | 51 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 9 | 120 | 220 | 0 | 0 | 900 | 0 | 5491.26 | 12712.26 | 96.53
Total KWH | 0 | 590400 | 648000 | 0 | 0 | 0 | 0 | 0 | 8679600 | 0 | 1042740 | 0 | 542520 | 571248 | 250560 | 0 | 0 | 186931 | 86400 | 0 | 8685000 | 7264320 | 0 | 0 | 0 | 7693712 | 0 | 0 | 36311 | 159600 | 580200 | 522720 | 0 | 9305454.55 | 0 | 0 | 0 | 0 | 1097760 | 114116 | 0 | 0 | 115200 | 177600 | 3602 | 4445485 | 0 | 411360 | 8705454.55 | 0 | 0 | 0 | 0 | 0 | 5242377 | 0 | 0 | 0 | 21365452 | 89775 | 1205615 | 0 | 1973818 | 0 | 8292700 | 7878000 | 1226880 | 4937000 | 445680 | 718080 | 0 | 1291680 | 291480 | 448190 | 343140 | 717120 | 95006 | 78200 | 129024 | 7153500 | 7684800 | 8589000 | 0 | 0 | 3471954 | 143208 | 0 | 1759680 | 661440 | 0 | 439000 | 3543930 | 70920 | 1294800 | 2006400 | 913920 | 3600 | 109440 | 193680 | 156724783.1 | 21603636 | 4948992 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 145440 | 19250909 | 32640 | 22216364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201810 | 0 | 58496 | 0 | 0 | 3791755 | 0 | 3564309 | 0 | 8865454 | 0 | 5460 | 4839000 | 1174254 | 1138750 | 148843 | 1506220 | 0 | 0 | 43368.6 | 898560 | 973.5 | 0 | 4407000 | 138117 | 2705000 | 5341350 | 0 | 0 | 20071272.73 | 0 | 128009973.83 | 284734756.93

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 09-07-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11975.95 | MW | 12:00 Hr. | Energy Generated |  |  | 284.7348 |  | MKWHr.
| Day Peak Demand |  |  | 11975.95 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 13092 | MW | 19:30 Hr. | Energy Demand |  |  | 284.7348 |  | MKWHr.
| Evening Peak Demand |  |  | 13092 | MW | 19:30 Hr. | Maximum Temperature |  |  | 29.1 |  | °C
| Minimum Generation of the Day |  |  | 10366.25 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 996.47 |  | MMCFD
| Maximum Generation of the Day |  |  | 13092 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 5.3661 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 43.7737 | 0 | 3.0357 | 0 | 0 | 0.036311 | 0 | 0 | 46.8457 | Gas | 139.5508 | Gas | 492284440.2435
| Chattogram Zone |  |  | 5.6537 | 30.0709 | 0.40692 | 0 | 4.4455 | 0.093377 | 0 | 1.0978 | 41.7682 | Coal | 79.8133 | Coal | 541541688.4865
| Cumilla Zone |  |  | 26.4079 | 0 | 2.8684 | 0 | 0 | 0.0782 | 0.71712 | 0 | 30.0716 | HFO | 12.5544 | HFO | 236091822.56
| Mymensingh Zone |  |  | 0.91392 | 0 | 3.5658 | 0 | 0 | 0.11304 | 0 | 0 | 4.5928 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 33.4465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.4465 | Hydro | 4.4455 | Hydro | 444548.5
| Khulna Zone |  |  | 4.949 | 19.2509 | 0.03264 | 0 | 0 | 0.14544 | 22.5156 | 0 | 46.8936 | Solar | 1.8239 | Solar | 31630854.571
| Barishal Zone |  |  | 8.1845 | 24.4783 | 0 | 0 | 0 | 0.0009735 | 0 | 0 | 32.6637 | Import | 45.4491 | Import | 209848553.64
| Rajshahi Zone |  |  | 16.2215 | 0 | 0 | 0 | 0 | 0.26577 | 22.2164 | 0 | 38.7036 | Wind | 1.0978 | Wind | 16071206.4
| Rangpur Zone |  |  | 0 | 6.0133 | 2.645 | 0 | 0 | 1.0908 | 0 | 0 | 9.749
| Total |  |  | 139.5508 | 79.8133 | 12.5544 | 0 | 4.4455 | 1.8239 | 45.4491 | 1.0978 | 284.7348
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 492284440.2435 |  | Hydro | 444548.5
|  |  |  | Coal | 541541688.4865 |  | Solar | 31630854.571
|  |  |  | HFO | 236091822.56 |  | Import | 209848553.64
|  |  |  | HSD | 0 |  | Wind | 16071206.4
[5 empty] | Total: | 152,79,13,114 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.6036 | Peak Hr Flow | 902.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 54870809.25 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 22.2164 | Peak Hr Flow | 1009.00 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 656 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.71712 | Peak Hr Flow | 30.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 896 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 44.5371 | Peak Hr Flow | 1941.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4618
|  |  |  | Chattogram |  | 0 |  | 1270
|  |  |  | Cumilla |  | 0 |  | 1111
|  |  |  | Mymensingh |  | 0 |  | 967
|  |  |  | Sylhet |  | 0 |  | 494
|  |  |  | Khulna |  | 0 |  | 1518
|  |  |  | Barishal |  | 0 |  | 384
|  |  |  | Rajshahi |  | 0 |  | 1247
|  |  |  | Rangpur |  | 0 |  | 939
|  |  |  | Total |  | 0 |  | 12548
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Chowmuhani 113 MW |  |  | 113
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
[7 empty] | 4 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 5 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[5 empty] | Total | 300 |  |  |  | Total | 589
|  |  |  | Total Unavailable Capacity |  |  |  | 889
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:32 | 17:00 | Rahanpur 400/132kV S/S AT-02 LT Project Work S/D Due to Due to project painting work
| 08:32 | 17:00 | Rahanpur 400/132kV S/S AT-02 HT Project Work S/D Due to Due to project painting work.
| 09:14 | 13:34 | Bogura 230/132kV S/S T-01 LT Scheduled S/D Due to City Test
| 09:14 | 13:34 | Bogura 230/132kV S/S T-01 HT Scheduled S/D Due to City test
| 09:25 | 09:56 | Kabirpur -Tongi 132kV Ckt-1 Tripped from Tongi 230/132/33kV end showing N/A relays Due
to Bad weather
| 09:25 | 09:55 | Kabirpur -Tongi 132kV Ckt-2 Tripped from Kabirpur 132/33kV end showing MCGG (Static | [7 empty] | 75.0MW load
|  |  | Relay) relays Due to Over current A& C Phase | [7 empty] | interrup. Kabirpur
132/33kV end
| 09:25 | 10:14 | Kabirpur 132/33kV S/S XFR, T-3 LT Tripped showing MiCom P 127 relays Due to Single line | [7 empty] | 70.0MW load
|  |  | to ground Fault | [7 empty] | interrup.
| 10:40 | 11:12 | Kabirpur -Tongi 132kV Ckt-1 Tripped from Tongi 230/132/33kV end showing N/A relays Due
to Bad weather
| 10:40 | 11:20 | Kabirpur -Tongi 132kV Ckt-2 Tripped from Kabirpur 132/33kV end showing MCGG (Static | [7 empty] | 35.0MW load
|  |  | Relay) relays Due to Over current A & C Phase | [7 empty] | interrup. Kabirpur
132/33kV end
| 10:47 | 21:03 | Khulna(S)-PDB 330MW CCPP 230kV Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end Due to
DFDR Intregration work
| 11:13 | 15:28 | Kabirpur -Tongi 132kV Ckt-1 Tripped from Tongi 230/132/33kV end showing N/A relays Due
to Bad weather
| 11:56 | 13:45 | Khulshi 132/33kV S/S 415T (T2) LT Scheduled S/D Due to 33 kv loop mainteaance
| 11:57 | 13:43 | Khulshi 132/33kV S/S 415T (T2) HT Scheduled S/D Due to 33 kv loop maintenance
| 11:58 |  | Matarbari 2*600 MW (CPGCBL) Synchronized with remarks:- U2
| 12:00 |  | Day Peak Generation: 11972 MW.
| 15:30 | 17:40 | Rangpur 132/33kV S/S 33KV Bus Scheduled S/D Due to temparature high | [7 empty] | 85.0MW load
interrup.
| 15:47 |  | JERA Meghnaghat Power Limited 718 MW CCPP GT was sync.
| 17:02 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is OFF with remarks:-
|  | 17:19 | Mirzapur 132/33kV S/S Transformer-02(E07) HT is restored.
|  | 17:51 | Shahjibazar-Sreemangal 132kV Ckt-1 is restored.
|  | 17:51 | Shahjibazar-Sreemangal 132kV Ckt-1 is restored.
| 19:30 |  | Evening Peak Generation 13092 MW.
|  | 19:45 | Siddhirganj 132/33kV S/S T-1 HT is restored.
| 19:46 |  | BIPTC S/S 10CF23 Tripped showing - relays Due to SF6 Protection operated (T1 CT)
| 20:15 | 21:00 | Chowmuhani 132/33kV S/S TR2 Scheduled S/D Due to 33KV L Bus Incoming DS B Phase (red | [7 empty] | 30.0MW load
|  |  | hot) Loop Maintenance. | [7 empty] | interrup.
| 21:07 |  | Saidpur - Saidpur 150 MW PS 132 KV syn.
| 21:37 | 23:30 | Chowmuhani 132/33kV S/S TR3 Scheduled S/D Due to Red Hot Maintenance | [7 empty] | 30.0MW load
interrup.
| 02:03 |  | HVDC(Nepal) Shutdown
| 07:19 |  | Chuadanga 132/33kV S/S 132kV Tr. T3 LT Forced S/D Due to Red hot maintenance work | [7 empty] | 12.0MW load
interrup.
| 07:20 |  | Chuadanga 132/33kV S/S 132kV Tr. T3 HT Forced S/D Due to Red hot maintenance work | [7 empty] | 12.0MW load
interrup.
| 07:24 | 07:30 | Narshingdi 132/33kV S/S T-4 LT Tripped showing Lockout operated relays Due to df/dt fault | [7 empty] | 7.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 09-07-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 406 | 8679600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 8685000 | Allocation limit by Titas, instructed by DS(Gen)
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 296 | 7264320 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7693712 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 0 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 48 | 250560 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 186931 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 25 | 580200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 522720 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 34 | 648000 | Engine Problem
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 51 | 571248 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 590400 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 16 | 86400 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 36311 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 542520 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 400 | 9305454.55 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 46 | 1042740 | Gas shortage instructed by DS(Gen)
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 52 | 159600 | Engine Problem
Dhaka Area Total |  |  |  |  | 5939.724 | 2253 | 46845716.55
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 89775 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 172 | 4445485 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 219 | 5242377 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 33 | 114116 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 115200 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 10 | 411360 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 3602 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 48 | 177600 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 890 | 21365452 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 22 | 1097760 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 752 | 8705454.55 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.72 | 2170 | 41768181.55
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 197 | 4937000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 357 | 8292700
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 330 | 7878000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 20 | 445680 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 52 | 1226880 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 63 | 1973818 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1205615 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 10 | 129024 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 136 | 1291680 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 30 | 717120 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 16 | 95006 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 448190 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 46 | 343140 | Engine Problem
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 291480 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 21 | 718080 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 78200 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1387 | 30071613
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 34 | 913920 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 3600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 110 | 2006400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 75 | 1294800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 109440 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 193680 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 70920 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 231 | 4592760
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | Gas shortage instructed by DS(Gen)
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 143 | 3471954 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 661440 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 1759680 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 172 | 3543930 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 439000 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 6 | 143208 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7153500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 345 | 8589000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7684800 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1418 | 33446512
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 902 | 21603636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 200 | 4948992 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 32640 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 145440 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 896 | 19250909 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2053 | 46893617
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 9 | 138117 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2705000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 900 | 20071272.73 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5341350 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 248 | 4407000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 973.5 | -
Barishal Area Total |  |  |  |  | 2236 | 1497 | 32663713.23
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 140 | 3791755 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 130 | 3564309 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 342 | 8865454 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 5460 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1009 | 22216364 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 58496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 201810 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 1621 | 38703648
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1174254 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 204 | 4839000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 1506220 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 43368.6 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 110 | 1138750 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 148843 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 898560 | -
Rangpur Area Total |  |  |  |  | 950 | 462 | 9748995.6
Eastern Grid Total |  |  |  |  | 16705.895 | 7459 | 156724783.1
Western Grid Total |  |  |  |  | 10378.16 | 5633 | 128009973.83
National Grid Total |  |  |  |  | 27084.055 | 13092 | 284734756.93
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 09-07-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8458.89 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4088.1 | MW
i) Dhaka area |  |  | 4617.52 |  | MW | i) Khulna area |  |  |  | 1518 | MW
ii) Chattogram area |  |  | 1269.5 |  | MW | ii) Barishal area |  |  |  | 384.5 | MW
iii) Cumilla area |  |  | 1110.87 |  | MW | iii) Rajshahi area |  |  |  | 1246.6 | MW
iv) Mymensingh area |  |  | 967 |  | MW | iv) Rangpur area |  |  |  | 939 | MW
v) Sylhet area |  |  | 494 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12546.99 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 69 | 18:30 | 133 | Pabna | 106 | 19:30
2 | AKSML | 127 | 17:00 | 68 | Ishurdi | 69 | 19:30 | 134 | Palashbari | 110 | 00:00
3 | Aftabnagar | 34 | 12:00 | 69 | Jaldhaka | 86 | 01:00 | 135 | Panchagarh | 64 | 00:00
4 | Agargaon | 114 | 14:00 | 70 | Jamalpur | 110 | 00:00 | 136 | Patuakhali | 67 | 22:00
5 | Agrabad | 82 | 15:00 | 71 | Jashore | 120 | 19:30 | 137 | Payra | 30 | 00:00
6 | Amnura | 37 | 00:00 | 72 | Jhenaidah | 104 | 19:30 | 138 | Postogola | 53 | 13:00
7 | Ashuganj | 73 | 00:00 | 73 | Joydebpur | 125 | 12:00 | 139 | Purbachal | 17 | 21:00
8 | BSRM | 205 | 00:00 | 74 | Joypurhat | 59 | 00:00 | 140 | Purbasadipur | 131 | 00:00
9 | Bagerhat | 74 | 21:00 | 75 | Juldah | 13.5 | 23:00 | 141 | Rahanpur | 28 | 00:00
10 | Bajitpur | 59 | 00:00 | 76 | KSRM | 24 | 23:00 | 142 | Rahim | 32 | 16:00
11 | Bakulia | 82 | 20:00 | 77 | Kabirpur | 221 | 09:00 | 143 | Rajbari | 68 | 00:00
12 | Banani | 31.6 | 13:00 | 78 | Kachua | 72 | 19:00 | 144 | Rajendrapur | 115 | 00:00
13 | Bangabhaban | 16 | 11:00 | 79 | Kallyanpur | 99 | 13:00 | 145 | Rajshahi | 107 | 00:00
14 | Barapukuria | 58 | 22:00 | 80 | Kalurghat | 38 | 23:00 | 146 | Rajshahi-230 | 72 | 13:00
15 | Barguna | 20 | 21:00 | 81 | Kamrangirchar | 66 | 13:00 | 147 | Ramganj | 104 | 23:00
16 | Barishal | 101 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Rampur | 47 | 12:00
17 | Barishal-230 | 94 | 21:00 | 83 | Kasba | 27 | 00:00 | 149 | Rangamati | 14 | 19:30
18 | Baroaulia | 54 | 10:00 | 84 | Kazla | 92 | 11:00 | 150 | Rangpur | 148 | 18:30
19 | Baroirhat | 51 | 19:30 | 85 | Keranigonj | 84 | 13:00 | 151 | Ruppur | 6.6 | 11:00
20 | Bashundhara | 155 | 13:00 | 86 | Khagrachori | 26 | 19:00 | 152 | SSM | 5 | 23:00
21 | BashundharaCement | 7 | 00:00 | 87 | Khulna | 63 | 12:00 | 153 | Saidpur | 101 | 12:00
22 | Beanibazar | 72 | 00:00 | 88 | Khulshi | 130 | 22:00 | 154 | Satkhira | 112 | 19:30
23 | Benapole | 54 | 00:00 | 89 | Kishoreganj | 109 | 22:00 | 155 | Satmasjid | 75 | 13:00
24 | Bhaluka | 123 | 11:00 | 90 | Kodda | 320 | 10:00 | 156 | Savar | 210 | 16:00
25 | Bhandaria | 46 | 21:00 | 91 | Kulaura | 46 | 20:00 | 157 | SevenRings | 2.99 | 05:00
26 | Bhangura | 29 | 00:00 | 92 | Kurigram | 64 | 00:00 | 158 | ShahCement | 24 | 00:00
27 | Bheramara(GK) | 55 | 00:00 | 93 | Kushtia | 140 | 00:00 | 159 | Shahjadpur | 67 | 20:00
28 | Bhulta | 237 | 13:00 | 94 | Lakshmipur | 30 | 22:00 | 160 | Shahjibazar | 104 | 00:00
29 | Bog-Sherpur | 60 | 00:00 | 95 | Lalbag | 56 | 13:00 | 161 | Shahmirpur | 60 | 17:00
30 | Bogura | 155 | 00:00 | 96 | Lalmonirhat | 66 | 00:00 | 162 | Shariatpur | 74 | 22:00
31 | Borhanuddin | 77 | 22:00 | 97 | MI_Cement | 3.8 | 23:00 | 163 | Sherpur | 126 | 00:00
32 | Brahmanbaria | 104 | 00:00 | 98 | Madanganj | 46 | 13:00 | 164 | Shikalbaha | 14 | 18:00
33 | Cantonment | 134 | 13:00 | 99 | Madaripur | 90 | 22:00 | 165 | Shitalakhya | 70.5 | 11:00
34 | Chandina | 9.87 | 19:30 | 100 | Madartek | 73.86 | 22:00 | 166 | Sholosohor | 39 | 10:00
35 | Chandpur | 66 | 21:00 | 101 | Madunaghat | 46 | 19:30 | 167 | Shyampur | 162 | 12:00
36 | Chandraghona | 31 | 19:30 | 102 | Magura | 53 | 19:30 | 168 | Siddhirganj | 108 | 10:00
37 | Chapai | 68 | 00:00 | 103 | Mahasthangarh | 76 | 00:00 | 169 | Sirajganj | 90 | 21:00
38 | Charsaidpur | 24 | 01:00 | 104 | Maijdee | 11 | 21:00 | 170 | Sonargaon | 93 | 09:00
39 | Chauddagram | 54 | 00:00 | 105 | Manikganj | 110 | 21:00 | 171 | Sreemongol | 65 | 00:00
40 | Chhatak | 34 | 00:00 | 106 | Maniknagar | 78 | 13:00 | 172 | Sreepur | 91 | 21:00
41 | Chowmuhani | 146 | 19:30 | 107 | Matarbari | 43 | 19:30 | 173 | Srinagar | 37.99 | 22:00
42 | Chuadanga | 91 | 19:30 | 108 | Matuail | 62 | 12:00 | 174 | Sunamganj | 54 | 00:00
43 | Coxsbazar | 125 | 19:30 | 109 | Millgate | 106 | 09:00 | 175 | Sylhet | 44 | 00:00
44 | Cumilla(N) | 115 | 20:00 | 110 | Mirpur | 107 | 14:00 | 176 | Sylhet-132 | 101 | 21:00
45 | Cumilla(S) | 142 | 19:00 | 111 | Mirsorai | 10 | 15:00 | 177 | TK | 32 | 21:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirzapur | 41 | 19:30 | 178 | Tangail | 140 | 19:30
47 | Daudkandi | 130 | 21:00 | 113 | Mithapukur | 68 | 20:00 | 179 | Taraganj | 18 | 00:00
48 | Dhaka | 62 | 11:00 | 114 | Modern | N/A | N/A | 180 | Thakurgaon | 108 | 00:00
49 | Dhamrai | 114 | 16:00 | 115 | Mogbazar | 128.4 | 14:00 | 181 | Tongi | 123 | 12:00
50 | Dhanmondi | 126 | 13:00 | 116 | Mongla | 41 | 12:00 | 182 | Ullahpara | 31 | 19:30
51 | Dohazari | 91 | 19:00 | 117 | Motijheel | 38 | 13:00 | 183 | Ullon | 34 | 22:00
52 | Faridpur | 140 | 19:30 | 118 | Muktagacha | 30 | 01:00 | 184 | Uttara | 63 | 13:00
53 | Fatullah | 95 | 12:00 | 119 | Munshiganj | 94 | 22:00 | 185 | UttaraNew | 50 | 21:00
54 | Fenchuganj | 36 | 00:00 | 120 | Muradnagar | 29 | 02:00 | 186 | Zigatola | 68 | 13:00
55 | Feni | 89 | 22:00 | 121 | Mymensingh | 174 | 00:00
56 | GPH | 78 | 01:00 | 122 | Naogaon | 123 | 00:00
57 | Ghatail | 62 | 00:00 | 123 | Narail | 48 | 19:30
58 | Ghorashal | 12 | 00:00 | 124 | Narinda | 71 | 13:00
59 | Ghorashal-230 | 77 | 21:00 | 125 | Narshingdi | 162 | 00:00
60 | Goalpara | 33 | 13:00 | 126 | Natore | 128 | 00:00
61 | Gollamari | 82 | 17:00 | 127 | Nawabganj | 48 | 22:00
62 | Gopalganj | 86 | 19:30 | 128 | Netrakona | 111 | 19:30
63 | Gulshan | 104 | 13:00 | 129 | New | 56.6 | 11:00
64 | Halishahar | 71 | 12:00 | 130 | Niamatpur | 68 | 00:00
65 | HaripurSBU | 168 | 12:00 | 131 | Noapara | 39 | 20:00
66 | Hasnabad | 58 | 11:00 | 132 | PHP | 9 | 16:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 09-07-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 12936 | 0 |  | 12936
1:00 | 12493 | 0 |  | 12493
2:00 | 11987 | 0 |  | 11987
3:00 | 11424 | 0 |  | 11424
4:00 | 10949 | 0 |  | 10949
5:00 | 10756 | 0 |  | 10756
6:00 | 10366.25 | 0 |  | 10366.25
7:00 | 10521.79 | 0 |  | 10521.79
8:00 | 10817.49 | 0 |  | 10817.49
9:00 | 11086.49 | 0 |  | 11086.49
10:00 | 11176.24 | 0 |  | 11176.24
11:00 | 11433.08 | 0 |  | 11433.08
12:00 | 11975.95 | 0 |  | 11975.95
13:00 | 12026.41 | 0 |  | 12026.41
14:00 | 11764.45 | 0 |  | 11764.45
15:00 | 11664.41 | 0 |  | 11664.41
16:00 | 11495.14 | 0 |  | 11495.14
17:00 | 11120.64 | 0 |  | 11120.64
18:00 | 11197.54 | 0 |  | 11197.54
19:00 | 12179 | 0 |  | 12179
19:30 | 13092 | 0 |  | 13092
20:00 | 13031 | 0 |  | 13031
21:00 | 12824.02 | 0 |  | 12824.02
22:00 | 12821.36 | 0 |  | 12821.36
23:00 | 12712.26 | 0 |  | 12712.26
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 09-07-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6885 | 6051 | 12936 | DAILY GENERATION CURVE
00:30 | 6836 | 5878.5 | 12714.5
01:00 | 6787 | 5706 | 12493 | 09-07-2025
01:30 | 6696.5 | 5543.5 | 12240
02:00 | 6606 | 5381 | 11987
02:30 | 6456 | 5249.5 | 11705.5
03:00 | 6306 | 5118 | 11424
03:30 | 6121 | 5065.5 | 11186.5
04:00 | 5936 | 5013 | 10949
04:30 | 5931.5 | 4921 | 10852.5
05:00 | 5927 | 4829 | 10756
05:30 | 5741.6 | 4819.525 | 10561.125
06:00 | 5556.2 | 4810.05 | 10366.25
06:30 | 5597.28 | 4846.74 | 10444.02
07:00 | 5638.36 | 4883.43 | 10521.79
07:30 | 5768.745 | 4900.895 | 10669.64
08:00 | 5899.13 | 4918.36 | 10817.49
08:30 | 6002.29 | 4949.7 | 10951.99
09:00 | 6105.45 | 4981.04 | 11086.49
09:30 | 6150.59 | 4980.775 | 11131.365
10:00 | 6195.73 | 4980.51 | 11176.24
10:30 | 6233.88 | 5070.78 | 11304.66
11:00 | 6272.03 | 5161.05 | 11433.08
11:30 | 6359 | 5345.515 | 11704.515
12:00 | 6445.97 | 5529.98 | 11975.95
12:30 | 6475.94 | 5525.24 | 12001.18
13:00 | 6505.91 | 5520.5 | 12026.41
13:30 | 6436.405 | 5459.025 | 11895.43
14:00 | 6366.9 | 5397.55 | 11764.45
14:30 | 6396.015 | 5318.415 | 11714.43
15:00 | 6425.13 | 5239.28 | 11664.41
15:30 | 6405.245 | 5174.53 | 11579.775
16:00 | 6385.36 | 5109.78 | 11495.14
16:30 | 6339.035 | 4968.855 | 11307.89
17:00 | 6292.71 | 4827.93 | 11120.64
17:30 | 6306.285 | 4852.805 | 11159.09
18:00 | 6319.86 | 4877.68 | 11197.54
18:30 | 6616.93 | 5071.34 | 11688.27
19:00 | 6914 | 5265 | 12179
19:30 | 7459 | 5633 | 13092
20:00 | 7482 | 5549 | 13031
20:30 | 7409 | 5518.51 | 12927.51 |  | Executive Engineer
21:00 | 7336 | 5488.02 | 12824.02 |  | Network Operation Division
21:30 | 7320.25 | 5502.44 | 12822.69
22:00 | 7304.5 | 5516.86 | 12821.36
22:30 | 7262.75 | 5504.06 | 12766.81
23:00 | 7221 | 5491.26 | 12712.26

## En-Curve
QF-LDC-12
Date | 09-07-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3724 | 2252 | 876 | 38 | 34 | 1061 | 172 | 3986 | 0 | 97 | 636 | 0 | 0 | 60 | 0 | DAILY ENERGY CURVE
00:30 | 3716 | 2258 | 875.5 | 38 | 33 | 1011 | 172 | 3833 | 0 | 81.5 | 636 | 0 | 0 | 60.5 | 0 | 09-07-2025
01:00 | 3708 | 2264 | 875 | 38 | 32 | 961 | 172 | 3680 | 0 | 66 | 636 | 0 | 0 | 61 | 0
01:30 | 3716.5 | 2256.5 | 875 | 38 | 32 | 914.5 | 172 | 3499.5 | 0 | 37 | 636.5 | 0 | 0 | 62.5 | 0 | Energy Generated | 284.7348 |  | MKWHr
02:00 | 3725 | 2249 | 875 | 38 | 32 | 868 | 172 | 3319 | 0 | 8 | 637 | 0 | 0 | 64 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3705.5 | 2236.5 | 875 | 38 | 31 | 864.5 | 172 | 3208.5 | 0 | 4 | 507 | 0 | 0 | 63.5 | 0 | Total Energy Requirement | 284.7348 |  | MKWHr
03:00 | 3686 | 2224 | 875 | 38 | 30 | 861 | 172 | 3098 | 0 | 0 | 377 | 0 | 0 | 63 | 0
03:30 | 3675.5 | 2123 | 875 | 38 | 30 | 866.5 | 172 | 3052.5 | 0 | 0 | 294 | 0 | 0 | 60 | 0
04:00 | 3665 | 2022 | 875 | 38 | 30 | 872 | 172 | 3007 | 0 | 0 | 211 | 0 | 0 | 57 | 0
04:30 | 3653 | 2023 | 876 | 38 | 29 | 868.5 | 172 | 2926 | 0 | 0 | 209.5 | 0 | 0 | 57.5 | 0
05:00 | 3641 | 2024 | 877 | 38 | 28 | 865 | 172 | 2845 | 0 | 0 | 208 | 0 | 0 | 58 | 0
05:30 | 3564 | 1952 | 877 | 38 | 28 | 867 | 172 | 2824.5 | 6.625 | 0 | 181.5 | 0 | 0 | 50.5 | 0
06:00 | 3487 | 1880 | 877 | 38 | 28 | 869 | 172 | 2804 | 13.25 | 0 | 155 | 0 | 0 | 43 | 0
06:30 | 3505.5 | 1882 | 877 | 38 | 28 | 881 | 172 | 2813.5 | 27.02 | 8.5 | 169.5 | 0 | 0 | 42 | 0
07:00 | 3524 | 1884 | 877 | 38 | 28 | 893 | 172 | 2823 | 40.79 | 17 | 184 | 0 | 0 | 41 | 0
07:30 | 3602 | 1924.5 | 881.5 | 38 | 27 | 880.865 | 172 | 2836 | 64.275 | 17 | 194 | 0 | 0 | 32.5 | 0
08:00 | 3680 | 1965 | 886 | 38 | 26 | 868.73 | 172 | 2849 | 87.76 | 17 | 204 | 0 | 0 | 24 | 0
08:30 | 3690.5 | 2036 | 889 | 38 | 26 | 871.585 | 172 | 2855.5 | 114.405 | 25.5 | 191.5 | 0 | 0 | 42 | 0
09:00 | 3701 | 2107 | 892 | 38 | 26 | 874.44 | 172 | 2862 | 141.05 | 34 | 179 | 0 | 0 | 60 | 0
09:30 | 3692 | 2104.5 | 892 | 38 | 27 | 873.73 | 172 | 2880.5 | 124.635 | 34 | 233.5 | 0 | 0 | 59.5 | 0
10:00 | 3683 | 2102 | 892 | 38 | 28 | 873.02 | 172 | 2899 | 108.22 | 34 | 288 | 0 | 0 | 59 | 0
10:30 | 3715.5 | 2082.5 | 896.5 | 38 | 28 | 871.905 | 172 | 2926.5 | 172.755 | 39 | 303 | 0 | 0 | 59 | 0
11:00 | 3748 | 2063 | 901 | 38 | 28 | 870.79 | 172 | 2954 | 237.29 | 44 | 318 | 0 | 0 | 59 | 0
11:30 | 3735.5 | 2076.25 | 901.5 | 38 | 29 | 921.305 | 187 | 3088.5 | 279.96 | 74 | 312.5 | 0 | 0 | 61 | 0
12:00 | 3723 | 2089.5 | 902 | 38 | 30 | 971.82 | 202 | 3223 | 322.63 | 104 | 307 | 0 | 0 | 63 | 0
12:30 | 3710 | 2086.75 | 902 | 38 | 30 | 961.61 | 202 | 3266 | 304.82 | 111 | 340 | 0 | 0 | 49 | 0
13:00 | 3697 | 2084 | 902 | 38 | 30 | 951.4 | 202 | 3309 | 287.01 | 118 | 373 | 0 | 0 | 35 | 0
13:30 | 3598 | 2016.5 | 902 | 38 | 30 | 968.2 | 202 | 3328 | 288.73 | 93 | 384 | 0 | 0 | 47 | 0
14:00 | 3499 | 1949 | 902 | 38 | 30 | 985 | 202 | 3347 | 290.45 | 68 | 395 | 0 | 0 | 59 | 0
14:30 | 3584 | 1992 | 902 | 38 | 29 | 981.5 | 202 | 3285.5 | 215.43 | 68 | 356 | 0 | 0 | 61 | 0
15:00 | 3669 | 2035 | 902 | 38 | 28 | 978 | 202 | 3224 | 140.41 | 68 | 317 | 0 | 0 | 63 | 0
15:30 | 3661.5 | 2028.5 | 901.5 | 38 | 27 | 978 | 187 | 3197.5 | 126.275 | 68 | 309.5 | 0 | 0 | 57 | 0
16:00 | 3654 | 2022 | 901 | 38 | 26 | 978 | 172 | 3171 | 112.14 | 68 | 302 | 0 | 0 | 51 | 0
16:30 | 3628 | 1954 | 901.5 | 38 | 27 | 927.5 | 172 | 3166.5 | 75.89 | 68 | 310 | 0 | 0 | 39.5 | 0
17:00 | 3602 | 1886 | 902 | 38 | 28 | 877 | 172 | 3162 | 39.64 | 68 | 318 | 0 | 0 | 28 | 0
17:30 | 3579 | 1874 | 902 | 38 | 27 | 884 | 172 | 3239.5 | 26.59 | 68 | 321.5 | 0 | 0 | 27.5 | 0
18:00 | 3556 | 1862 | 902 | 38 | 26 | 891 | 172 | 3317 | 13.54 | 68 | 325 | 0 | 0 | 27 | 0
18:30 | 3542.5 | 1918 | 902 | 38 | 29 | 923.5 | 172 | 3429 | 6.77 | 160.5 | 545.5 | 0 | 0 | 21.5 | 0
19:00 | 3529 | 1974 | 902 | 38 | 32 | 956 | 172 | 3541 | 0 | 253 | 766 | 0 | 0 | 16 | 0
19:30 | 3715 | 2147 | 902 | 38 | 30 | 1009 | 172 | 3940 | 0 | 247 | 870 | 0 | 0 | 22 | 0
20:00 | 3705 | 2221 | 902 | 38 | 32 | 1010 | 212 | 3794 | 0 | 240 | 847 | 0 | 0 | 30 | 0
20:30 | 3730 | 2229 | 902 | 38 | 34 | 997.01 | 212 | 3770 | 0 | 198.5 | 789 | 0 | 0 | 28 | 0
21:00 | 3755 | 2237 | 902 | 38 | 36 | 984.02 | 212 | 3746 | 0 | 157 | 731 | 0 | 0 | 26 | 0
21:30 | 3754 | 2236.25 | 902 | 38 | 35 | 981.94 | 212 | 3757.5 | 0 | 157 | 725.5 | 0 | 0 | 23.5 | 0
22:00 | 3753 | 2235.5 | 902 | 38 | 34 | 979.86 | 212 | 3769 | 0 | 157 | 720 | 0 | 0 | 21 | 0
22:30 | 3724 | 2220.75 | 902 | 38 | 34 | 977.56 | 212 | 3763 | 0 | 157 | 720.5 | 0 | 0 | 18 | 0
23:00 | 3695 | 2206 | 902 | 38 | 34 | 975.26 | 212 | 3757 | 0 | 157 | 721 | 0 | 0 | 15 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 09-07-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 392 | 05:00 | 87 | 09:00 | Payra | 417 | 05:00 | 412 | 00:00
Ashuganj | 409 | 3:00 | 387 | 14:00 | Rahanpur | 398 | 17:00 | 383 | 00:00
Bhulta | 405 | 03:00 | 388 | 15:00 | Rampal | 406 | 03:00 | 396 | 00:00
Bibiana | 390 | 02:00 | 386 | 15:00
BIPTC | 402 | 05:00 | 395 | 21:00
Bogura | 388 | 17:00 | 372 | 00:00
Gopalganj | 404 | 05:00 | 393 | 22:00
Kaliakoir | 381 | 05:00 | 371 | 15:00
Madunaghat | 400 | 06:00 | 392 | 00:00
Meghnaghat | 395 | 05:00 | 378 | 18:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 229 | 05:00 | 221 | 12:00 | Keranigonj | 227 | 05:00 | 219 | 12:00
AKSML | 235 | 06:00 | 227 | 00:00 | Khulna(S) | 233 | 05:00 | 222 | 21:00
Aminbazar | 230 | 04:00 | 222 | 12:00 | Madunaghat | 235 | 07:00 | 230 | 00:00
Ashuganj | 236 | 05:00 | 228 | 15:00 | Madunaghat-400 | 236 | 05:00 | 231 | 00:00
Ashuganj-400 | 236 | 5:00 | 228 | 23:00 | Maniknagar | 224 | 04:00 | 218 | 12:00
Baghabari | 235 | 04:00 | 228 | 20:00 | Meghnaghat | 232 | 06:00 | 225 | 11:00
Barapukuria | 227 | 17:00 | 217 | 00:00 | Meghnaghat-400 | 228 | 05:00 | 222 | 12:00
Barapukuria-230 | 227 | 17:00 | 218 | 23:00 | Mirsorai | 231 | 03:00 | 224 | 00:00
Barishal | 235 | 06:00 | 228 | 00:00 | Rajshahi | 234 | 05:00 | 224 | 19:30
Bheramara | 233 | 03:00 | 223 | 23:00 | Rampal | 233 | 04:00 | 223 | 19:30
Bhulta | 234 | 05:00 | 218 | 16:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 232 | 05:00 | 226 | 00:00 | Rampura | 233 | 05:00 | 221 | 12:00
BIPTC | 237 | 05:00 | 224 | 23:00 | Shikalbaha | 233 | 07:00 | 227 | 00:00
Bogura | 235 | 17:00 | 224 | 01:00 | Shyampur | 227 | 06:00 | 220 | 12:00
Bogura-400 | 236 | 17:00 | 225 | 00:00 | Siddhirganj | 224 | 04:00 | 220 | 12:00
Borhanuddin | 241 | 16:00 | 234 | 00:00 | Sirajgonj | 239 | 04:00 | 235 | 00:00
BSRM | 231 | 03:00 | 223 | 00:00 | Sreepur | 230 | 05:00 | 224 | 00:00
Cumilla(N) | 226 | 06:00 | 220 | 00:00 | Tongi | 227 | 07:00 | 222 | 12:00
Faridpur | 231 | 05:00 | 224 | 00:00
Fenchuganj | 232 | 06:00 | 227 | 08:00
Ghorashal | 240 | 04:00 | 230 | 00:00
Ghorashal-230 | 232 | 05:00 | 222 | 15:00
Gopalganj | 232 | 05:00 | 225 | 22:00
GPH | 232 | 05:00 | 226 | 00:00
Haripur | 225 | 05:00 | 220 | 00:00
Hasnabad | 227 | 07:00 | 220 | 12:00
Hathazari | 233 | 05:00 | 227 | 00:00
Ishurdi | 237 | 05:00 | 226 | 23:00
Jhenaidah | 233 | 05:00 | 220 | 21:00
Kaliakoir | 235 | 04:00 | 228 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 00:00 | 128 | 12:00 | Madanganj | 132 | 04:00 | 127 | 13:00
Agargaon | 138 | 13:00 | 129 | 12:00 | Madaripur | 138 | 07:00 | 132 | 22:00
Agrabad | 133 | 06:00 | 129 | 00:00 | Madartek | 136 | 03:00 | 128 | 15:00
AKS | 130 | 01:00 | 127 | 23:00 | Madunaghat | 133 | 07:00 | 130 | 00:00
Aminbazar | 135 | 05:00 | 129 | 00:00 | Magura | 135 | 04:00 | 128 | 19:30
Amnura | 135 | 04:00 | 125 | 00:00 | Mahasthangarh | 137 | 17:00 | 129 | 00:00
Ashuganj | 141 | 04:00 | 138 | 00:00 | Maijdee | 122 | 21:00 | 111 | 00:00
Bagerhat | 135 | 06:00 | 125 | 21:00 | Manikganj | 129 | 06:00 | 124 | 15:00
Bajitpur | 133 | 05:00 | 128 | 22:00 | Maniknagar | 134 | 06:00 | 128 | 13:00
Bakulia | 133 | 05:00 | 130 | 15:00 | Matarbari | 127 | 09:00 | 116 | 08:00
Banani | 137 | 04:00 | 128 | 15:00 | Matuail | 131 | 07:00 | 127 | 12:00
Bangabhaban | 134 | 06:00 | 129 | 11:00 | Millgate | 135 | 02:00 | 129 | 12:00
Barapukuria | 139 | 17:00 | 130 | 07:00 | Mirpur | 133 | 02:00 | 128 | 12:00
Barguna | 136 | 05:00 | 132 | 22:00 | Mirzapur | 132 | 08:00 | 126 | 00:00
Barishal | 138 | 06:00 | 131 | 23:00 | Mithapukur | 134 | 17:00 | 123 | 00:00
Barishal-230 | 138 | 05:00 | 132 | 23:00 | MI_Cement | 132 | 05:00 | 128 | 12:00
Baroaulia | 133 | 08:00 | 129 | 00:00 | Modern | N/A | N/A | N/A | N/A
Baroirhat | 125 | 21:00 | 120 | 00:00 | Mogbazar | 137 | 04:00 | 13 | 04:00
Bashundhara | 137 | 03:00 | 128 | 15:00 | Mongla | 135 | 06:00 | 126 | 21:00
BashundharaCement | 132 | 04:00 | 127 | 13:00 | Motijheel | 134 | 06:00 | 129 | 11:00
Beanibazar | 130 | 07:00 | 125 | 00:00 | Muktagacha | 135 | 09:00 | 128 | 03:00
Benapole | 135 | 03:00 | 126 | 19:30 | Munshiganj | 131 | 04:00 | 126 | 12:00
Bhaluka | 131 | 04:00 | 125 | 22:00 | Muradnagar | 126 | 05:00 | 123 | 00:00
Bhandaria | 137 | 05:00 | 126 | 22:00 | Mymensingh | 136 | 10:00 | 121 | 00:00
Bhangura | 135 | 05:00 | 130 | 00:00 | Naogaon | 134 | 16:00 | 124 | 00:00
Bheramara | 137 | 03:00 | 133 | 23:00 | Narail | 137 | 04:00 | 128 | 19:30
Bheramara(GK) | 138 | 04:00 | 133 | 23:00 | Narinda | 134 | 6:00 | 128 | 13:00
Bhulta | 126 | 07:00 | 118 | 06:00 | Narshingdi | 134 | 07:00 | 123 | 00:00
Bog-Sherpur | 137 | 17:00 | 130 | 00:00 | Natore | 135 | 08:00 | 130 | 00:00
Bogura | 139 | 17:00 | 132 | 00:00 | Nawabganj | 136 | 04:00 | 131 | 12:00
Bogura-230 | 139 | 17:00 | 131 | 01:00 | Netrakona | 127 | 13:00 | 119 | 22:00
Brahmanbaria | 136 | 06:00 | 131 | 00:00 | New | 136 | 04:00 | 130 | 12:00
Cantonment | 136 | 05:00 | 129 | 12:00 | Niamatpur | 135 | 18:30 | 129 | 00:00
Chandina | 128 | 05:00 | 125 | 00:00 | Noapara | 139 | 05:00 | 128 | 21:00
Chandpur | 126 | 21:00 | 115 | 08:00 | Pabna | 135 | 05:00 | 131 | 19:30
Chandraghona | 135 | 08:00 | 131 | 00:00 | Palashbari | 133 | 17:00 | 121 | 00:00
Chapai | 134 | 17:00 | 124 | 00:00 | Panchagarh | 136 | 18:30 | 122 | 03:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 132 | 05:00 | 127 | 13:00 | Patuakhali | 135 | 05:00 | 132 | 23:00
Chauddagram | 124 | 21:00 | 119 | 00:00 | Payra | 137 | 05:00 | 135 | 00:00
Chhatak | 129 | 08:00 | 123 | 00:00 | PHP | 124 | 21:00 | 118 | 00:00
Chowmuhani | 120 | 20:00 | 112 | 00:00 | Postogola | 134 | 05:00 | 129 | 12:00
Chuadanga | 134 | 06:00 | 127 | 00:00 | Purbachal | 138 | 04:00 | 128 | 15:00
Coxsbazar | 128 | 12:00 | 116 | 23:00 | Purbasadipur | 133 | 18:30 | 120 | 20:00
Cumilla(N) | 128 | 05:00 | 125 | 12:00 | Rahanpur | 136 | 17:00 | 130 | 00:00
Cumilla(S) | 132 | 00:00 | 123 | 00:00 | Rahanpur-400 | 136 | 18:30 | 130 | 00:00
Daganbhuiyan | 123 | 21:00 | 114 | 00:00 | Rahim | 131 | 07:00 | 127 | 12:00
Daudkandi | 126 | 06:00 | 122 | 00:00 | Rajbari | 136 | 06:00 | 131 | 00:00
Dhaka | 137 | 00:00 | 129 | 12:00 | Rajendrapur | 133 | 13:00 | 126 | 22:00
Dhamrai | 134 | 04:00 | 126 | 16:00 | Rajshahi | 134 | 05:00 | 130 | 23:00
Dhanmondi | 137 | 04:00 | 128 | 15:00 | Rajshahi-230 | 135 | 03:00 | 119 | 00:00
Dohazari | 132 | 04:00 | 125 | 23:00 | Ramganj | 122 | 21:00 | 111 | 00:00
Faridpur | 136 | 05:00 | 133 | 00:00 | Rampur | 134 | 06:00 | 129 | 00:00
Fatullah | 133 | 04:00 | 128 | 12:00 | Rampura | 137 | 05:00 | 128 | 15:00
Fenchuganj | 137 | 06:00 | 134 | 00:00 | Rangamati | 134 | 04:00 | 130 | 00:00
Feni | 124 | 21:00 | 117 | 15:00 | Rangpur | 135 | 17:00 | 125 | 07:00
Ghatail | 132 | 13:00 | 125 | 00:00 | Ruppur | 137 | 02:00 | 133 | 21:00
Ghorashal | 138 | 06:00 | 135 | 00:00 | Saidpur | 133 | 17:00 | 123 | 00:00
Goalpara | 138 | 05:00 | 131 | 00:00 | Satkhira | 137 | 05:00 | 126 | 19:30
Gollamari | 139 | 05:00 | 132 | 19:30 | Satmasjid | 135 | 04:00 | 120 | 12:00
Gopalganj | 138 | 05:00 | 132 | 19:30 | Savar | 132 | 01:00 | 126 | 14:00
Gopalganj-400 | 139 | 05:00 | 134 | 22:00 | SevenRings | 138 | 03:00 | 133 | 15:00
Gulshan | 136 | 04:00 | 128 | 15:00 | ShahCement | 132 | 05:00 | 127 | 13:00
Halishahar | 135 | 03:00 | 130 | 00:00 | Shahjadpur | 136 | 04:00 | 135 | 00:00
Haripur | 132 | 05:00 | 128 | 00:00 | Shahjibazar | 137 | 07:00 | 131 | 00:00
HaripurSBU | 132 | 05:00 | 128 | 00:00 | Shahmirpur | 135 | 07:00 | 131 | 00:00
Hasnabad | 134 | 05:00 | 129 | 11:00 | Shariatpur | 138 | 04:00 | 131 | 22:00
Hathazari | 135 | 06:00 | 131 | 23:00 | Sherpur | 137 | 10:00 | 125 | 11:00
Ishurdi | 139 | 05:00 | 133 | 20:00 | Shikalbaha | 124 | 14:00 | 119 | 01:00
Jaldhaka | 132 | 17:00 | 120 | 00:00 | Shikalbaha-230 | 136 | 06:00 | 131 | 00:00
Jamalpur | 138 | 10:00 | 128 | 05:00 | Shitalakhya | 132 | 05:00 | 128 | 12:00
Jashore | 133 | 04:00 | 125 | 19:30 | Sholosohor | 133 | 03:00 | 130 | 00:00
Jhenaidah | 137 | 05:00 | 127 | 23:00 | Shyampur | 131 | 08:00 | 127 | 12:00
Jhenaidah-230 | 138 | 05:00 | 130 | 19:30 | Shyampur-230 | 133 | 05:00 | 128 | 12:00
Joydebpur | 137 | 13:00 | 129 | 00:00 | Siddhirganj | 132 | 05:00 | 127 | 12:00
Joypurhat | 133 | 17:00 | 123 | 00:00 | Sirajganj | 134 | 05:00 | 129 | 00:00
Juldah | 134 | 05:00 | 130 | 18:00 | Sonargaon | 130 | 01:00 | 126 | 12:00
Kabirpur | 133 | 19:00 | 125 | 14:00 | Sreemongol | 135 | 08:00 | 130 | 00:00
Kachua | 124 | 20:00 | 117 | 06:00 | Sreepur | 133 | 04:00 | 129 | 00:00
Kaliakoir | 136 | 03:00 | 130 | 16:00 | Srinagar | 137 | 05:00 | 131 | 12:00
Kallyanpur | 134 | 04:00 | 129 | 15:00 | SSM | 139 | 08:00 | 125 | 19:00
Kalurghat | 134 | 03:00 | 130 | 00:00 | Sunamganj | 128 | 08:00 | 121 | 01:00
Kamrangirchar | 137 | 04:00 | 131 | 12:00 | Sylhet | 132 | 08:00 | 127 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet-132 | 130 | 05:00 | 127 | 00:00
Kasba | 126 | 05:00 | 123 | 00:00 | Tangail | 130 | 13:00 | 124 | 00:00
Kazla | 134 | 05:00 | 128 | 13:00 | Taraganj | 134 | 17:00 | 123 | 00:00
Keranigonj | 137 | 05:00 | 131 | 12:00 | Thakurgaon | 136 | 19:00 | 121 | 03:00
Khagrachori | 134 | 06:00 | 130 | 00:00 | TK | 134 | 06:00 | 130 | 23:00
Khulna | 137 | 04:00 | 129 | 19:00 | Tongi | 136 | 06:00 | 131 | 12:00
Khulna(S) | 140 | 05:00 | 131 | 19:30 | Ullahpara | 135 | 06:00 | 131 | 00:00
Khulshi | 133 | 06:00 | 128 | 23:00 | Ullon | 136 | 00:00 | 128 | 12:00
Kishoreganj | 131 | 05:00 | 126 | 00:00 | Uttara | 134 | 06:00 | 127 | 12:00
Kodda | 134 | 11:00 | 124 | 16:00 | UttaraNew | 133 | 05:00 | 127 | 12:00
KSRM | 134 | 03:00 | 130 | 15:00 | Zigatola | 137 | 07:00 | 131 | 12:00
Kulaura | 135 | 08:00 | 132 | 00:00
Kurigram | 133 | 16:00 | 122 | 19:30
Kushtia | 135 | 04:00 | 130 | 19:30
Lakshmipur | 123 | 21:00 | 114 | 00:00
Lalbag | 137 | 05:00 | 131 | 09:00
Lalmonirhat | 132 | 17:00 | 123 | 07:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division