## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID BANGLADESH PLC
SYSTEM OPERATION DATA
Month: May 2025
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2025-05-02 |  | 2025-04-01 |  | 2024-05-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 16603 | 2025-05-10 | 16365.8 | 2025-04-24 | 16067 | 2024-05-23 | 16603 | 2025-05-10
|  |  | 21:00 Hr. |  | 19:30 Hr. |  | 21:00 |  | 21:00 Hr.
2 | Minimum Generation (MW) | 7297.96 | 2025-05-30 | 9058.19 | 2025-04-29 | 3651 | 2024-05-28 | - | -
|  |  | 6:00 |  | 05:00 Hr. |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 16365.8 | 2025-04-24 | 16365.8 | 2025-04-24 | 16067 | 2024-05-23 | 16477 | 2024-04-30
|  |  | 19:30 Hr. |  | 19:30 Hr. |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 14834 | 2025-05-08 | 14594.67 | 2025-04-24 | 14488 | 2024-05-16 | 14594.67 | 2025-04-24
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 16999.06 | 2025-05-10 | 16510.8 | 2025-04-24 | 16400 | 2024-05-23 | 17200 | 2024-04-29
|  |  | 21:00 Hr. |  | 19:30 Hr. |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 14759.5487 |  | 14342.7523 |  | 14021 |  | - | -
7 | Average Generation (MW) at Day Peak | 13259.9958 |  | 12823.5187 |  | 12364.2258 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 941 | 2025-05-13 | 924 | 2025-04-28 | 939 | 2024-05-08 | 970 | 2024-07-06
|  |  | 1:30 |  | 12:00 |  | 10:30 |  | 14:30
9 | Maximum Power Import from Tripura, India (MW) | 62 | 2025-05-22 | 106 | 2025-04-20 | 100 | 2024-05-25 | 194 | 12/06/19
|  |  | 18:30 |  | 22:00 |  | 19:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 380 | 2025-05-27 | 1491 | 2025-04-26 | 845 | 2024-05-16 | 4395 | 04/10/2022
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 16023.29 | 2025-05-27 | 14440.43 | 2025-04-26 | 14965 | 45428 | 14965 | 2024-05-16
|  |  | 21:00 |  | 21:00 | - | 0.875 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2025-05-01 | 0 | 2025-04-01 | 0 | 45423 | - | -
|  |  | 20:00 |  | 20:00 |  | 19:30 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 11428 | 2025-05-01 | 12576 | 2025-04-01 | 13341 | 2024-05-11 | - | -
|  |  | 20:00 |  | 20:00 |  | 19:30 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 300 | 2025-05-14 | 196 | 2025-04-12 | 526 | 45414 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 13979.15 | 2025-05-14 | 13140 | 2025-04-12 | 14149 | 45414 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2025-05-01 | 0 | 2025-04-01 | 0 | 45423 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 10976.06 | 2025-05-01 | 10576.14 | 2025-04-01 | 10559 | 45414 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 24 |  | 16 |  | 22 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 22 |  | 17 |  | 21 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 1192.13 |  | 1417.8481 |  | 2216.8164 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 56.7683 |  | 50.0825 |  | 116.8801 |  | - | -
22 | Net Generation of BPDB (MKWH) | 1135.3617 |  | 1367.7656 |  | 2099.9364 |  | - | -
23 | Net Generation of IPP (MKWH) | 4035.8994 |  | 3367.4554 |  | 3521.1555 |  | - | -
23b | Net Generation by Generation Companies | 2948.2899 |  | 2738.0106 |  | 2617.8799
24 | Net Generation of REB (MKWH) | 37.7987 |  | 116.0982 |  | 99.879 |  | - | -
25 | Net Generation of Rental Power Plant (MKWH) | 130.595 |  | 225.7863 |  | 239.9743 |  | - | -
26 | Total Net Generation (MKHWh) (Excluding Import) | 8287.9448 |  | 7815.1161 |  | 8578.8251 |  | - | -
27 | Energy Generation by Gas (MKWH) | 4159.3337 |  | 4009.324 |  | 4771.0602 |  | - | -
28 | Energy Generation by Diesel (MKWH) | 0.03 |  | 219.8468 |  | 20.5221 |  | - | -
29 | Energy Generation by Furnace Oil (MKWH) | 1116.0073 |  | 1171.3858 |  | 1295.8587 |  | - | -
30 | Energy Generation by Hydro (MKWH) | 28.7773 |  | 0.70868 |  | 22.2695 |  | - | -
31 | Energy Generation by Solar (MKWH) | 118.4392 |  | 149.0391 |  | 89.3041 |  | - | -
31b | Energy Generation by Wind (MKWH) | 9.2213 |  | 0.1 |  | 9.2856 |  | - | -
32 | Energy Generation by Coal (MKWH) | 2912.9044 |  | 2314.7942 |  | 2487.2899 |  | - | -
33 | Enegry Import from India (MKWH) | 1553.6413 |  | 1413.5762 |  | 646.3346 |  | - | -
34 | Monthly Load Factor (%) | 80.1315 |  | 78.7446 |  | 78.2556 |  | - | -

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: May 2025
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 16603 | 2025-05-10 | 21:00 Hr.
Generation Period
| Dhaka | MW | 5823.36
| Chattogram | MW | 1602.9
| Cumilla | MW | 1402.27
| Mymensingh | MW | 1160
| Sylhet | MW | 661
a) | Total supply in East zone | MW | 10649.53
| Khulna | MW | 1965.8
| Barisal | MW | 554.8
| Rajshahi | MW | 1819.8
| Rangpur | MW | 1044
b) | Total supply in West zone | MW | 5384.4
c) | Total supply in both zone ( a+b) | MW | 16033.93
Ref: | 27.21.0000.603.16.087.20.917 | Date: 15/06/2025
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:May 2025
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 558 | 2025-05-07 | 0:00
| b) Ishurdi end | MW | 450 | 2025-05-02 | 19:30
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 1128 | 2025-05-02 | 11:00
| b) Ishurdi end | MW | 226 | 2025-05-07 | 0:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 0
| b) Ishurdi end | MKWH | 163.7751
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 158.8618
| b) Ishurdi end | MKWH | 0
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 250 | 2025-05-18 | 23:00
| b)Serajganj end | MW | 750 | 2025-05-21 | 23:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 370 | 2025-05-13 | 9:00
| b)Sirajganj end | MW | -140 | 2025-05-29 | 20:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end(Sreepur) | MKWH | 356.6826
| b)Sirajganj end | MKWH | 0
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end(Sreepur) | MKWH | 0
| b)Sirajganj end | MKWH | 368.536
30 | Transmission loss of EWI /NO-2 | % | 3.22'%
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 2846 | 28/5/2025 | 23:00
|  | MW | 1850
| b) Aminbazar end | AMPS | -
|  | MW | -
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | -
|  | MW | -
| b) Aminbazar end | AMPS | 2815 | 28/5/2025 | 23:00
|  | MW | 1849
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 37205 | 2025-05-28 | N/A
| a) Aminbazar end | MWh | -
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | - | - | N/A
| a) Aminbazar end | MWh | 37188 | 2025-05-28
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MKWH | 933.38
| b) Aminbazar end (ckt-1 ) | MWh | -
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | -
| b) Aminbazar end (ckt-2 ) | MKWH | 919.942
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 1.44%
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: May 2025
| Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | 230/132kv Tr-03 | 2025-05-07 06:03 | 2025-05-08 07:25 | 1899-12-31 01:22 | E/O | Hot spot | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 230/132kv Tr-03 | 2025-05-09 12:28 | 2025-05-09 13:57 | 0.061806 | T | 132kv side Control Panel signal 1. General Trip Realy Panel signal 1. General Trip | 0 | 0 | No interruption
Bhaluka 132/33kV | Transformer- 01 | 2025-05-20 06:47 | 2025-05-20 09:02 | 0.09375 | E/O | 33 kv bus section-01-bus loop( sokhipur feeder) red hot | 60 | 135 | Power interruption
Bhaluka 132/33kV | Transformer- 01 | 2025-05-28 17:48 | 2025-05-28 17:54 | 0.0041667 | T | Frequency low df/dt(sps) | 0 | 0 | No interruption
Bhaluka 132/33kV | Transformer- 02 | 2025-05-28 17:49 | 2025-05-28 17:54 | 0.0034722 | T | Low frequency df/dt | 0 | 0 | No interruption
Jamalpur 132/33kV | T-3 | 2025-05-17 15:27 | 2025-05-17 15:44 | 0.011806 | T | Bird fall in 33 kv R& B phase Micom p132 | 15 | 4.25 | Power interruption
Jamalpur 132/33kV | T-1 | 2025-05-17 21:42 | 2025-05-17 23:17 | 0.065972 | T | 33kv Jamuna feeder loop disconnected by flashing Micom 132 | 20 | 31.6667 | Power interruption
Jamalpur 132/33kV | T-2 | 2025-05-17 21:42 | 2025-05-17 23:18 | 0.066667 | T | 33kv Jamuna feeder loop disconnected by flashing Micom 132 | 20 | 32 | Power interruption
Joydebpur 132/33kV | GT-2 | 2025-05-28 11:56 | 2025-05-28 12:45 | 0.034028 | E/O | Loop Maintenance | 0 | 0 | No interruption
Kabirpur 132/33kV | XFR, T-3 HT | 2025-05-03 15:45 | 2025-05-03 23:27 | 0.32083 | E/O | TR-3,3kV Bus PT change & 33kV DEPZ hit shink change | 50 | 385 | Power interruption
Kabirpur 132/33kV | XFR, T-2 | 2025-05-11 11:45 | 2025-05-12 00:22 | 0:37 | T | Trip Micom p127 | 0 | 0 | No interruption
Kabirpur 132/33kV | XFR, T-I | 2025-05-11 11:45 | 2025-05-11 12:16 | 0.021528 | T | Trip Micomp127 | 200 | 103.3333 | Power interruption
Kishoreganj 132/33kV | Tr-3 (424T) | 2025-05-09 08:50 | 2025-05-09 09:10 | 0.013889 | E/O | 33Kv T-3 Bus Shutdown due to Pakundia feeder incoming bus loop change | 30 | 10 | Power interruption
Kishoreganj 132/33kV | Tr-1 (404T) | 2025-05-22 18:12 | 2025-05-22 18:32 | 0.013889 | E/O | New energy meter installation by energy audit56 | 56 | 18.6667 | Power interruption
Kishoreganj 132/33kV | Tr-3 (424T) | 2025-05-22 18:38 | 2025-05-22 18:46 | 0.0055556 | E/O | New energy meter installation by energy audit | 44 | 5.8667 | Power interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-3 (50/75 MVA) | 2025-05-18 23:45 | 2025-05-19 00:27 | 0.029167 | T | OSR OSR | 45 | 31.5 | Power interruption
Mirzapur 132/33kV | Transformer-01(E05) | 2025-05-27 04:55 | 2025-05-27 05:17 | 0.015278 | T | 33 kv Square PBS feeder fault SIEMENS ( 7UT61) SIEMENS ( 7SJ85) | 35 | 12.8333 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-2 | 2025-05-05 22:57 | 2025-05-05 23:54 | 0.039583 | E/O | PBS Work. | 30 | 28.5 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-2 | 2025-05-14 12:26 | 2025-05-14 12:28 | 0.0013889 | T | df/dt FBCPU | 26 | 0.86667 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-2 | 2025-05-18 23:43 | 2025-05-19 00:44 | 0.042361 | E/O | Red hot maintenance (pbs 7 no feeder) | 50 | 50.8333 | Power interruption
Sreepur 230/132/33kV | 132 kV BUS-1 | 2025-05-21 10:53 | 2025-05-21 12:35 | 0.070833 | E/O | Bird Nest Removal. | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132 kV BUS-1 | 2025-05-24 01:10 | 2025-05-24 10:26 | 0.38611 | E/O | Kite | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132/33 kV T-1 LT | 2025-05-29 12:03 | 2025-05-29 12:07 | 0.0027778 | T | df/dt FBCPU | 44 | 2.9333 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-2 LT | 2025-05-29 12:03 | 2025-05-29 12:07 | 0.0027778 | T | df/dt FBCPU | 48 | 3.2 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-2 HT | 2025-05-29 14:06 | 2025-05-29 15:04 | 0.040278 | E/O | maintenance of Jack Bus | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132/33 kV T-1 HT | 2025-05-31 10:07 | 2025-05-31 10:47 | 0.027778 | E/O | Jumper Maintenance of 33kv side | 25 | 16.6667 | Power interruption
Tangail 132/33kV | Tr-2 | 2025-05-15 21:11 | 2025-05-15 22:15 | 0.044444 | E/O | high temperature | 90 | 96 | Power interruption
Tangail 132/33kV | Tr-1 | 2025-05-26 12:49 | 2025-05-26 13:01 | 0.0083333 | T | Due to new feeder trial BPDB. REF615 | 46 | 9.2 | Power interruption
Tangail 132/33kV | Tr-2 | 2025-05-26 12:49 | 2025-05-26 13:01 | 0.0083333 | T | Due to new feeder trial BPDB. REF615 | 46 | 9.2 | Power interruption
|  |  | Total : | 1900-01-01 12:28 |  | Unserved Energy: |  | 987.5167
Dhaka (South) Grid Circle :
Ghorashal 230kV | TARFO-2 | 2025-05-17 01:52 | 2025-05-17 02:47 | 0.038194 | T | Outgonig-1 CT jumper out Over current Earth fault | 70 | 64.1667 | Power interruption
Ghorashal 230kV | TARFO-2 | 2025-05-20 18:24 | 2025-05-20 20:10 | 0.073611 | T | 33 kv pbs outgoing -1 DS insulator ceack siemens | 74 | 130.7333 | Power interruption
Gulshan 132/33kV | MT-2 | 2025-05-17 15:07 | 2025-05-17 15:43 | 0.025 | E/O | Emergency maintenance | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 414 T-2 | 2025-05-16 06:39 | 2025-05-16 08:35 | 0.080556 | T | PBS faulty feeder not operate. Master trip | 25 | 48.3333 | Power interruption
Hasnabad 132/33kV | 33kv Reserve Bus | 2025-05-16 06:39 | 2025-05-16 08:35 | 0.080556 | T | 33kv feeders not operate. E/F | 25 | 48.3333 | Power interruption
Hasnabad 132/33kV | 132/33kV 414 T-2 | 2025-05-27 14:25 | 2025-05-27 15:03 | 0.026389 | T | 33 Lalbagh-1 fault,trip by O/C & E/F and PT explode Over current & Earth Fault | 28 | 17.7333 | Power interruption
Hasnabad 132/33kV | 33kv Reserve Bus | 2025-05-27 14:25 | 2025-05-27 15:03 | 0.026389 | T | 33kv lalbagh-1 fault,PT explode O/C & E/F | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-1 | 2025-05-31 04:52 | 2025-06-03 21:23 | 1900-01-02 16:31 | T | 230 kV ATR-1 Differential Relay (87T) 230 kV ATR-1 Differential Relay (87T) Gen. Trip R,Y,B Stage-1 86-T1,86-T2 | 0 | 0 | No interruption
Madanganj 132/33kV | GT-2 | 2025-05-03 13:00 | 2025-05-03 13:57 | 0.039583 | T | Due to 33 kv DPDC Shah cement trip Phase instantaneous relay | 3 | 2.85 | Power interruption
Madanganj 132/33kV | BUS Coupler | 2025-05-22 06:07 | 2025-05-22 06:07 | 0 | E/O | Emergency maintenance | 0 | 0 | No interruption
Maniknagar 230/132kV | Auto Transformer-01(705T) | 2025-05-16 21:05 | 2025-05-16 22:31 | 0.059722 | T | N/A | 0 | 0 | No interruption
Munshiganj 132/33kV | Transformer-2 | 2025-05-07 16:31 | 2025-05-07 17:40 | 0.047917 | E/O | 33 kv incoming -02 Isolator Maintenance due to Red Hot | 55 | 63.25 | Power interruption
Munshiganj 132/33kV | Transformer-2 | 2025-05-11 06:20 | 2025-05-11 08:30 | 0.090278 | E/O | Emergency maintenance on PBS 33 KV Feeder Red Hot | 30 | 65 | Power interruption
Munshiganj 132/33kV | Transformer-1 | 2025-05-16 06:27 | 2025-05-16 09:05 | 0.10972 | E/O | Emergency Maintenance on Isolator loop point of 33KV Incoming-1 due to Red Hot | 20 | 52.6667 | Power interruption
Munshiganj 132/33kV | Transformer-1 | 2025-05-24 06:12 | 2025-05-24 07:57 | 0.072917 | E/O | Red hot on 33 KV bus section -1 jumper connection point | 20 | 35 | Power interruption
Narshingdi 132/33kV | T-1 | 2025-05-07 10:35 | 2025-05-07 12:33 | 0.081944 | E/O | T-1 ট্রান্সফরমারের ৩৩ কেভি Bushing ( Y-Phase) টার্মিনাল পয়েন্টে Oil Leakage হওয়ায় | 0 | 0 | No interruption
Narshingdi 132/33kV | T-4 | 2025-05-16 12:40 | 2025-05-16 12:54 | 0.0097222 | T | df/dt fault Lockout relay | 21 | 4.9 | Power interruption
Narshingdi 132/33kV | T-4 | 2025-05-29 22:23 | 2025-05-29 22:38 | 0.010417 | T | df/dt fault Lockout operated | 2 | 0.5 | Power interruption
Narshingdi 132/33kV | T-4 | 2025-05-30 05:57 | 2025-05-30 06:12 | 0.010417 | T | df/dt Lockout | 4 | 1 | Power interruption
Nawabganj 132/33kV | TR-2 | 2025-05-12 13:42 | 2025-05-12 13:48 | 0.0041667 | T | Due to 33kv Dohar & Nikra feeder fault. Overcurrent relay P142 | 0 | 0 | No interruption
Nawabganj 132/33kV | TR-1 | 2025-05-29 15:37 | 2025-05-29 15:44 | 0.0048611 | T | 33 kV Sholla feeder Lock out relay 1,2 | 12 | 1.4 | Power interruption
Nawabganj 132/33kV | TR-1 | 2025-05-29 17:37 | 2025-05-29 17:42 | 0.0034722 | T | Incomer 1 tripped due to Sholla feeder fault Lock out relay1,2 | 12 | 1 | Power interruption
Nawabganj 132/33kV | TR-2 | 2025-05-29 17:37 | 2025-05-29 17:43 | 0.0041667 | T | Tripped due to Sholla feeder fault Lock out relay 1,2 | 12.5 | 1.25 | Power interruption
Nawabganj 132/33kV | TR-1 | 2025-05-31 14:56 | 2025-05-31 15:06 | 0.0069444 | T | Due to Sholla feeder fault Lock out relay,over current relay | 17 | 2.8333 | Power interruption
Nawabganj 132/33kV | TR-2 | 2025-05-31 14:56 | 2025-05-31 15:07 | 0.0076389 | T | Due to Sholla feeder fault Lock out relay, over current relay | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-2 | 2025-05-07 15:34 | 2025-05-07 16:45 | 0.049306 | E/O | 33 KV side Red hot at Anondoh Bazar feeder | 45 | 53.25 | Power interruption
Sonargaon 132/33kV | Tr-2 | 2025-05-17 06:53 | 2025-05-17 07:08 | 0.010417 | T | PBS 33kv Langulbanbo feeder phase to earth fault. DIR O/C & E/F relay. | 20 | 5 | Power interruption
|  |  | Total : | 1900-01-03 15:54 |  | Unserved Energy: |  | 599.2
Chattogram Grid Circle :
Chandraghona 132/33kV | TR-02(416T) | 2025-05-10 08:55 | 2025-05-10 10:36 | 0.070139 | E/O | টি-০২ ২৫/৪১ এমভিএ (৪১৬টি) এর ৩৩ কেভি ব্লু- ফেইজ এর নীচের কানেক্টরে সংরক্ষণ ও মেরামত কাজ। | 0 | 0 | No interruption
Coxsbazar 132/33kV | 415T-T2 | 2025-05-29 21:44 | 2025-05-29 23:38 | 0.079167 | T | PBS Ukhiya 33KV Feeder Cable flashing. Phase-A/B/C Trip, L/V- O/C,E/F Trip | 15 | 28.5 | Power interruption
GPH 230/33kV | Transformer-01(D05) | 2025-05-12 11:07 | 2025-05-22 17:00 | 1900-01-09 05:53 | T | internal fault 86.1,86.2,87T1/T2 | 0 | 0 | No interruption
GPH 230/33kV | Transformer -2 (D07) HT | 2025-05-24 14:48 | 2025-05-24 18:17 | 0.14514 | E/O | Oil leakage checking. | 0 | 0 | No interruption
Halishahar 132/33kV | 405T(TR-1) | 2025-05-30 03:43 | 2025-05-30 04:22 | 0.027083 | T | Over voltage. Transformer relay. | 12 | 7.8 | Power interruption
Halishahar 132/33kV | 415T(TR-2) | 2025-05-30 03:43 | 2025-05-30 04:23 | 0.027778 | T | Over voltage Transformer relay. | 13 | 8.6667 | Power interruption
Hathazari 230/132/33kV | T-01 HT | 2025-05-08 16:40 | 2025-05-08 17:39 | 0.040972 | E/O | Emergency maintenance | 0 | 0 | No interruption
Hathazari 230/132/33kV | T-01 LT | 2025-05-15 07:00 | 2025-05-15 11:20 | 0.18056 | E/O | 33 kV BUS conductor R Ph, DS B Ph repair By PBS | 35 | 151.6667 | Power interruption
Hathazari 230/132/33kV | T-01 HT | 2025-05-28 01:30 | 2025-05-28 03:04 | 0.065278 | E/O | redhot | 30 | 47 | Power interruption
Kalurghat 132/33kV | TRFO-01(506T) | 2025-05-22 11:30 | 2025-05-22 12:10 | 0.027778 | E/O | BPDB 33KV Feeder (incomer-2) red hot maintenance. | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-01(506T) | 2025-05-26 08:36 | 2025-05-26 09:50 | 0.051389 | E/O | Bus section DS maintenance by BPDB | 14 | 17.2667 | Power interruption
Kalurghat 132/33kV | TRFO-02(516T) | 2025-05-26 09:37 | 2025-05-26 09:49 | 0.0083333 | E/O | Bus section DS Maintenance by BPDB | 14 | 2.8 | Power interruption
Khagrachori 132/33kV | TR-1 LT | 2025-05-30 11:49 | 2025-05-30 18:29 | 0.27778 | E/O | Fire incident at 33 kV incomer-1 cable(Y Phase). | 0 | 0 | No interruption
Khagrachori 132/33kV | TR-1 HT | 2025-05-30 12:51 | 2025-05-30 18:26 | 0.23264 | E/O | Fire incident at 33 kV incomer-1 cable(Y Phase). | 0 | 0 | No interruption
Khagrachori 132/33kV | TR-1 HT | 2025-05-31 09:37 | 2025-05-31 13:42 | 0.17014 | E/O | S/D for fire incident at incomer cable(Y Phase). | 0 | 0 | No interruption
Khulshi 132/33kV | 405T (T1) | 2025-05-09 05:11 | 2025-05-09 05:46 | 0.024306 | T | 132kV Grid power failure. Under Frequency Relay | 50 | 29.1667 | Power interruption
Khulshi 132/33kV | 415T (T2) | 2025-05-09 05:11 | 2025-05-09 05:46 | 0.024306 | T | 132kV Grid power failure. Under Frequency | 47 | 27.4167 | Power interruption
Mirsorai 230/33kV | Bus-2 | 2025-05-27 15:27 | 2025-05-27 16:53 | 0.059722 | T | DS (Q1) adjacent to Bus-1, Flashing of EGCB Feeder due to release gas from DS Compartment by Contractor. Bus-bar Protection Relay. | 0 | 0 | Power interruption | ok
Mirsorai 230/33kV | TR-1, 718T | 2025-05-27 15:27 | 2025-05-27 16:54 | 0.060417 | T | DS (Q1) adjacent to Bus-1, Flashing of EGCB Feeder due to release gas from DS Compartment by Contractor. Bus-ber Protection Relay | 0 | 0 | No interruption
Mirsorai 230/33kV | TR-2, 728T | 2025-05-27 15:27 | 2025-05-27 17:20 | 0.078472 | T | DS (Q1) adjacent to Bus-1, Flashing of EGCB Feeder due to release gas from DS Compartment by Contractor. Bus-ber protection Relay | 0 | 0 | Power interruption | ok
Shikalbaha 230/132kV | ATR 01 | 2025-05-09 05:11 | 2025-05-09 08:09 | 0.12361 | T | FN-6 | 0 | 0 | No interruption
Shikalbaha 230/132kV | ATR 02 | 2025-05-09 05:11 | 2025-05-09 08:11 | 0.125 | T | FN-6 | 0 | 0 | No interruption
|  |  | Total : | 1900-01-11 03:29 |  | Unserved Energy: |  | 320.2833
Cumilla Grid Circle :
Beanibazar 132/33kV | 132KV Transformer TR-02 | 2025-05-07 13:34 | 2025-05-07 14:58 | 0.058333 | E/O | Red hot appeared in bus coupler between 33kv Bus section 02 and 03 | 45 | 63 | Power interruption
Beanibazar 132/33kV | 132 KV Transformer TR-01 | 2025-05-15 11:20 | 2025-05-15 14:42 | 0.14028 | E/O | For maintenance work | 0 | 0 | No interruption
Beanibazar 132/33kV | 132KV Transformer TR-02 | 2025-05-15 14:49 | 2025-05-15 16:52 | 0.085417 | E/O | PRD capping due to rain | 0 | 0 | No interruption
Chandina 132/33kV | TR-3 | 2025-05-18 03:03 | 2025-05-18 05:07 | 0.086111 | T | Due to cumilla pbs-01 feeder earth fault. K86L1 lock out relay-1 K86L2 lock out relay-2 F87T1, F87T2. | 18 | 37.2 | Power interruption
Chandina 132/33kV | TR-3 | 2025-05-20 06:37 | 2025-05-20 06:52 | 0.010417 | T | PBS-01, over current & earth fault K86L, lock out relay 1&2 both, F87T1, F87T2, F87BB, BCU | 13 | 3.25 | Power interruption
Chowmuhani 132/33kV | TR1-415T | 2025-05-03 08:05 | 2025-05-03 12:50 | 0.19792 | E/O | 33kv Tr-1 Bus Maintenance | 25 | 118.75 | Power interruption
Chowmuhani 132/33kV | TR2-415T | 2025-05-14 07:20 | 2025-05-14 09:06 | 0.073611 | E/O | tr-2 33 kv bus Maintanance | 40 | 70.6667 | Power interruption
Chowmuhani 132/33kV |  | 2025-05-17 07:57 | 2025-05-17 15:29 | 0.31389 | E/O | Tr-2 bus maintenance | 50 | 376.6667 | Power interruption
Chowmuhani 132/33kV | TR1-415T | 2025-05-30 09:30 | 2025-05-30 10:02 | 0.022222 | E/O | DS A Phase Red Hot Maintenance | 15 | 8 | Power interruption
Cumilla(N) 230/132/33kV | 132KV T-03 | 2025-05-22 08:34 | 2025-05-22 11:14 | 0.11111 | T | 33KV Under ground R-phase Cable Blast No | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 132KV T-04 | 2025-05-22 08:34 | 2025-05-22 09:58 | 0.058333 | T | 33KV T-03 Under ground R-phase Cable Blast No | 50 | 70 | Power interruption
Cumilla(S) 132/33kV | TR-4 | 2025-05-11 17:02 | 2025-05-11 17:11 | 0.00625 | T | 33 KV Shafiul Alam Feeder fault(PDB) 1.RET650 2.REF615 | 26 | 3.9 | Power interruption
Cumilla(S) 132/33kV | TR-2 | 2025-05-14 16:46 | 2025-05-14 16:57 | 0.0076389 | T | 33 KV Laksham REB feeder fault. 1.RET650 2.REF615 | 7 | 1.2833 | Power interruption
Cumilla(S) 132/33kV | TR-3 | 2025-05-26 21:18 | 2025-05-26 21:38 | 0.013889 | T | 33 KV Nangolkot REB feeder fault. 1.RET650 2.REF615 | 30 | 10 | Power interruption
Cumilla(S) 132/33kV | TR-2 | 2025-05-29 23:40 | 2025-05-29 23:51 | 0.0076389 | T | 33 KV Laksham REB feeder fault. RET670,REF615 | 4 | 0.73333 | Power interruption
Cumilla(S) 132/33kV | TR-2 | 2025-05-31 20:20 | 2025-05-31 21:01 | 0.028472 | T | 33KV Laksam REB & Chauddagram REB feeder fault. RET -650 | 46 | 31.4333 | Power interruption
Shahjibazar 132/33kV | TR-04 | 2025-05-11 15:30 | 2025-05-11 18:50 | 0.13889 | T | 33 KV Bus loop and BISIC Feeder Earth Fault O/C,Earth Fault Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 LT | 2025-05-11 15:30 | 2025-05-11 18:50 | 0.13889 | T | 33KV BUs Loop and BISIC Feeder Earth Fault O/C,Earth Fault Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 LT | 2025-05-12 07:50 | 2025-05-12 08:22 | 0.022222 | T | Chunarughat feeder O/C Earth fault Relay. O/C, E/F Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 LT | 2025-05-12 07:50 | 2025-05-12 08:22 | 0.022222 | T | Chunarughat feeder O/C Earth fault Relay. O/C , E/F Relay | 0 | 0 | No interruption
Sreemongol 132/33kV | 132/33kv T-3 | 2025-05-30 13:51 | 2025-05-30 14:01 | 0.0069444 | T | fromm 33kv feeder fault o/c | 0 | 0 | No interruption
Sylhet 132/33kV | T2 | 2025-05-01 20:36 | 2025-05-01 21:44 | 0.047222 | T | Flashing Over Current | 26 | 29.4667 | Power interruption
Sylhet 132/33kV | T2 | 2025-05-02 07:07 | 2025-05-02 08:42 | 0.065972 | E/O | 33 KV T-2 Bus S/D for BPDB feeder Maintenance work Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV | T2 | 2025-05-05 04:41 | 2025-05-05 05:09 | 0.019444 | T | fault of 33 KV Amborkhana-1 Feeder OC -B phase | 0 | 0 | No interruption
Sylhet 132/33kV | T1 | 2025-05-11 08:42 | 2025-05-11 10:54 | 0.091667 | E/O | Red hot Maintenance of Upashahar feeder. | 28 | 61.6 | Power interruption
Sylhet 132/33kV | T2 | 2025-05-27 02:42 | 2025-05-27 03:41 | 0.040972 | T | IC-2 Burst LV O/C A B C Phase E/F General Trip | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 19:35 |  | Unserved Energy: |  | 885.95
Khulna Grid Circle :
Barishal 132/33kV | T-2 (415T) | 2025-05-10 21:07 | 2025-05-10 21:21 | 0.0097222 | T | 33kv feeder fault Ins O/C,Ins E/F | 47 | 10.9667 | Power interruption
Barishal 132/33kV | T-2 (415T) LT | 2025-05-29 05:17 | 2025-05-29 05:26 | 0.00625 | T | 33 kv feeder fault Ins o/c,deff o/ c. | 10 | 1.5 | Power interruption
Barishal 132/33kV | T-2 (415T) LT | 2025-05-30 01:30 | 2025-05-30 01:38 | 0.0055556 | T | 33 kV nolcity feeder trip. Instt. OC, Definite OC, Lock out. | 34 | 4.5333 | Power interruption
Barishal 230/132kV | T-5 | 2025-05-29 13:55 | 2025-05-29 14:43 | 0.033333 | T | 33 kv Korapur feeder fault Over current | 13 | 10.4 | Power interruption
Barishal 230/132kV | T-4 LT | 2025-05-29 13:55 | 2025-05-29 15:55 | 0.083333 | T | 33kv Korapur feeder fault Over current | 13 | 26 | Power interruption
Benapole 132/33kV | Transformer-1(406T) LT | 2025-05-06 13:05 | 2025-05-06 13:17 | 0.0083333 | T | 33 KV Sharsha Benapole Feeder trip REF 630 | 15 | 3 | Power interruption
Benapole 132/33kV | Transformer-1(406T) | 2025-05-19 08:24 | 2025-05-19 08:48 | 0.016667 | T | Under Frequency REF 630 | 30 | 12 | Power interruption
Benapole 132/33kV | Transformer-2(416T) | 2025-05-19 08:24 | 2025-05-19 08:49 | 0.017361 | T | Under Frequency REF 630 | 20 | 8.3333 | Power interruption
Bhandaria 132/33kV | Transformer-1 | 2025-05-21 09:15 | 2025-05-21 09:52 | 0.025694 | E/O | 33 kV incomming Meter change by BPDB. | 0 | 0 | No interruption
Bhandaria 132/33kV | Transformer-1 HT | 2025-05-21 09:35 | 2025-05-21 09:50 | 0.010417 | E/O | 33 kV incomming Meter change by BPDB. | 0 | 0 | No interruption
Borhanuddin 230/33kV | Tr-Load | 2025-05-25 10:33 | 2025-05-25 11:18 | 0.03125 | T | Buchholz | 52 | 39 | Power interruption
Borhanuddin 230/33kV | Tr-Load | 2025-05-26 15:07 | 2025-05-26 16:59 | 0.077778 | E/O | PDB Tx operation | 60 | 112 | Power interruption
Borhanuddin 230/33kV | Tr-Load LT | 2025-05-26 15:10 | 2025-05-26 17:05 | 0.079861 | E/O | PDB Tx operation | 0 | 0 | No interruption
Chandina 132/33kV | TR-2 HT | 2025-05-06 14:28 | 2025-05-06 14:51 | 0.015972 | T | Relay AF87T1 Relay AF87T12 K86L1 K86L2 | 0 | 0 | No interruption
Chandina 132/33kV | TR-3 | 2025-05-07 07:10 | 2025-05-07 08:05 | 0.038194 | T | TR BACKUP RELAY -F51 BCU1 | 4.11 | 3.7675 | Power interruption
Faridpur 132/33kV | Transformer-1 | 2025-05-21 12:40 | 2025-05-21 12:55 | 0.010417 | T | 33kV Earth Fault | 0 | 0 | No interruption
Faridpur 132/33kV | Transformer-2 | 2025-05-21 12:40 | 2025-05-21 12:55 | 0.010417 | T | 33kV PBS feeder fault. 33kV Earth fault, | 60 | 15 | Power interruption
Goalpara 132/33kV | T-5 | 2025-05-18 10:24 | 2025-05-18 10:35 | 0.0076389 | T | Due to 33 kV Senerbazar Feeder Fault. Micom P127 | 16 | 2.9333 | Power interruption
Goalpara 132/33kV | T-6 | 2025-05-18 10:24 | 2025-05-18 10:35 | 0.0076389 | T | Due to 33 kV Senerbazar Feeder Fault Micom P127 | 16 | 2.9333 | Power interruption
Gopalganj 132/33kV | T2 | 2025-05-09 16:15 | 2025-05-09 17:40 | 0.059028 | E/O | Section Ds Clamp maintenance | 30 | 42.5 | Power interruption
Gopalganj 132/33kV | T2 | 2025-05-12 16:43 | 2025-05-12 16:59 | 0.011111 | T | Reb- 8 feeder fault. Inst over current | 50 | 13.3333 | Power interruption
Khulna (C) | TR-1 425T | 2025-05-27 11:16 | 2025-05-27 12:48 | 0.063889 | E/O | ৩৩ কেভি সাইডের কেবল মাটির মধ্যে ঢেকে রাখার জন্য সাটডাউন নেয়া হয়। | 0 | 0 | No interruption
Khulna(S) 230/132kV | TR-1 | 2025-05-19 08:27 | 2025-05-19 09:55 | 0.061111 | T | BBP/BFP BAY UNIT | 111 | 162.8 | Power interruption
Khulna(S) 230/132kV | TR-2 LT | 2025-05-19 08:27 | 2025-05-19 09:51 | 0.058333 | T | BBP/BFP BAY UNIT | 111 | 155.4 | Power interruption
Khulna(S) 230/132kV | TR-3 | 2025-05-19 08:27 | 2025-05-19 11:08 | 0.11181 | T | BUSBER PROTECTION TRIP | 143 | 383.7167 | Power interruption
Mongla 132/33kV | T-1 | 2025-05-17 22:39 | 2025-05-18 00:13 | 0.065278 | T | 33kv Seven Cercle Feeder fault O/C | 11 | 17.2333 | Power interruption
Mongla 132/33kV | T-1 | 2025-05-19 08:25 | 2025-05-19 08:58 | 0.022917 | T | CB Open Because of Black out No | 41 | 22.55 | Power interruption
Mongla 132/33kV | T-1 | 2025-05-23 00:58 | 2025-05-24 00:38 | 0.027778 | T | Over Current Earth Fault Lockout Relay | 33 | 22 | Power interruption
Noapara 132/33kV | T-1 | 2025-05-28 16:26 | 2025-05-28 16:41 | 0.010417 | T | Earth fault and over current fault occure in the feeder of REB-4 33kV. SIPROTEC 7SJ81 (SIEMENS) | 22 | 5.5 | Power interruption
Noapara 132/33kV | T-2 | 2025-05-28 16:26 | 2025-05-28 16:43 | 0.011806 | T | Earth fault and over current fault occure in the feeder of REB-4 33kV. SIPROTEC 7SJ81 (SIEMENS) | 21.5 | 6.0917 | Power interruption
Rajbari 132/33kV | Transformer-3 | 2025-05-16 08:56 | 2025-05-16 09:17 | 0.014583 | T | Tr-3 incoming trip due to fault of 33 kv sajankanda feeder. 50 DMT & 51 DMT O/C, 86.1&86.2 Operate. | 10 | 3.5 | Power interruption
Rajbari 132/33kV | Transformer-3 | 2025-05-19 15:09 | 2025-05-19 15:36 | 0.01875 | T | O/C, 86.1 & 86.2 operated. | 7 | 3.15 | Power interruption
Satkhira 132/33kV | Transformer-2 (T-2) | 2025-05-15 00:35 | 2025-05-15 00:37 | 0.0013889 | T | Due to capacitor bank trip Over current | 58 | 1.9333 | Power interruption
|  |  | Total : | 1899-12-31 00:49 |  | Unserved Energy: |  | 1092.0758
HVDC Grid Circle :
Bhangura 132/33kV | Tr-1(403T) | 2025-05-13 20:25 | 2025-05-13 21:21 | 0.038889 | E/O | Red hot 33kv incomer BREAK | 15 | 14 | Power interruption
Bhangura 132/33kV | Tr-1(403T) | 2025-05-29 06:05 | 2025-05-29 07:34 | 0.061806 | T | Aux Tr-1 fuse and insulator blast. O/C,E/F | 25 | 37.0833 | Power interruption
Bhangura 132/33kV | Tr-2(413T) | 2025-05-29 06:05 | 2025-05-29 07:35 | 0.0625 | T | Aux Tr-1 fuse and insulator blast. O/C,E/F | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-1(403T) | 2025-05-29 11:37 | 2025-05-29 13:11 | 0.065278 | E/O | Emergency maint.work | 10 | 15.6667 | Power interruption
Bhangura 132/33kV | Tr-2(413T) | 2025-05-30 16:42 | 2025-05-30 17:32 | 0.034722 | E/O | Emergency maint.work | 9 | 7.5 | Power interruption
Bhangura 132/33kV | Tr-1(403T) | 2025-05-30 17:42 | 2025-05-30 19:02 | 0.055556 | E/O | Emergency maint.work | 10 | 13.3333 | Power interruption
Bheramara 230/132kV | Transformer-2 | 2025-05-14 11:29 | 2025-05-14 17:28 | 0.24931 | E/O | Under Ground Cable Oil Leakage | 0 | 0 | No interruption
Chuadanga 132/33kV | 132kV Tr. T1(416T) | 2025-05-07 21:35 | 2025-05-08 09:58 | 0.51597 | T | Flashing OC/EF | 55 | 681.0833 | Power interruption
Chuadanga 132/33kV | 132kV Tr. T1(416T) | 2025-05-07 23:41 | 2025-05-08 09:57 | 0.42778 | E/O | Red hot maintenance | 30 | 308 | Power interruption
Chuadanga 132/33kV | 132kV Tr. T1(416T) | 2025-05-16 10:18 | 2025-05-16 12:06 | 0.075 | E/O | Red hot Maintenance at 33kV side. | 30 | 54 | Power interruption
Chuadanga 132/33kV | 132kV Tr. T1(416T) HT | 2025-05-28 07:00 | 2025-05-28 09:15 | 0.09375 | E/O | Red hot maintenance at 33 kV Bus-section-1. | 25 | 56.25 | Power interruption
Chuadanga 132/33kV | 132kV Tr. T2(426T) HT | 2025-05-28 07:02 | 2025-05-28 09:15 | 0.092361 | E/O | Red hot maintenance at 33 kV Bus-section-1. | 25 | 55.4167 | Power interruption
Chuadanga 132/33kV | 132kV Tr. T3 | 2025-05-30 03:35 | 2025-05-31 18:47 | 1899-12-31 15:12 | T | Diff trip C phase Diff, Master trip | 0 | 0 | No interruption
Chuadanga 132/33kV | 132kV Tr. T1(416T) | 2025-05-30 21:23 | 2025-05-30 22:46 | 0.057639 | E/O | Red hot maintenance of 33kV busber | 40 | 55.3333 | Power interruption
Ishurdi 230/132kV | 230/132 kV T-03 | 2025-05-27 21:07 | 2025-05-28 10:26 | 0.55486 | E/O | 230/132 x-former T-03 LT side connector redhot. | 0 | 0 | No interruption
Jhenaidah 132/33kV | Transformer T-2 LT | 2025-05-03 15:14 | 2025-05-03 16:31 | 0.053472 | E/O | Maintenance for 33kv bus section Ds. | 35 | 44.9167 | Power interruption
Jhenaidah 132/33kV | Transformer T-2 | 2025-05-03 15:14 | 2025-05-03 16:30 | 0.052778 | E/O | Maintenance for 33kv bus section Ds. | 0 | 0 | No interruption
Jhenaidah 132/33kV | Transformer T-1 | 2025-05-20 07:09 | 2025-05-20 09:20 | 0.090972 | E/O | 33kV DS of T-1A R-Phase Red Hot Manitenance. | 0 | 0 | No interruption
Jhenaidah 132/33kV | Transformer T-1 | 2025-05-28 07:04 | 2025-05-28 08:44 | 0.069444 | E/O | Redhot maintenance | 47 | 78.3333 | Power interruption
Kushtia 132/33kV | T2 | 2025-05-05 22:02 | 2025-05-05 22:50 | 0.033333 | E/O | Emergency Shut down for PBS Feeder Red hot | 34 | 27.2 | Power interruption
Kushtia 132/33kV | T-3 | 2025-05-17 20:25 | 2025-05-17 21:25 | 0.041667 | E/O | Bus Section-3 auxillary transformer post insulator crak | 60 | 60 | Power interruption
Kushtia 132/33kV | T-1 | 2025-05-18 16:09 | 2025-05-18 17:37 | 0.061111 | E/O | Wzpdcl 33kV h-3 feeder bus side red hot maintenance | 6 | 8.8 | Power interruption
Kushtia 132/33kV | T-1 HT | 2025-05-20 16:41 | 2025-05-20 17:54 | 0.050694 | E/O | 33 KV PBS FEEDER RED HOT MAINTENANCE | 10 | 12.1667 | Power interruption
Kushtia 132/33kV | T-3 | 2025-05-28 07:07 | 2025-05-28 09:36 | 0.10347 | E/O | T -3 A , 33 KV incomer Side U clamp a Red Hot Maintenance work . | 50 | 124.1667 | Power interruption
Ruppur 132/11kV | TR-01 | 2025-05-19 04:03 | 2025-05-19 11:24 | 0.30625 | T | Under Frequency Relay Not Connected. Diff:. R,Y,B & K31,K32 | 2.8 | 20.58 | Power interruption
Ruppur 132/11kV | TR-01 | 2025-05-20 10:48 | 2025-05-20 12:04 | 0.052778 | T | Under Frequency Relay Not Connected. Differential relay | 0 | 0 | No interruption
|  |  | Total : | 1900-01-03 22:26 |  | Unserved Energy: |  | 1673.83
Bogura Grid Circle:
Amnura 132/33kV | T-1 (406T) | 2025-05-23 14:55 | 2025-05-23 15:02 | 0.0048611 | T | Gobratola 33kV fdr. Fault Earth fault | 4 | 0.46667 | Power interruption
Amnura 132/33kV | T-2 (416T) | 2025-05-23 14:55 | 2025-05-23 15:02 | 0.0048611 | T | Gobratola 33kV fdr. Fault Earth fault | 4 | 0.46667 | Power interruption
Barapukuria 230/132/33kV | 132/33 KV T-5, 424T | 2025-05-23 22:08 | 2025-05-23 22:46 | 0.026389 | E/O | Emergency red hot maintenance. | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 230/132 KV T-01, 703T | 2025-05-27 17:35 | 2025-05-29 01:15 | 1899-12-31 07:40 | E/O | Emergency maintenance. | 22 | 696.6667 | Power interruption
Bogura 132/33kV | Transformer-1 | 2025-05-08 17:54 | 2025-05-08 18:36 | 0.029167 | T | DEW TO TALORA 33KV & PURAN BOGURA 33KV FEEDER FAULT. O/C E/F &33 KV LOCKOUT OPERATED. | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-2 | 2025-05-08 17:54 | 2025-05-08 18:36 | 0.029167 | T | DEW TO TALORA 33KV & PURAN BOGURA 33KV FEEDER FAULT.. O/C, E/F & 33KV LOCKOUT OPERATED. | 50 | 35 | Power interruption
Bogura 132/33kV | Transformer-3 LT | 2025-05-17 15:14 | 2025-05-17 16:14 | 0.041667 | E/O | banani 33kv nesco work | 23 | 23 | Power interruption
Bogura 132/33kV | Transformer-3 | 2025-05-17 15:15 | 2025-05-17 16:14 | 0.040972 | E/O | banani 33kv nesco work | 0 | 0 | No interruption
Bogura 230/132kV | T-02 | 2025-05-03 11:48 | 2025-05-03 13:30 | 0.070833 | E/O | 132kV CT Oil Leakage maintenance | 0 | 0 | No interruption
Bogura 230/132kV | T-02 | 2025-05-27 02:26 | 2025-05-28 12:37 | 1899-12-31 10:11 | T | REL505C1 (No alarm) | 0 | 0 | No interruption
Bogura 230/132kV | T-02 | 2025-05-27 08:40 | 2025-05-27 21:12 | 0.52222 | E/O | Emergency maintenance. | 0 | 0 | No interruption
Bogura 230/132kV | T-02 | 2025-05-28 09:55 | 2025-05-28 12:31 | 0.10833 | E/O | Oil Refilling Inspection. | 0 | 0 | No interruption
Bogura 230/132kV | T-02 | 2025-05-30 07:17 | 2025-05-30 12:34 | 0.22014 | T | No relay indication | 0 | 0 | No interruption
Chapai 132/33kV | T-2 (415T) | 2025-05-18 22:40 | 2025-05-19 01:02 | 0.098611 | E/O | red hot maintenance | 0 | 0 | No interruption
Jaldhaka 132/33kV | 406T-1 | 2025-05-18 10:18 | 2025-05-18 11:29 | 0.049306 | E/O | Domer-02 | 12 | 14.2 | Power interruption
Joypurhat 132/33kV | Transformer T-3 (427 T) | 2025-05-26 20:57 | 2025-05-26 22:59 | 0.084722 | T | 50/51 (Over corrent) PBS Auxiliary Transformer Fault Relay- P122 | 15 | 30.5 | Power interruption
Joypurhat 132/33kV | Transformer T-4 (437 T) HT | 2025-05-26 20:57 | 2025-05-26 21:24 | 0.01875 | T | REF Trip (P-632) PBS Auxiliary Transformer Fault P-632 (Dffifrential Relay) | 0 | 0 | No interruption
Lalmonirhat 132/33kV | T-1 (425T) LT | 2025-05-30 16:36 | 2025-05-30 20:05 | 0.14514 | T | Pbs ckt -1 feeder fault MCGG 51G | 0 | 0 | No interruption
Lalmonirhat 132/33kV | T-2 (415T) | 2025-05-30 16:36 | 2025-05-30 17:30 | 0.0375 | T | Pbs1 feeder fault MCCG 51G | 10.5 | 9.45 | Power interruption
Mahasthangarh 132/33kV | 406T MTR1 | 2025-05-04 17:24 | 2025-05-04 17:48 | 0.016667 | T | 33 kv (BPBS-2)Feeder Fault Micom P142 | 0 | 0 | No interruption
Mahasthangarh 132/33kV | 406T MTR1 | 2025-05-11 18:44 | 2025-05-11 18:55 | 0.0076389 | T | Due to 33kv Sukanpukur Feeder fault. Micom-P142 | 0 | 0 | No interruption
Mahasthangarh 132/33kV | 416T MTR 2 | 2025-05-13 06:52 | 2025-05-13 10:07 | 0.13542 | E/O | T-2 33 kv bus Amtoli feeder bus loop Red hot maintenance work.. | 35 | 113.75 | Power interruption
Mahasthangarh 132/33kV | 406T MTR1 | 2025-05-17 10:10 | 2025-05-17 10:25 | 0.010417 | T | BPBS-2 33 kv Sukanpukor Feeder Earth fault Micom-P139 | 0 | 0 | No interruption
Mithapukur 132/33kV | TR-2 (414T) | 2025-05-21 22:34 | 2025-05-21 23:25 | 0.035417 | E/O | Red hot maintenance. | 0 | 0 | No interruption
Naogaon 132/33kV | T-1 | 2025-05-13 19:40 | 2025-05-13 20:20 | 0.027778 | T | Badalgachi 33kv PBS feeder tripped by O/C(Ia=0.099KA, Ib= 13.63KA, Ic= 0.112KA,In=14.18KA,Ig=2.698KA) & E/F MCGG relay (inst. E/F) | 0 | 0 | No interruption
Naogaon 132/33kV | T-2 | 2025-05-13 19:40 | 2025-05-13 20:10 | 0.020833 | T | Badalgachi 33kv PBS feeder tripped by O/C(Ia=0.099KA, Ib= 13.63KA, Ic= 0.112KA,In=14.18KA,Ig=2.698KA) & E/F MCGG relay (inst. E/F) | 0 | 0 | No interruption
Naogaon 132/33kV | T-3 | 2025-05-18 05:40 | 2025-05-18 06:40 | 0.041667 | T | Nesco T-5 Bus DS side ( B Phase) heavy flashing & cut off from 33 kv Bus.For that T-3 (33KV) CB off by hand. No | 0 | 0 | No interruption
Naogaon 132/33kV | T-2 | 2025-05-18 05:40 | 2025-05-18 07:12 | 0.063889 | T | Nesco T-5 Bus DS side ( B Phase) heavy flashing & cut off from 33 kv Bus.For that T-2 (33KV) CB off by hand. under bus-1 & bus-2 the Badalgachi & chowmasia 33 KV feeder trip by over current. No | 0 | 0 | No interruption
Naogaon 132/33kV | T-1 LT | 2025-05-18 05:40 | 2025-05-18 06:25 | 0.03125 | T | Nesco T-5 Bus DS side ( B Phase) heavy flashing & cut off from 33 kv Bus.For that T-1 (33KV) CB off by hand. under bus-1 & bus-2 the Badalgachi & chowmasia 33 KV feeder trip by over current. No | 0 | 0 | No interruption
Naogaon 132/33kV | T-3 LT | 2025-05-18 14:24 | 2025-05-18 15:28 | 0.044444 | E/O | T-3 33KV Bus Isolator Loop change work for Isolator loop Burnt. | 0 | 0 | No interruption
Naogaon 132/33kV | T-3 | 2025-05-18 14:25 | 2025-05-18 15:26 | 0.042361 | E/O | T-3 33KV Bus loop change for the reason off 33kv Bus loop Burnt | 0 | 0 | No interruption
Naogaon 132/33kV | T-3 | 2025-05-19 02:42 | 2025-05-19 10:17 | 0.31597 | T | Atrai 33KV PBS feeder Incoming DS loop Cut-off from 33KV T-3 Bus(B & Y Phase). O/C (a,b phase), 1st Stage U/F | 20 | 151.6667 | Power interruption
Naogaon 132/33kV | T-3 LT | 2025-05-19 06:50 | 2025-05-19 10:17 | 0.14375 | E/O | Atrai PBS 33KV feeder Bus DS connecting R & Y Phase loop Maintenance. | 27 | 93.15 | Power interruption
Naogaon 132/33kV | T-3 HT | 2025-05-19 06:50 | 2025-05-19 10:18 | 0.14444 | E/O | Atrai PBS 33KV feeder Bus DS connecting R & Y Phase loop Maintenance. | 0 | 0 | No interruption
Natore 132/33kV | TR-3 (425 T) | 2025-05-23 08:40 | 2025-05-23 10:18 | 0.068056 | E/O | T-3 33 kv bus emergency maintenance | 20 | 32.6667 | Power interruption
Niamatpur 132/33kV | Transformer-1(407T) | 2025-05-05 16:27 | 2025-05-05 16:37 | 0.0069444 | T | 33 kv sapahar feeder fault. Dir O/C & E/F Relay 67/67N. | 15 | 2.5 | Power interruption
Niamatpur 132/33kV | Transformer-1(407T) | 2025-05-28 12:39 | 2025-05-28 14:04 | 0.059028 | E/O | Emergency maintenance. | 0 | 0 | No interruption
Niamatpur 132/33kV | Transformer-2 (417T) | 2025-05-28 19:28 | 2025-05-28 20:42 | 0.051389 | E/O | 33kV DS R Phase Red Hot | 28 | 34.5333 | Power interruption
Palashbari 132/33kV | TR1-414T | 2025-05-03 09:23 | 2025-05-03 10:02 | 0.027083 | E/O | Red Hot Maintenance | 15 | 9.75 | Power interruption
Palashbari 132/33kV | TR1-414T | 2025-05-17 08:28 | 2025-05-17 11:37 | 0.13125 | E/O | Shutdown Proposal Due to T1 Transformer 33 kV B phase CT P1 terminal connector red hot. | 0 | 0 | No interruption
Palashbari 132/33kV | TR3-424T | 2025-05-18 11:46 | 2025-05-18 13:32 | 0.073611 | E/O | Oil leakage | 0 | 0 | No interruption
Palashbari 132/33kV | TR4-434T | 2025-05-20 13:48 | 2025-05-20 15:27 | 0.06875 | E/O | Due to T4 Transformer 33 kV Breaker R phase Connector Change | 0 | 0 | No interruption
Palashbari 132/33kV | TR2-404T | 2025-05-25 10:31 | 2025-05-25 11:05 | 0.023611 | E/O | Red hot maintenance | 0 | 0 | No interruption
Panchagarh 132/33kV | T-3(A+B)(427T) | 2025-05-01 08:58 | 2025-05-01 12:00 | 0.12639 | E/O | T-3(A+B) Transformer (A) underground cable and 33KV R phase bussing juntion abnormal sound | 0 | 0 | No interruption
Purbasadipur 132/33kV | T-3 Transformer (423T) | 2025-05-21 15:36 | 2025-05-21 17:21 | 0.072917 | E/O | 33kV feeder Uthrail and chirirbandor red hot maintenance | 40 | 70 | Power interruption
Sirajganj 132/33kV | T1-(415) | 2025-05-01 14:04 | 2025-05-01 14:08 | 0.0027778 | E/O | Due to the T-1 33kV Section BUS charge after maintenance work, T-1 33kV has been taken Shutdown.This Shutdown has been taken By AGM Com Sirajgonj PBS-2 | 0 | 0 | No interruption
|  |  | Total : | 1900-01-05 01:41 |  | Unserved Energy: |  | 1317.7667
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 1900-02-01 04:22 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: May 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | Gopalganj-2 | 2025-05-27 18:41 | 2025-05-27 19:54 | 0.050694 | T | Unknown | 0 | 0 | No interruption
Bhaluka 132/33kV | BR Powergen Ckt- 02 | 2025-05-14 12:30 | 2025-05-14 12:44 | 0.0097222 | T | Distance R-Ph, Zone -1 | 0 | 0 | No interruption
Ghatail 132/33kV | Muktagacha-2 | 2025-05-26 11:04 | 2025-05-26 12:07 | 0.04375 | E/O | Emergency maint.work | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-02 | 2025-05-11 16:21 | 2025-05-11 16:33 | 0.0083333 | T | Tripped | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-01 | 2025-05-31 12:26 | 2025-05-31 12:40 | 0.0097222 | T | Fault | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Kodda ckt-1 | 2025-05-13 16:32 | 2025-05-13 16:44 | 0.0083333 | T | Fault at Kodda end. | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Kodda ckt-2 | 2025-05-13 16:32 | 2025-05-13 17:41 | 0.047917 | T | Tripped | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-1 | 2025-05-16 19:33 | 2025-05-17 10:57 | 0.64167 | T | STROM | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Aminbazar -1 | 2025-05-05 06:26 | 2025-05-05 17:33 | 0.46319 | E/O | by NLDC | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Dhamrai-1 | 2025-05-13 11:36 | 2025-05-13 15:47 | 0.17431 | E/O | By NLDC | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Dhamrai-2 | 2025-05-19 09:40 | 2025-05-19 17:50 | 0.34028 | E/O | By NLDC | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Dhamrai-2 | 2025-05-20 09:14 | 2025-05-20 18:02 | 0.36667 | E/O | By NLDC | 0 | 0 | No interruption
Rajendrapur 132/33kV | Kodda-1 | 2025-05-08 05:18 | 2025-05-08 14:25 | 0.37986 | E/O | For kodda ckt-1 red hot maintenance work in DS at kodda sub-station | 0 | 0 | No interruption
Rajendrapur 132/33kV | Kodda-1 | 2025-05-25 03:58 | 2025-05-25 12:34 | 0.35833 | E/O | Emergency maint.work | 0 | 0 | No interruption
Rajendrapur 132/33kV | Kodda-1 | 2025-05-29 06:26 | 2025-05-31 12:49 | 1900-01-01 06:23 | E/O | Ordered By NLDC | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Basundhara Ckt-1 | 2025-05-05 12:28 | 2025-05-05 12:42 | 0.0097222 | T | Tripped | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Uttara 3rd Phase Ckt | 2025-05-10 18:19 | 2025-05-10 19:48 | 0.061806 | T | Tripped | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2025-05-11 17:00 | 2025-05-11 17:07 | 0.0048611 | T | Tripped | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Uttara 3rd Phase Ckt | 2025-05-11 17:10 | 2025-05-13 15:45 | 1899-12-31 22:35 | T | Tripped | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Basundhara Ckt-1 | 2025-05-16 19:44 | 2025-05-16 20:21 | 0.025694 | T | Stormy weather | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Ghorashal Ckt-1 | 2025-05-17 05:28 | 2025-05-17 06:42 | 0.051389 | T | Tripped | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2025-05-30 09:03 | 2025-05-30 19:40 | 0.44236 | T | Tripped | 0 | 0 | No interruption
|  |  | Total : | 1900-01-06 16:56 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Fatullah 132/33kV | 132 kV Shyampur-2 | 2025-05-07 17:40 | 2025-05-07 18:03 | 0.015972 | T | None | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi circuit-1 | 2025-05-06 12:04 | 2025-05-06 14:45 | 0.11181 | T | Bammbo | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi Circuit-2 | 2025-05-10 11:44 | 2025-05-10 13:37 | 0.078472 | T | PBS transformer blust at Dhamrai. | 0 | 0 | No interruption
Haripur 230/132kV | Ullon (Maniknagar-2) | 2025-05-03 12:16 | 2025-05-03 13:19 | 0.04375 | T | Thundering & Rainfall | 0 | 0 | No interruption
Haripur 230/132kV | Ullon (Maniknagar-2) | 2025-05-14 15:24 | 2025-05-14 21:01 | 0.23403 | T | Raining & Thundering. | 0 | 0 | No interruption
Haripur 230/132kV | Ullon (Maniknagar-2) | 2025-05-16 19:55 | 2025-05-16 20:30 | 0.024306 | T | Tripped | 0 | 0 | No interruption
Haripur 230/132kV | Meghnaghat-1 | 2025-05-16 21:37 | 2025-05-16 22:44 | 0.046528 | T | Tripped | 0 | 0 | No interruption
Haripur 230/132kV | Madanganj-1 | 2025-05-16 21:38 | 2025-05-16 21:43 | 0.0034722 | T | Thunderstorm. | 0 | 0 | No interruption
Hasnabad 132/33kV | Shitallakhya | 2025-05-11 17:30 | 2025-05-11 17:42 | 0.0083333 | T | Tripped | 0 | 0 | No interruption
Hasnabad 132/33kV | Shitallakhya | 2025-05-16 21:35 | 2025-05-16 22:22 | 0.032639 | T | Tripped | 70 | 54.8333 | Power interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 2 | 2025-05-18 18:44 | 2025-05-18 21:15 | 0.10486 | T | Distance relay operated. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Aminbazar Ckt. 2 | 2025-05-26 12:51 | 2025-05-26 13:35 | 0.030556 | T | Tripped | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Munshiganj 132 kv Ckt-2 | 2025-05-17 00:09 | 2025-05-17 11:45 | 0.48333 | T | Due to heavy rain & storm | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Shitalakhya 132 kv Ckt | 2025-05-22 06:11 | 2025-05-22 10:08 | 0.16458 | E/O | Due Load management of NLDC | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -DPDC Char sayedpur 132k Ckt-1 | 2025-05-28 16:13 | 2025-05-28 20:04 | 0.16042 | E/O | DPDC work | 0 | 0 | No interruption
Maniknagar 230/132kV | 230kV Siddhirganj-Maniknagar ckt-1 | 2025-05-16 21:05 | 2025-05-16 22:31 | 0.059722 | T | Trip | 0 | 0 | No interruption
Meghnaghat 230/132kV | Meghnaghat-Haripur-01 | 2025-05-16 21:37 | 2025-05-16 22:48 | 0.049306 | T | Trip | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat- Shyampur 230kv -Ckt 2 | 2025-05-14 19:01 | 2025-05-14 20:03 | 0.043056 | T | Trip | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Shyampur 230kV Ckt-1 | 2025-05-16 21:40 | 2025-05-16 23:50 | 0.090278 | T | Trip | 0 | 0 | No interruption
Munshiganj 132/33kV | Madanganj- Munshiganj- Ckt-2 | 2025-05-17 00:10 | 2025-05-17 11:48 | 0.48472 | T | Unblance Load Current in red phase | 0 | 0 | No interruption
Rampura 230/132kV | Basundhara-01 | 2025-05-05 16:16 | 2025-05-05 16:27 | 0.0076389 | T | Unknown. | 0 | 0 | No interruption
Rampura 230/132kV | Ullon-01 | 2025-05-25 17:58 | 2025-05-26 11:58 | 0.75 | T | R-ph LA burned/burst at the time of the restoring shutdown event. | 0 | 0 | No interruption
Rampura 230/132kV | Bhulta Ckt-04 | 2025-05-31 16:10 | 2025-05-31 16:18 | 0.0055556 | T | N/A | 0 | 0 | No interruption
Shyampur 132/33kV | Shyampur Circuit-2 | 2025-05-08 15:09 | 2025-05-08 18:32 | 0.14097 | T | None | 0 | 0 | No interruption
Shyampur 132/33kV | Shyampur Circuit-1 | 2025-05-08 15:11 | 2025-05-08 15:55 | 0.030556 | T | Trip | 80 | 58.6667 | Power interruption
Shyampur 132/33kV | Shyampur Circuit-1 | 2025-05-14 22:48 | 2025-05-15 20:35 | 0.90764 | T | LA flashing of Y phase & Line conductor of Red phase Breaks | 60 | 25 | Power interruption
Shyampur 230/132kV | 132 kV Shyampur old-1(E07) | 2025-05-14 18:51 | 2025-05-14 20:10 | 0.054861 | T | Distance protection. | 0 | 0 | No interruption
Shyampur 230/132kV | 132 kV Shyampur old-1(E07) | 2025-05-14 22:50 | 2025-05-15 20:36 | 0.90694 | T | Distance protection, Loop open at Shyampur substation. | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV Meghnaghat-1(D06) | 2025-05-16 21:38 | 2025-05-16 23:50 | 0.091667 | T | Distance Protection Operated, | 0 | 0 | No interruption
Siddhirganj 132/33kV | Ullon 1 | 2025-05-03 12:16 | 2025-05-03 12:53 | 0.025694 | T | Storm & Lightning | 37 | 22.8167 | Power interruption
Siddhirganj 132/33kV | 100MW Dutch Bangla | 2025-05-08 08:50 | 2025-05-08 14:44 | 0.24583 | T | E/F, | 0 | 0 | No interruption
Siddhirganj 132/33kV | 120MW EGCB GT1 | 2025-05-08 08:50 | 2025-05-08 11:48 | 0.12361 | T | Dutchbangla Line fault | 0 | 0 | No interruption
Siddhirganj 132/33kV | 100MW Dutch Bangla | 2025-05-08 14:59 | 2025-05-08 21:08 | 0.25625 | E/O | Y Ph Lope Disconnect | 0 | 0 | No interruption
Sonargaon 132/33kV | Daudkandi-01 | 2025-05-15 15:28 | 2025-05-15 16:07 | 0.027083 | T | Perhaps bad weather , NB: no sound during trip | 0 | 0 | No interruption
|  |  | Total : | 1900-01-04 20:16 |  | Unserved Energy: |  | 161.3167
Chattogram Grid Circle :
BSRM 230/33kV | GPH Ispat Ckt. -01 | 2025-05-06 15:21 | 2025-05-06 17:16 | 0.079861 | E/O | Baro Awlia Substation Emergency Work. | 0 | 0 | No interruption
Coxsbazar 132/33kV | Doh-Cox Ckt-1 | 2025-05-26 12:32 | 2025-05-26 12:53 | 0.014583 | T | Phase B,C & Zone-2 fault | 0 | 0 | No interruption
Coxsbazar 132/33kV | Doh-Cox Ckt-1 | 2025-05-31 07:50 | 2025-05-31 08:08 | 0.0125 | T | Phase A & zone 1 fault | 25 | 7.5 | Power interruption
Coxsbazar 132/33kV | Doh-Cox Ckt-2 | 2025-05-31 07:51 | 2025-05-31 08:05 | 0.0097222 | T | Phase R & B, Zone-1 fault | 64 | 14.9333 | Power interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-1 | 2025-05-26 12:25 | 2025-05-26 12:51 | 0.018056 | T | Tripped | 38 | 16.4667 | Power interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-1 | 2025-05-30 11:22 | 2025-05-30 11:45 | 0.015972 | T | Tripped | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-2 | 2025-05-30 11:22 | 2025-05-30 11:30 | 0.0055556 | T | Tripped | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-1 | 2025-05-31 07:51 | 2025-05-31 08:07 | 0.011111 | T | Tripped | 66 | 17.6 | Power interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-2 | 2025-05-31 07:51 | 2025-05-31 08:04 | 0.0090278 | T | Tripped | 55 | 11.9167 | Power interruption
GPH 230/33kV | BSRM CKT-1 | 2025-05-06 15:13 | 2025-05-06 17:17 | 0.086111 | E/O | To remove the kite | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Rampur Ckt-1 | 2025-05-30 03:48 | 2025-05-30 04:38 | 0.034722 | T | Over voltage. | 0 | 0 | No interruption
Hathazari 230/132/33kV | Baroaulia-01 | 2025-05-09 05:11 | 2025-05-09 05:42 | 0.021528 | T | over current | 40 | 20.6667 | Power interruption
Hathazari 230/132/33kV | Baroaulia-02 | 2025-05-09 05:11 | 2025-05-09 05:42 | 0.021528 | T | over current | 40 | 20.6667 | Power interruption
Hathazari 230/132/33kV | Baroiarhat-01 | 2025-05-13 12:54 | 2025-05-13 13:21 | 0.01875 | T | Tripped | 0 | 0 | No interruption
Hathazari 230/132/33kV | Baroiarhat-02 | 2025-05-13 12:54 | 2025-05-13 13:22 | 0.019444 | T | Tripped | 0 | 0 | No interruption
Hathazari 230/132/33kV | Kaptai-01 | 2025-05-26 18:40 | 2025-05-26 19:39 | 0.040972 | T | trip outside heavily rain | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2025-05-03 00:26 | 2025-05-03 00:40 | 0.0097222 | T | Tripped | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Sikalbaha | 2025-05-03 13:05 | 2025-05-03 15:10 | 0.086806 | E/O | work at Sikalbaha end | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Sikalbaha | 2025-05-09 10:58 | 2025-05-09 11:12 | 0.0097222 | T | Tripped | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-T.K. chemical complex | 2025-05-09 04:33 | 2025-05-09 07:41 | 0.13056 | T | The bus loop conductor is broken at the TK Chemical Grid Substation. | 0 | 0 | No interruption
Mirsorai 230/33kV | EGCB 75MW Solar Power Station | 2025-05-27 15:27 | 2025-05-28 10:58 | 0.81319 | T | DS (Q1) adjacent to Bus-1, Flashing of EGCB Feeder due to release gas from DS Compartment by Contractor. | 0 | 0 | No interruption
Mirsorai 230/33kV | 150 MW Power Station -02 | 2025-05-27 15:27 | 2025-05-27 16:58 | 0.063194 | T | DS (Q1) adjacent to Bus-1, Flashing of EGCB Feeder due to release gas from DS Compartment by Contractor. | 12 | 18.2 | Power interruption
Mirsorai 230/33kV | 150 MW Power Station -01 | 2025-05-27 15:27 | 2025-05-27 17:24 | 0.08125 | T | DS (Q1) adjacent to Bus-1, Flashing of EGCB Feeder due to release gas from DS Compartment by Contractor. | 0 | 0 | No interruption
Mirsorai 230/33kV | BSRM-1 | 2025-05-27 15:27 | 2025-05-27 17:22 | 0.079861 | T | DS (Q1) adjacent to Bus-1, Flashing of EGCB Feeder due to release gas from DS Compartment by Contractor. | 12 | 23 | Power interruption
Shahmirpur 132/33kV | Sikalbaha-1 | 2025-05-10 12:44 | 2025-05-10 15:45 | 0.12569 | E/O | Works at Sikalbaha end | 0 | 0 | No interruption
Shahmirpur 132/33kV | Julda-1 | 2025-05-22 14:40 | 2025-05-22 15:36 | 0.038889 | T | Julda Unit 3 power plant fault. | 53 | 49.4667 | Power interruption
Shahmirpur 132/33kV | Julda-2 | 2025-05-22 14:41 | 2025-05-22 15:36 | 0.038194 | T | Julda Unit 3 power plant fault. | 53 | 48.5833 | Power interruption
Shikalbaha 230/132kV | Modunaghat Ckt-2(T.K Chemical) | 2025-05-09 04:33 | 2025-05-09 04:33 | 0 | T | Tripped | 0 | 0 | No interruption
Shikalbaha 230/132kV | Julda | 2025-05-09 05:11 | 2025-05-09 08:49 | 0.15139 | T | Tripped | 1 | 3.6333 | Power interruption
Shikalbaha 230/132kV | Shahmirpur-1 | 2025-05-09 05:11 | 2025-05-09 07:53 | 0.1125 | T | Tripped | 0 | 0 | No interruption
Shikalbaha 230/132kV | Shahmirpur-2 | 2025-05-09 05:11 | 2025-05-09 07:54 | 0.11319 | T | Tripped | 0 | 0 | No interruption
Shikalbaha 230/132kV | Dohazari ckt-1 | 2025-05-09 05:11 | 2025-05-09 07:21 | 0.090278 | T | Tripped | 0 | 0 | No interruption
Shikalbaha 230/132kV | Dohazari Ckt-2 | 2025-05-09 05:11 | 2025-05-09 07:49 | 0.10972 | T | Tripped | 0 | 0 | No interruption
Shikalbaha 230/132kV | Bakulia-1 | 2025-05-09 05:11 | 2025-05-09 07:19 | 0.088889 | T | Tripped | 0 | 0 | No interruption
Shikalbaha 230/132kV | Bakulia-2 | 2025-05-09 05:11 | 2025-05-09 08:02 | 0.11875 | T | Tripped | 0 | 0 | No interruption
Shikalbaha 230/132kV | Interconnection-1 | 2025-05-09 05:11 | 2025-05-09 08:14 | 0.12708 | T | Tripped | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 19:24 |  | Unserved Energy: |  | 252.6333
Cumilla Grid Circle :
Ashuganj 230/132/33kV | Ghorashal 132 kV Ckt-2 | 2025-05-10 14:44 | 2025-05-10 15:13 | 0.020139 | T | Trip | 0 | 0 | No interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-2 | 2025-05-11 06:16 | 2025-05-11 07:02 | 0.031944 | T | Sulhet-Fenchugang line -2 trip | 4 | 3.0667 | Power interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-1 | 2025-05-05 06:06 | 2025-05-05 08:31 | 0.10069 | E/O | Emergency Maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-1 | 2025-05-06 14:04 | 2025-05-06 15:01 | 0.039583 | T | Trip | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-2 | 2025-05-12 06:04 | 2025-05-12 07:30 | 0.059722 | E/O | S/D taken by NLDC | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-1 | 2025-05-17 14:36 | 2025-05-17 15:09 | 0.022917 | T | Trip | 0 | 0 | No interruption
Chauddagram 132/33kV | Feni-2 | 2025-05-24 15:30 | 2025-05-24 19:30 | 0.16667 | E/O | Emergency Maintenance in Feni Grid. | 0 | 0 | No interruption
Chowmuhani 132/33kV | Feni line-01 | 2025-05-24 20:10 | 2025-05-25 16:29 | 0.84653 | T | Chowmuhoni-Feni-1 Jumper out Phase-c | 0 | 0 | No interruption
Chowmuhani 132/33kV | Feni line-01 | 2025-05-24 22:35 | 2025-05-25 16:29 | 0.74583 | E/O | Distance Relay A & B Phase SOTF Shown C Phase Jumper Out | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 132KV Cumilla(N)-Kachua Ckt-1 | 2025-05-02 12:46 | 2025-05-03 18:15 | 1899-12-31 05:29 | T | Trip | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-BSRM Ckt-1 | 2025-05-10 11:48 | 2025-05-10 12:14 | 0.018056 | T | Trip | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 132KV Cumilla(N)-Daudkandi Ckt-1 | 2025-05-10 15:42 | 2025-05-10 15:54 | 0.0083333 | T | Trip | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 132KV Cumilla(N)-Daudkandi Ckt-1 | 2025-05-10 15:59 | 2025-05-10 18:24 | 0.10069 | T | Trip | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Meghnagat Ckt 1 | 2025-05-27 14:01 | 2025-05-27 15:19 | 0.054167 | T | Trip | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Tripura Ckt-1 | 2025-05-28 16:50 | 2025-05-28 17:40 | 0.034722 | T | Tripura end Trip, Bangladesh end C.B not trip. | 18 | 15 | Power interruption
Cumilla(S) 132/33kV | Tripura Ckt-2 | 2025-05-28 16:50 | 2025-05-28 17:42 | 0.036111 | T | Tripura end Trip, Bangladesh end C.B not trip. | 18 | 15.6 | Power interruption
Daudkandi 132/33kV | Sonargaon-1 | 2025-05-15 15:28 | 2025-05-15 16:10 | 0.029167 | T | over current Earth Fault | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sylhet-2 | 2025-05-11 06:16 | 2025-05-11 06:21 | 0.0034722 | T | Bad Weather | 24 | 2 | Power interruption
Fenchuganj 230/132/33kV | Sylhet-2 | 2025-05-11 06:22 | 2025-05-11 07:03 | 0.028472 | E/O | Emergency Maintenance | 24 | 16.4 | Power interruption
Fenchuganj 230/132/33kV | Sreemongal-1 | 2025-05-19 14:18 | 2025-05-19 14:50 | 0.022222 | T | Bad weather | 0 | 0 | No interruption
Kachua 132/33kV | Cumilla North CKT | 2025-05-01 09:16 | 2025-05-01 10:13 | 0.039583 | T | Due to kite flying on the kachua -cumilla north ckt line. | 0 | 0 | No interruption
Kachua 132/33kV | Cumilla North CKT | 2025-05-02 12:47 | 2025-05-02 13:05 | 0.0125 | T | Trip | 0 | 0 | No interruption
Kachua 132/33kV | Cumilla North CKT | 2025-05-02 13:05 | 2025-05-02 13:05 | 0 | E/O | Emergency Maintenance | 0 | 0 | No interruption
Kachua 132/33kV | Cumilla North CKT | 2025-05-03 09:50 | 2025-05-03 10:20 | 0.020833 | T | not found yet | 0 | 0 | No interruption
Kachua 132/33kV | Cumilla North CKT | 2025-05-03 10:20 | 2025-05-03 10:20 | 0 | E/O | for fault remove. | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-01 | 2025-05-17 14:39 | 2025-05-17 15:08 | 0.020139 | T | Heavy Rain and Stormy Weather | 0 | 0 | No interruption | 0
Shahjibazar 132/33kV | BPDB 60 MW | 2025-05-19 13:38 | 2025-05-19 14:07 | 0.020139 | T | Heavy Rain stormy weather, CT blust from 86 MW power plant. | 0 | 0 | No interruption | 0
Shahjibazar 132/33kV | SPCL 86 MW | 2025-05-19 13:38 | 2025-05-19 14:05 | 0.01875 | T | Heavy Rain stormy weather, CT blust from 86 MW power plant. | 0 | 0 | No interruption | 0.0125
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-01 | 2025-05-27 11:25 | 2025-05-27 11:36 | 0.0076389 | T | N/A | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal-Fenchugonj circuit-1 | 2025-05-19 14:18 | 2025-05-19 14:49 | 0.021528 | T | Stormy weather | 0 | 0 | No interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-1 | 2025-05-11 06:15 | 2025-05-11 07:26 | 0.049306 | T | Thundering | 1 | 1.1833 | Power interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-2 | 2025-05-11 06:15 | 2025-05-11 07:26 | 0.049306 | T | Thundering | 1 | 1.1833 | Power interruption
|  |  | Total : | 1900-01-02 20:35 |  | Unserved Energy: |  | 54.4333
Khulna Grid Circle :
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2025-05-08 11:43 | 2025-05-08 12:12 | 0.020139 | T | Tripped | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2025-05-09 11:35 | 2025-05-09 12:10 | 0.024306 | T | Unknown | 0 | 0 | No interruption
Barishal 132/33kV | 132kv Bhandaria ckt | 2025-05-11 11:13 | 2025-05-11 12:33 | 0.055556 | T | Unknown. | 43 | 57.3333 | Power interruption
Barishal 230/132kV | Madaripur ckt-02 | 2025-05-17 18:27 | 2025-05-17 22:18 | 0.16042 | E/O | Taken by ALDC | 0 | 0 | No interruption
Barishal 230/132kV | Madaripur ckt-02 | 2025-05-22 15:48 | 2025-05-22 18:04 | 0.094444 | E/O | TCS -1 fail repair | 0 | 0 | No interruption
Bhandaria 132/33kV | Barishal (L4) | 2025-05-11 22:21 | 2025-05-11 23:14 | 0.036806 | E/O | Red hot maintenance of barishal grid end. | 30 | 26.5 | Power interruption
Gollamari 132/33kV | E01 Gollamari-Gopalgonj Line - 1 | 2025-05-13 09:42 | 2025-05-13 10:49 | 0.046528 | E/O | To Remove Kite near (Tower-02) location | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-3 | 2025-05-19 17:39 | 2025-05-19 21:09 | 0.14583 | T | Phase to phase fault | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- South -1 | 2025-05-23 21:06 | 2025-05-24 02:53 | 0.24097 | T | R Phase wire tear up. | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-1 | 2025-05-19 08:27 | 2025-05-19 09:55 | 0.061111 | T | Tripped | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-2 | 2025-05-19 08:27 | 2025-05-19 09:59 | 0.063889 | T | Tripped | 0 | 0 | No interruption
Khulna(S) 230/132kV | Satkhira Ckt-1 | 2025-05-19 08:27 | 2025-05-19 10:00 | 0.064583 | T | Tripped | 0 | 0 | No interruption
Khulna(S) 230/132kV | Satkhira Ckt-2 | 2025-05-19 08:27 | 2025-05-19 10:09 | 0.070833 | T | Tripped | 0 | 0 | No interruption
Khulna(S) 230/132kV | Gallamari Ckt-1 | 2025-05-19 08:27 | 2025-05-19 11:20 | 0.12014 | T | Tripped | 0 | 0 | No interruption
Khulna(S) 230/132kV | Gallamari Ckt-2 | 2025-05-19 08:27 | 2025-05-19 11:20 | 0.12014 | T | Tripped | 0 | 0 | No interruption
Khulna(S) 230/132kV | Capacitor Bank 1 & 2 | 2025-05-19 08:27 | 2025-05-21 11:39 | 1900-01-01 03:12 | T | Tripped | 0 | 0 | No interruption
Madaripur 132/33kV | Gopaganj North CKT-03 | 2025-05-19 17:39 | 2025-05-19 21:09 | 0.14583 | T | A-B-N Trip ABC Over Current Earth Fault Z-1, 1.388 km A- 9732, B- 9827, C - 238.7 | 0 | 0 | No interruption
Mongla 132/33kV | 100MW ERBL Solar PS | 2025-05-19 08:56 | 2025-05-19 08:59 | 0.0020833 | T | CB Open instruction by ALDC Due to Black out. | 68 | 3.4 | Power interruption
Rajbari 132/33kV | Bheramara-2 | 2025-05-17 21:21 | 2025-05-17 22:12 | 0.035417 | T | 3 phase fault. | 0 | 0 | No interruption
Satkhira 132/33kV | Khulna South-1 (L-1) | 2025-05-19 09:23 | 2025-05-19 10:01 | 0.026389 | E/O | Khulna south grid maintenance work | 55 | 34.8333 | Power interruption
Satkhira 132/33kV | Khulna South-2 (L-2) | 2025-05-19 09:23 | 2025-05-19 10:09 | 0.031944 | E/O | Khulna south grid maintenance work | 55 | 42.1667 | Power interruption
|  |  | Total : | 1900-01-02 16:49 |  | Unserved Energy: |  | 164.2333
HVDC Grid Circle :
Bhangura 132/33kV | Bhangura-Bhagabari ckt-1 | 2025-05-08 11:41 | 2025-05-08 12:25 | 0.030556 | T | Bagabari side trip | 37 | 27.1333 | Power interruption
BIPTC | 20DF24 | 2025-05-09 12:17 | 2025-05-12 16:41 | 1900-01-02 04:24 | T | Tripped by impedance 21R | 0 | 0 | No interruption
BIPTC | 10CF16 | 2025-05-15 10:21 | 2025-05-15 11:12 | 0.035417 | E/O | Due to unbalance 60/61 instant L3 | 0 | 0 | No interruption
BIPTC | 20DF12 | 2025-05-16 20:17 | 2025-05-17 12:29 | 0.675 | T | Tripped by C1 unbalance 60/61 instant L1-Trip. | 0 | 0 | No interruption
BIPTC | 20DF22 | 2025-05-23 03:33 | 2025-05-24 13:37 | 1899-12-31 10:04 | T | C1 unbalance 60/61 CPR04 tripped | 0 | 0 | No interruption
BIPTC | 20DF22 | 2025-05-24 10:00 | 2025-05-24 13:37 | 0.15069 | E/O | Emergency maint.work | 0 | 0 | No interruption
BIPTC | 10CF25 | 2025-05-30 15:53 | 2025-05-30 16:26 | 0.022917 | E/O | Emergency maint.work | 0 | 0 | No interruption
Chuadanga 132/33kV | Jhenaidah-Chuadanga Ckt-2 | 2025-05-10 09:52 | 2025-05-10 20:58 | 0.4625 | T | Line -2 LA Blust. | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2025-05-02 11:05 | 2025-05-02 11:39 | 0.023611 | T | C phase to Ground fault | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2025-05-06 12:00 | 2025-05-06 14:44 | 0.11389 | T | C Phase to ground fault distance -134 Km Zone-1 SOTF | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 2 | 2025-05-10 11:44 | 2025-05-10 13:38 | 0.079167 | T | Trip | 0 | 0 | No interruption
Jhenaidah 132/33kV | Jhenaidah-Magura 132kV Circuit-2(L6) | 2025-05-06 11:38 | 2025-05-06 12:05 | 0.01875 | T | Trip | 0 | 0 | No interruption
Jhenaidah 132/33kV | Jhenaidah-Chuadanga, 132kV Circuit-2(L8) | 2025-05-10 09:52 | 2025-05-10 21:08 | 0.46944 | T | Trip | 0 | 0 | No interruption
Jhenaidah 132/33kV | Jhenaidah1-Jhenaidah2,132kV Circuit-2(L3) | 2025-05-12 07:28 | 2025-05-12 10:01 | 0.10625 | E/O | Maintenance work for jhenaidah 230 kv ss. | 0 | 0 | No interruption
Jhenaidah 132/33kV | Jhenaidah1-Jhenaidah2,132kV Circuit-3(L5) | 2025-05-20 07:18 | 2025-05-20 10:05 | 0.11597 | E/O | 132kV Jhenaidah-230kV Jhenaidah CKT-3 (L-5) Red Hot Manitenance at Jhenaidah 230kV SS End. | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-Jhenaidah (Old) Ckt-3 | 2025-05-20 07:17 | 2025-05-20 10:04 | 0.11597 | E/O | Red Hot maintenance | 0 | 0 | No interruption
Pabna 132/33kV | Pabna-Shahjadpur Line | 2025-05-22 09:40 | 2025-05-22 13:59 | 0.17986 | E/O | CB SF6 Gas leakage maintenance. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-06 04:52 |  | Unserved Energy: |  | 27.1333
Bogura Grid Circle:
Amnura 132/33kV | Amnura - Rajshahi | 2025-05-17 02:30 | 2025-05-17 02:53 | 0.015972 | T | N/A | 0 | 0 | No interruption
Bogura 132/33kV | Mahasthangarh-2 | 2025-05-02 10:36 | 2025-05-02 18:31 | 0.32986 | E/O | Mahasthan ckt-2 CB SF6 gas leakage problem. | 0 | 0 | No interruption
Bogura 230/132kV | Confidance UN-2 | 2025-05-17 01:12 | 2025-05-17 02:33 | 0.05625 | T | Due to Rain | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-1 | 2025-05-21 22:33 | 2025-05-22 00:25 | 0.077778 | T | Rain & Storming | 59 | 110.1333 | Power interruption
Bogura 230/132kV | Naogaon 132 KV Line-2 | 2025-05-21 22:33 | 2025-05-21 23:17 | 0.030556 | T | Rain & Storming | 59 | 43.2667 | Power interruption
Bogura 230/132kV | Naogaon 132 KV Line-1 | 2025-05-22 16:19 | 2025-05-22 17:14 | 0.038194 | E/O | Emergency maint.work | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-2 | 2025-05-22 16:19 | 2025-05-23 17:23 | 1899-12-31 01:04 | E/O | Emergency maint.work | 0 | 0 | No interruption
Bogura 400/230kV | 400 KV Reactor (125 MVAR) | 2025-05-03 17:21 | 2025-05-17 01:19 | 1900-01-12 07:58 | E/O | ALDC Instruction. | 0 | 0 | No interruption
Kurigram 132/33kV | Rangpur-Kurigram Ckt-01 | 2025-05-01 10:03 | 2025-05-01 10:20 | 0.011806 | T | N/A | 32 | 9.0667 | Power interruption
Kurigram 132/33kV | Rangpur-Kurigram Ckt-01 | 2025-05-19 13:08 | 2025-05-19 16:20 | 0.13333 | E/O | Signal checking & annunciator | 30 | 96 | Power interruption
Mahasthangarh 132/33kV | Mahasthangarh-Bogura 2 | 2025-05-02 10:36 | 2025-05-02 18:30 | 0.32917 | E/O | Bogura ckt-02 CB gas leakage work at bogura end. | 0 | 0 | No interruption
Mithapukur 132/33kV | Palashbari-2 | 2025-05-11 22:06 | 2025-05-11 22:43 | 0.025694 | T | Tripped | 0 | 0 | No interruption
Naogaon 132/33kV | Nao-Bog Ckt-2 | 2025-05-10 09:49 | 2025-05-10 12:37 | 0.11667 | E/O | As following instruction of ALDC Bogura. | 0 | 0 | No interruption
Naogaon 132/33kV | Nao-Bog Ckt-1 | 2025-05-22 11:17 | 2025-05-22 11:26 | 0.00625 | T | Tripped | 0 | 0 | No interruption
Naogaon 132/33kV | Nao-Bog Ckt-1 | 2025-05-22 16:14 | 2025-05-22 17:25 | 0.049306 | E/O | Removing the string of kite. | 0 | 0 | No interruption
Naogaon 132/33kV | Nao-Bog Ckt-2 | 2025-05-22 16:16 | 2025-05-23 17:22 | 1899-12-31 01:06 | E/O | Removing the string of kite. | 0 | 0 | No interruption
Niamatpur 132/33kV | 132 kV Rahanpur Ckt-2 | 2025-05-19 08:20 | 2025-05-19 08:20 | 0 | T | Poesha feeder trial এ o/c & E/F signal এসে ট্রিপ করে । | 0 | 0 | No interruption
Niamatpur 132/33kV | 132 kV Naogaon ckt-1 | 2025-05-22 17:22 | 2025-05-22 17:22 | 0 | E/O | NLDC এর নির্দেশে CB ( 102 B ) ওপেন করা হল . | 0 | 0 | No interruption
Palashbari 132/33kV | Mithapukur-02 | 2025-05-11 22:06 | 2025-05-11 22:43 | 0.025694 | T | Tripped | 0 | 0 | No interruption
Panchagarh 132/33kV | Thakurgaon-1 | 2025-05-31 22:56 | 2025-05-31 23:56 | 0.041667 | T | Tripped | 0 | 0 | No interruption
Purbasadipur 132/33kV | Saidpur Line-1 | 2025-05-21 13:14 | 2025-05-21 13:14 | 0 | E/O | To Check Saidpur-01 Protection Circuit | 0 | 0 | No interruption
Purbasadipur 132/33kV | Saidpur Line-2 | 2025-05-22 13:10 | 2025-05-22 13:56 | 0.031944 | T | Tripped | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Confidence-2 | 2025-05-07 21:25 | 2025-05-07 22:43 | 0.054167 | E/O | teamparature high | 26 | 33.8 | Power interruption
Rangpur 132/33kV | Rangpur-Confidence-1 | 2025-05-15 02:46 | 2025-05-15 03:44 | 0.040278 | T | Thandaring and Rain | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Saidpur-2 | 2025-05-30 20:16 | 2025-06-02 09:19 | 1900-01-01 13:03 | E/O | Emergency maint.work | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Saidpur-1 | 2025-05-31 18:28 | 2025-06-02 09:18 | 1899-12-31 14:50 | E/O | Emergency maint.work | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Purbosadipur CKT-02 | 2025-05-22 13:11 | 2025-05-22 13:55 | 0.030556 | T | Tripped | 0 | 0 | No interruption
Thakurgaon 132/33kV | Panchagar CKT-1 | 2025-05-13 05:37 | 2025-05-13 05:58 | 0.014583 | T | Tripped | 15 | 5.25 | Power interruption
Thakurgaon 132/33kV | Panchagar CKT-2 | 2025-05-13 05:37 | 2025-05-13 07:40 | 0.085417 | T | Tripped | 15 | 30.75 | Power interruption
Thakurgaon 132/33kV | Panchagar CKT-1 | 2025-05-31 22:59 | 2025-05-31 23:55 | 0.038889 | T | Thundering and Heavy Rain | 0 | 0 | No interruption
|  |  | Total : | 1900-01-20 04:02 |  | Unserved Energy: |  | 328.2667
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 1900-02-20 06:54 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
| Ashuganj-2 | 2024-11-13 12:06 | 2024-11-13 12:18

## QF-LDC-25
QF-LDC-25
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: May 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV | 230kV Transformer-2 ( 715T2) | 2025-05-13 05:29 | 2025-05-13 08:52 | 3:23 | S/O | Red Hot Maintenance | 0 | 0 | No interruption
Agargaon 230/132kV | 132kV Transformer-2 (415T2) | 2025-05-14 05:30 | 2025-05-14 07:11 | 1:41 | S/O | Red Hot maintenance. | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Bus-1 (400kV) | 2025-05-01 06:48 | 2025-05-02 18:57 | 36:09 | S/O | 400KV Bay extention | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 132 kv Bus 01 | 2025-05-08 05:53 | 2025-05-08 08:23 | 2:30 | S/O | Maintenance work | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 230/132kv Tr-01 | 2025-05-08 07:30 | 2025-05-08 08:12 | 0:42 | S/O | Maintenance work | 0 | 0 | No interruption
Bhaluka 132/33kV | Transformer- 01 LT | 2025-05-06 04:26 | 2025-05-06 08:16 | 3:50 | S/O | Red hot | 0 | 0 | No interruption
Bhaluka 132/33kV | Transformer- 01 | 2025-05-06 04:28 | 2025-05-06 08:15 | 3:47 | S/O | Red hot | 60 | 227 | Power interruption
Bhaluka 132/33kV | Transformer- 02 | 2025-05-10 08:14 | 2025-05-10 17:27 | 9:13 | S/O | T2 33kv bushing clamp change | 0 | 0 | No interruption
Bhaluka 132/33kV | Transformer- 02 | 2025-05-12 21:42 | 2025-05-12 22:36 | 0:54 | S/O | Red Hot maintenance at 33 kV feeder. | 35 | 31.5 | Power interruption
Bhaluka 132/33kV | Bus A | 2025-05-13 05:26 | 2025-05-13 08:03 | 2:37 | S/O | Maintenance work | 0 | 0 | No interruption
Bhaluka 132/33kV | Transformer- 01 | 2025-05-15 09:56 | 2025-05-15 14:05 | 4:09 | S/O | Temperature correction | 15 | 62.25 | Power interruption
Dhamrai 132/33kV | Main Bus-2 | 2025-05-13 10:34 | 2025-05-15 17:10 | 54:36 | S/O | Project Work | 0 | 0 | No interruption
Dhamrai 132/33kV | Main Bus-1 | 2025-05-17 10:11 | 2025-05-19 15:54 | 53:43 | S/O | Bay Extention work | 0 | 0 | No interruption
Dhamrai 132/33kV | Transformer-2 | 2025-05-22 10:03 | 2025-05-22 12:08 | 2:05 | S/O | Redhot maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV | Transformer-2 | 2025-05-25 06:40 | 2025-05-25 08:28 | 1:48 | S/O | Redhot maintenance | 0 | 0 | No interruption
Jamalpur 132/33kV | T-2 | 2025-05-22 07:28 | 2025-05-22 08:48 | 1:20 | S/O | 33kv Jamuna feeder bus Loop re -connect work | 12 | 16 | Power interruption
Jamalpur 132/33kV | T-3 | 2025-05-26 08:25 | 2025-05-26 09:37 | 1:12 | S/O | 33kv shahapur pdb feeder B-phase Bus connector clamp maintenance work. | 10 | 12 | Power interruption
Kabirpur 132/33kV | XFR, T-I | 2025-05-02 07:21 | 2025-05-02 22:05 | 14:44 | S/O | Aircell bag & Magnetic Oil Indicator replacement | 0 | 0 | No interruption
Kabirpur 132/33kV | XFR, T-3 | 2025-05-09 06:21 | 2025-05-09 11:24 | 5:03 | S/O | 33kV Bus maintenance | 50 | 252.5 | Power interruption
Kabirpur 132/33kV | XFR, T-I | 2025-05-09 06:27 | 2025-05-09 11:13 | 4:46 | S/O | 33kv Bus maintenance | 95 | 452.8333 | Power interruption
Kabirpur 132/33kV | XFR, T-2 | 2025-05-09 06:27 | 2025-05-09 11:13 | 4:46 | S/O | 33kV Bus maintenance | 95 | 452.8333 | Power interruption
Kabirpur 132/33kV | XFR, T-2 | 2025-05-12 12:42 | 2025-05-12 14:09 | 1:27 | S/O | 33 kV ashulia feeder Bus DS High temperature maintenance. | 80 | 116 | Power interruption
Kabirpur 132/33kV | XFR, T-3 | 2025-05-19 07:12 | 2025-05-19 09:11 | 1:59 | S/O | Tr1 33 kv bus section ds maintenance | 65 | 128.9167 | Power interruption
Kabirpur 132/33kV | XFR, T-I | 2025-05-19 07:19 | 2025-05-19 09:10 | 1:51 | S/O | Tr1 33 kv bus section ds maintenance. | 85 | 157.25 | Power interruption
Kabirpur 132/33kV | XFR, T-2 | 2025-05-29 06:45 | 2025-05-29 08:05 | 1:20 | S/O | 33 KV Hi-tech Feeder 33 KV bus DS high temperature maintenance work. | 100 | 133.3333 | Power interruption
Kaliakoir 400/230/132kV | 400kV Bus 1 | 2025-05-07 07:36 | 2025-05-07 12:58 | 5:22 | S/O | Project Work | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400/230kV TR2 | 2025-05-25 06:22 | 2025-05-25 07:41 | 1:19 | S/O | maintenance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400/230kV TR1 | 2025-05-25 08:31 | 2025-05-25 09:25 | 0:54 | S/O | maintenance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400/230kV TR1 HT | 2025-05-25 08:31 | 2025-05-25 09:24 | 0:53 | S/O | maintenance | 0 | 0 | No interruption
Kishoreganj 132/33kV | Tr-1 (404T) | 2025-05-03 08:34 | 2025-05-03 14:02 | 5:28 | S/O | 33 kv T1&T2 Bus -Section DS change | 60 | 328 | Power interruption
Kishoreganj 132/33kV | Tr-2 (414T) | 2025-05-03 08:35 | 2025-05-03 17:55 | 9:20 | S/O | 33 kv T1&T2 Bus -Section DS change | 0 | 0 | No interruption
Kishoreganj 132/33kV | Tr-2 (414T) | 2025-05-05 09:59 | 2025-05-05 09:59 | 0:00 | S/O | T-2 Transformer 33kv bay upgradatio work | 0 | 0 | No interruption
Kishoreganj 132/33kV | 33 kV T2 Bus | 2025-05-07 07:05 | 2025-05-07 07:53 | 0:48 | S/O | PT connection work by PBS | 20 | 16 | Power interruption
Kishoreganj 132/33kV | Tr-1 (404T) | 2025-05-28 06:16 | 2025-05-28 08:01 | 1:45 | S/O | Due to PBD hotspot maintenance | 0 | 0 | No interruption
Kodda 132/33kV | Tr-5 (446T) | 2025-05-07 18:51 | 2025-05-07 19:52 | 1:01 | S/O | 33 KV Feeder Fault | 0 | 0 | No interruption
Kodda 132/33kV | Tr-2 (416T) | 2025-05-11 06:22 | 2025-05-11 08:30 | 2:08 | S/O | Maintenance work | 0 | 0 | No interruption
Kodda 132/33kV | Tr-3 (426T) | 2025-05-24 05:59 | 2025-05-24 08:16 | 2:17 | S/O | Red hot maintenance | 40 | 91.3333 | Power interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-3 (50/75 MVA) HT | 2025-05-07 13:17 | 2025-05-07 15:27 | 2:10 | S/O | Maintenance work | 0 | 0 | Power interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-2(35/50 MVA) LT | 2025-05-08 13:31 | 2025-05-08 14:34 | 1:03 | S/O | Maintenance work | 15 | 15.75 | Power interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-2(35/50 MVA) HT | 2025-05-08 13:32 | 2025-05-08 14:34 | 1:02 | S/O | Maintenance work | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-2(35/50 MVA) | 2025-05-15 10:46 | 2025-05-15 12:55 | 2:09 | S/O | SPMD multifunction meter installation | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-4 (50/75 MVA) | 2025-05-26 07:15 | 2025-05-26 08:45 | 1:30 | S/O | GT -4 33kV BUS section PBS side redhot maintenance | 20 | 30 | Power interruption
Mirpur 132/33kV | T2 | 2025-05-07 05:46 | 2025-05-07 07:37 | 1:51 | S/O | Maintenance work | 0 | 0 | No interruption
Mirpur 132/33kV | T2 | 2025-05-09 06:17 | 2025-05-09 07:44 | 1:27 | S/O | Maintenance work | 0 | 0 | No interruption
Muktagacha 132/33kV | T-3(424T) | 2025-05-17 10:35 | 2025-05-17 14:30 | 3:55 | S/O | Maintenance work | 0 | 0 | No interruption
Muktagacha 132/33kV | T-1(404T) | 2025-05-17 10:58 | 2025-05-17 11:52 | 0:54 | S/O | Maintenance work | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-1 (404T) | 2025-05-14 06:16 | 2025-05-14 07:42 | 1:26 | S/O | Hotspot maintenance of Muktagasa feeder. | 0 | 0 | No interruption
New Tongi | T1(403T) | 2025-05-09 09:45 | 2025-05-09 14:10 | 4:25 | S/O | 33kv cable laying work | 0 | 0 | No interruption
Rajendrapur 132/33kV | MTR-1 | 2025-05-06 13:36 | 2025-05-06 16:26 | 2:50 | S/O | Rajendrapur Substation Metering Division Work Purpose. Load Share By MTR-1 &MTR-2. | 0 | 0 | No interruption
Rajendrapur 132/33kV | MTR-2 | 2025-05-08 13:52 | 2025-05-08 14:57 | 1:05 | S/O | For 33 KV incomer -2 meter installation work by metering division | 0 | 0 | No interruption
Rajendrapur 132/33kV | MTR-3 | 2025-05-08 15:07 | 2025-05-08 15:45 | 0:38 | S/O | For 33 KV incomer -3 meter installation work by metering division | 0 | 0 | No interruption
Rajendrapur 132/33kV | MTR-2 | 2025-05-17 09:22 | 2025-05-17 15:55 | 6:33 | S/O | Project Work | 0 | 0 | No interruption
Rajendrapur 132/33kV | MTR-2 | 2025-05-18 09:24 | 2025-05-18 16:50 | 7:26 | S/O | 132 KV GIS line bay extension work. | 0 | 0 | No interruption
Rajendrapur 132/33kV | MTR-2 | 2025-05-19 09:12 | 2025-05-19 16:41 | 7:29 | S/O | Bay extension work at Rajendrapur grid. | 0 | 0 | No interruption
Rajendrapur 132/33kV | MTR-2 | 2025-05-20 09:22 | 2025-05-20 16:46 | 7:24 | S/O | Bay extension Project work | 0 | 0 | No interruption
Rajendrapur 132/33kV | MTR-2 | 2025-05-21 09:37 | 2025-05-21 17:25 | 7:48 | S/O | GIS Installation of Sreepur Bay. | 0 | 0 | No interruption
Rajendrapur 132/33kV | MTR-2 | 2025-05-22 09:34 | 2025-05-22 16:11 | 6:37 | S/O | Bay Extension work in Rajendrapur S/S. | 0 | 0 | No interruption
Rajendrapur 132/33kV | MTR-2 | 2025-05-22 09:34 | 2025-05-22 16:11 | 6:37 | S/O | Bay Extension work in Rajendrapur S/S. | 0 | 0 | No interruption
Savar 132/33kV | T-3 | 2025-05-25 06:55 | 2025-05-25 09:45 | 2:50 | S/O | Bucholz checking | 0 | 0 | No interruption
Savar 132/33kV | T-3 | 2025-05-25 17:07 | 2025-05-25 19:52 | 2:45 | S/O | Buchholz maintenance | 0 | 0 | No interruption
Savar 132/33kV | T-4 | 2025-05-29 11:13 | 2025-05-29 15:58 | 4:45 | S/O | busbar protection work | 41 | 194.75 | Power interruption
Savar 132/33kV | T-1 | 2025-05-29 11:17 | 2025-05-29 15:57 | 4:40 | S/O | busbar protection work | 41 | 191.3333 | Power interruption
Savar 132/33kV | T-2 | 2025-05-30 15:24 | 2025-05-30 16:58 | 1:34 | S/O | Hot spot maintenance | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 03 | 2025-05-02 09:04 | 2025-05-02 16:50 | 7:46 | S/O | Blast Wall painting. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 04 | 2025-05-03 10:16 | 2025-05-03 13:28 | 3:12 | S/O | Blast wall painting | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 01 | 2025-05-07 09:12 | 2025-05-07 11:19 | 2:07 | S/O | Maintenance work | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 02 | 2025-05-10 09:57 | 2025-05-10 15:12 | 5:15 | S/O | blast wall painting work. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 04 | 2025-05-11 09:21 | 2025-05-11 12:21 | 3:00 | S/O | Maintenance work | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 03 | 2025-05-12 13:10 | 2025-05-12 17:56 | 4:46 | S/O | Blast Wall Painting | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132/33 kV T-1 | 2025-05-27 11:50 | 2025-05-27 12:24 | 0:34 | S/O | Multifunctional meter changed. | 50 | 28.3333 | Power interruption
Tongi 230/132/33kV | T-02 | 2025-05-01 06:12 | 2025-05-01 12:37 | 6:25 | S/O | 230kV Dia-2 Control Panel Annunciators Replacement Work | 0 | 0 | No interruption
Tongi 230/132/33kV | 230 kV Bus-2 | 2025-05-26 09:30 | 2025-05-26 12:26 | 2:56 | S/O | Maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV | T-03 | 2025-05-30 06:35 | 2025-05-30 12:57 | 6:22 | S/O | Spare Transformer Charge. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-15 02:06 |  | Unserved Energy: |  | 2937.9167
Dhaka (South) Grid Circle :
Ghorashal 230kV | TARFO-2 | 2025-05-11 07:28 | 2025-05-11 10:17 | 2:49 | S/O | Shutdown requisition from Project-1(EnergyPack) for repair oil leakage in X-former & 33kV CT, earthing and replacing damage Nut-Bolt in switchyard. | 50 | 140.8333 | Power interruption
Gulshan 132/33kV | MT-2 | 2025-05-20 06:05 | 2025-05-20 06:59 | 0:54 | S/O | Aux-01 transformer maintenance work | 0 | 0 | No interruption
Haripur 230/132kV | Auto TR-1 | 2025-05-18 08:20 | 2025-05-18 10:18 | 1:58 | S/O | Neutral Point Connect to new earthing mash. | 0 | 0 | No interruption
Haripur 230/132kV | Auto TR-3 | 2025-05-18 10:23 | 2025-05-18 12:21 | 1:58 | S/O | Neutral Point Connect to new earthing mash. | 0 | 0 | No interruption
Haripur 230/132kV | Auto TR-2 | 2025-05-18 12:26 | 2025-05-18 21:04 | 8:38 | S/O | Neutral Point Connect to new earthing mesh | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 414 T-2 | 2025-05-12 10:40 | 2025-05-12 20:24 | 9:44 | S/O | 33kv CT raiser string repair | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 404 T-1 | 2025-05-13 15:45 | 2025-05-13 18:05 | 2:20 | S/O | Maint.work | 0 | 0 | No interruption
Hasnabad 132/33kV | 33kv Reserve Bus | 2025-05-17 09:52 | 2025-05-17 17:40 | 7:48 | S/O | 33 kv pangaon, nawabgonj -2, lalbagh -1 bus insulator work. | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-1 | 2025-05-11 09:05 | 2025-05-11 11:44 | 2:39 | S/O | 132kV CB(R-phase) clamp connector maintenance due to high temperature. | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-3 | 2025-05-25 11:57 | 2025-05-25 16:51 | 4:54 | S/O | High Temp Maintenance | 0 | 0 | No interruption
Madanganj 132/33kV | BUS Coupler | 2025-05-17 10:36 | 2025-05-17 17:16 | 6:40 | S/O | Red hot maintenance. | 0 | 0 | No interruption
Maniknagar 132/33kV | Transformer GT-2 | 2025-05-22 06:43 | 2025-06-11 14:53 | 488:10 | S/O | PT(Y-ph) slow oil leakage maintenance work by DPDC. Shutdown taken by Mr. Rokonul Islam, SDE, DPDC. | 0 | 0 | No interruption
Maniknagar 230/132kV | Auto Transformer-02 (715T) | 2025-05-09 09:36 | 2025-05-10 00:06 | 14:30 | S/O | Changing the Relay RET 670 of Main1 protection unit FP1 of Transformer-2. | 0 | 0 | No interruption
Narshingdi 132/33kV | 132 kV Main Bus-2 | 2025-05-12 06:10 | 2025-05-12 07:35 | 1:25 | S/O | Hotspot maintenance work | 0 | 0 | No interruption
Narshingdi 132/33kV | T-4 | 2025-05-23 11:39 | 2025-05-23 13:04 | 1:25 | S/O | For PBS 33 kV bus redhot maintenance work | 12 | 17 | Power interruption
Nawabganj 132/33kV | TR-2 | 2025-05-09 08:35 | 2025-05-09 10:37 | 2:02 | S/O | 33 kV Nikra feeder red hot maintenance | 0 | 0 | No interruption
Nawabganj 132/33kV | TR-2 | 2025-05-29 15:28 | 2025-05-29 16:11 | 0:43 | S/O | Replacing energy meter by metering division. | 0 | 0 | No interruption
Srinagar 132/33kV | Tr-01 | 2025-05-15 06:38 | 2025-05-15 09:31 | 2:53 | S/O | ৩৩ কেভি বাস রেড হট হওয়ায় | 15 | 43.25 | Power interruption
Srinagar 132/33kV | Tr-02 | 2025-05-15 07:31 | 2025-05-15 08:33 | 1:02 | S/O | For reason 33kv bus coupler faulty. | 10 | 10.3333 | Power interruption
Srinagar 132/33kV | Tr-01 | 2025-05-16 08:11 | 2025-05-16 09:29 | 1:18 | S/O | ৩৩ কেভি ইনকামার-০১ এর বাস-এ ক্লাম্প প্রতিস্থাপনের জন্য | 15 | 19.5 | Power interruption
Srinagar 132/33kV | Tr-02 | 2025-05-21 07:33 | 2025-05-21 09:54 | 2:21 | S/O | ৩৩ কেভি ইনকামার-০২ এর আইসোলেটরের উপরে রেড হট হওয়ায়। | 10 | 23.5 | Power interruption
Srinagar 132/33kV | Tr-01 | 2025-05-29 09:35 | 2025-05-29 11:02 | 1:27 | S/O | ৩৩ কেভি ইনকামার-০১ এর backup energy meter প্রতিস্থাপনের জন্য | 0 | 0 | No interruption
Srinagar 132/33kV | Tr-02 | 2025-05-29 11:03 | 2025-05-29 11:59 | 0:56 | S/O | ৩৩ কেভি ইনকামার-০২ এর backup energy meter প্রতিস্থাপনের জন্য Shutdown নেয়া হয়। | 0 | 0 | No interruption
|  |  | Total : | 1900-01-22 16:34 |  | Unserved Energy: |  | 254.4167
Chattogram Grid Circle :
Bakulia 132/33kV | T-1 (402T) | 2025-05-16 07:03 | 2025-05-16 09:07 | 2:04 | S/O | ট্রান্সফরমার -০১(৪০২টি) সেকেন্ডারি Y-phase এর ক্যাবল সংযোগ কাজ। | 0 | 0 | No interruption
BSRM 230/33kV | 230/33 kV Transformer-2 (125/140 MVA) | 2025-05-10 10:51 | 2025-05-17 11:07 | 168:16 | S/O | BSRM Maintenance | 0 | 0 | No interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2025-05-03 15:42 | 2025-05-03 16:06 | 0:24 | S/O | Fuse replacement of station supply transformer. | 40 | 16 | Power interruption
GPH 230/33kV | Transformer-01(D05) | 2025-05-02 09:27 | 2025-05-02 13:19 | 3:52 | S/O | maintenance at gph | 0 | 0 | No interruption
GPH 230/33kV | Transformer -2 (D07) | 2025-05-02 14:18 | 2025-05-02 16:38 | 2:20 | S/O | maintenance at gph | 0 | 0 | No interruption
Halishahar 132/33kV | 423T(TR-3) | 2025-05-09 08:59 | 2025-05-09 08:59 | 0:00 | S/O | ESPNER project work | 0 | 0 | No interruption
Halishahar 132/33kV | 415T(TR-2) | 2025-05-09 11:34 | 2025-05-09 13:43 | 2:09 | S/O | Due to secondary 33 kv cable connection. | 0 | 0 | No interruption
Hathazari 230/132/33kV | MT-03 | 2025-05-17 13:05 | 2025-05-18 00:26 | 11:21 | S/O | 230 KV Old CB removed and New CB Installation | 0 | 0 | No interruption
Hathazari 230/132/33kV | MT-03 | 2025-05-17 13:05 | 2025-05-18 00:26 | 11:21 | S/O | 230 KV Old CB removed and New CB Installation | 0 | 0 | No interruption
Hathazari 230/132/33kV | T-01 | 2025-05-22 08:40 | 2025-05-22 11:25 | 2:45 | S/O |  | 0 | 0 | No interruption
Hathazari 230/132/33kV | T-02 | 2025-05-29 07:21 | 2025-05-29 10:07 | 2:46 | S/O | R ph cable puncture | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-02(516T) | 2025-05-17 10:45 | 2025-05-17 19:21 | 8:36 | S/O | CB and isolator change by PDB | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-02(516T) | 2025-05-18 09:23 | 2025-05-18 21:18 | 11:55 | S/O | CB & Isoalator upgrading by BPDB | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-02(516T) | 2025-05-20 12:33 | 2025-05-20 22:50 | 10:17 | S/O | CB & Isolation upgrading by BPDB | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-02(516T) | 2025-05-22 12:35 | 2025-05-22 20:51 | 8:16 | S/O | 33kV new CB and Isolator installation by BPDB. | 0 | 0 | No interruption
Madunaghat 132/33kV | TR-2(517T) | 2025-05-08 21:23 | 2025-05-08 22:41 | 1:18 | S/O | Maintenance work by PDB. | 10 | 13 | Power interruption
Madunaghat 132/33kV | TR-1(507T) | 2025-05-18 09:53 | 2025-05-22 15:29 | 101:36 | S/O | For Painting Work | 0 | 0 | No interruption
Madunaghat 132/33kV | TR-1(507T) | 2025-05-25 09:23 | 2025-05-27 10:08 | 48:45 | S/O | Painting work. | 0 | 0 | No interruption
Rampur 230/132/33 | ATR-02 (716T) | 2025-05-27 12:05 | 2025-05-27 16:00 | 3:55 | S/O | GIS bay commission work of TR-02 132kv bay. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-15 17:56 |  |  |  | 29
Cumilla Grid Circle :
Beanibazar 132/33kV | 132 KV Transformer TR-01 | 2025-05-04 09:46 | 2025-05-04 17:25 | 7:39 | S/O | CB density monitor and maintenance of local-remote switch | 0 | 0 | No interruption
Beanibazar 132/33kV | 132 KV Transformer TR-01 | 2025-05-05 09:47 | 2025-05-05 17:59 | 8:12 | S/O | 132KV Tr-1 CB density monitor repair | 0 | 0 | No interruption
Chauddagram 132/33kV | 132 kv T-1 | 2025-05-03 07:40 | 2025-05-03 11:18 | 3:38 | S/O | Maintenance work | 23 | 83.5667 | Power interruption
Chauddagram 132/33kV | 132 kv T-2 | 2025-05-10 07:40 | 2025-05-10 12:17 | 4:37 | S/O | Red-hot Maintenance. | 27 | 124.65 | Power interruption
Chhatak 132/33kV | T-3 | 2025-05-18 23:31 | 2025-05-19 12:56 | 13:25 | S/O | 132KV T-3 Transformer CB(423B) hydraulic oil leakage and low pressure. | 6 | 80.5 | Power interruption
Chowmuhani 132/33kV | TR3-435T | 2025-05-06 20:49 | 2025-05-06 21:35 | 0:46 | S/O | TR-03 33kv side B-phase red hot maintenance. | 15 | 11.5 | Power interruption
Cumilla(N) 230/132/33kV | 132KV T-03 | 2025-05-20 18:00 | 2025-05-20 19:55 | 1:55 | S/O | 33 Companygonj Feeder Bus DS Bus side red hot | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 132KV T-03 | 2025-05-22 15:48 | 2025-05-22 16:22 | 0:34 | S/O | 33KV underground cable termination work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 132KV T-03 | 2025-05-30 10:34 | 2025-05-30 12:43 | 2:09 | S/O | 33kv bus section DS redhot maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | AT-02 | 2025-05-14 00:46 | 2025-05-14 12:42 | 11:56 | S/O | PRD OSR maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | TR-02 | 2025-05-17 23:07 | 2025-05-18 00:17 | 1:10 | S/O | For pbs rajnogor 33 kv load side red hot problem | 15 | 17.5 | Power interruption
Feni 132/33kV | T-1(405T) | 2025-05-19 07:27 | 2025-05-19 08:35 | 1:08 | S/O | 33 kV CT loop maintenance work | 0 | 0 | No interruption
Feni 132/33kV | T-1(405T) | 2025-05-31 07:40 | 2025-05-31 12:20 | 4:40 | S/O | CT clamp punching | 0 | 0 | No interruption
Kachua 132/33kV | Main Bus-1 | 2025-05-10 15:28 | 2025-05-10 19:17 | 3:49 | S/O | ESPN project bus loop conection | 0 | 0 | No interruption
Kachua 132/33kV | Main Bus-2 | 2025-05-11 10:12 | 2025-05-11 17:30 | 7:18 | S/O | ESPNER project work | 0 | 0 | No interruption
Kachua 132/33kV | Main Bus-2 | 2025-05-12 09:56 | 2025-05-12 13:38 | 3:42 | S/O | For project work | 0 | 0 | No interruption
Ramganj 132/33kV | Transformer -02 | 2025-05-15 23:24 | 2025-05-16 00:51 | 1:27 | S/O | Red hot maintenance. | 50 | 72.5 | Power interruption
Ramganj 132/33kV | Transformer-01 | 2025-05-15 23:25 | 2025-05-16 02:23 | 2:58 | S/O | Red hot maintenance | 50 | 148.3333 | Power interruption
Shahjibazar 132/33kV | TR-04 | 2025-05-13 15:08 | 2025-05-13 18:05 | 2:57 | S/O | Shutdown Taken By Shahjibazar Grid Sub-Station | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 | 2025-05-13 15:09 | 2025-05-13 18:03 | 2:54 | S/O | Shutdown Taken By Shahjibazar Grid Sub-Station | 80 | 232 | Power interruption
Sreemongol 132/33kV | 132/33kv T-3 | 2025-05-18 14:33 | 2025-05-18 14:48 | 0:15 | S/O | For 33 kV GCB gas refill. | 0 | 0 | No interruption
Sunamganj 132/33kV | Tr-1 | 2025-05-10 08:22 | 2025-05-10 17:21 | 8:59 | S/O | 132 KV Transformer-1 Shutdown due to BPDB, 33 KV Sunamganj and Derai Feeder Bay-Extension. | 12 | 107.8 | Power interruption
Sylhet (South) | Trafo-2 | 2025-05-24 07:20 | 2025-05-24 18:24 | 11:04 | S/O | for 33 kv bay extention work requested by bpdb. | 0 | 0 | No interruption
Sylhet 132/33kV | T2 | 2025-05-06 13:45 | 2025-05-06 13:50 | 0:05 | S/O | 132 KV T4 X-Former Red Hot Maintenance Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV | T4 | 2025-05-06 13:50 | 2025-05-06 15:09 | 1:19 | S/O | 132 KV T4 X-Former Red Hot Maintenance Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV | T2 | 2025-05-06 15:12 | 2025-05-06 15:15 | 0:03 | S/O | Maintenance of T4 X-Former. | 0 | 0 | No interruption
Sylhet 132/33kV | T2 | 2025-05-24 10:26 | 2025-05-24 10:30 | 0:04 | S/O | for t-2 and t-4 parallel | 30 | 2 | Power interruption
Sylhet 132/33kV | T4 | 2025-05-27 03:52 | 2025-05-27 09:26 | 5:34 | S/O | work of 33kv bus | 0 | 0 | No interruption
Sylhet 132/33kV | T4 | 2025-05-29 07:45 | 2025-05-29 10:37 | 2:52 | S/O | work of PDB | 10 | 28.6667 | Power interruption
|  |  | Total : | 1900-01-03 21:09 |  |  |  | 909.0167
Khulna Grid Circle :
Bagerhat 132/33kV | Transformer-3 ( 423 T) | 2025-05-11 08:25 | 2025-05-11 10:36 | 2:11 | S/O | 33 kv pirojpur pbs feeder red hot maintenance work. | 30 | 65.5 | Power interruption
Barguna 132/33kV | Transformer-1 | 2025-05-16 08:38 | 2025-05-16 10:31 | 1:53 | S/O | Emergency Shotdown for Betagi 33kv Feeder Maintenance | 5 | 9.4167 | Power interruption
Barguna 132/33kV | Transformer-2 | 2025-05-26 10:53 | 2025-05-26 13:01 | 2:08 | S/O | To remove oil level alarm in main tank of T2-Transformer. | 0 | 0 | No interruption
Barishal 132/33kV | T-2 (415T) | 2025-05-01 19:16 | 2025-05-01 22:06 | 2:50 | S/O | OLTC Bucholz check | 0 | 0 | No interruption
Barishal 132/33kV | T-1 (405T) | 2025-05-03 18:20 | 2025-05-03 19:40 | 1:20 | S/O | WZPDCL (Jhalokathi 33kV loop disconnect near 33kv bus) | 20 | 26.6667 | Power interruption
Barishal 132/33kV | T-2 (415T) | 2025-05-25 06:55 | 2025-05-25 08:21 | 1:26 | S/O | To remove high temperature problem (nut bolt tightening) | 0 | 0 | No interruption
Barishal 230/132kV | T-5 | 2025-05-01 06:22 | 2025-05-01 08:08 | 1:46 | S/O | Banaripara 33 kv feeder Bus DS repair maintenance work. | 30 | 53 | Power interruption
Barishal 230/132kV | ATR-1 LT | 2025-05-18 14:30 | 2025-05-18 15:58 | 1:28 | S/O | Oil leakage repair. | 0 | 0 | No interruption
Barishal 230/132kV | ATR-1 HT | 2025-05-18 14:33 | 2025-05-18 15:59 | 1:26 | S/O | Oil repair | 0 | 0 | No interruption
Barishal 230/132kV | T-4 | 2025-05-29 14:40 | 2025-05-29 15:50 | 1:10 | S/O | 33kv Busbar maintenance due to Korapur 33kv feeder fault | 12 | 14 | Power interruption
Barishal 230/132kV | 230kV BUS | 2025-05-31 15:42 | 2025-05-31 16:22 | 0:40 | S/O | TCS check | 0 | 0 | No interruption
Benapole 132/33kV | Transformer-1(406T) | 2025-05-07 15:24 | 2025-05-07 17:40 | 2:16 | S/O | 33 KV feeder maintenance work of pbs | 25 | 56.6667 | Power interruption
Benapole 132/33kV | Transformer-2(416T) | 2025-05-24 15:20 | 2025-05-24 17:30 | 2:10 | S/O | 33 KV feeder maintenance work of pbs | 30 | 65 | Power interruption
Benapole 132/33kV | Transformer-2(416T) HT | 2025-05-31 09:26 | 2025-05-31 11:23 | 1:57 | S/O | 33 KV Purapara feeder Ds red hot maintenance. | 28 | 54.6 | Power interruption
Borhanuddin 230/33kV | Tr-Load | 2025-05-03 07:08 | 2025-05-03 15:09 | 8:01 | S/O | Red hot maintenance & ROW. | 45 | 360.75 | Power interruption
Faridpur 132/33kV | Transformer-2 | 2025-05-09 07:22 | 2025-05-09 09:20 | 1:58 | S/O | hotspot maintenance | 10 | 19.6667 | Power interruption
Faridpur 132/33kV | Transformer-1 | 2025-05-09 09:34 | 2025-05-09 10:56 | 1:22 | S/O | Red hot maintenance | 0 | 0 | No interruption
Faridpur 132/33kV | Transformer-3 | 2025-05-14 09:24 | 2025-05-14 17:50 | 8:26 | S/O | Underground Cable Replacement. | 0 | 0 | No interruption
Faridpur 132/33kV | Transformer-3 | 2025-05-16 08:54 | 2025-05-16 18:05 | 9:11 | S/O | Under Ground Cable Maintenance. | 0 | 0 | No interruption
Faridpur 132/33kV | Transformer-3 | 2025-05-20 07:23 | 2025-05-20 11:16 | 3:53 | S/O | Underground cable replacement | 0 | 0 | No interruption
Faridpur 132/33kV | Transformer-1 | 2025-05-20 07:27 | 2025-05-20 09:35 | 2:08 | S/O | Underground cable replacement | 27 | 57.6 | Power interruption
Faridpur 132/33kV | Transformer-1 | 2025-05-30 08:47 | 2025-05-30 09:57 | 1:10 | S/O | Bus D/S Redhot Maintenance. | 20 | 23.3333 | Power interruption
Goalpara 132/33kV | Bus 1 | 2025-05-14 08:33 | 2025-05-14 10:00 | 1:27 | S/O | 3rd transformer installation work | 0 | 0 | No interruption
Goalpara 132/33kV | T-5 | 2025-05-16 07:15 | 2025-05-16 10:47 | 3:32 | S/O | TR-7 installation work | 5.5 | 19.4333 | Power interruption
Goalpara 132/33kV | T-6 | 2025-05-16 07:15 | 2025-05-16 10:47 | 3:32 | S/O | TR-7 installation work | 0 | 0 | Power interruption
Goalpara 132/33kV | Bus 2 | 2025-05-28 08:23 | 2025-05-28 17:15 | 8:52 | S/O | Maintenance | 0 | 0 | No interruption
Goalpara 132/33kV | T-5 | 2025-05-30 15:24 | 2025-05-30 17:23 | 1:59 | S/O | Red hot maintenance work in 33 kV Chandanimohol Feeder | 5 | 9.9167 | Power interruption
Goalpara 132/33kV | T-6 | 2025-05-30 15:27 | 2025-05-30 17:20 | 1:53 | S/O | Red hot maintenance work in 33 kV Chandanimohol Feeder | 5 | 9.4167 | Power interruption
Gollamari 132/33kV | Tr-2 | 2025-05-17 07:03 | 2025-05-17 09:07 | 2:04 | S/O | Hot Spot Maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV | T1 | 2025-05-10 07:31 | 2025-05-10 12:43 | 5:12 | S/O | Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Bus-01 | 2025-05-07 07:40 | 2025-05-07 18:45 | 11:05 | S/O | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Bus-02 | 2025-05-08 07:47 | 2025-05-08 15:56 | 8:09 | S/O | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Bus-01 | 2025-05-17 06:29 | 2025-05-17 13:16 | 6:47 | S/O | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Bus-02 | 2025-05-17 13:56 | 2025-05-17 18:42 | 4:46 | S/O | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Bus-01 | 2025-05-19 07:01 | 2025-05-19 21:27 | 14:26 | S/O | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Bus-02 | 2025-05-20 07:28 | 2025-05-20 21:06 | 13:38 | S/O | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Bus-02 | 2025-05-24 13:00 | 2025-05-24 13:24 | 0:24 | S/O | Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Bus-01 | 2025-05-25 14:08 | 2025-05-26 00:26 | 10:18 | S/O | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Bus-01 | 2025-05-26 10:50 | 2025-05-27 01:39 | 14:49 | S/O | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Bus-02 | 2025-05-27 11:26 | 2025-05-27 19:41 | 8:15 | S/O | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Bus-01 | 2025-05-28 14:37 | 2025-05-29 00:55 | 10:18 | S/O | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Bus-02 | 2025-05-29 11:34 | 2025-05-29 18:49 | 7:15 | S/O | Project work | 0 | 0 | No interruption
Khulna (C) | Tr-2 415 T LT | 2025-05-02 07:10 | 2025-05-02 11:46 | 4:36 | S/O | Maintenance of GP-1 ckt. Bus DS | 0 | 0 | No interruption
Khulna (C) | Tr-2 415 T | 2025-05-02 07:11 | 2025-05-02 11:46 | 4:35 | S/O | Maintenance of GP-1 ckt. Bus DS | 0 | 0 | No interruption
Khulna (C) | Tr-3 405T | 2025-05-02 07:11 | 2025-05-02 11:48 | 4:37 | S/O | Maintenance of GP-1 ckt. Bus DS | 0 | 0 | No interruption
Khulna(S) 230/132kV | TR-1 | 2025-05-10 05:56 | 2025-05-10 11:04 | 5:08 | S/O | Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | TR-2 | 2025-05-10 05:56 | 2025-05-10 11:08 | 5:12 | S/O | Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | TR-3 | 2025-05-10 05:57 | 2025-05-10 11:06 | 5:09 | S/O | Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | 132 KV Main Bus | 2025-05-10 06:05 | 2025-05-10 11:04 | 4:59 | S/O | Red hot maintenance work | 0 | 0 | Power interruption | 0
Khulna(S) 230/132kV | TR-2 | 2025-05-27 10:09 | 2025-05-27 13:40 | 3:31 | S/O | Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | TR-1 | 2025-05-28 07:23 | 2025-05-28 13:57 | 6:34 | S/O | Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | 230 KV Main Bus 1 | 2025-05-29 13:16 | 2025-05-29 15:37 | 2:21 | S/O | Maintenance | 0 | 0 | No interruption
Mongla 132/33kV | Main Bus | 2025-05-03 02:56 | 2025-05-03 06:31 | 3:35 | S/O | Project work | 27 | 96.75 | Power interruption
Mongla 132/33kV | Main Bus | 2025-05-31 05:36 | 2025-05-31 07:17 | 1:41 | S/O | Project work | 33 | 55.55 | Power interruption
Narail 132/33kV | TR1 (403-T) | 2025-05-10 08:52 | 2025-05-10 08:52 | 0:00 | S/O | 33 kb Bay Extension | 0 | 0 | No interruption
Patuakhali 132/33kV | 425T (T-3) | 2025-05-10 12:51 | 2025-05-10 15:31 | 2:40 | S/O | Red hot maintenance | 0 | 0 | No interruption
Payra 400/132/33kV | 400/132/33 kV Auto Transformer-01 | 2025-05-28 12:45 | 2025-05-28 14:55 | 2:10 | S/O | High temperature point maintenance | 0 | 0 | No interruption
Satkhira 132/33kV | Transformer-1 (T-1) | 2025-05-23 17:07 | 2025-05-23 18:24 | 1:17 | S/O | Maintenance | 50 | 64.1667 | Power interruption
Shariatpur 132/33kV | T2-416T | 2025-05-11 10:07 | 2025-05-11 12:12 | 2:05 | S/O | Red Hot Maintenance by PBS | 28 | 58.3333 | Power interruption
|  |  | Total : | 1900-01-09 19:41 |  | Unserved Energy : |  | 1119.7667
HVDC Grid Circle
Bheramara 230/132kV | Transformer-2 HT | 2025-05-16 07:24 | 2025-05-16 14:06 | 6:42 | S/O | Underground cable maintenance | 0 | 0 | No interruption
Bheramara(GK) 132/33kV | TR-3 | 2025-05-10 08:26 | 2025-05-10 17:33 | 9:07 | S/O | PBS 33kV feeder underground from Overhead Shifting. | 52 | 474.0667 | Power interruption
Bheramara(GK) 132/33kV | TR-1 HT | 2025-05-24 10:34 | 2025-05-24 11:41 | 1:07 | S/O | 132/33 kv, 25/41 Tr-01 & Tr-02 ,33 kv bus cupler red hot removing work . | 15 | 16.75 | Power interruption
Bheramara(GK) 132/33kV | TR-2 HT | 2025-05-24 10:34 | 2025-05-24 11:41 | 1:07 | S/O | 132/33 kv, 25/41 Tr-01 & Tr-02 ,33 kv bus cupler red hot removing work . | 15 | 16.75 | Power interruption
Chuadanga 132/33kV | 132kV Tr. T2(426T) | 2025-05-17 07:02 | 2025-05-17 09:25 | 2:23 | S/O | Due to 33kv faulty D/S maintenance | 25 | 59.5833 | Power interruption
Ishurdi 132/33kV | 132/33 kV T-1 | 2025-05-11 07:15 | 2025-05-11 09:16 | 2:01 | S/O | Maintenance | 30 | 60.5 | Power interruption
Ishurdi 132/33kV | 132/33 kV T-2 | 2025-05-21 15:49 | 2025-05-21 17:19 | 1:30 | S/O | Maintenance | 20 | 30 | Power interruption
Ishurdi 230/132kV | 230/132 kV T-03 | 2025-05-28 08:51 | 2025-05-28 10:25 | 1:34 | S/O | Redhot maintenance work | 0 | 0 | No interruption
Jashore 132/33kV | 132 kV Bus-A | 2025-05-21 11:07 | 2025-05-21 16:19 | 5:12 | S/O | 132 KV R-phase PT change work | 0 | 0 | No interruption
Jashore 132/33kV | 132 kV Bus-A | 2025-05-22 13:01 | 2025-05-22 19:10 | 6:09 | S/O | For replacing R phase PT of 132 kv Capacitor Bank. | 0 | 0 | No interruption
Jhenaidah 132/33kV | Transformer T-2 | 2025-05-16 07:25 | 2025-05-16 10:58 | 3:33 | S/O | 33 kv Bus isolator-1 loop wire change | 35 | 124.25 | Power interruption
Kushtia 132/33kV | T2 | 2025-05-11 07:07 | 2025-05-11 09:27 | 2:20 | S/O | Red hot T-2A 33kv CT Clamp Connector | 10 | 23.3333 | Power interruption
Kushtia 132/33kV | T2 | 2025-05-30 08:05 | 2025-05-30 09:48 | 1:43 | S/O | Maintenance | 30 | 51.5 | Power interruption
Magura 132/33kV | T-3 (425T) | 2025-05-09 10:11 | 2025-05-09 12:02 | 1:51 | S/O | Feeder maintenance by PBS. | 22 | 40.7 | Power interruption
Magura 132/33kV | T-1 (405T) | 2025-05-16 07:28 | 2025-05-16 09:06 | 1:38 | S/O | WZPDCL -Magura feeder red hot maintenance. | 12 | 19.6 | Power interruption
|  |  | Total : | 1899-12-31 23:57 |  | Unserved Energy : |  | 917.0333
Bogura Grid Circle:
Bogura 132/33kV | Transformer-4 | 2025-05-17 07:35 | 2025-05-17 09:25 | 1:50 | S/O | Red hot. | 10 | 18.3333 | Power interruption
Bogura 132/33kV | Transformer-1 HT | 2025-05-20 11:06 | 2025-05-20 12:14 | 1:08 | S/O | T-1 Shut Down Due To Energy Meter Change. | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-2 | 2025-05-20 12:32 | 2025-05-20 13:52 | 1:20 | S/O | T-2 Shut Down Due To Energy Meter Change. | 0 | 0 | No interruption
Bogura 132/33kV | 132KV Bus-B | 2025-05-21 15:50 | 2025-05-21 15:50 | 0:00 | S/O | 132kv Circuit Breaker Change. | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-1 | 2025-05-31 07:27 | 2025-05-31 09:40 | 2:13 | S/O | Red hot. | 20 | 44.3333 | Power interruption
Joypurhat 132/33kV | Transformer T-4 (437 T) | 2025-05-26 21:25 | 2025-05-27 00:32 | 3:07 | S/O | Maint.work | 0 | 0 | No interruption
Lalmonirhat 132/33kV | T-1 (425T) | 2025-05-22 11:40 | 2025-05-22 12:15 | 0:35 | S/O | R phase red hot | 0 | 0 | No interruption
Natore 132/33kV | TR-1 (405 T) | 2025-05-27 07:05 | 2025-05-27 09:40 | 2:35 | S/O | Maint.work | 0 | 0 | No interruption
Natore 132/33kV | TR-2 (415 T) | 2025-05-27 07:05 | 2025-05-27 09:40 | 2:35 | S/O | Project work | 0 | 0 | No interruption
Rahanpur 400/132kV | HV 400 KV BUS | 2025-05-31 09:10 | 2025-05-31 12:55 | 3:45 | S/O | Es operation checking | 0 | 0 | No interruption
Rahanpur 400/132kV | HV 400 KV BUS | 2025-05-31 13:19 | 2025-05-31 16:20 | 3:01 | S/O | Project work at BUS 02 400 kv | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-3 (425T) HT | 2025-05-10 12:25 | 2025-05-10 13:47 | 1:22 | S/O | Red hot maintance | 25 | 34.1667 | Power interruption
Rajshahi 132/33kV | Transformer T-3 (425T) | 2025-05-31 08:02 | 2025-05-31 10:39 | 2:37 | S/O | Regular Maintenance Work Before Eid Ul Adha | 20 | 52.3333 | Power interruption
Rajshahi 132/33kV | Transformer T-2(415T) HT | 2025-05-31 10:49 | 2025-05-31 13:02 | 2:13 | S/O | Maint.work | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-1(405T) | 2025-05-31 13:13 | 2025-05-31 15:15 | 2:02 | S/O | Maint.work | 0 | 0 | No interruption
Rangpur 132/33kV | T-2 (404T) | 2025-05-30 15:48 | 2025-05-30 17:28 | 1:40 | S/O | None | 25 | 41.6667 | Power interruption
|  |  | Total : | 1899-12-31 08:03 |  | Unserved Energy : |  | 190.8333
Others :Nil
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1813:26 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:May 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV | Aminbazar Ckt-2 | 2025-05-22 08:44 | 2025-05-22 15:39 | 6:55 | S/O | 6 No. Earthing pit maintenanc work. | 0 | 0 | No interruption
Agargaon 230/132kV | Aminbazar Ckt-2 | 2025-05-22 21:08 | 2025-05-22 23:02 | 1:54 | S/O | For Earthing pit Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Keranigonj-01 | 2025-05-03 09:49 | 2025-05-03 18:01 | 8:12 | S/O | Disc cleaning | 0 | 0 | No interruption
Bajitpur 132/33kV | Ashuganj Ckt-2 | 2025-05-24 06:00 | 2025-05-24 18:23 | 12:23 | S/O | Tower interchange by project. | 0 | 0 | No interruption
Bajitpur 132/33kV | Ashuganj Ckt-2 | 2025-05-27 06:37 | 2025-05-27 12:11 | 5:34 | S/O | Maint.work | 0 | 0 | No interruption
Bhaluka 132/33kV | Mymensingh Ckt- 01 | 2025-05-13 04:57 | 2025-05-13 09:49 | 4:52 | S/O | Emergency maintenance work. | 0 | 0 | No interruption
Bhaluka 132/33kV | Mymensingh Ckt- 02 | 2025-05-13 04:57 | 2025-05-13 09:49 | 4:52 | S/O | Emergency maintenance work. | 0 | 0 | No interruption
Dhamrai 132/33kV | 132 KV Kaliakoir-Dhamrai CKT-01 | 2025-05-13 11:31 | 2025-05-13 15:48 | 4:17 | S/O | Project work | 0 | 0 | No interruption
Dhamrai 132/33kV | 132 KV Kaliakoir-Dhamrai CKT-01 | 2025-05-14 16:15 | 2025-05-14 17:37 | 1:22 | S/O | Project Work | 0 | 0 | No interruption
Dhamrai 132/33kV | 132 KV Kaliakoir-Dhamrai CKT-02 | 2025-05-19 09:41 | 2025-05-19 17:51 | 8:10 | S/O | Project work.15 MW Load shifted by manikgonj grid | 0 | 0 | No interruption
Dhamrai 132/33kV | 132 KV Kaliakoir-Dhamrai CKT-02 | 2025-05-20 09:12 | 2025-05-20 18:03 | 8:51 | S/O | Bay extension work | 0 | 0 | No interruption
Dhamrai 132/33kV | 132 KV Kaliakoir-Dhamrai CKT-02 | 2025-05-21 09:43 | 2025-05-21 18:27 | 8:44 | S/O | Dhamrai Nobinagor new line project work by EEGBPS project. | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-01 | 2025-05-04 10:56 | 2025-05-04 12:49 | 1:53 | S/O | Work on mymensingh grid | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-01 | 2025-05-16 08:27 | 2025-05-16 17:51 | 9:24 | S/O | G2G project work (guktagacha grid) | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-02 | 2025-05-17 08:52 | 2025-05-17 15:26 | 6:34 | S/O | Maint.work | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-2 | 2025-05-29 06:26 | 2025-05-29 11:37 | 5:11 | S/O | Hotspot maintenance | 0 | 0 | No interruption
Kabirpur 132/33kV | Tongi-1 | 2025-05-30 09:01 | 2025-05-30 15:08 | 6:07 | S/O | Tongi ckt-1 45 no tower line conductor replacement work. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Dhamrai-2 | 2025-05-21 09:41 | 2025-05-21 18:26 | 8:45 | S/O | Maint.work | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Aminbazar -1 | 2025-05-24 07:14 | 2025-05-24 07:14 | 0:00 | S/O | by NLDC (Project work) | 0 | 0 | No interruption
Kodda 132/33kV | Rajendrapur Ckt-1 | 2025-05-06 13:32 | 2025-05-06 16:05 | 2:33 | S/O | LDS RED HIT MAINTENANCE | 0 | 0 | No interruption
Manikganj 132/33kV | Manikganj- Kabirpur CKT-1 | 2025-05-07 13:13 | 2025-05-07 15:20 | 2:07 | S/O | Maint.work | 50 | 105.8333 | Power interruption
Mirpur 132/33kV | RPC Main | 2025-05-10 08:40 | 2025-05-10 16:53 | 8:13 | S/O | RPC Bank Unit# 2 ractor reaplacement work. | 0 | 0 | No interruption
Mirpur 132/33kV | RPC Main | 2025-05-12 09:55 | 2025-05-12 09:55 | 0:00 | S/O | Replacement work of unit-2 | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Jamalpur Ckt-1 | 2025-05-04 10:58 | 2025-05-04 12:48 | 1:50 | S/O | Density monitor replace. | 0 | 0 | No interruption
Rajendrapur 132/33kV | Kodda-1 | 2025-05-06 13:30 | 2025-05-06 16:24 | 2:54 | S/O | Kodda end Work Purpose | 0 | 0 | No interruption
Savar 132/33kV | 132kV Manikganj PS-Savar Ckt-2 | 2025-05-30 15:10 | 2025-05-30 16:56 | 1:46 | S/O | Hot spot maintenance | 30 | 53 | Power interruption
Sreepur 230/132/33kV | Sreepur-Sirajganj Ckt-2 | 2025-05-14 08:33 | 2025-05-14 11:48 | 3:15 | S/O | Line Repair (Armoring) | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Ghorashal Ckt-2 | 2025-05-01 06:10 | 2025-05-01 12:40 | 6:30 | S/O | 230kV Dia-2 Control Panel Annunciators Replacement Work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Uttara 3rd Phase Ckt | 2025-05-06 07:37 | 2025-05-10 17:42 | 106:05 | S/O | Shutdown taken by NLDC | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Basundhara Ckt-1 | 2025-05-07 09:38 | 2025-05-07 12:32 | 2:54 | S/O | Emergency maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Uttara Ckt | 2025-05-13 07:43 | 2025-05-17 18:26 | 106:43 | S/O | Shutdown taken by NLDC | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Uttara 3rd Phase Ckt | 2025-05-13 10:51 | 2025-05-13 15:45 | 4:54 | S/O | Maint.work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2025-05-13 21:40 | 2025-05-13 22:41 | 1:01 | S/O | redhot maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2025-05-30 09:02 | 2025-05-30 15:08 | 6:06 | S/O | Shutdown taken by Kabirpur grid substations | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2025-05-30 15:09 | 2025-05-30 19:40 | 4:31 | S/O | Shutdown taken by Kabirpur grid substations | 0 | 0 | No interruption
|  |  | Total : | 1900-01-14 15:22 |  | Unserved Energy: |  | 158.8333
Dhaka (South) Grid Circle :
Haripur 230/132kV | Meghnaghat-1 | 2025-05-21 05:53 | 2025-05-21 08:50 | 2:57 | S/O | Line DS Y phase Changing Work | 0 | 0 | No interruption
Haripur 230/132kV | Meghnaghat-2 | 2025-05-22 05:14 | 2025-05-22 08:59 | 3:45 | S/O | Line DS Hotspot Maintenance. | 0 | 0 | No interruption
Hasnabad 230/132kV | Shyampur-APR-Hasnabad Ckt-2 | 2025-05-23 07:31 | 2025-05-23 10:17 | 2:46 | S/O | High temperature maintenance of 71 No Tower R Phase Jumper joint. | 0 | 0 | No interruption
Hasnabad 230/132kV | Shyampur-Hasnabad Ckt-1 | 2025-05-25 07:34 | 2025-05-25 11:53 | 4:19 | S/O | Maintenance work due to temperature rise. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Aminbazar Ckt. 1 | 2025-05-03 09:47 | 2025-05-03 18:02 | 8:15 | S/O | As NLDC instruction. | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Summit 102 MW 132 kv Ckt | 2025-05-15 16:48 | 2025-05-15 16:48 | 0:00 | S/O | PDB Letter & NLDC Order For Complete Disconnect | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-2 | 2025-05-01 11:31 | 2025-05-01 20:02 | 8:31 | S/O | Maintenance work done. | 0 | 0 | No interruption
Narshingdi 132/33kV | Brahmanbaria-01 | 2025-05-12 06:07 | 2025-05-12 07:35 | 1:28 | S/O | Hotspot maintenance work | 0 | 0 | No interruption
Narshingdi 132/33kV | Brahmanbaria-02 | 2025-05-12 06:08 | 2025-05-12 07:43 | 1:35 | S/O | Hotspot maintenance work | 0 | 0 | No interruption
Narshingdi 132/33kV | Haripur | 2025-05-17 06:25 | 2025-05-17 16:28 | 10:03 | S/O | Line LILO work | 0 | 0 | No interruption
Narshingdi 132/33kV | Haripur | 2025-05-23 07:03 | 2025-05-29 11:59 | 148:56 | S/O | LILO Stringing work | 0 | 0 | No interruption
Nawabganj 132/33kV | Keraniganj-2 | 2025-05-29 13:44 | 2025-05-29 14:29 | 0:45 | S/O | Replacing energy meter by metering division. | 0 | 0 | No interruption
Rampura 230/132kV | Ullon-01 | 2025-05-05 06:21 | 2025-05-05 11:21 | 5:00 | S/O | Command by NLDC | 0 | 0 | No interruption
Rampura 230/132kV | Ullon-01 | 2025-05-25 10:43 | 2025-05-25 17:57 | 7:14 | S/O | Shutdown from NLDC | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV APR (D04) | 2025-05-23 07:34 | 2025-05-23 10:16 | 2:42 | S/O | Red hot on red phase Jumper Connection point of Tower no 71 of 230 kV Hasnabad -Shyampur Ckt -2 (The work will be done by Hasnabad SS) | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV Hasnabad-1(D02) | 2025-05-25 07:34 | 2025-05-25 11:54 | 4:20 | S/O | Redhot at Hasnabad substation | 0 | 0 | No interruption
Siddhirganj 230/132kV | Maniknagar 2 | 2025-05-09 09:45 | 2025-05-10 00:06 | 14:21 | S/O | Emergency maintenance work | 0 | 0 | No interruption
Siddhirganj 230/132kV | 335MW EGCB 1 | 2025-05-09 09:59 | 2025-05-09 12:19 | 2:20 | S/O | Emergency maintenceance work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-08 13:17 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
AKS 132/33kV | Bar Aulia | 2025-05-17 08:45 | 2025-05-17 14:29 | 5:44 | S/O | Akspl to Baraulia 132kv(ckt-1) line shutdown due to maintenance for Tower No. 57 . | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Sikalbaha ckt-1 | 2025-05-07 11:12 | 2025-05-07 14:05 | 2:53 | S/O | High Temperature maintenance of Gantry Clam-T | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Sikalbaha ckt-1 | 2025-05-08 13:51 | 2025-05-08 17:27 | 3:36 | S/O | High Temperature maintenance of Gantry Clam-T | 0 | 0 | No interruption
GPH 230/33kV | HATHAZARI | 2025-05-23 05:48 | 2025-05-23 13:18 | 7:30 | S/O | for Hathazari line maintenance | 0 | 0 | No interruption
Hathazari 230/132/33kV | GPH-01 | 2025-05-23 05:38 | 2025-05-23 13:24 | 7:46 | S/O | Maint.work | 0 | 0 | No interruption
Hathazari 230/132/33kV | AKSML-02 | 2025-05-23 05:38 | 2025-05-23 13:24 | 7:46 | S/O | Maint.work | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2025-05-09 09:18 | 2025-05-09 13:21 | 4:03 | S/O | The jumper of the halishahar line from juldha to khulsi line is open | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-Halishahar CKT-3 | 2025-05-09 09:13 | 2025-05-09 13:23 | 4:10 | S/O | 132kV Jumper out in Halishahar Sub-station end. | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-Madunaghat CKT-2 | 2025-05-24 06:54 | 2025-05-24 09:20 | 2:26 | S/O | Khulshi-Sholoshar ckt-02 Red hot maintenance of H-pole nearby substation. | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Sikalbaha ckt | 2025-05-10 12:30 | 2025-05-10 15:48 | 3:18 | S/O | Shut down taken by Shikalbaha. | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Sikalbaha ckt | 2025-05-11 06:44 | 2025-05-11 17:20 | 10:36 | S/O | Shikalbaha circuit-1 maintenance work shut down. | 0 | 0 | No interruption
Mirsorai 230/33kV | EGCB 75MW Solar Power Station | 2025-05-22 20:56 | 2025-05-22 22:27 | 1:31 | S/O | bashundhara 230 kv project work | 0 | 0 | No interruption
Mirsorai 230/33kV | 150 MW Power Station -02 | 2025-05-23 09:39 | 2025-05-25 12:05 | 50:26 | S/O | For Bashundhara Project Work | 0 | 0 | No interruption
Shahmirpur 132/33kV | Sikalbaha-1 | 2025-05-11 06:53 | 2025-05-11 18:06 | 11:13 | S/O | Maint.work | 0 | 0 | No interruption
Shikalbaha 230/132kV | Shahmirpur-1 | 2025-05-11 06:56 | 2025-05-11 06:56 | 0:00 | S/O | Maint.work | 0 | 0 | No interruption
|  |  | Total : | 122:58 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj 230/132/33kV | B.Baria 132 kV Ckt-1 | 2025-05-05 06:07 | 2025-05-05 08:30 | 2:23 | S/O | Circuit breaker oil filling | 0 | 0 | No interruption
Ashuganj 230/132/33kV | Ghorashal 132 kV Ckt-1 | 2025-05-15 08:26 | 2025-05-18 16:22 | 79:56 | S/O | conductor change | 0 | 0 | No interruption
Ashuganj 230/132/33kV | Ghorashal 132 kV Ckt-2 | 2025-05-19 06:22 | 2025-05-21 17:05 | 58:43 | S/O | Re-routing of 3 nos tower | 0 | 0 | No interruption
Ashuganj 230/132/33kV | Kishoreganj 132 kV Ckt-2 | 2025-05-23 06:53 | 2025-05-24 16:25 | 33:32 | S/O | Maint.work | 0 | 0 | No interruption
Ashuganj 230/132/33kV | Kishoreganj 132 kV Ckt-2 | 2025-05-27 06:37 | 2025-05-27 12:09 | 5:32 | S/O | Re-routing of 3 nos tower | 0 | 0 | No interruption
Chauddagram 132/33kV | Feni-2 | 2025-05-22 09:15 | 2025-05-22 13:21 | 4:06 | S/O | For maintenance in Feni grid substation. | 0 | 0 | No interruption
Chhatak 132/33kV | Sylhet 01 | 2025-05-03 06:15 | 2025-05-03 13:27 | 7:12 | S/O | Shut Down Take From Sylhet End. | 0 | 0 | No interruption
Chowmuhani 132/33kV | Ramganj line-01 | 2025-05-21 06:48 | 2025-05-21 09:29 | 2:41 | S/O | Temporary Jumper Remove from Ramgonj -1 to Chowmuhoni Maijdi | 0 | 0 | No interruption
Chowmuhani 132/33kV | Ramganj line-01 | 2025-05-24 06:38 | 2025-05-24 17:17 | 10:39 | S/O | 132 kv Bus section -01 to GIS Connect | 0 | 0 | No interruption
Chowmuhani 132/33kV | Ramganj line-02 | 2025-05-24 06:38 | 2025-05-24 17:18 | 10:40 | S/O | 132 KV Bus Section -01 To GIS Connect | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 132KV Cumilla(N)-Kachua Ckt-1 | 2025-05-04 08:56 | 2025-05-04 16:19 | 7:23 | S/O | Line checking | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 132KV Cumilla(N)-Kachua Ckt-1 | 2025-05-12 09:49 | 2025-05-12 13:49 | 4:00 | S/O | Maint.work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Shahajibazar Ckt-2 | 2025-05-22 20:49 | 2025-05-22 23:45 | 2:56 | S/O | Maintenance work 330MW Shahjibazar end. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 132KV Cumilla(N)-Daudkandi Ckt-1 | 2025-05-25 06:51 | 2025-05-25 09:55 | 3:04 | S/O | CVT R phase Replacement | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Kachua | 2025-05-10 15:01 | 2025-05-10 18:26 | 3:25 | S/O | Bus extension of Kachua S/S | 0 | 0 | No interruption
Feni 132/33kV | Chowddagram Ckt-2 | 2025-05-22 09:16 | 2025-05-22 13:22 | 4:06 | S/O | Transfer DS maintenance work | 0 | 0 | No interruption
Feni 132/33kV | Chowmuhani Ckt-1 | 2025-05-24 06:20 | 2025-05-24 06:33 | 0:13 | S/O | For load shift to transfer bus at Chawmuhani grid end | 0 | 0 | No interruption
Feni 132/33kV | Chowmuhani Ckt-2 | 2025-05-24 06:20 | 2025-05-24 06:33 | 0:13 | S/O | For load shift to transfer bus at Chawmuhani grid end | 0 | 0 | No interruption
Feni 132/33kV | Chowmuhani Ckt-1 | 2025-05-25 12:35 | 2025-05-25 16:29 | 3:54 | S/O | 54 no tower R(Phase) Jumper maintenance | 0 | 0 | No interruption
Kachua 132/33kV | Cumilla North CKT | 2025-05-04 08:55 | 2025-05-04 16:20 | 7:25 | S/O | fault find out in line . | 0 | 0 | No interruption
Kachua 132/33kV | Cumilla South CKT | 2025-05-10 15:01 | 2025-05-10 18:27 | 3:26 | S/O | ESPN project for bus loop connection | 0 | 0 | No interruption
Kachua 132/33kV | Cumilla North CKT | 2025-05-12 09:49 | 2025-05-12 13:50 | 4:01 | S/O | Project work | 0 | 0 | No interruption
Ramganj 132/33kV | Ramgonj-Chowmuhani Ckt-01 | 2025-05-24 06:43 | 2025-05-24 17:17 | 10:34 | S/O | work at chowmuhani end | 24 | 253.6 | Power interruption
Ramganj 132/33kV | Ramgonj-Chowmuhani Ckt-02 | 2025-05-24 06:43 | 2025-05-24 17:17 | 10:34 | S/O | Work at Chowmuhani end. | 24 | 253.6 | Power interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-1 | 2025-05-03 06:15 | 2025-05-03 13:27 | 7:12 | S/O | Due to Conductors Armoring Section 608 to 609 and Phase Y&B | 0 | 0 | No interruption
|  |  | Total : | 1900-01-10 23:50 |  | Unserved Energy: |  | 507.2
Khulna Grid Circle :
Bagerhat 132/33kV | Bagerhat-Mongla 1 | 2025-05-03 02:58 | 2025-05-03 06:29 | 3:31 | S/O | Mongla substation shutdown is taken to perform the project work on the mongla edge. | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat-Mongla 2 | 2025-05-03 02:59 | 2025-05-03 06:32 | 3:33 | S/O | Mongla substation shutdown is taken to perform the project work on the mongla edge. | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2025-05-14 06:22 | 2025-05-14 11:41 | 5:19 | S/O | Bhandaria grid have been taken SD | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat-Mongla 1 | 2025-05-31 05:38 | 2025-05-31 07:16 | 1:38 | S/O | Due to project work of Mongla ss | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat-Mongla 2 | 2025-05-31 05:39 | 2025-05-31 07:16 | 1:37 | S/O | Due to project work of Mongla SS. | 0 | 0 | No interruption
Barishal 132/33kV | 132kv Bhandaria ckt | 2025-05-11 22:26 | 2025-05-11 23:13 | 0:47 | S/O | For R phase line side temperature rise mitigate works. | 25 | 19.5833 | Power interruption
Barishal 132/33kV | 132kv Bhandaria ckt | 2025-05-14 06:21 | 2025-05-14 10:05 | 3:44 | S/O | S/d taken by bhandaria ss | 0 | 0 | No interruption
Barishal 230/132kV | Gopalgonj CKT-1 | 2025-05-07 09:21 | 2025-05-07 15:18 | 5:57 | S/O | Line differential and teleprotection establishment work. | 0 | 0 | No interruption
Barishal 230/132kV | Gopalgonj CKT-2 | 2025-05-07 15:28 | 2025-05-07 18:47 | 3:19 | S/O | Line differential and teleprotection work | 0 | 0 | No interruption
Bhandaria 132/33kV | Barishal (L4) | 2025-05-14 06:19 | 2025-05-14 10:05 | 3:46 | S/O | Bhandaria-Barishal North Ckt 1&2 loop change | 46 | 173.2667 | No interruption
Bhandaria 132/33kV | Bagerhat (L3) | 2025-05-14 06:19 | 2025-05-14 11:38 | 5:19 | S/O | Bhandaria -Barishal North ckt 1&2 loop change | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Khulna Central-1 | 2025-05-02 07:22 | 2025-05-02 11:44 | 4:22 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Barisal CKT-01 | 2025-05-07 09:22 | 2025-05-07 15:19 | 5:57 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Barisal CKT-02 | 2025-05-07 15:27 | 2025-05-07 18:47 | 3:20 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rampal Ckt-1 | 2025-05-21 15:23 | 2025-05-21 16:21 | 0:58 | S/O | Maint.work | 0 | 0 | No interruption
Khulna (C) | 132kV Central-Goalpara-1 | 2025-05-02 07:18 | 2025-05-02 11:43 | 4:25 | S/O | Maintenance of GP-1 ckt. Bus DS | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- South -1 | 2025-05-10 06:10 | 2025-05-10 11:10 | 5:00 | S/O | Red hot maintenance. | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- South -2 | 2025-05-26 06:11 | 2025-05-26 09:44 | 3:33 | S/O | Due to replace defective loop for reduce temperature. | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- South -1 | 2025-05-30 06:12 | 2025-05-30 09:28 | 3:16 | S/O | RED HOT MAINTENANCE. | 0 | 0 | No interruption
Khulna(S) 230/132kV | Gallamari Ckt-1 | 2025-05-10 05:37 | 2025-05-10 11:11 | 5:34 | S/O | Maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Gallamari Ckt-2 | 2025-05-10 05:37 | 2025-05-10 11:12 | 5:35 | S/O | Maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Satkhira Ckt-1 | 2025-05-10 05:40 | 2025-05-10 11:07 | 5:27 | S/O | Maint.work | 50 | 272.5 | Power interruption
Khulna(S) 230/132kV | Satkhira Ckt-2 | 2025-05-10 05:40 | 2025-05-10 11:12 | 5:32 | S/O | None | 50 | 276.6667 | Power interruption
Khulna(S) 230/132kV | Khulna Central Ckt-1 | 2025-05-10 05:51 | 2025-05-10 11:09 | 5:18 | S/O | Maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-2 | 2025-05-26 06:11 | 2025-05-26 09:44 | 3:33 | S/O | Maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Satkhira Ckt-2 | 2025-05-27 07:43 | 2025-05-27 09:56 | 2:13 | S/O | Maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-1 | 2025-05-30 06:12 | 2025-05-30 09:28 | 3:16 | S/O | Maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-2 | 2025-05-30 09:31 | 2025-05-30 11:48 | 2:17 | S/O | Maint.work | 0 | 0 | No interruption
Madaripur 132/33kV | Barishal CKT-02 | 2025-05-17 20:30 | 2025-05-17 22:18 | 1:48 | S/O | 132 kV Madaripur-Barishal(N) CKT-2 due to Line DS problem. | 0 | 0 | No interruption
Mongla 132/33kV | 100MW ERBL Solar PS | 2025-05-03 02:55 | 2025-05-03 06:30 | 3:35 | S/O | G to G Project Work | 0 | 0 | No interruption
Mongla 132/33kV | Bagerhat-Mongla Line-1 | 2025-05-03 02:58 | 2025-05-03 06:29 | 3:31 | S/O | G to G Project Work | 0 | 0 | Power interruption
Mongla 132/33kV | Bagerhat-Mongla Line-2 | 2025-05-03 02:58 | 2025-05-03 06:32 | 3:34 | S/O | G to G Project Work | 0 | 0 | Power interruption
Patuakhali 132/33kV | PAYRA-PATUAKHALI CKT-2 | 2025-05-28 16:05 | 2025-05-28 18:44 | 2:39 | S/O | Red-hot maintenance work at Payra end. | 0 | 0 | No interruption
Payra 400/132/33kV | Payra Patuakhali Line-02 | 2025-05-28 16:08 | 2025-05-28 17:45 | 1:37 | S/O | High Temperature | 0 | 0 | No interruption
Satkhira 132/33kV | Khulna South-2 (L-2) | 2025-05-27 07:40 | 2025-05-27 09:57 | 2:17 | S/O | Maintenance work for Khulna south grid | 0 | 0 | No interruption
|  |  | Total : | 1900-01-04 07:07 |  | Unserved Energy: |  | 742.0167
HVDC Grid Circle :
Baghabari 230/132kV | Baghabari- Ishurdi -1 | 2025-05-09 07:08 | 2025-05-09 17:26 | 10:18 | S/O | Project work | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari- Ishurdi-2 | 2025-05-09 07:09 | 2025-05-09 17:26 | 10:17 | S/O | Project work | 0 | 0 | No interruption
Bheramara 230/132kV | HVDC 1 | 2025-05-02 07:20 | 2025-05-02 18:50 | 11:30 | S/O | Maint.work | 0 | 0 | No interruption
Bheramara 230/132kV | HVDC 2 | 2025-05-02 07:20 | 2025-05-02 18:51 | 11:31 | S/O | Maint.work | 0 | 0 | No interruption
Bheramara 230/132kV | HVDC 1 | 2025-05-31 06:04 | 2025-05-31 13:07 | 7:03 | S/O | Ruppur 400 KV line charge | 0 | 0 | No interruption
Bheramara 230/132kV | HVDC 2 | 2025-05-31 06:12 | 2025-05-31 13:08 | 6:56 | S/O | Ruppur 400 kv line charge | 0 | 0 | No interruption
Bheramara 230/132kV | Ishurdi 1 | 2025-05-31 06:19 | 2025-05-31 13:48 | 7:29 | S/O | Ruppur 400 kv line charge | 0 | 0 | No interruption
Bheramara 230/132kV | Ishurdi 2 | 2025-05-31 06:20 | 2025-05-31 13:49 | 7:29 | S/O | Ruppur 400 kv line charge | 0 | 0 | No interruption
BIPTC | Jhenaidah 1 | 2025-05-02 06:31 | 2025-05-02 18:44 | 12:13 | S/O | Shutdown has been taken for the installation of the cradle guard under Rooppur-Gopalganj 400KV Single Circuit Transmission Line Project. | 0 | 0 | No interruption
BIPTC | Jhenaidah 2 | 2025-05-02 06:31 | 2025-05-02 18:26 | 11:55 | S/O | Shutdown has been taken for the installation of the cradle guard under Rooppur-Gopalganj 400KV Single Circuit Transmission Line Project. | 0 | 0 | No interruption
BIPTC | Bheramara-1 | 2025-05-02 06:51 | 2025-05-02 18:46 | 11:55 | S/O | Shutdown has been taken for the installation of the cradle guard under Rooppur-Gopalganj 400KV Single Circuit Transmission Line Project. | 0 | 0 | No interruption
BIPTC | Bheramara-2 | 2025-05-02 06:51 | 2025-05-02 18:51 | 12:00 | S/O | Shutdown has been taken for the installation of the cradle guard under Rooppur-Gopalganj 400KV Single Circuit Transmission Line Project. | 0 | 0 | No interruption
BIPTC | Jhenaidah 1 | 2025-05-10 07:46 | 2025-05-10 10:48 | 3:02 | S/O | Maint.work | 0 | 0 | No interruption
BIPTC | Jhenaidah 2 | 2025-05-11 07:51 | 2025-05-11 10:02 | 2:11 | S/O | Shutdown is taken by WGND project for energy meter replacement | 0 | 0 | No interruption
BIPTC | 20DF12 | 2025-05-17 11:42 | 2025-05-17 12:29 | 0:47 | S/O | Corrective maintenance work | 0 | 0 | No interruption
BIPTC | 10CF25 | 2025-05-21 08:55 | 2025-05-21 12:44 | 3:49 | S/O | Capacitor bank T1-60C current unbalance | 0 | 0 | No interruption
BIPTC | Bheramara-1 | 2025-05-31 06:04 | 2025-05-31 13:07 | 7:03 | S/O | Shutdown has been taken for withdrawn of the cradle guard under Rooppur-Gopalganj 400KV Single Circuit Transmission Line Project. | 0 | 0 | No interruption
BIPTC | Bheramara-2 | 2025-05-31 06:11 | 2025-05-31 13:08 | 6:57 | S/O | Shutdown has been taken for withdrawn of the cradle guard under Rooppur-Gopalganj 400KV Single Circuit Transmission Line Project. | 0 | 0 | No interruption
BIPTC | Jhenaidah 1 | 2025-05-31 07:01 | 2025-05-31 13:27 | 6:26 | S/O | Shutdown has been taken for withdrawn of the cradle guard under Rooppur-Gopalganj 400KV Single Circuit Transmission Line Project. | 0 | 0 | No interruption
BIPTC | Jhenaidah 2 | 2025-05-31 07:02 | 2025-05-31 13:28 | 6:26 | S/O | Shutdown has been taken for withdrawn of the cradle guard under Rooppur-Gopalganj 400KV Single Circuit Transmission Line Project. | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kv Natore-1 | 2025-05-20 08:34 | 2025-05-20 09:43 | 1:09 | S/O | Line parameter test | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kv Natore-2 | 2025-05-25 09:24 | 2025-05-25 12:33 | 3:09 | S/O | Maint.work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Baghabari Line | 2025-05-27 09:14 | 2025-05-27 11:59 | 2:45 | S/O | 82 no tower loop jumper connection | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Bheramara -1 | 2025-05-31 06:01 | 2025-05-31 13:47 | 7:46 | S/O | Maint.work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Bheramara -2 | 2025-05-31 06:01 | 2025-05-31 13:48 | 7:47 | S/O | Maint.work | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2025-05-07 13:58 | 2025-05-07 19:37 | 5:39 | S/O | Request by NLDC | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Baghabari 1 | 2025-05-09 07:08 | 2025-05-09 17:22 | 10:14 | S/O | Maint.work | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Baghabari 2 | 2025-05-09 07:09 | 2025-05-09 17:25 | 10:16 | S/O | Maint.work | 0 | 0 | No interruption
Jashore 132/33kV | Cap. Bank-1 | 2025-05-21 09:55 | 2025-06-04 15:53 | 341:58 | S/O | R-Phase PT change | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-HVDC Ckt-1 | 2025-05-02 06:31 | 2025-05-02 18:25 | 11:54 | S/O | Maint.work | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-HVDC Ckt-2 | 2025-05-02 06:31 | 2025-05-02 18:44 | 12:13 | S/O | Maint.work | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-HVDC Ckt-1 | 2025-05-10 07:51 | 2025-05-10 10:47 | 2:56 | S/O | Energy meter change | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-HVDC Ckt-2 | 2025-05-11 07:52 | 2025-05-11 10:03 | 2:11 | S/O | For Faulty Energy Meter Replacing work | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-Jhenaidah (Old) Ckt-2 | 2025-05-12 07:28 | 2025-05-12 10:02 | 2:34 | S/O | Faulty energy meter replacement work | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-HVDC Ckt-2 | 2025-05-31 06:42 | 2025-05-31 13:28 | 6:46 | S/O | Maint.work | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-HVDC Ckt-1 | 2025-05-31 07:00 | 2025-05-31 13:27 | 6:27 | S/O | Maint.work | 0 | 0 | No interruption
Shahjadpur 132/33kV | 132 KV Shahjadpur-Bghabari-2 | 2025-05-16 09:27 | 2025-05-24 16:32 | 199:05 | S/O | Bagabari Ckt -2 Reconducting work. | 0 | 0 | No interruption
Shahjadpur 132/33kV | 132 KV Shahjadpur-Sirajgonj | 2025-05-16 09:27 | 2025-05-17 17:53 | 32:26 | S/O | Bagabari ckt-02 Reconducting work. | 0 | 0 | No interruption
Ullahpara 132/33kV | Shahjadpur Ckt | 2025-05-16 09:25 | 2025-05-18 00:10 | 38:45 | S/O | Project Work. | 0 | 0 | No interruption
|  |  | Total : | 1900-02-03 23:17 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Bogura 132/33kV | Mahasthangarh-2 | 2025-05-18 11:17 | 2025-05-18 18:37 | 7:20 | S/O | Maint.work | 0 | 0 | No interruption
Bogura 132/33kV | Mahasthangarh-2 | 2025-05-19 11:35 | 2025-05-19 19:16 | 7:41 | S/O | Bogura132 kv ckt-02, Q2 DS Finger Change, | 0 | 0 | No interruption
Bogura 132/33kV | Mahasthangarh-2 | 2025-05-20 09:40 | 2025-05-20 18:52 | 9:12 | S/O | Bogura132 kv ckt-02, Q2 DS Finger Change, | 0 | 0 | No interruption
Bogura 132/33kV | Mahasthangarh-2 | 2025-05-21 15:51 | 2025-05-21 18:15 | 2:24 | S/O | Line checking | 0 | 0 | No interruption
Mahasthangarh 132/33kV | Mahasthangarh-Bogura 2 | 2025-05-18 11:14 | 2025-05-18 18:38 | 7:24 | S/O | Line checking | 0 | 0 | No interruption
Mahasthangarh 132/33kV | Mahasthangarh-Bogura 2 | 2025-05-19 11:29 | 2025-05-19 19:16 | 7:47 | S/O | Line checking | 0 | 0 | No interruption
Mahasthangarh 132/33kV | Mahasthangarh-Bogura 2 | 2025-05-20 09:36 | 2025-05-20 18:53 | 9:17 | S/O | Line checking | 0 | 0 | No interruption
Mahasthangarh 132/33kV | Mahasthangarh-Bogura 2 | 2025-05-21 15:42 | 2025-05-21 18:17 | 2:35 | S/O | Line checking | 0 | 0 | No interruption
Natore 132/33kV | Rajlanka | 2025-05-02 10:09 | 2025-05-02 15:07 | 4:58 | S/O | Punch list Problem solving. | 0 | 0 | No interruption
Natore 132/33kV | Rajlanka | 2025-05-18 06:19 | 2025-05-18 08:12 | 1:53 | S/O | Tree Trimming | 0 | 0 | No interruption
Natore 132/33kV | Ishurdi-1 | 2025-05-20 08:35 | 2025-05-20 09:47 | 1:12 | S/O | Tree Trimming | 0 | 0 | No interruption
Rajshahi 132/33kV | 132 kV Raj(new)-1 | 2025-05-25 08:25 | 2025-05-25 13:29 | 5:04 | S/O | Tree Trimming work | 0 | 0 | No interruption
Rajshahi 132/33kV | 132 kV PPP 50 Mw | 2025-05-27 09:01 | 2025-05-27 10:51 | 1:50 | S/O | Tree Trimming work | 0 | 0 | No interruption
Rajshahi 230/132/33kV | 132 kV Rajshahi ckt-01 | 2025-05-25 08:28 | 2025-05-25 13:30 | 5:02 | S/O | Project work | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Confidence-2 | 2025-05-09 12:04 | 2025-05-09 18:33 | 6:29 | S/O | Project work | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Confidence-1 | 2025-05-22 16:05 | 2025-06-02 15:41 | 263:36 | S/O | Tree cutting and aviation light setting on Parbatipur Ckt-01 | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Rangpur CKT-02 | 2025-05-13 16:53 | 2025-05-19 10:20 | 137:27 | S/O | Tree cutting and aviation light setting on Parbatipur Ckt-02 | 0 | 0 | No interruption
|  |  | Total : | 1900-01-19 01:11 |  | Unserved Energy: |  | 0
Others :Nil
No interruption
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1900-04-12 15:02 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:May 2025
| Area | Previous Month (April' 2025) |  |  |  | Current Month (May '2025)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 38 | 19 | 90 | 147 | 29 | 22 | 108 | 159
2 | Dhaka (South) Grid Circle. | 23 | 10 | 55 | 88 | 50 | 11 | 41 | 102
3 | Chattogram Grid Circle. | 14 | 14 | 24 | 52 | 43 | 15 | 34 | 92
4 | Cumilla Grid Circle. | 32 | 14 | 43 | 89 | 41 | 16 | 54 | 111
5 | Khulna Grid Circle. | 43 | 15 | 62 | 120 | 42 | 12 | 94 | 148
6 | HVDC Grid Circle | 5 | 20 | 49 | 74 | 16 | 27 | 54 | 97
7 | Bogura Grid Circle. | 45 | 27 | 47 | 119 | 36 | 40 | 33 | 109
8 | Others
9 | Total | 200 | 119 | 370 | 689 | 257 | 143 | 418 | 818
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:May 2025
| Area | Previous Month (April' 2025) |  |  |  | Current Month (May '2025)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 455.38 | 151.38 | 1813.52 | 2420.28 | 240.98 | 746.53 | 3096.75 | 4084.26
2 | Dhaka (South) Grid Circle. | 208.57 | 316.67 | 128.08 | 653.32 | 491.35 | 269.17 | 254.42 | 1014.93
3 | Chattogram Grid Circle. | 45.85 | 90.01 | 195.17 | 331.03 | 354.18 | 218.73 | 29 | 601.91
4 | Cumilla Grid Circle. | 266.57 | 67 | 328.15 | 661.72 | 225.3 | 715.08 | 1416.22 | 2356.6
5 | Khulna Grid Circle. | 255.63 | 48.73 | 1633.75 | 1938.11 | 998.32 | 258 | 1861.79 | 3118.11
6 | HVDC Grid Circle | 57.07 | 89.18 | 706.02 | 852.27 | 765.88 | 935.08 | 917.03 | 2617.99
7 | Bogura Grid Circle. | 421.95 | 252.42 | 171.95 | 846.32 | 428.52 | 1217.52 | 190.83 | 1836.87
8 | Others
9 | Total | 1711.02 | 1015.39 | 4976.64 | 7703.05 | 3504.53 | 4360.11 | 7766.04 | 15630.66
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-29
QF-LDC-29
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:May 2025
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 20 | 20 | 40 | 10 | 7 | 25 | 3925.44
2 | Dhaka (South) | 5031.6 | 20 | 6 | 26 | 9 | 2 | 13 | 853.617
3 | Chattogram | 2042 | 6 | 2 | 8 | 2 | 2 | 4 | 349.28
4 | Khulna | 2434 | 27 | 19 | 46 | 16 | 5 | 25 | 2211.84
5 | HVDC | 5954.3 | 19 | 11 | 30 |  | 4 | 26 | 2590.86
6 | Bogura | 3145.6 | 16 | 5 | 21 | 2 | 4 | 15 | 1508.6
7 | Cumilla | 2981 | 15 | 11 | 26 | 6 | 3 | 17 | 1794.96
8 | Others | - | - | - | - | - | - | - | -
| Total | 30390.1 | [6 empty] | 13234.597
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.98%
4 | Khulna | 99.97%
5 | HVDC | 99.97%
6 | Bogura | 99.97%
7 | Cumilla | 99.98% | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:May 2025
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | - | 2 | 2 |  | - | 2 | 158.8333
2 | Dhaka (South) | 990.29 | - | 4 | - | 4 | 1 | 3 | 1 | 161.3167
3 | Chattogram | 917 | - | 12 | - | 12 | 5 | 4 | 3 | 252.6333
4 | Khulna | 1238.4 | - | 5 | 4 | 9 | 1 | 3 | 5 | 906.25
5 | HVDC | 1325 | - | 1 |  | 1 |  |  | 1 | 27.1333
6 | Bogura | 1803.3 | - | 7 |  | 7 | 1 | 1 | 5 | 328.2667
7 | Cumilla | 1648.16 | - | 7 | 2 | 9 | 1 | 4 | 4 | 561.63
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 2396.0633
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 100%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.98%
4 | Khulna | 99.98%
5 | Bheramara (HVDC) | 99.99%
6 | Bogura | 99.98%
7 | Cumilla | 99.99% | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:May 2025
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks | 0:20 | 0:53
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm | [6 empty] | 0:08 | 0:38
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. |  | 1:04 | 0:46
2025-05-01 | 17 | - | 17 | 64hr 57 min | 5 | 06hr 47 min | - | - | - | - | - | - |  | 1:34 | 3:12
[14 empty] | 7:32 | 1:18
0:32
2:12
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption. | [13 empty] | 1:25
1:34
0:50
1:20
10:16
[12 empty] | Executive Engineer |  | 1:40
[12 empty] | Information Management Division |  | 1:00
[12 empty] | LDC, Power Grid, Dhaka. |  | 31:40
1:11
0:39
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-32
QF-LDC-32
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:May 2025
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Bhaluka 132/33kV | 1 | 2:15 | 135
Jamalpur 132/33kV | 3 | 3:28 | 67.92
Kabirpur 132/33kV | 2 | 8:13 | 488.33
Kishoreganj 132/33kV | 3 | 0:48 | 34.53
Manikganj 132/33kV | 1 | 0:42 | 31.5
Mirzapur 132/33kV | 1 | 0:22 | 12.8333
Sreepur 230/132/33kV | 6 | 2:48 | 103
Tangail 132/33kV | 3 | 1:28 | 114.4
Bhaluka 132/33kV | 3 | 8:50 | 320.75
Kabirpur 132/33kV | 9 | 23:44 | 1721.67
Kishoreganj 132/33kV | 2 | 6:16 | 344
Kodda 132/33kV | 1 | 2:17 | 91.3333
Manikganj 132/33kV | 2 | 2:33 | 45.75
Savar 132/33kV | 2 | 9:25 | 386.08
Sreepur 230/132/33kV | 1 | 0:34 | 28.3333
Manikganj 132/33kV | 1 | 2:07 | 105.8333
Savar 132/33kV | 1 | 1:46 | 53
Ghorashal 230kV | 2 | 2:41 | 194.9
Hasnabad 132/33kV | 3 | 4:30 | 114.4
Madanganj 132/33kV | 1 | 0:57 | 2.85
Munshiganj 132/33kV | 4 | 7:42 | 215.92
Narshingdi 132/33kV | 3 | 0:44 | 6.4
Nawabganj 132/33kV | 4 | 0:28 | 6.48
Sonargaon 132/33kV | 2 | 1:26 | 58.25
Hasnabad 132/33kV | 1 | 0:47 | 54.8333
Shyampur 132/33kV | 2 | 22:31 | 83.67
Siddhirganj 132/33kV | 1 | 0:37 | 22.8167
Ghorashal 230kV | 1 | 2:49 | 140.8333
Narshingdi 132/33kV | 1 | 1:25 | 17
Srinagar 132/33kV | 4 | 7:34 | 96.58
Coxsbazar 132/33kV | 1 | 1:54 | 28.5
Halishahar 132/33kV | 2 | 1:19 | 16.47
Hathazari 230/132/33kV | 2 | 5:54 | 198.67
Kalurghat 132/33kV | 2 | 1:26 | 20.07
Khulshi 132/33kV | 2 | 1:10 | 56.58
Coxsbazar 132/33kV | 2 | 0:32 | 22.43
Dohazari 132/33kV | 3 | 0:55 | 45.98
Hathazari 230/132/33kV | 2 | 1:02 | 41.33
Mirsorai 230/33kV | 2 | 3:26 | 41.2
Shahmirpur 132/33kV | 2 | 1:51 | 98.05
Shikalbaha 230/132kV | 1 | 3:38 | 3.6333
Dohazari 132/33kV | 1 | 1:24 | 16
Madunaghat 132/33kV | 1 | 1:18 | 13
Beanibazar 132/33kV | 1 | 1:24 | 63
Chandina 132/33kV | 2 | 2:19 | 40.45
Chowmuhani 132/33kV | 4 | 14:35 | 574.08
Cumilla(N) 230/132/33kV | 1 | 1:24 | 70
Cumilla(S) 132/33kV | 5 | 1:32 | 47.35
Sylhet 132/33kV | 2 | 3:20 | 91.07
Beanibazar 132/33kV | 1 | 0:46 | 3.0667
Cumilla(S) 132/33kV | 2 | 1:42 | 30.6
Fenchuganj 230/132/33kV | 2 | 0:46 | 18.4
Sylhet (South) | 2 | 2:22 | 2.37
Chauddagram 132/33kV | 2 | 8:15 | 208.22
Chhatak 132/33kV | 1 | 13:25 | 80.5
Chowmuhani 132/33kV | 1 | 0:46 | 11.5
Fenchuganj 230/132/33kV | 1 | 1:10 | 17.5
Ramganj 132/33kV | 2 | 4:25 | 220.83
Shahjibazar 132/33kV | 1 | 2:54 | 232
Sunamganj 132/33kV | 1 | 8:59 | 107.8
Sylhet 132/33kV | 2 | 2:56 | 30.67
Ramganj 132/33kV | 2 | 21:08 | 507.2
Barishal 132/33kV | 5 | 3:19 | 53.4
Benapole 132/33kV | 3 | 1:01 | 23.33
Borhanuddin 230/33kV | 2 | 2:37 | 151
Chandina 132/33kV | 1 | 0:55 | 3.7675
Faridpur 132/33kV | 1 | 0:15 | 15
Goalpara 132/33kV | 2 | 0:22 | 5.87
Gopalganj 132/33kV | 2 | 1:41 | 55.83
Khulna(S) 230/132kV | 3 | 5:33 | 701.92
Mongla 132/33kV | 3 | 2:47 | 61.78
Noapara 132/33kV | 2 | 0:32 | 11.59
Rajbari 132/33kV | 2 | 0:48 | 6.65
Satkhira 132/33kV | 1 | 0:02 | 1.9333
Barishal 132/33kV | 1 | 1:20 | 57.3333
Bhandaria 132/33kV | 1 | 0:53 | 26.5
Mongla 132/33kV | 1 | 0:03 | 3.4
Satkhira 132/33kV | 2 | 1:24 | 77
Bagerhat 132/33kV | 1 | 2:11 | 65.5
Barguna 132/33kV | 1 | 1:53 | 9.4167
Barishal 132/33kV | 3 | 4:16 | 93.67
Benapole 132/33kV | 3 | 6:23 | 176.27
Borhanuddin 230/33kV | 1 | 8:01 | 360.75
Faridpur 132/33kV | 3 | 5:16 | 100.6
Goalpara 132/33kV | 3 | 7:24 | 38.77
Mongla 132/33kV | 2 | 5:16 | 152.3
Satkhira 132/33kV | 1 | 1:17 | 64.1667
Shariatpur 132/33kV | 1 | 2:05 | 58.3333
Barishal 132/33kV | 1 | 0:47 | 19.5833
Bhandaria 132/33kV | 1 | 3:46 | 173.2667
Khulna(S) 230/132kV | 2 | 10:59 | 549.17
Bhangura 132/33kV | 5 | 6:09 | 87.58
Chuadanga 132/33kV | 6 | 30:18 | 1210.08
Jhenaidah 132/33kV | 2 | 2:57 | 123.25
Kushtia 132/33kV | 5 | 6:58 | 232.33
Ruppur 132/11kV | 1 | 7:21 | 20.58
Bhangura 132/33kV | 1 | 0:44 | 27.1333
Bheramara(GK) 132/33kV | 3 | 11:21 | 507.57
Chuadanga 132/33kV | 1 | 2:23 | 59.5833
Ishurdi 132/33kV | 2 | 3:31 | 90.5
Jhenaidah 132/33kV | 1 | 3:33 | 124.25
Kushtia 132/33kV | 2 | 4:03 | 74.83
Magura 132/33kV | 2 | 3:29 | 60.3
Amnura 132/33kV | 2 | 0:14 | 0.93
Barapukuria 230/132/33kV | 1 | 31:40 | 696.6667
Bogura 132/33kV | 2 | 1:42 | 58
Jaldhaka 132/33kV | 1 | 1:11 | 14.2
Joypurhat 132/33kV | 1 | 2:02 | 30.5
Lalmonirhat 132/33kV | 1 | 0:54 | 9.45
Mahasthangarh 132/33kV | 1 | 3:15 | 113.75
Naogaon 132/33kV | 2 | 11:02 | 244.82
Natore 132/33kV | 1 | 1:38 | 32.6667
Niamatpur 132/33kV | 2 | 1:24 | 37.03
Palashbari 132/33kV | 1 | 0:39 | 9.75
Purbasadipur 132/33kV | 1 | 1:45 | 70
Bogura 230/132kV | 2 | 2:36 | 153.4
Kurigram 132/33kV | 2 | 3:29 | 105.07
Rangpur 132/33kV | 1 | 1:18 | 33.8
Thakurgaon 132/33kV | 2 | 2:24 | 36
Bogura 132/33kV | 2 | 4:03 | 62.67
Rajshahi 132/33kV | 2 | 3:59 | 86.5
Rangpur 132/33kV | 1 | 1:40 | 41.6667
| 243 | 494:32 | 15630.6742
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: May 2025
Sl No. | Sub-station | Load (MW) | Date & Time
1 | AKS | 18 | 2025-05-30 08:00
2 | AKSML | 145 | 2025-05-31 21:00
3 | Aftabnagar | 68 | 2025-05-19 13:00
4 | Agargaon | 150 | 2025-05-08 15:00
5 | Agrabad | 110 | 2025-05-13 15:00
6 | Amnura | 52 | 2025-05-01 12:00
7 | Ashuganj | 136.5 | 2025-05-06 01:00
8 | BSRM | 210 | 2025-05-21 07:00
9 | Bagerhat | 92 | 2025-05-07 23:00
10 | Bajitpur | 62 | 2025-05-10 19:00
11 | Bakulia | 117 | 2025-05-17 16:00
12 | Banani | 58 | 2025-05-19 12:00
13 | Bangabhaban | 20 | 2025-05-14 10:00
14 | Barapukuria | 76 | 2025-05-11 19:30
15 | Barguna | 34 | 2025-05-11 23:00
16 | Barishal | 126 | 2025-05-22 12:00
17 | Barishal-230 | 130 | 2025-05-10 21:00
18 | Baroaulia | 85.5 | 2025-05-07 16:00
19 | Baroirhat | 87 | 2025-05-10 23:00
20 | Bashundhara | 226 | 2025-05-10 15:00
21 | BashundharaCement | 17 | 2025-05-21 23:00
22 | Beanibazar | 87 | 2025-05-27 22:00
23 | Benapole | 77 | 2025-05-13 19:00
24 | Bhaluka | 190 | 2025-05-28 19:00
25 | Bhandaria | 70 | 2025-05-17 22:00
26 | Bhangura | 54 | 2025-05-10 19:00
27 | Bheramara(GK) | 80 | 2025-05-10 19:30
28 | Bhulta | 269 | 2025-05-31 22:00
29 | Bog-Sherpur | 80 | 2025-05-10 19:30
30 | Bogura | 211 | 2025-05-10 22:00
31 | Borhanuddin | 105 | 2025-05-17 00:00
32 | Brahmanbaria | 137 | 2025-05-08 22:00
33 | Cantonment | 168 | 2025-05-11 16:00
34 | Chandina | 26.1 | 2025-05-16 21:00
35 | Chandpur | 81 | 2025-05-13 21:00
36 | Chandraghona | 40 | 2025-05-09 19:00
37 | Chapai | 81 | 2025-05-10 22:00
38 | Charsaidpur | 50 | 2025-05-19 12:00
39 | Chauddagram | 82 | 2025-05-27 20:00
40 | Chhatak | 43 | 2025-05-25 19:30
41 | Chowmuhani | 243 | 2025-05-09 23:00
42 | Chuadanga | 132 | 2025-05-10 23:00
43 | Coxsbazar | 154 | 2025-05-15 12:00
44 | Cumilla(N) | 172 | 2025-05-09 21:00
45 | Cumilla(S) | 197 | 2025-05-11 15:00
46 | Daudkandi | 160 | 2025-05-07 21:00
47 | Dhaka | 88 | 2025-05-17 12:00
48 | Dhamrai | 144 | 2025-05-08 14:00
49 | Dhanmondi | 185.7 | 2025-05-14 13:00
50 | Dohazari | 116 | 2025-05-15 19:30
51 | Faridpur | 183 | 2025-05-14 00:00
52 | Fatullah | 111 | 2025-05-10 15:00
53 | Fenchuganj | 51 | 2025-05-09 19:30
54 | Feni | 134 | 2025-05-16 22:00
55 | GPH | 99 | 2025-05-23 18:00
56 | Ghatail | 86 | 2025-05-08 19:00
57 | Ghorashal | 18 | 2025-05-10 10:00
58 | Ghorashal-230 | 106 | 2025-05-28 22:00
59 | Goalpara | 52 | 2025-05-14 00:00
60 | Gollamari | 114 | 2025-05-12 00:00
61 | Gopalganj | 122 | 2025-05-11 19:30
62 | Gulshan | 154 | 2025-05-14 13:00
63 | Halishahar | 99 | 2025-05-13 15:00
64 | HaripurSBU | 197 | 2025-05-20 11:00
65 | Hasnabad | 98 | 2025-05-13 20:00
66 | Hathazari | 94 | 2025-05-10 23:00
67 | Ishurdi | 95 | 2025-05-10 19:30
68 | Jaldhaka | 88 | 2025-05-09 20:00
69 | Jamalpur | 146 | 2025-05-07 19:30
70 | Jashore | 165 | 2025-05-10 20:00
71 | Jhenaidah | 154 | 2025-05-11 19:30
72 | Joydebpur | 169 | 2025-05-13 16:00
73 | Joypurhat | 87 | 2025-05-10 23:00
74 | Juldah | 20 | 2025-05-10 23:00
75 | KSRM | 46 | 2025-05-22 15:00
76 | Kabirpur | 289 | 2025-05-20 09:00
77 | Kachua | 114 | 2025-05-27 21:00
78 | Kallyanpur | 132 | 2025-05-12 23:00
79 | Kalurghat | 52 | 2025-05-18 19:00
80 | Kamrangirchar | 73 | 2025-05-13 18:00
81 | Kaptai | N/A | N/A
82 | Kasba | 43 | 2025-05-09 23:00
83 | Kazla | 121 | 2025-05-14 12:00
84 | Keranigonj | 105 | 2025-05-21 12:00
85 | Khagrachori | 38 | 2025-05-09 19:00
86 | Khulna | 88 | 2025-05-16 13:00
87 | Khulshi | 216 | 2025-05-10 17:00
88 | Kishoreganj | 155 | 2025-05-09 21:00
89 | Kodda | 319 | 2025-05-27 20:00
90 | Kulaura | 60 | 2025-05-27 19:00
91 | Kurigram | 71 | 2025-05-09 19:00
92 | Kushtia | 177 | 2025-05-14 19:30
93 | Lalbag | 80 | 2025-05-17 11:00
94 | Lalmonirhat | 68 | 2025-05-09 19:30
95 | MI_Cement | 18.3 | 2025-05-11 12:00
96 | Madanganj | 56 | 2025-05-08 16:00
97 | Madaripur | 134 | 2025-05-10 22:00
98 | Madartek | 113.46 | 2025-05-11 01:00
99 | Madunaghat | 71 | 2025-05-16 19:30
100 | Magura | 75 | 2025-05-10 19:30
101 | Mahasthangarh | 100 | 2025-05-10 20:00
102 | Manikganj | 151 | 2025-05-10 21:00
103 | Maniknagar | 100 | 2025-05-14 13:00
104 | Matarbari | 55 | 2025-05-08 19:30
105 | Matuail | 74 | 2025-05-08 12:00
106 | Millgate | 135 | 2025-05-10 16:00
107 | Mirpur | 161 | 2025-05-13 19:00
108 | Mirsorai | 12 | 2025-05-19 13:00
109 | Mirzapur | 53 | 2025-05-15 15:00
110 | Mithapukur | 82 | 2025-05-27 20:00
111 | Modern | 13 | 2025-05-23 01:00
112 | Mogbazar | 173.6 | 2025-05-14 13:00
113 | Mongla | 55 | 2025-05-17 22:00
114 | Motijheel | 48 | 2025-05-14 13:00
115 | Muktagacha | 44 | 2025-05-09 19:30
116 | Munshiganj | 128 | 2025-05-10 19:00
117 | Muradnagar | 33 | 2025-05-02 22:00
118 | Mymensingh | 228 | 2025-05-08 20:00
119 | Naogaon | 167 | 2025-05-10 21:00
120 | Narail | 68 | 2025-05-10 19:30
121 | Narinda | 91 | 2025-05-19 13:00
122 | Narshingdi | 202 | 2025-05-28 19:30
123 | Natore | 184 | 2025-05-10 19:30
124 | Nawabganj | 68.4 | 2025-05-13 22:00
125 | Netrakona | 130 | 2025-05-08 18:30
126 | New | 97.1 | 2025-05-28 16:00
127 | Niamatpur | 100 | 2025-05-10 22:00
128 | Noapara | 64 | 2025-05-11 21:00
129 | PHP | 9 | 2025-05-08 08:00
130 | Pabna | 140 | 2025-05-13 19:30
131 | Palashbari | 143 | 2025-05-08 20:00
132 | Panchagarh | 66 | 2025-05-30 19:30
133 | Patuakhali | 91 | 2025-05-15 23:00
134 | Payra | 38 | 2025-05-09 21:00
135 | Postogola | 67 | 2025-05-11 16:00
136 | Purbachal | 24 | 2025-05-11 00:00
137 | Purbasadipur | 146 | 2025-05-31 22:00
138 | Rahanpur | 34 | 2025-05-13 22:00
139 | Rahim | 57 | 2025-05-11 14:00
140 | Rajbari | 96 | 2025-05-10 19:30
141 | Rajendrapur | 151 | 2025-05-08 19:30
142 | Rajshahi | 156 | 2025-05-15 00:00
143 | Rajshahi-230 | 108 | 2025-05-10 23:00
144 | Ramganj | 126 | 2025-05-27 19:00
145 | Rampur | 51 | 2025-05-11 00:00
146 | Rangamati | 22 | 2025-05-10 19:00
147 | Rangpur | 165 | 2025-05-08 19:00
148 | Ruppur | 8.8 | 2025-05-21 15:00
149 | SSM | 16 | 2025-05-28 02:00
150 | Saidpur | 122 | 2025-05-07 19:30
151 | Satkhira | 154 | 2025-05-17 21:00
152 | Satmasjid | 128 | 2025-05-11 16:00
153 | Savar | 240 | 2025-05-08 16:00
154 | SevenRings | 22.95 | 2025-05-29 13:00
155 | ShahCement | 38 | 2025-05-15 17:00
156 | Shahjadpur | 103 | 2025-05-10 22:00
157 | Shahjibazar | 123 | 2025-05-15 23:00
158 | Shahmirpur | 67 | 2025-05-11 00:00
159 | Shariatpur | 99 | 2025-05-10 23:00
160 | Sherpur | 166 | 2025-05-05 19:00
161 | Shikalbaha | 36 | 2025-05-15 13:00
162 | Shitalakhya | 100.6 | 2025-05-10 16:00
163 | Sholosohor | 54 | 2025-05-15 16:00
164 | Shyampur | 202 | 2025-05-16 11:00
165 | Siddhirganj | 136 | 2025-05-11 15:00
166 | Sirajganj | 142 | 2025-05-07 22:00
167 | Sonargaon | 134 | 2025-05-08 19:00
168 | Sreemongol | 96 | 2025-05-10 19:00
169 | Sreepur | 117 | 2025-05-28 12:00
170 | Srinagar | 54.56 | 2025-05-10 21:00
171 | Sunamganj | 64 | 2025-05-09 19:00
172 | Sylhet | 53 | 2025-05-10 19:30
173 | Sylhet-132 | 144 | 2025-05-10 19:00
174 | TK | 37.6 | 2025-05-13 19:00
175 | Tangail | 210 | 2025-05-11 20:00
176 | Thakurgaon | 120 | 2025-05-31 21:00
177 | Tongi | 146 | 2025-05-28 15:00
178 | Ullahpara | 52 | 2025-05-09 23:00
179 | Ullon | 65 | 2025-05-10 00:00
180 | Uttara | 111 | 2025-05-11 16:00
181 | UttaraNew | 69 | 2025-05-14 00:00
182 | Zigatola | 84 | 2025-05-10 16:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID BANGLADESH PLC. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: May 2025
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 5982.3 | 2025-05-28 | 15:00
Chattogram | 1716.7 | 2025-05-15 | 0:00
Cumilla | 1534.34 | 2025-05-09 | 22:00
Mymensingh | 1283 | 2025-05-07 | 19:00
Sylhet | 675 | 2025-05-10 | 19:00
Khulna | 2038.2 | 2025-05-10 | 23:00
Barishal | 554.8 | 2025-05-10 | 21:00
Rajshahi | 1863.8 | 2025-05-10 | 22:00
Rangpur | 1051 | 2025-05-07 | 19:30
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: May 2025
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar | 400 | 394 | 2025-05-30 04:00 | 300 | 2025-05-07 02:00
2 | Ashuganj | 400 | N/A | N/A | N/A | N/A
3 | Bhulta | 400 | 408 | 2025-05-30 05:00 | 351 | 2025-05-13 12:00
4 | Bibiana | 400 | 398 | 2025-05-30 03:00 | 283 | 2025-05-10 22:00
5 | BIPTC | 400 | 409 | 2025-05-30 08:00 | 385 | 2025-05-08 16:00
6 | Bogura | 400 | 409 | 2025-05-17 02:00 | 365 | 2025-05-03 19:00
7 | Gopalganj | 400 | 407 | 2025-05-30 06:00 | 375 | 2025-05-13 23:00
8 | Kaliakoir | 400 | 387 | 2025-05-01 22:00 | 355 | 2025-05-26 11:00
9 | Madunaghat | 400 | 405 | 2025-05-30 04:00 | 381 | 2025-05-12 11:00
10 | Meghnaghat | 400 | 400 | 2025-05-01 18:00 | 348 | 2025-05-04 21:00
11 | Payra | 400 | 420 | 2025-05-30 04:00 | 403 | 2025-05-11 20:00
12 | Rahanpur | 400 | 417 | 2025-05-17 02:00 | 381 | 2025-05-03 19:00
13 | Rampal | 400 | 411 | 2025-05-30 03:00 | 289 | 2025-05-30 22:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon | 230 | 255 | 2025-05-31 16:00 | 209 | 2025-05-13 12:00
2 | AKSML | 230 | 243 | 2025-05-30 04:00 | 201 | 2025-05-23 10:00
3 | Aminbazar | 230 | 233 | 2025-05-30 06:00 | 210 | 2025-05-14 13:00
4 | Ashuganj | 230 | 238 | 2025-05-30 03:00 | 213 | 2025-05-26 11:00
5 | Ashuganj-400 | 230 | N/A | N/A | N/A | N/A
6 | Baghabari | 230 | 237 | 2025-05-17 06:00 | 221 | 2025-05-25 22:00
7 | Barapukuria | 230 | 231 | 2025-05-17 01:00 | 213 | 2025-05-22 19:30
8 | Barapukuria-230 | 230 | N/A | N/A | N/A | N/A
9 | Barishal | 230 | 243 | 2025-05-30 03:00 | 224 | 2025-05-28
10 | Bheramara | 230 | 235 | 2025-05-04 18:00 | 188 | 2025-05-02 15:00
11 | Bhulta | 230 | 236 | 2025-05-30 03:00 | 202 | 2025-05-13 12:00
12 | Bibiana | 230 | 235 | 2025-05-30 04:00 | 216 | 2025-05-09 16:00
13 | BIPTC | 230 | 239 | 2025-05-02 08:00 | 221 | 2025-05-07 12:00
14 | Bogura | 230 | 239 | 2025-05-17 01:00 | 215 | 2025-05-22 21:00
15 | Bogura-400 | 230 | 240 | 2025-05-17 01:00 | 215 | 2025-05-22 21:00
16 | Borhanuddin | 230 | 248 | 2025-05-30 05:00 | 230 | 2025-05-31 23:00
17 | BSRM | 230 | 238 | 2025-05-30 03:00 | 202 | 2025-05-23 10:00
18 | Cumilla(N) | 230 | 233 | 2025-05-30 06:00 | 210 | 2025-05-21 01:30
19 | Faridpur | 230 | 240 | 2025-05-30 04:00 | 217 | 2025-05-25 22:00
20 | Fenchuganj | 230 | 236 | 2025-05-30 11:00 | 215 | 2025-05-27 14:00
21 | Ghorashal | 230 | 240 | 2025-05-30 03:00 | 210 | 2025-05-13 12:00
22 | Ghorashal-230 | 230 | 235 | 2025-05-30 04:00 | 210 | 2025-05-13 12:00
23 | Gopalganj | 230 | 260 | 2025-05-24 13:00 | 221 | 2025-05-13 23:00
24 | GPH | 230 | 241 | 2025-05-30 04:00 | 201 | 2025-05-23 10:00
25 | Haripur | 230 | 229 | 2025-05-01 07:00 | 209 | 2025-05-13 12:00
26 | Hasnabad | 230 | 231 | 2025-05-28 18:00 | 209 | 2025-05-13 12:00
27 | Hathazari | 230 | 243 | 2025-05-30 03:00 | 219 | 2025-05-26 11:00
28 | Ishurdi | 230 | 238 | 2025-05-21 18:30 | 217 | 2025-05-18 19:00
29 | Jhenaidah | 230 | 234 | 2025-05-30 00:00 | 195 | 2025-05-31 13:00
30 | Kaliakoir | 230 | 238 | 2025-05-02 05:00 | 215 | 2025-05-18 15:00
31 | Keranigonj | 230 | 231 | 2025-05-01 18:00 | 207 | 2025-05-13 13:00
32 | Khulna(S) | 230 | 237 | 2025-05-30 06:00 | 207 | 2025-05-14 23:00
33 | Madunaghat | 230 | 242 | 2025-05-30 04:00 | 221 | 2025-05-04 12:00
34 | Madunaghat-400 | 230 | 242 | 2025-05-30 04:00 | 221 | 2025-05-04 13:00
35 | Maniknagar | 230 | 228 | 2025-05-01 08:00 | 206 | 2025-05-13 13:00
36 | Meghnaghat | 230 | 238 | 2025-05-01 19:30 | 216 | 2025-05-13 12:00
37 | Meghnaghat-400 | 230 | 231 | 2025-05-01 08:00 | 211 | 2025-05-21 12:00
38 | Mirsorai | 230 | 239 | 2025-05-30 03:00 | 207 | 2025-05-23 12:00
39 | Rajshahi | 230 | 266 | 2025-05-29 19:30 | 219 | 2025-05-08 13:00
40 | Rampal | 230 | 236 | 2025-05-30 03:00 | 210 | 2025-05-10 19:30
41 | Rampur | 230 | N/A | N/A | N/A | N/A
42 | Rampura | 230 | 237 | 2025-05-30 04:00 | 202 | 2025-05-13 12:00
43 | Shikalbaha | 230 | 244 | 2025-05-11 08:00 | 220 | 2025-05-04 12:00
44 | Shyampur | 230 | 230 | 2025-05-01 18:00 | 208 | 2025-05-13 13:00
45 | Siddhirganj | 230 | 231 | 2025-05-01 17:00 | 214 | 2025-05-24 16:00
46 | Sirajgonj | 230 | 241 | 2025-05-01 06:00 | 228 | 2025-05-30 19:30
47 | Sreepur | 230 | 233 | 2025-05-03 16:00 | 213 | 2025-05-26 11:00
48 | Tongi | 230 | 233 | 2025-05-30 07:00 | 202 | 2025-05-26 10:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar | 132 | 141 | 2025-05-16 21:00 | 121 | 2025-05-13 11:00
2 | Agargaon | 132 | 160 | 2025-05-15 18:30 | 119 | 2025-05-13 13:00
3 | Agrabad | 132 | 144 | 2025-05-30 04:00 | 124 | 2025-05-26 10:00
4 | AKS | 132 | 137 | 2025-05-30 05:00 | 123 | 2025-05-04 12:00
5 | Aminbazar | 132 | 135 | 2025-05-16 21:00 | 119 | 2025-05-13 10:00
6 | Amnura | 132 | 152 | 2025-05-28 23:00 | 118 | 2025-05-03 19:00
7 | Ashuganj | 132 | 142 | 2025-05-29 21:00 | 127 | 2025-05-24 18:30
8 | Bagerhat | 132 | 140 | 2025-05-30 02:00 | 110 | 2025-05-10 22:00
9 | Bajitpur | 132 | 139 | 2025-05-30 00:00 | 119 | 2025-05-24 12:00
10 | Bakulia | 132 | 158 | 2025-05-28 12:00 | 124 | 2025-05-04 12:00
11 | Banani | 132 | 141 | 2025-05-17 06:00 | 111 | 2025-05-19 18:00
12 | Bangabhaban | 132 | 138 | 2025-05-30 08:00 | 117 | 2025-05-14 11:00
13 | Barapukuria | 132 | 142 | 2025-05-17 01:00 | 121 | 2025-05-31 20:00
14 | Barguna | 132 | 139 | 2025-05-30 03:00 | 127 | 2025-05-11 02:00
0 | Barishal | 132 | 138 | 2025-05-30 03:00 | 121 | 2025-05-27 22:00
16 | Barishal-230 | 132 | 138 | 2025-05-30 03:00 | 122 | 2025-05-10 19:00
17 | Baroaulia | 132 | 139 | 2025-05-09 09:00 | 124 | 2025-05-04 12:00
18 | Baroirhat | 132 | 140 | 2025-05-30 04:00 | 115 | 2025-05-04 11:00
19 | Bashundhara | 132 | 140 | 2025-05-16 21:00 | 117 | 2025-05-07 12:00
20 | BashundharaCement | 132 | 133 | 2025-05-01 18:00 | 119 | 2025-05-13 13:00
21 | Beanibazar | 132 | 139 | 2025-05-30 08:00 | 119 | 2025-05-27 11:00
22 | Benapole | 132 | 138 | 2025-05-30 03:00 | 111 | 2025-05-10 22:00
23 | Bhaluka | 132 | 137 | 2025-05-29 23:00 | 119 | 2025-05-25 12:00
24 | Bhandaria | 132 | 135 | 2025-05-29 08:00 | 108 | 2025-05-17 22:00
25 | Bhangura | 132 | 137 | 2025-05-17 06:00 | 125 | 2025-05-22 19:30
26 | Bheramara | 132 | 139 | 2025-05-09 08:00 | 110 | 2025-05-02 15:00
27 | Bheramara(GK) | 132 | 138 | 2025-05-08 07:00 | 109 | 2025-05-02 15:00
28 | Bhulta | 132 | 128 | 2025-05-01 18:00 | 112 | 2025-05-19 12:00
29 | Bog-Sherpur | 132 | 139 | 2025-05-06 11:00 | 122 | 2025-05-22 21:00
30 | Bogura | 132 | 141 | 2025-05-06 07:00 | 126 | 2025-05-22 21:00
31 | Bogura-230 | 132 | 142 | 2025-05-17 01:00 | 125 | 2025-05-22 21:00
32 | Brahmanbaria | 132 | 138 | 2025-05-29 21:00 | 114 | 2025-05-26 13:00
33 | Cantonment | 132 | 140 | 2025-05-30 07:00 | 119 | 2025-05-13 13:00
34 | Chandina | 132 | 140 | 2025-05-30 03:00 | 118 | 2025-05-26 11:00
35 | Chandpur | 132 | 140 | 2025-05-30 03:00 | 112 | 2025-05-29 11:00
36 | Chandraghona | 132 | 141 | 2025-05-30 04:00 | 124 | 2025-05-26 11:00
37 | Chapai | 132 | 137 | 2025-05-17 02:00 | 121 | 2025-05-02 22:00
39 | Charsaidpur | 132 | 135 | 2025-05-27 08:00 | 120 | 2025-05-13 13:00
40 | Chauddagram | 132 | 140 | 2025-05-30 04:00 | 115 | 2025-05-09 12:00
41 | Chhatak | 132 | 136 | 2025-05-30 06:00 | 116 | 2025-05-27 11:00
42 | Chowmuhani | 132 | 140 | 2025-05-30 05:00 | 107 | 2025-05-24 19:30
43 | Chuadanga | 132 | 141 | 2025-05-17 21:00 | 110 | 2025-05-10 19:00
44 | Coxsbazar | 132 | 140 | 2025-05-30 06:00 | 106 | 2025-05-16 23:00
45 | Cumilla(N) | 132 | 141 | 2025-05-18 12:00 | 119 | 2025-05-21 14:00
46 | Cumilla(S) | 132 | 138 | 2025-05-30 04:00 | 116 | 2025-05-26 11:00
47 | Daudkandi | 132 | 136 | 2025-05-30 03:00 | 115 | 2025-05-18 14:00
48 | Dhaka | 132 | 140 | 2025-05-16 21:00 | 121 | 2025-05-13 11:00
49 | Dhamrai | 132 | 143 | 2025-05-16 21:00 | 123 | 2025-05-31 11:00
50 | Dhanmondi | 132 | 142 | 2025-05-28 05:00 | 121.5 | 2025-05-13 11:00
51 | Dohazari | 132 | 139 | 2025-05-30 07:00 | 119 | 2025-05-16 23:00
52 | Faridpur | 132 | 140 | 2025-05-30 04:00 | 125 | 2025-05-11 00:00
53 | Fatullah | 132 | 135 | 2025-05-01 18:00 | 120 | 2025-05-13 13:00
54 | Fenchuganj | 132 | 141 | 2025-05-30 06:00 | 128 | 2025-05-24 01:00
55 | Feni | 132 | 139 | 2025-05-30 04:00 | 110 | 2025-05-03 01:00
56 | Ghatail | 132 | 138 | 2025-05-29 23:00 | 118 | 2025-05-02 01:00
57 | Ghorashal | 132 | 141 | 2025-05-17 06:00 | 124 | 2025-05-13 12:00
58 | Goalpara | 132 | 142 | 2025-05-30 04:00 | 119 | 2025-05-14 23:00
59 | Gollamari | 132 | 142 | 2025-05-30 04:00 | 121 | 2025-05-10 11:00
60 | Gopalganj | 132 | 140 | 2025-05-30 05:00 | 121 | 2025-05-10 19:30
61 | Gopalganj-400 | 132 | 140 | 2025-05-30 04:00 | 127 | 2025-05-10 19:30
62 | Gulshan | 132 | 141 | 2025-05-16 21:00 | 120 | 2025-05-13 11:00
63 | Halishahar | 132 | 144 | 2025-05-30 04:00 | 123 | 2025-05-04 12:00
64 | Haripur | 132 | 134 | 2025-05-01 08:00 | 121 | 2025-05-13 12:00
65 | HaripurSBU | 132 | 139 | 2025-05-30 10:00 | 121 | 2025-05-11 08:00
66 | Hasnabad | 132 | 137 | 2025-05-30 03:00 | 122 | 2025-05-11 11:00
67 | Hathazari | 132 | 142 | 2025-05-30 05:00 | 219 | 2025-05-26 11:00
68 | Ishurdi | 132 | 140 | 2025-05-01 18:00 | 130 | 2025-05-07 19:30
69 | Jaldhaka | 132 | 138 | 2025-05-06 07:00 | 114 | 2025-05-02 12:00
70 | Jamalpur | 132 | 142 | 2025-05-20 09:00 | 121 | 2025-05-01 17:00
71 | Jashore | 132 | 138 | 2025-05-01 18:00 | 108 | 2025-05-31 13:00
72 | Jhenaidah | 132 | 140 | 2025-05-17 22:00 | 114 | 2025-05-31 13:00
73 | Jhenaidah-230 | 132 | 140 | 2025-05-17 21:00 | 115 | 2025-05-31 13:00
74 | Joydebpur | 132 | 143 | 2025-05-01 14:00 | 116 | 2025-05-26 10:00
75 | Joypurhat | 132 | 140 | 2025-05-17 01:00 | 106 | 2025-05-22 21:00
76 | Juldah | 132 | 140 | 2025-05-30 07:00 | 124 | 2025-05-26 11:00
77 | Kabirpur | 132 | 141 | 2025-05-31 16:00 | 124 | 2025-05-05 20:00
78 | Kachua | 132 | 141 | 2025-05-30 03:00 | 141 | 2025-05-30 03:00
79 | Kaliakoir | 132 | 143 | 2025-05-02 02:00 | 126 | 2025-05-07 01:00
80 | Kallyanpur | 132 | 135 | 2025-05-01 18:00 | 119 | 2025-05-13 11:00
81 | Kalurghat | 132 | 140 | 2025-05-30 04:00 | 124 | 2025-05-26 11:00
82 | Kamrangirchar | 132 | 138 | 2025-05-01 07:00 | 122 | 2025-05-13 13:00
83 | Kaptai | 132 | N/A | N/A | N/A | N/A
84 | Kasba | 132 | 139 | 2025-05-30 03:00 | 117 | 2025-05-11 13:00
85 | Kazla | 132 | 138 | 2025-05-30 04:00 | 118 | 2025-05-13 13:00
86 | Keranigonj | 132 | 139 | 2025-05-01 18:00 | 122 | 2025-05-13 13:00
87 | Khagrachori | 132 | 140 | 2025-05-30 04:00 | 122 | 2025-05-26 11:00
88 | Khulna | 132 | 141 | 2025-05-30 03:00 | 117 | 2025-05-10 19:30
89 | Khulna(S) | 132 | 143 | 2025-05-30 04:00 | 120 | 2025-05-10 19:30
90 | Khulshi | 132 | 142 | 2025-05-30 04:00 | 122 | 2025-05-13 13:00
91 | Kishoreganj | 132 | 138 | 2025-05-29 23:00 | 115 | 2025-05-10 22:00
92 | Kodda | 132 | 139 | 2025-05-16 19:30 | 116 | 2025-05-26 12:00
93 | KSRM | 132 | 141 | 2025-05-30 03:00 | 124 | 2025-05-04 12:00
94 | Kulaura | 132 | 141 | 2025-05-30 07:00 | 126 | 2025-05-26 20:00
95 | Kurigram | 132 | 139 | 2025-05-30 05:00 | 115 | 2025-05-22 19:00
96 | Kushtia | 132 | 139 | 2025-05-17 21:00 | 110 | 2025-05-02 15:00
97 | Lalbag | 132 | 138 | 2025-05-01 18:30 | 120 | 2025-05-13 13:00
98 | Lalmonirhat | 132 | 137 | 2025-05-30 03:00 | 115 | 2025-05-26 19:30
99 | Madanganj | 132 | 133 | 2025-05-01 18:00 | 119 | 2025-05-13 13:00
100 | Madaripur | 132 | 139 | 2025-05-29 08:00 | 125 | 2025-05-10 23:00
101 | Madartek | 132 | 141 | 2025-05-16 21:00 | 120 | 2025-05-13 12:00
102 | Madunaghat | 132 | 138 | 2025-05-30 11:00 | 120 | 2025-05-22 10:00
103 | Magura | 132 | 140 | 2025-05-17 21:00 | 114 | 2025-05-31 13:00
104 | Mahasthangarh | 132 | 140 | 2025-05-17 03:00 | 122 | 2025-05-22 21:00
105 | Manikganj | 132 | 150 | 2025-05-06 15:00 | 114 | 2025-05-05 15:00
106 | Maniknagar | 132 | 138 | 2025-05-30 04:00 | 117 | 2025-05-14 11:00
107 | Matarbari | 132 | 139 | 2025-05-30 04:00 | 106 | 2025-05-16 23:00
108 | Matuail | 132 | 134 | 2025-05-01 18:00 | 120.5 | 2025-05-14 10:00
109 | Millgate | 132 | 158 | 2025-05-17 17:00 | 120 | 2025-05-07 11:00
110 | Mirpur | 132 | 135 | 2025-05-30 03:00 | 117 | 2025-05-13 11:00
111 | Mirzapur | 132 | 136 | 2025-05-17 04:00 | 124 | 2025-05-02 15:00
112 | Mithapukur | 132 | 140 | 2025-05-30 03:00 | 119 | 2025-05-26 19:30
113 | MI_Cement | 132 | 134 | 2025-05-01 18:00 | 120 | 2025-05-13 13:00
114 | Modern | 132 | 113 | 2025-05-23 01:00 | 113 | 2025-05-23 01:00
115 | Mogbazar | 132 | 142 | 2025-05-17 05:00 | 120 | 2025-05-13 11:00
116 | Mongla | 132 | 140 | 2025-05-30 02:00 | 112 | 2025-05-10 19:00
117 | Motijheel | 132 | 138 | 2025-05-30 08:00 | 117 | 2025-05-14 11:00
118 | Muktagacha | 132 | 140 | 2025-05-29 23:00 | 118 | 2025-05-06 11:00
119 | Munshiganj | 132 | 133 | 2025-05-01 07:00 | 119 | 2025-05-13 11:00
120 | Muradnagar | 132 | 139 | 2025-05-30 03:00 | 117 | 2025-05-11 13:00
121 | Mymensingh | 132 | 140 | 2025-05-29 23:00 | 109 | 2025-05-27 21:00
122 | Naogaon | 132 | 141 | 2025-05-17 01:00 | 107 | 2025-05-22 20:00
123 | Narail | 132 | 140 | 2025-05-17 21:00 | 113 | 2025-05-31 13:00
124 | Narinda | 132 | 0 | 2025-05-17 08:00 | 0 | 2025-05-17 08:00
125 | Narshingdi | 132 | 138 | 2025-05-29 19:30 | 109 | 2025-05-26 10:00
126 | Natore | 132 | 138 | 2025-05-17 05:00 | 125 | 2025-05-11 21:00
127 | Nawabganj | 132 | 138 | 2025-05-01 08:00 | 121 | 2025-05-13 12:00
128 | Netrakona | 132 | 137 | 2025-05-30 02:00 | 106 | 2025-05-25 22:00
129 | New | 132 | 141 | 2025-05-30 03:00 | 121 | 2025-05-26 11:00
130 | Niamatpur | 132 | 139 | 2025-05-17 06:00 | 125 | 2025-05-02 19:00
131 | Noapara | 132 | 140 | 2025-05-30 03:00 | 115 | 2025-05-23 23:00
132 | Pabna | 132 | 137 | 2025-05-01 04:00 | 125 | 2025-05-22 19:30
133 | Palashbari | 132 | 139 | 2025-05-30 03:00 | 117 | 2025-05-22 21:00
134 | Panchagarh | 132 | 141 | 2025-05-15 02:00 | 116 | 2025-05-02 12:00
135 | Patuakhali | 132 | 139 | 2025-05-13 23:00 | 128 | 2025-05-11 20:00
136 | Payra | 132 | 165 | 2025-05-07 08:00 | 132 | 2025-05-07 23:00
137 | PHP | 132 | 141 | 2025-05-30 04:00 | 114 | 2025-05-09 13:00
139 | Postogola | 132 | 137 | 2025-05-30 03:00 | 122 | 2025-05-11 11:00
140 | Purbachal | 132 | 140 | 2025-05-16 21:00 | 118 | 2025-05-13 12:00
141 | Purbasadipur | 132 | 136 | 2025-05-06 07:00 | 113 | 2025-05-31 14:00
142 | Rahanpur | 132 | 139 | 2025-05-17 02:00 | 126 | 2025-05-02 19:00
143 | Rahanpur-400 | 132 | 140 | 2025-05-17 02:00 | 127 | 2025-05-02 19:00
144 | Rahim | 132 | 146 | 2025-05-29 06:00 | 120 | 2025-05-13 13:00
145 | Rajbari | 132 | 140 | 2025-05-30 07:00 | 123 | 2025-05-10 19:00
146 | Rajendrapur | 132 | 139 | 2025-05-16 19:00 | 115 | 2025-05-18 15:00
147 | Rajshahi | 132 | 138 | 2025-05-15 17:00 | 126 | 2025-05-03 19:00
148 | Rajshahi-230 | 132 | 138 | 2025-05-15 17:00 | 113 | 2025-05-03 19:00
149 | Ramganj | 132 | 140 | 2025-05-30 03:00 | 108 | 2025-05-11 07:00
150 | Rampur | 132 | 143 | 2025-05-30 04:00 | 123 | 2025-05-04 12:00
151 | Rampura | 132 | 145 | 2025-05-01 08:00 | 119 | 2025-05-13 12:00
152 | Rangamati | 132 | 139 | 2025-05-30 04:00 | 123 | 2025-05-26 11:00
153 | Rangpur | 132 | 139 | 2025-05-06 08:00 | 116 | 2025-05-26 19:30
154 | Ruppur | 132 | 139 | 2025-05-01 04:00 | 129 | 2025-05-22 22:00
155 | Saidpur | 132 | 138 | 2025-05-06 07:00 | 116 | 2025-05-02 12:00
156 | Satkhira | 132 | 141 | 2025-05-30 04:00 | 110 | 2025-05-10 19:30
157 | Satmasjid | 132 | 140 | 2025-05-30 04:00 | 118 | 2025-05-13 13:00
158 | Savar | 132 | 135 | 2025-05-16 21:00 | 117 | 2025-05-13 11:00
159 | SevenRings | 132 | 142 | 2025-05-17 06:00 | 122 | 2025-05-26 11:00
160 | ShahCement | 132 | 134 | 2025-05-01 18:00 | 120 | 2025-05-13 13:00
161 | Shahjadpur | 132 | 139 | 2025-05-17 03:00 | 130 | 2025-05-11 21:00
162 | Shahjibazar | 132 | 138 | 2025-05-30 00:00 | 117 | 2025-05-26 12:00
163 | Shahmirpur | 132 | 141 | 2025-05-30 07:00 | 126 | 2025-05-04 12:00
164 | Shariatpur | 132 | 139 | 2025-05-30 04:00 | 123 | 2025-05-07 19:30
165 | Sherpur | 132 | 141 | 2025-05-12 06:00 | 116 | 2025-05-01 18:00
166 | Shikalbaha | 132 | 132 | 2025-05-30 04:00 | 115 | 2025-05-04 11:00
167 | Shikalbaha-230 | 132 | 142 | 2025-05-30 04:00 | 126 | 2025-05-04 13:00
168 | Shitalakhya | 132 | 134 | 2025-05-01 18:00 | 120 | 2025-05-13 13:00
169 | Sholosohor | 132 | 143 | 2025-05-30 04:00 | 123 | 2025-05-26 11:00
170 | Shyampur | 132 | 134 | 2025-05-01 09:00 | 120 | 2025-05-13 13:00
171 | Shyampur-230 | 132 | 135 | 2025-05-01 18:00 | 118 | 2025-05-14 11:00
172 | Siddhirganj | 132 | 134 | 2025-05-01 08:00 | 121 | 2025-05-13 12:00
173 | Sirajganj | 132 | 138 | 2025-05-17 00:00 | 121 | 2025-05-22 21:00
174 | Sonargaon | 132 | 135 | 2025-05-29 18:00 | 118 | 2025-05-19 13:00
175 | Sreemongol | 132 | 138 | 2025-05-30 07:00 | 120 | 2025-05-25 17:00
176 | Sreepur | 132 | 138 | 2025-05-29 23:00 | 122 | 2025-05-26 12:00
177 | Srinagar | 132 | 138 | 2025-05-01 08:00 | 121 | 2025-05-21 12:00
178 | SSM | 132 | 140 | 2025-05-09 08:00 | 122 | 2025-05-24 10:00
179 | Sunamganj | 132 | 136 | 2025-05-30 06:00 | 114 | 2025-05-27 11:00
180 | Sylhet | 132 | 139 | 2025-05-30 08:00 | 119 | 2025-05-27 11:00
181 | Sylhet-132 | 132 | 137 | 2025-05-30 07:00 | 120 | 2025-05-27 11:00
182 | Tangail | 132 | 135 | 2025-05-06 12:00 | 120 | 2025-05-28 19:00
183 | Thakurgaon | 132 | 143 | 2025-05-15 02:00 | 114 | 2025-05-31 14:00
184 | TK | 132 | 161 | 2025-05-09 12:00 | 120 | 2025-05-24 06:00
185 | Tongi | 132 | 140 | 2025-05-16 21:00 | 122 | 2025-05-26 10:00
186 | Ullahpara | 132 | 139 | 2025-05-17 05:00 | 123 | 2025-05-21 13:00
187 | Ullon | 132 | 140 | 2025-05-16 21:00 | 119 | 2025-05-13 12:00
188 | Uttara | 132 | 153 | 2025-05-27 15:00 | 116 | 2025-05-13 11:00
189 | UttaraNew | 132 | 135 | 2025-05-30 05:00 | 117 | 2025-05-13 11:00
190 | Zigatola | 132 | 138 | 2025-05-01 06:00 | 121 | 2025-05-13 13:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-36
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month: May 2025
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Aminbazar 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 09-05-2025 | 18:00 | 398 | 122 | 80.0536
Aminbazar 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 09-05-2025 | 18:00 | 398 | 122 | 80.0536
Aminbazar 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 520 | 09-05-2025 | 18:00 | 398 | 122 | 80.0536
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 325 | 09-05-2025 | 6:00 | 0 | 0 | 0
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 14-05-2025 | 12:00 | 210 | 102 | 44.8963
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 14-05-2025 | 12:00 | 210 | 102 | 44.8963
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | 520 | 27-05-2025 | 14:00 | 248 | 66 | 49.3523
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | 520 | 27-05-2025 | 14:00 | 239 | 78 | 48.3473
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 750 | 13-05-2025 | 19:00 | 429 | 61 | 57.7754
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 750 | 16-05-2025 | 00:00 | 736 | 66 | 98.5271
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 750 | 13-05-2025 | 19:00 | 429 | 61 | 57.7754
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | 325 | 27-05-2025 | 19:30 | 185 | 57 | 59.5637
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | 325 | 05-05-2025 | 19:30 | 185 | 51 | 59.0465
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | 325 | 27-05-2025 | 19:30 | 185 | 57 | 59.5637
Gopalganj 400/230kV Grid Sub-Station | ATR-04 | 400/230 | 750 | 17-05-2025 | 19:30 | 245 | 7 | 32.68
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 520 | 26-05-2025 | 09:00 | 332 | 181 | 72.718
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 520 | 25-05-2025 | 09:00 | 380 | 278 | 90.5449
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 325 | 26-05-2025 | 05:00 | 302 | 73 | 95.5993
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 325 | 26-05-2025 | 05:00 | 302 | 73 | 95.5993
Madunaghat 400/230kV Grid Sub-Station | ATR-1 7006T | 400/230 | 750 | 24-05-2025 | 00:00 | 441 | 152 | 62.1947
Madunaghat 400/230kV Grid Sub-Station | ATR-2 7106T | 400/230 | 750 | 24-05-2025 | 00:00 | 441 | 152 | 62.1947
Madunaghat 400/230kV Grid Sub-Station | ATR-3 7206T | 400/230 | 750 | 24-05-2025 | 00:00 | 441 | 152 | 62.1947
Meghnaghat 400/230kV Grid Sub-Station | ATR-1 | 400/230 | 750 | 10-05-2025 | 02:00 | 500 | 105 | 68.1208
Meghnaghat 400/230kV Grid Sub-Station | ATR-2 | 400/230 | 750 | 10-05-2025 | 02:00 | 499 | 104 | 67.963
Meghnaghat 400/230kV Grid Sub-Station | ATR-3 | 400/230 | 750
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | 520 | 27-05-2025 | 21:00 | 435 | 82 | 85.1272
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | 520 | 27-05-2025 | 21:00 | 431 | 82 | 84.3714
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | 325 | 17-05-2025 | 23:00 | 72 | 26 | 23.554
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | 325 | 28-05-2025 | 13:00 | 79 | 20 | 25.0746
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 520 | 10-05-2025 | 22:00 | 188 | 65 | 38.2538
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 520 | 10-05-2025 | 22:00 | 188 | 65 | 38.2538
Amtali 400/132kV Grid Sub-Station
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 300 | 13-05-2025 | 08:00 | 232 | 79 | 81.6939
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 300 | 11-05-2025 | 16:00 | 222 | 94 | 80.3603
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 225 | 14-05-2025 | 12:00 | 186 | 53 | 85.9572
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 225 | 14-05-2025 | 12:00 | 186 | 53 | 85.9572
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 225 | 06-05-2025 | 09:00 | 189 | 56 | 87.6097
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 300 | 09-05-2025 | 23:00 | 200 | 100 | 74.5356
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 300 | 23-05-2025 | 03:00 | 240 | 45 | 81.3941
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 300 | 03-05-2025 | 20:00 | 166 | 52 | 57.9847
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 225 | 27-05-2025 | 23:00 | 189 | 30 | 85.0516
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 225 | 16-05-2025 | 19:00 | 184 | 52 | 84.9808
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 225 | 27-05-2025 | 19:00 | 207 | 55 | 95.1921
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 300 | 27-05-2025 | 19:00 | 270 | 38 | 90.887
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 27-05-2025 | 22:00 | 133 | 33 | 45.6776
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 04-05-2025 | 22:00 | 188 | 18 | 62.9532
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | 225 | 14-05-2025 | 13:00 | 182 | 15 | 81.1631
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | 225 | 03-05-2025 | 19:30 | 131 | 45 | 61.5616
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 225 | 11-05-2025 | 21:00 | 178 | 60 | 83.4846
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 225 | 11-05-2025 | 21:00 | 178 | 60 | 83.4846
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 300 | 11-05-2025 | 21:00 | 239 | 84 | 84.4439
Bogura 230/132kV Grid Sub-Station | T-04 | 230/132 | 300 | 11-05-2025 | 21:00 | 239 | 84 | 84.4439
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-01 | 230/132 | 225 | 02-05-2025 | 00:00 | 180 | 70 | 85.8365
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-02 | 230/132 | 225 | 02-05-2025 | 00:00 | 179 | 68 | 85.1027
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-03 | 230/132 | 225 | 02-05-2025 | 00:00 | 191 | 68 | 90.1083
Fenchuganj 230/132/33kV Grid Sub-Station | AT-01 | 230/132 | 300 | 05-04-2025 | 21:00 | 151 | 60 | 54.1613
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 300 | 27-05-2025 | 21:00 | 211 | 76 | 74.7566
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 125 | 26-05-2025 | 14:00 | 100 | 0 | 80
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 125 | 26-05-2025 | 14:00 | 100 | 0 | 80
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 225 | 10-05-2025 | 10:00 | 106 | 76 | 57.9689
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 225 | 10-05-2025 | 10:00 | 116 | 76 | 61.6353
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 225 | 10-05-2025 | 10:00 | 110 | 80 | 60.451
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 225 | 15-05-2025 | 10:00 | 103 | 74 | 56.3674
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 225 | 15-05-2025 | 10:00 | 103 | 74 | 56.3674
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 225 | 11-05-2025 | 10:00 | 94 | 59 | 49.3253
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 150 | 17-05-2025 | 19:00 | 118 | 48 | 84.9261
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 150 | 17-05-2025 | 19:00 | 118 | 48 | 84.9261
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 150 | 11-05-2025 | 08:00 | 112 | 43 | 79.9806
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 150 | 17-05-2025 | 19:00 | 118 | 48 | 84.9261
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 225 | 27-05-2025 | 22:00 | 126 | 68 | 63.6348
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 225 | 27-05-2025 | 22:00 | 126 | 68 | 63.6348
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 225 | 27-05-2025 | 21:00 | 106 | 51 | 52.2803
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | 300 | 14-05-2025 | 19:00 | 238 | 60 | 81.8155
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | 300 | 14-05-2025 | 19:00 | 238 | 60 | 81.8155
Kaliakoir 230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 300 | 09-05-2025 | 09:00 | 210 | 90 | 76.1577
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 10-05-2025 | 19:00 | 214 | 76 | 75.6982
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 10-05-2025 | 19:00 | 214 | 76 | 75.6982
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 300 | 10-05-2025 | 00:00 | 0 | 0 | 0
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | 225 | 27-05-2025 | 12:00 | 171 | 60 | 80.5426
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | 225 | 16-05-2025 | 23:00 | -68 | -6 | 30.3396
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | 300 | 27-05-2025 | 12:00 | 223 | 72 | 78.1117
Madunaghat 230/132/33kV Grid Sub-Station | ATR-1(705T) | 230/132 | 300 | 07-05-2025 | 16:00 | 130 | 13 | 43.5495
Madunaghat 230/132/33kV Grid Sub-Station | ATR-2(715T) | 230/132 | 300 | 07-05-2025 | 19:00 | 124 | 15 | 41.6347
Madunaghat 230/132/33kV Grid Sub-Station | ATR-3(725T) | 230/132 | 300 | 07-05-2025 | 19:00 | 124 | 15 | 41.6347
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 300 | 09-05-2025 | 23:00 | 222 | 80 | 78.6582
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 300 | 16-05-2025 | 22:00 | 192 | 61 | 67.1524
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | 300 | 03-05-2025 | 22:00 | 80 | 13 | 27.0165
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | 300 | 11-05-2025 | 21:00 | 81 | 11 | 27.2478
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 300 | 01-05-2025 | 00:00 | 1 | 0 | 0.33333
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 300 | 01-05-2025 | 00:00 | 0 | 0 | 0
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 230/132 | 450 | 13-05-2025 | 16:00 | 278 | 86 | 64.6663
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 LT | 230/132 | 450 | 13-05-2025 | 16:00 | 278 | 86 | 64.6663
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 LT | 230/132 | 450 | 13-05-2025 | 16:00 | 278 | 86 | 64.6663
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 300 | 11-05-2025 | 08:00 | 223 | 108 | 82.592
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 300 | 11-05-2025 | 08:00 | 223 | 108 | 82.592
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 300 | 11-05-2025 | 10:00 | 152 | 52 | 53.5496
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 300 | 11-05-2025 | 10:00 | 152 | 52 | 53.5496
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 300 | 10-05-2025 | 18:00 | 124 | 5 | 41.3669
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 300 | 13-05-2025 | 18:30 | 197 | 41 | 67.0738
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 300 | 25-05-2025 | 12:00 | 241 | 96 | 86.4722
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 300 | 15-05-2025 | 19:00 | 241 | 71 | 83.747
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 225 | 09-05-2025 | 23:00 | 210 | 36 | 94.6948
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 225 | 05-05-2025 | 18:30 | 192 | 52 | 88.4076
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 225 | 25-05-2025 | 11:00 | 61 | 0 | 27.1111
Executive Engineer
Information Management Division
[5 empty] | LDC, Power Grid, Dhaka. |  |  |  | 270

## QF-LDC-37
|  |  |  | POWER GRID BANGLADESH PLC. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID BANGLADESH PLC. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[5 empty] | Report on load shedding | [12 empty] | Report on load shedding
Month: May 2025 |  |  |  | (For Evening Peak) | [10 empty] | Month: May 2025 |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur
2025-05-01 | 11428 | 11428 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-05-01 | 10976.06 | 10976.06 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-05-02 | 13676.86 | 13676.86 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-05-02 | 11647.93 | 11680.93 | 32 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | -
2025-05-03 | 14876 | 14886 | 10 | 20:00 Hr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | - | 2025-05-03 | 12710.03 | 12710.03 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-05-04 | 14784.67 | 14820.67 | 34 | 19:30 Hr. | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-05-04 | 13686.96 | 13686.96 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-05-05 | 15486.17 | 15551.17 | 62 | 19:30 Hr. | 37 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | - | 2025-05-05 | 13847.41 | 13894.44 | 45 | 12:00 Hr. | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-05-06 | 14692.27 | 14725.27 | 32 | 19:30 Hr. | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-05-06 | 13041.54 | 13087.54 | 44 | 12:00 Hr. | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-05-07 | 16063.78 | 16133.78 | 67 | 20:00 Hr | 18 | 0 | 10 | 25 | 0 | 0 | 0 | 0 | 14 | - | 2025-05-07 | 13962.71 | 14001.38 | 37 | 12:00 Hr. | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-05-08 | 16036.7 | 16170.7 | 128 | 21:00 Hr. | 50 | 0 | 10 | 68 | 0 | 0 | 0 | 0 | 0 | - | 2025-05-08 | 14834 | 14898.79 | 62 | 12:00 Hr. | 50 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | -
2025-05-09 | 16085.89 | 16201.89 | 111 | 21:00 Hr. | 35 | 0 | 10 | 60 | 0 | 0 | 0 | 0 | 6 | - | 2025-05-09 | 13559.95 | 13559.95 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-05-10 | 16603 | 16999.06 | 379 | 21:00 Hr. | 55 | 0 | 0 | 272 | 0 | 52 | 0 | 0 | 0 | - | 2025-05-10 | 14210 | 14466.03 | 245 | 12:00 Hr. | 160 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | - | 0
2025-05-11 | 15044.5 | 15044.5 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-05-11 | 14736.73 | 14952.73 | 207 | 12:00 Hr. | 75 | 0 | 0 | 132 | 0 | 0 | 0 | 0 | 0 | -
2025-05-12 | 15343.95 | 15343.95 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-05-12 | 12939.46 | 12967.46 | 27 | 12:00 Hr. | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-05-13 | 15936.79 | 16059.79 | 118 | 20:00 Hr | 80 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | - | 2025-05-13 | 14475.95 | 14543.95 | 65 | 12:00 Hr. | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-05-14 | 15783.03 | 15950.03 | 160 | 21:00 Hr. | 40 | 0 | 0 | 70 | 0 | 50 | 0 | 0 | 0 | - | 2025-05-14 | 13979.15 | 14293.15 | 300 | 12:00 Hr. | 198 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-05-15 | 14848.37 | 14921.37 | 70 | 21:00 Hr. | 35 | 0 | 10 | 25 | 0 | 0 | 0 | 0 | 0 | - | 2025-05-15 | 13580.81 | 13648.74 | 65 | 12:00 Hr. | 55 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
2025-05-16 | 14077.51 | 14077.51 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-05-16 | 13318.72 | 13318.72 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-05-17 | 14219.08 | 14219.08 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-05-17 | 13204.68 | 13204.68 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-05-18 | 14672 | 14750 | 75 | 19:30 Hr. | 35 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | - | 2025-05-18 | 13059.31 | 13087.53 | 27 | 12:00 Hr. | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-05-19 | 14729.75 | 14775.75 | 44 | 19:30 Hr. | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-05-19 | 13029.32 | 13123.32 | 90 | 12:00 Hr. | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-05-20 | 13365 | 13406 | 39 | 19:30 Hr. | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-05-20 | 12994.27 | 13042.27 | 46 | 12:00 Hr. | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-05-21 | 14262.08 | 14311.08 | 47 | 19:30 Hr. | 0 | 0 | 30 | 17 | 0 | 0 | 0 | 0 | 0 | - | 2025-05-21 | 13596.48 | 13648.48 | 50 | 12:00 Hr. | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-05-22 | 15215.43 | 15281.43 | 63 | 19:30 Hr. | 55 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 3 | - | 2025-05-22 | 13337.82 | 13376.82 | 37 | 12:00 Hr. | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-05-23 | 14160.5 | 14185.5 | 24 | 19:30 Hr. | 10 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | - | 2025-05-23 | 12616.14 | 12616.14 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-05-24 | 15316.2 | 15400.2 | 80 | 21:00 Hr. | 50 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-05-24 | 13321.71 | 13354.11 | 31 | 12:00 Hr. | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-05-25 | 15403.04 | 15501.04 | 94 | 19:30 Hr. | 44 | 0 | 10 | 25 | 15 | 0 | 0 | 0 | 0 | - | 2025-05-25 | 14124.65 | 14312.75 | 180 | 12:00 Hr. | 60 | 0 | 10 | 110 | 0 | 0 | 0 | 0 | 0 | -
2025-05-26 | 15016.2 | 15130.2 | 109 | 21:00 Hr. | 45 | 0 | 25 | 19 | 20 | 0 | 0 | 0 | 0 | - | 2025-05-26 | 13975.44 | 14082.44 | 102 | 12:00 Hr. | 55 | 0 | 0 | 35 | 12 | 0 | 0 | 0 | 0 | -
2025-05-27 | 16023.29 | 16420.29 | 380 | 21:00 Hr. | 140 | 0 | 15 | 45 | 15 | 0 | 0 | 0 | 165 | - | 2025-05-27 | 14147.6 | 14234.6 | 83 | 12:00 Hr. | 58 | 0 | 10 | 0 | 15 | 0 | 0 | 0 | 0 | -
2025-05-28 | 15624.72 | 15801.72 | 169 | 21:00 Hr. | 30 | 0 | 20 | 10 | 0 | 0 | 0 | 0 | 109 | - | 2025-05-28 | 14323.56 | 14503.56 | 172 | 12:00 Hr. | 32 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | -
2025-05-29 | 10776.15 | 10776.15 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2025-05-29 | 11290.51 | 11312.51 | 21 | 12:00 Hr. | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-05-30 | 13299.2 | 13299.2 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2025-05-30 | 9416.92 | 9416.92 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-05-31 | 14695.88 | 14695.88 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2025-05-31 | 13114.05 | 13114.05 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
[16 empty] | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: May 2025
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 16603 | 2025-05-10 | 21:00 Hr.
2 | Maximum Day Peak Genaration | MW | 14834 | 2025-05-08 | 12:00 Hr.
3 | Maximum Evening Peak Demand | MW | 16999.06 | 2025-05-10 | 21:00 Hr.
4 | Minimum Generation | MW | 7297.96 | 2025-05-30 | 06:00 Hr.
5 | Average of the daily evening peak Genaration | MW | 14759.5487 | - | -
6 | Average of the daily day peak Genaration | MW | 13259.9958 | - | -
7 | Maximum load shed (Evening Peak) | MW | 380 | 2025-05-27 | 21:00 Hr.
8 | Minimum load shed | MW | 0 | 2025-05-01 | 19:30 Hr.
9 | Total nos. of load shed days | Day | 24 | - | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 76.5 | - | -
11 | Total Generation | MkWh | 9898.3544 | - | -
12 | Total Generation by BPDB | MkWh | 1192.13 | % of total Gen. | 12.04%
13 | Total Generation by IPP | MkWh | 4035.8994 | '' | 40.77%
14 | A) Total Generation by Generation Companies | MkWh | 2948.2899 | '' | 29.79%
| B) Total Generation by REB | MkWh | 37.7987 | " | 0.3819%
| C) Total Generation by RENTAL | MkWh | 130.595 | " | 1.319%
| D) Total Imported from India (BIPTC) | MkWh | 669.7273 | " | 6.766%
| E) Total Imported from Tripura, India (A.C) | MkWh | 25.8422 | " | 0.2611%
| F) Total Imported from Nepal | MkWh | 0 | " | 0%
| E) Total Imported from India (Adani Power Jharkhanda Ltd) | MkWh | 858.0718 | " | 8.669%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4159.3337 | % of total Gen. | 42.02%
| B) Oil | MkWh | 1116.0373 | '' | 11.27%
| C) Hydro | MkWh | 28.7773 | '' | 0.2907%
| D) Solar | MkWh | 118.4392 | '' | 1.197%
| E) Coal | MkWh | 2912.9044 | '' | 29.43%
| F) BIPTC (Import from India) | MkWh | 669.7273 | '' | 6.766%
| G) A.C (Import from Tripura, India) | MkWh | 25.8422 | '' | 0.2611%
| H) Total Imported from Nepal | MkWh | 0 | '' | 0%
| I) Adani (Import from India) | MkWh | 858.0718 | '' | 8.669%
| J) Wind | MkWh | 9.2213 | '' | 0.09316%
16 | Maximun of the daily total Generation . | MkWh | 357.7556 | 2025-05-11
17 | Monthly Load factor | % | 80.1315 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 64935.3158 | - | -
| A) Gas | M.Taka | 14854.358 | - | -
| B) Coal | M.Taka | 19025.6595 | - | -
| C) HFO | M.Taka | 20904.2327 | - | -
| D) HSD | M.Taka | 1.6647 | - | -
| E) Hydro | M.Taka | 2.8777 | - | -
| F) Solar | M.Taka | 1924.5798 | - | -
| G) Total Import | M.Taka | 8221.9434 | - | -
| H) Wind |  | 134.9995
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 2767.7748 | 2025-05-10
| A) Gas | M.Taka | 544.9319 | 2025-05-03
| B) Coal | M.Taka | 738.2249 | 2025-05-27
| C) HFO | M.Taka | 1275.6726 | 2025-05-10
| D) HSD | M.Taka | 1.6647 | 2025-05-14 | -
| E) Hydro | M.Taka | 0.18933 | 2025-05-31 | -
| F) Solar | M.Taka | 87.6932 | 2025-05-07 | -
| G) Total Import |  | 324.2332 | 2025-05-13
| H) Wind | M.Taka | 21.1167 | 2025-05-29
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 6.5739
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 6.6794
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 76.2 | 31/05/2025 | 06:00
b) | Actual | FT (MSL) | 80.16 | 31/05/2025 | 06:00
22 | Peak Genaration of May 2024 | MW | 16067 | 2024-05-23 | 21:00
23 | Peak Demand of May 2024 | MW | 16400 | 2024-05-23 | 21:00
24 | Maximum peak Generation recorded upto 31/05/2025 | MW | 16477 | 2024-04-30 | 21:00
25 | Maximum peak Demand recorded upto 31/05/2025 | MW | 17200 | 29/04/2024 | 21:00
26 | Maximum load shed recorded upto 31/05/2025 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## FGMO Weekly
Power Grid Bangladesh PLC.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status | [13 empty] | SR at 50 Hz (MW)
SL | Plant Name | Owner | Installed capacity | Capability Status of Last Week | 29.05.2025 | 22.05.2025 | 15.05.2025 | 08.05.2025 | 01.05.2025 | 24.04.2025 | 17.04.2025 | 10.04.2025 | 03.04.2025 | 27.03.2025 | 20.03.2025 | 13.03.2025 | 06.03.2025 | 27.02.2025 | 20.02.2025 | 13.02.2025 | 06.02.2025 | 30.01.2025 | 23.01.2025 | 16.01.2025 | 09.01.2025 | 02.01.2025 | 28.11.2024 | 21.11.2024 | 14.11.2024 | 07.11.2024 | 31.10.2024 | 24.10.2024 | 17.10.2024 | 10.10.2024 | 03.10.2024 | 26.09.2024 | 19.09.2024 | 05.09.2024 | 12.09.2024 | 29.08.2024 | 22.08.2024 | 15.08.2024 | 08.08.2024 | 01.08.2024 | 25.07.2024 | 18.07.2024 | 11.07.2024 | 04.07.2024 | 27.06.2024 | 20.06.2024 | 13.06.2024 | 06.06.2024 | 30.05.2024 | 22.05.2024 | 16.05.2024 | 09.05.2024 | 02.05.2024 | 25.04.2024 | 18.04.2024 | 11.04.2024 | 04.04.2024 | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
(MW)
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | Capable | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70 | Capable
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | Capable | [7 empty] | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | Capable | [40 empty] | 20 | [7 empty] | 20 | 20 | 20 | 20
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 | Capable | [40 empty] | 20 |  | 15 | 15 |  | 15 |  |  |  | 20 | 20 | 20 | 20
6 | Meghnaghat CCPP(Summit) | IPP | 335 | Capable | 35 | 10 | 10 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 15 | 30 | [7 empty] | 35 | [6 empty] | 25 | 15 | 15 | 15 | 15 | 30 | 30 | 30 |  |  |  | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
7 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | Capable | [21 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 |  |  | 30 | 30 | 30 |  |  |  | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
8 | Ashuganj 225 MW CCPP | APSCL | 221 | Capable | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | [11 empty] | 15 | 15 | 15 | 15 | [15 empty] | 16 | 16 | 16 | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
9 | Bheramara 410 MW CCPP | NWPGCL | 410 | Capable | [38 empty] | 40 | [6 empty] | 30 |  |  |  | 30 | 30 | 30 | 30 | 30
10 | Haripur 412 MW CCPP | EGCB | 412 | Capable | 30 | 30 | 30 | 30 | 30 | 30
11 | Fenchugonj CCPP Phase-1 | BPDB | 97 | Capable | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
12 | Chandpur 150 MW CCPP | BPDB | 163 | Capable
13 | Siddhirganj 2x120 MW GTPP | EGCB | 210 | Capable
14 | Shikalbaha 225 MW CCPP | BPDB | 225 | Capable
15 | Shikalbaha Peaking GT | BPDB | 150 | Capable
16 | Shahjibazar 330 MW CCPP | BPDB | 330 | Capable
17 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | Capable | [14 empty] | 40 | [20 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 |  |  |  | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
18 | Fenchugonj CCPP Phase-2 | BPDB | 104 | Capable | [11 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
19 | Bhola 225 MW CCPP | BPDB | 194 | Capable | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
20 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365 | Capable
21 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 | Capable | [38 empty] | 20 | [6 empty] | 15 | [6 empty] | 15 | 20 | 20 | 20
22 | Siddhirganj 335 MW CCPP | EGCB | 335 | Capable but not tested recently | 30 | 30 | 30 |  | 30 | 30
23 | Bibiyana-III 400 MW CCPP | BPDB | 400 | Capable | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 |  |  |  |  | 35 | 35 | 35 | 35 | 35 | [14 empty] | 35 | 35 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
24 | Sylhet 225 MW CCPP | BPDB | 231 | Capable
25 | RPCL 210 MW CCPP | IPP | 210 | Capable but not tested recently
26 | Khulna 225 MW CCPP | NWPGCL | 230 | Capable but not tested recently
27 | a) Baghabari 71 MW GTPP | BPDB | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | 100 | Not Capable but feasible
28 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50 | Not Capable but feasible
29 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410 | Not Capable but feasible
30 | Bibiyana South 400 MW CCPP | BPDB | 383 | Capable | [19 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30
31 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274 | Not Capable but feasible
32 | Shajibazar 100 MW PP | BPDB | 100 | Not Capable but feasible
33 | Payra 1320 MW Unit-1 | BCPCL | 622 | Capable |  |  |  | 20 | 20
34 | Kushiara 163 MW CCPP (KP) | IPP | 163 | Not Capable but feasible | 16 | 16 | 16 | 10 | 10 | 10 | 10 | 10
35 | Bhola Nutan Bidyut | IPP | 220 | Capable
36 | Haripur 360MW CCPP(HPL) | IPP | 360 | Not Capable but feasible
37 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450 | Not Capable but feasible
38 | Payra 1320 MW Unit-2 | BCPCL | 622 | Capable |  |  |  | 20 | 20
Total Installed capacity |  |  |  |  | 14388 | 14388 | 14388 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity |  |  |  |  | 2325 | 2165 | 2165 | 2525 | 2855 | 2325 | 1595 | 1635 | 1072 | 1812 | 1432 | 1464 | 1064 | 592 | 1332 | 1282 | 1682 | 1302 | 1302 | 1685 | 1685 | 1315 | 1813 | 2027 | 1475 | 1475 | 1092 | 1124 | 744 | 712 | 712 | 1802 | 1492 | 1152 | 1492 | 2442 | 2442 | 2036 | 2956 | 2416 | 2476 | 1836 | 1696 | 1696 | 1876 | 3336 | 1196 | 1196 | 1796 | 3416 | 3436 | 3076 | 3038 | 2824 | 2996 | 2996 | 2024 | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve |  |  |  |  | 218 | 193 | 193 | 202 | 232 | 212 | 152 | 137 | 92 | 172 | 142 | 144 | 109 | 67 | 137 | 132 | 167 | 137 | 137 | 162 | 162 | 122 | 160 | 179 | 132 | 132 | 107 | 109 | 79 | 77 | 77 | 172 | 137 | 107 | 137 | 217 | 217 | 186 | 271 | 216 | 226 | 156 | 141 | 156 | 171 | 291 | 111 | 111 | 161 | 311 | 316 | 276 | 269 | 254 | 280 | 280 | 198 | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO |  |  |  |  | 9 | 9 | 9 | 10 | 11 | 9 | 7 | 7 | 5 | 7 | 6 | 7 | 6 | 3 | 5 | 5 | 6 | 5 | 5 | 6 | 6 | 5 | 6 | 8 | 5 | 5 | 4 | 5 | 4 | 3 | 3 | 6 | 5 | 4 | 5 | 8 | 8 | 8 | 11 | 9 | 10 | 7 | 7 | 7 | 7 | 12 | 5 | 5 | 7 | 12 | 12 | 11 | 11 | 10 | 11 | 11 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list |  |  |  |  | 64 | 64 | 64 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list |  |  |  |  | 70 | 70 | 70 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable |  |  |  |  | 58 | 58 | 58 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently |  |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible |  |  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD
New FGMO capable plants under BPSREIP:
Letter date: 09/06/2024
1. Anwara 300 MW Power Plant (United)
2.Chandpur 200 MW Power Plant (Desh energy)
3. Rupsha 105 MW Power Plant (Orion rupsha)
4. Gazipur 100 MW Power Ltd
5. United Payra Power Ltd
6.Sikalbaha 105 MW Power Plant (Baraka Sikalbaha)
7.Karnaphuli Power Ltd
8. Feni Lanka Power Ltd
9. Barisal 110 MW Power Plant (Summit)
10. Madanganj-55 MW Power Plant (Summit)
11. Madhumati 100 MW Power Plant
12. Nawabganj 55 MW Power Plant(Dhaka Southern Power)
13.Manikganj 55 MW Power plant ((Dhaka Southern Power)
14. Manikganj 162 MW Power Plant (MPGL)
15. Zodiac 54 MW Power Plant

## FGMO
Power Grid Bangladesh PLC.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month: May 2025
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Bibiyana-III 400 MW CCPP | BPDB | 400 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √
3 | Bibiyana South 400 MW | BPDB | 383
4 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
5 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
6 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
7 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 |  |  | √ | √
8 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 |  |  | √ | √
9 | Bagura 113 MW PP (Confidence)-2 | IPP | 113
10 | Energypac Power Venture Thakurgaon Ltd. | IPP | 115
11 | Meghnaghat CCPP(Summit) | IPP | 335 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
12 | Nababganj 55 MW PP (Southern power ) | IPP | 55
13 | Ashuganj 225 MW CCPP | APSCL | 221 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
14 | Ashuganj 450 MW CCPP(North) | APSCL | 361
15 | Ashuganj 450 MW CCPP(South) | APSCL | 360
16 | Ashuganj 420 MW CCPP(East) | APSCL | 400
17 | Ashuganj 55 MW PP (Precision) | QRPP | 55
18 | Bheramara 410 MW CCPP | NWPGCL | 410
19 | Haripur 412 MW CCPP | EGCB | 412 | √ | √ | √ | √ |  | √ | [8 empty] | √ | √ | √ |  |  |  | √ |  |  |  |  | √ |  | √ | √ |  | √
20 | Fenchugonj CCPP Phase-1 | BPDB | 97 |  |  |  | √ |  |  |  | √ | [14 empty] | √ |  |  |  |  | √
21 | Fenchugonj CCPP Phase-2 | BPDB | 104
22 | Siddhirganj 2x120 MW GTPP | EGCB | 210
23 | Shikalbaha 225 MW CCPP | BPDB | 225
24 | Shikalbaha Peaking GT | BPDB | 150
25 | Shahjibazar 330 MW CCPP | BPDB | 330
26 | Chandpur 150 MW CCPP | BPDB | 163
27 | Chandpur 200MW (Desh energy) | IPP | 200 | [6 empty] | √
28 | Feni Lanka Power | IPP | 114
29 | Bhola 225 MW CCPP | BPDB | 194 | [5 empty] | √ | [22 empty] | √
30 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
31 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
32 | Siddhirganj 335 MW CCPP | EGCB | 335 | √ | √ | √ | [11 empty] | √ | √ | √ |  |  |  | √ |  |  |  |  | √ |  |  | √
33 | Bibiyana-III 400 MW CCPP | BPDB | 400
34 | Sylhet 225 MW CCPP | BPDB | 231
35 | RPCL 210 MW CCPP | IPP | 210
36 | Khulna 225 MW CCPP | NWPGCL | 230
37 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
38 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
39 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
40 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
41 | Shajibazar 100 MW PP | BPDB | 100
42 | Payra 1320 MW Unit-1 | BCPCL | 622 | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
43 | Kushiara 163 MW CCPP (KP) | IPP | 163 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ |  | √ | √ | √ | √
44 | Haripur 360MW CCPP(HPL) | IPP | 360
45 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450