## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 11-07-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 10-07-2025 | during | 11-07-2025 | during | 11-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 354 | 406 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 420 | 450 | 450 | 420 | 420 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 308 | 307 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 331 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 24 | 25 | 33 | 33 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 34 | 52.19 | 52.19 | 42 | 42 | Engine Problem
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 34 | 34 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 70 | 105 | 105 | 50 | 90 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 68 | 68 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 30 | 17 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 4 | 0 | 10 | 0 | 10 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 300 | 0 | 584 | 584 | 450 | 450 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 309 | 158 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 52 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2128 | 1915 | 5104.4 | 5126.4 | 3273.58 | 3335.58
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 17 | 0 | 17 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 216 | 216 | 230 | 230 | 230 | 230 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 222 | 222 | 213 | 213 | 219 | 219 | Machine Problem
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 24 | 80 | 80 | 80 | 80 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 33 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 25 | 2 | 25 | 2 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1 | 0 | 3.81 | 0 | 3.81 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 850 | 1050 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 56 | 22 | 36 | 38 | 36 | 38 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 639 | 782 | 875 | 875 | 680 | 680 | FGMO
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 2029 | 2574 | 3974.53 | 3978.72 | 3785.53 | 3789.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 211 | 201 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 353 | 320 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 340 | 340 | 340 | 340 | 340 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 20 | 20 | 46.7 | 46.7 | 10 | 10 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 48 | 52 | 55 | 55 | 52 | 52 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 33 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 38 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 64 | 180 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 32 | 34 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 16 | 16 | 24.5 | 24.5 | 15 | 15 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 16 | 50 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 39 | 113 | 113 | 9 | 28 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 17 | 17 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 6 | 0 | 20 | 0 | 20 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1191 | 1399 | 2420.75 | 2400.75 | 2088.55 | 2087.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 10-07-2025 | during | 11-07-2025 | during | 11-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 32 | 33 | 157.5 | 157.5 | 30 | 30 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.4 | 0 | 1.4 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 75 | 183 | 200 | 200 | 185 | 185 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 75 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 21.4 | 0 | 39 | 0 | 39 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 35 | 35 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 203.4 | 320 | 589.4 | 549 | 417.4 | 377
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage instructed by DS(Gen)
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 160 | 147 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 20 | 20 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 79 | 83 | 83 | 81 | 81 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 172 | 172 | 172 | 172 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 6 | 8 | 25 | 25 | 6 | 6 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 337 | 385 | 380 | 380 | 332 | 332 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | Machine Problem
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1429 | 1464 | 1532 | 1532 | 1391 | 1391
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 902 | 902 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 220 | 191 | 410 | 410 | 190 | 190 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 70 | 70 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 4 | 0 | 40 | 0 | 40 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 819 | 971 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1945 | 2064 | 3258.2 | 3218.2 | 2773.2 | 2733.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 77 | 304 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 6 | 11 | 10 | 10 | 2 | 2 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 711 | 1110 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 173 | 200 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.47 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1307.47 | 1965 | 2172 | 2171 | 2102 | 2101
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 140 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 140 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 382 | 405 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0.61 | 0 | 3.6 | 0 | 3.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 901.15 | 1034 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 7.91 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 23 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 1594.67 | 1719 | 2968.47 | 2814.87 | 2920.09 | 2766.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 51 | 48 | 50 | 50 | 50 | 50 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 143 | 162 | 200 | 200 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 98 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.7 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 17 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 175 | 0 | 171.07 | 0 | 171.07 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 393.7 | 423 | 719.67 | 512 | 685.67 | 478
System Total |  |  |  |  | 28565.2 | 27084.055 | 12221.24 | 13843 | 22739.42 | 22302.94 | 19437.02 | 19059.54
Forecast Scenario (11-07-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13571 |  | 0 |  | 13571
|  |  |  | 1:00 | 13150 |  | 0 |  | 13150
|  |  |  | 2:00 | 12691 |  | 0 |  | 12691
|  |  |  | 3:00 | 12216 |  | 0 |  | 12216
|  |  |  | 4:00 | 11866 |  | 0 |  | 11866
|  |  |  | 5:00 | 11484 |  | 0 |  | 11484
|  |  |  | 6:00 | 10740 |  | 0 |  | 10740
|  |  |  | 7:00 | 10364 |  | 0 |  | 10364
|  |  |  | 8:00 | 9942 |  | 0 |  | 9942
|  |  |  | 9:00 | 9716 |  | 0 |  | 9716
|  |  |  | 10:00 | 9455 |  | 0 |  | 9455
|  |  |  | 11:00 | 9672 |  | 0 |  | 9672
|  |  |  | 12:00 | 10371 |  | 0 |  | 10371
|  |  |  | 13:00 | 10930 |  | 0 |  | 10930
|  |  |  | 14:00 | 10673 |  | 0 |  | 10673
|  |  |  | 15:00 | 10491 |  | 0 |  | 10491
|  |  |  | 16:00 | 9985 |  | 0 |  | 9985
|  |  |  | 17:00 | 9708 |  | 0 |  | 9708
|  |  |  | 18:00 | 9392 |  | 0 |  | 9392
|  |  |  | 18:30 | 10300 |  | 0 |  | 10300
|  |  |  | 19:00 | 10692 |  | 0 |  | 10692
|  |  |  | 19:30 | 11834 |  | 0 |  | 11834
|  |  |  | 20:00 | 12078 |  | 0 |  | 12078
|  |  |  | 21:00 | 12229 |  | 0 |  | 12229
|  |  |  | 22:00 | 12415 |  | 0 |  | 12415
|  |  |  | 23:00 | 12470 |  | 0 |  | 12470
Probable Maximum Temperature: |  |  | 32.00°C
Probable Maximum Demand at Day Peak: |  |  | 10371.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12229.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12229.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 266.301 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 07:53 hrs on 11-07-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 10-07-2025 | [28 empty] | Date: | 10-07-2025 | [28 empty] | Date: | 10-07-2025 | [28 empty] | Date: | 10-07-2025 | [28 empty] | Date: | 10-07-2025 | [12 empty] | Date: | 10-07-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [12 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 310 | 0 | 35 | 33 | 32 | 0 | 0 | 0 | 0 | 0 | 300 | 296 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 17 | 14 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 24 | 17 | 0 | 0 | 12 | 12 | 0 | 214 | 0 | 32 | 682 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 840 | 0 | 51 | 0 | 63 | 0 | 357 | 340 | 52 | 194 | 20 | 16 | 0 | 136 | 13 | 19 | 44 | 32 | 16 | 0 | 23 | 305 | 320 | 359 | 0 | 0 | 134 | 6 | 0 | 81 | 30 | 0 | 18 | 172 | 11 | 65 | 95 | 33 | 0 | 0 | 12 | 7171 | 901 | 205 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 830 | 0 | 962.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 130 | 0 | 336 | 0 | 0 | 200 | 51 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 9 | 120 | 220 | 0 | 0 | 900 | 0 | 5450.86 | 12621.86 | 96.57
01:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 307 | 0 | 35 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 300 | 294 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 17 | 21.2 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 12 | 12 | 0 | 214 | 0 | 32 | 686 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 827 | 0 | 51 | 0 | 63 | 0 | 356 | 300 | 52 | 189 | 20 | 17 | 0 | 136 | 0 | 19 | 57 | 30 | 16 | 0 | 23 | 300 | 320 | 349 | 0 | 0 | 131 | 6 | 0 | 81 | 30 | 0 | 18 | 172 | 17 | 65 | 95 | 50 | 0 | 0 | 12 | 7081.2 | 902 | 203 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 762 | 0 | 858.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 130 | 0 | 336 | 0 | 0 | 201 | 52 | 72 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 9 | 120 | 220 | 0 | 0 | 800 | 0 | 5108.33 | 12189.53 | 96.61
02:00 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 310 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 299 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 21.2 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 12 | 12 | 0 | 213 | 0 | 32 | 680 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 836 | 0 | 51 | 0 | 26 | 0 | 290 | 280 | 52 | 193 | 20 | 17 | 0 | 136 | 0 | 18 | 63 | 30 | 8 | 0 | 0 | 300 | 320 | 300 | 0 | 0 | 132 | 6 | 0 | 81 | 30 | 0 | 18 | 172 | 17 | 45 | 95 | 50 | 0 | 0 | 12 | 6776.2 | 902 | 204 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 741 | 0 | 822.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 130 | 0 | 343 | 0 | 0 | 201 | 52 | 35 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 8 | 120 | 220 | 0 | 0 | 375 | 0 | 4594.74 | 11370.94 | 96.65
03:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 308 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 296 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 21.2 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 12 | 0 | 212 | 0 | 32 | 680 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 845 | 0 | 51 | 0 | 26 | 0 | 290 | 280 | 52 | 190 | 20 | 17 | 0 | 120 | 0 | 19 | 54 | 30 | 0 | 0 | 0 | 300 | 320 | 296 | 0 | 0 | 130 | 6 | 0 | 81 | 30 | 0 | 18 | 173 | 17 | 45 | 95 | 50 | 0 | 0 | 12 | 6657.2 | 902 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 734 | 0 | 825.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 130 | 0 | 339 | 0 | 0 | 200 | 52 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 6 | 120 | 220 | 0 | 0 | 600 | 0 | 4737.2 | 11394.4 | 96.69
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 279 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 20.2 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 33 | 684 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 665 | 0 | 51 | 0 | 26 | 0 | 290 | 280 | 52 | 183 | 20 | 17 | 0 | 100 | 0 | 19 | 30 | 30 | 0 | 0 | 0 | 290 | 320 | 288 | 0 | 0 | 130 | 6 | 0 | 81 | 30 | 0 | 18 | 173 | 17 | 25 | 65 | 50 | 0 | 0 | 12 | 6310.2 | 897 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 736 | 0 | 822.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 130 | 0 | 330 | 0 | 0 | 200 | 52 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 8 | 120 | 180 | 0 | 0 | 580 | 0 | 4658.48 | 10968.68 | 96.73
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 291 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 20.2 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 34 | 612 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 615 | 0 | 10 | 0 | 26 | 0 | 290 | 280 | 46 | 196 | 20 | 16 | 0 | 84 | 0 | 19 | 14 | 26 | 0 | 0 | 0 | 300 | 320 | 290 | 0 | 0 | 131 | 6 | 0 | 42 | 30 | 0 | 18 | 173 | 17 | 25 | 65 | 50 | 0 | 0 | 12 | 6061.2 | 898 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 740 | 0 | 823.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 130 | 0 | 346 | 0 | 0 | 197 | 52 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 8 | 120 | 180 | 0 | 0 | 590 | 0 | 4640.77 | 10701.97 | 96.77
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 287 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 20.2 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 34 | 586 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 615 | 0 | 10 | 0 | 8 | 0 | 290 | 280 | 12 | 193 | 20 | 17 | 0 | 68 | 0 | 19 | 14 | 28 | 0 | 6 | 0 | 305 | 290 | 298 | 0 | 0 | 132 | 6 | 0 | 11 | 20 | 0 | 18 | 171 | 17 | 25 | 55 | 50 | 0 | 0.33 | 12 | 5875.53 | 897 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 742 | 0 | 827.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 130 | 0 | 300 | 0 | 0.07 | 200 | 50 | 0 | 1 | 34 | 0 | 0 | 0.3 | 6 | 0.01 | 0 | 140 | 7 | 120 | 180 | 0 | 0 | 560 | 0 | 4558.04 | 10433.57 | 96.81
07:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 308 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 297 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 20.2 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 30 | 622 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 615 | 3 | 10 | 0 | 8 | 0 | 290 | 280 | 10 | 204 | 20 | 17 | 0 | 60 | 0 | 19 | 14 | 24 | 0 | 2 | 0 | 315 | 290 | 323 | 0 | 0 | 137 | 6 | 0 | 11 | 20 | 0 | 18 | 172 | 17 | 45 | 55 | 50 | 0 | 4.52 | 12 | 5965.72 | 897 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 756 | 0 | 821.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0.58 | 0 | 0 | 140 | 0 | 130 | 0 | 300 | 0 | 0.07 | 207 | 51 | 0 | 4 | 34 | 0 | 0 | 1.9 | 30 | 0 | 0 | 140 | 6 | 120 | 180 | 0 | 0 | 560 | 0 | 4609.39 | 10575.11 | 96.85
08:00 | 0 | 5 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 310 | 0 | 6 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 304 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 20.2 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 1 | 214 | 0 | 5 | 635 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 617 | 6 | 10 | 0 | 8 | 0 | 290 | 280 | 10 | 206 | 20 | 17 | 0 | 62 | 0 | 19 | 17 | 18 | 0 | 1 | 0 | 305 | 290 | 345 | 0 | 0 | 140 | 6 | 0 | 11 | 20 | 0 | 18 | 172 | 17 | 45 | 75 | 50 | 1 | 2.49 | 12 | 6048.69 | 902 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 760 | 0 | 827.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 1.91 | 0 | 0 | 140 | 0 | 130 | 0 | 376 | 0 | 0.16 | 203 | 51 | 35 | 2 | 34 | 0 | 0 | 2.1 | 20 | 0.23 | 0 | 173 | 0 | 120 | 180 | 0 | 0 | 561 | 0 | 4757.12 | 10805.81 | 96.89
09:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 308 | 0 | 17 | 15 | 0 | 0 | 0 | 1 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 250 | 0 | 0 | 1 | 17 | 26.2 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 2 | 214 | 0 | 2 | 639 | 0 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 620 | 7 | 10 | 0 | 8 | 0 | 355 | 335 | 10 | 221 | 20 | 17 | 0 | 66 | 0 | 19 | 17 | 28 | 0 | 2 | 0 | 310 | 295 | 324 | 0 | 0 | 152 | 6 | 0 | 11 | 30 | 0 | 18 | 172 | 17 | 45 | 75 | 51 | 1 | 19.35 | 12 | 6311.55 | 902 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 797 | 0 | 827.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 6.49 | 0 | 0 | 140 | 0 | 140 | 0 | 370 | 0 | 0.62 | 180 | 51 | 35 | 5 | 34 | 0 | 0 | 6.8 | 41 | 0.13 | 0 | 173 | 4 | 120 | 220 | 0 | 0 | 555 | 0 | 4856.28 | 11167.83 | 96.91
10:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 311 | 0 | 19 | 28 | 0 | 0 | 0 | 35 | 0 | 0 | 300 | 305 | 0 | 0 | 0 | 280 | 0 | 0 | 3 | 17 | 25 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 2 | 214 | 0 | 2 | 640 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 705 | 6 | 10 | 0 | 8 | 0 | 349 | 340 | 10 | 214 | 20 | 17 | 0 | 66 | 0 | 19 | 17 | 28 | 0 | 20 | 0 | 305 | 320 | 340 | 0 | 0 | 161 | 6 | 0 | 50 | 30 | 0 | 18 | 172 | 17 | 45 | 75 | 47 | 1 | 18.12 | 12 | 6609.12 | 902 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 787 | 0 | 855.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 7.38 | 0 | 0 | 140 | 0 | 140 | 0 | 394 | 0 | 0.67 | 143 | 51 | 0 | 12 | 34 | 0 | 0 | 3.3 | 64 | 0.77 | 0 | 177 | 6 | 120 | 220 | 0 | 0 | 600 | 0 | 4902.45 | 11511.57 | 96.93
11:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 349 | 0 | 35 | 34 | 0 | 0 | 0 | 35 | 0 | 0 | 300 | 294 | 0 | 0 | 0 | 335 | 0 | 0 | 9 | 0 | 25 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 12 | 12 | 1 | 214 | 0 | 2 | 644 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 850 | 8 | 25 | 0 | 8 | 0 | 357 | 335 | 17 | 200 | 20 | 17 | 0 | 65 | 0 | 19 | 16 | 28 | 0 | 16 | 0 | 305 | 320 | 320 | 0 | 0 | 162 | 6 | 0 | 78 | 30 | 0 | 18 | 172 | 17 | 45 | 75 | 44 | 1 | 10.74 | 12 | 6864.74 | 902 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 802 | 0 | 815.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 6.3 | 0 | 0 | 140 | 0 | 140 | 0 | 355 | 0 | 0.56 | 142 | 51 | 0 | 9 | 0 | 0 | 0 | 7 | 94 | 0.27 | 0 | 172 | 5 | 120 | 220 | 0 | 66 | 671 | 0 | 4962.37 | 11827.11 | 96.95
12:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 309 | 0 | 35 | 34 | 0 | 0 | 0 | 35 | 30 | 0 | 300 | 308 | 0 | 0 | 0 | 331 | 0 | 0 | 4 | 0 | 24 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 12 | 12 | 1 | 216 | 0 | 2 | 639 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 850 | 19 | 51 | 0 | 8 | 0 | 353 | 340 | 48 | 211 | 20 | 17 | 0 | 64 | 9 | 16 | 16 | 32 | 0 | 6 | 0 | 310 | 320 | 337 | 0 | 0 | 160 | 6 | 0 | 76 | 30 | 0 | 18 | 172 | 17 | 45 | 75 | 32 | 1 | 21.4 | 12 | 6980.4 | 902 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 819 | 0 | 901.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 7.91 | 0 | 0 | 140 | 0 | 140 | 0 | 382 | 0 | 0.61 | 143 | 51 | 0 | 17 | 0 | 0 | 0 | 7.7 | 175 | 0.47 | 0 | 173 | 6 | 120 | 220 | 0 | 77 | 711 | 0 | 5240.84 | 12221.24 | 96.97
13:00 | 0 | 22 | 25 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 309 | 0 | 35 | 33 | 0 | 0 | 0 | 35 | 32 | 0 | 300 | 296 | 0 | 0 | 0 | 332 | 0 | 0 | 4 | 0 | 24 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 12 | 0 | 216 | 0 | 8 | 600 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 905 | 14 | 43 | 0 | 8 | 0 | 351 | 335 | 52 | 203 | 20 | 17 | 0 | 66 | 9 | 16 | 16 | 32 | 0 | 22 | 0 | 310 | 320 | 388 | 0 | 0 | 160 | 6 | 0 | 76 | 30 | 0 | 18 | 172 | 17 | 45 | 86 | 32 | 1 | 16.39 | 12 | 7084.39 | 901 | 213 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12 | 828 | 0 | 1014.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 13.01 | 0 | 0 | 140 | 0 | 140 | 0 | 414 | 0 | 1.62 | 138 | 51 | 0 | 15 | 0 | 0 | 0 | 6 | 126 | 0.46 | 0 | 172 | 4 | 100 | 220 | 0 | 96 | 827 | 0 | 5488.79 | 12573.18 | 96.99
14:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 308 | 0 | 35 | 34 | 0 | 0 | 0 | 35 | 31 | 0 | 300 | 296 | 0 | 0 | 0 | 330 | 0 | 0 | 3 | 0 | 24 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 12 | 12 | 1 | 216 | 0 | 4 | 605 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 863 | 18 | 43 | 0 | 8 | 0 | 350 | 340 | 50 | 203 | 20 | 17 | 0 | 88 | 23 | 16 | 15 | 32 | 0 | 16 | 0 | 310 | 320 | 346 | 0 | 0 | 138 | 6 | 0 | 76 | 30 | 0 | 18 | 172 | 17 | 45 | 95 | 33 | 1 | 6.81 | 12 | 7032.81 | 902 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 783 | 0 | 1020.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 24.5 | 0 | 0 | 140 | 0 | 140 | 0 | 363 | 0 | 2.01 | 137 | 50 | 0 | 31 | 0 | 0 | 0 | 3.5 | 81 | 0.18 | 0 | 172 | 7 | 100 | 220 | 0 | 144 | 800 | 0 | 5387.46 | 12420.27 | 97.01
15:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 308 | 0 | 35 | 34 | 0 | 0 | 0 | 35 | 35 | 0 | 350 | 306 | 0 | 0 | 0 | 331 | 0 | 0 | 3 | 0 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 12 | 12 | 0.73 | 216 | 0 | 2 | 640 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 855 | 11 | 43 | 0 | 8 | 0 | 346 | 335 | 50 | 211 | 18 | 17 | 0 | 96 | 28 | 16 | 16 | 26 | 0 | 11 | 0 | 310 | 320 | 385 | 0 | 0 | 144 | 6 | 0 | 76 | 30 | 0 | 18 | 170 | 17 | 45 | 95 | 33 | 1 | 30.96 | 12 | 6881.69 | 902 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 766 | 0 | 1036.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 7.47 | 0 | 0 | 140 | 0 | 140 | 0 | 385 | 0 | 0.39 | 144 | 50 | 0 | 21 | 0 | 0 | 0 | 1.2 | 111 | 0.59 | 0 | 176 | 6 | 120 | 220 | 0 | 215 | 802 | 0 | 5486.38 | 12368.07 | 97.03
16:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 326 | 0 | 35 | 34 | 0 | 0 | 0 | 35 | 35 | 0 | 350 | 302 | 0 | 0 | 0 | 333 | 0 | 0 | 4 | 0 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 12 | 12 | 1 | 216 | 0 | 3 | 633 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 850 | 9 | 43 | 0 | 8 | 0 | 348 | 340 | 50 | 205 | 20 | 17 | 0 | 98 | 29 | 19 | 16 | 24 | 0 | 5 | 0 | 315 | 320 | 388 | 0 | 0 | 143 | 6 | 0 | 78 | 30 | 0 | 18 | 169 | 17 | 45 | 95 | 33 | 1 | 13.47 | 12 | 6859.47 | 902 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 764 | 0 | 960.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 7.65 | 0 | 0 | 140 | 0 | 140 | 0 | 365 | 0 | 0.59 | 200 | 50 | 0 | 10 | 0 | 0 | 0 | 0.8 | 68 | 0.57 | 0 | 173 | 3 | 120 | 220 | 0 | 217 | 798 | 0 | 5365.05 | 12224.52 | 97.05
17:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 371 | 0 | 35 | 34 | 0 | 0 | 0 | 35 | 34 | 0 | 350 | 290 | 0 | 0 | 0 | 335 | 0 | 0 | 3 | 0 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 12 | 12 | 0.45 | 216 | 0 | 9 | 607 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 820 | 3 | 51 | 0 | 8 | 0 | 354 | 340 | 50 | 197 | 17 | 17 | 0 | 100 | 33 | 16 | 16 | 30 | 0 | 3 | 0 | 310 | 320 | 361 | 0 | 0 | 141 | 6 | 0 | 76 | 30 | 0 | 18 | 170 | 17 | 45 | 95 | 33 | 0 | 10.58 | 12 | 6802.03 | 902 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 756 | 0 | 825.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 3.69 | 0 | 0 | 140 | 0 | 140 | 0 | 341 | 0 | 0.45 | 203 | 48 | 0 | 9 | 0 | 0 | 0 | 1 | 42 | 0.01 | 0 | 169 | 5 | 120 | 220 | 0 | 216 | 797 | 0 | 5177.86 | 11979.89 | 97.07
18:00 | 0 | 35 | 43 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 484 | 0 | 35 | 34 | 0 | 0 | 0 | 35 | 32 | 0 | 350 | 295 | 0 | 0 | 0 | 280 | 0 | 0 | 2 | 0 | 23.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 12 | 12 | 0.08 | 172 | 0 | 2 | 625 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 863 | 1 | 51 | 0 | 8 | 0 | 320 | 340 | 50 | 204 | 20 | 18 | 0 | 96 | 38 | 16 | 16 | 30 | 0 | 3 | 0 | 315 | 320 | 374 | 0 | 0 | 136 | 6 | 0 | 78 | 30 | 0 | 18 | 172 | 17 | 45 | 99 | 33 | 0 | 3.15 | 12 | 6867.73 | 902 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 743 | 0 | 831.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3.58 | 0 | 0 | 140 | 0 | 140 | 0 | 364 | 0 | 0.32 | 165 | 48 | 0 | 2 | 10 | 0 | 0 | 1.6 | 14 | 0 | 0 | 173 | 4 | 120 | 220 | 0 | 222 | 700 | 0 | 5018.06 | 11885.79 | 97.09
19:00 | 8 | 70 | 43 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 17 | 41 | 42 | 32 | 0 | 0 | 35 | 96 | 8 | 320 | 310 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 70 | 24 | 22 | 0 | 0 | 0 | 15 | 0 | 0 | 19 | 33 | 14 | 0 | 62 | 88 | 0 | 216 | 0 | 11 | 760 | 0 | 0 | 3 | 0 | 0 | 221 | 0 | 0 | 0 | 1070 | 0 | 51 | 23 | 8 | 0 | 320 | 300 | 51 | 211 | 20 | 17 | 0 | 110 | 38 | 16 | 44 | 36 | 0 | 0 | 4 | 310 | 320 | 393 | 0 | 0 | 143 | 6 | 0 | 78 | 30 | 0 | 18 | 172 | 17 | 65 | 172 | 33 | 0 | 0 | 12 | 7406 | 902 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 836 | 6 | 831.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 383 | 0 | 0 | 164 | 49 | 70 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 226 | 11 | 120 | 220 | 0 | 222 | 777 | 0 | 5382.34 | 12788.34 | 97.11
19:30 | 8 | 70 | 43 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 17 | 54 | 50 | 32 | 0 | 0 | 35 | 97 | 16 | 420 | 299 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 25 | 22 | 0 | 0 | 0 | 15 | 0 | 0 | 24 | 33 | 19 | 0 | 100 | 88 | 0 | 216 | 0 | 17 | 774 | 0 | 0 | 18 | 0 | 0 | 220 | 0 | 0 | 0 | 1085 | 0 | 51 | 50 | 8 | 0 | 355 | 340 | 50 | 195 | 20 | 17 | 0 | 170 | 39 | 16 | 44 | 28 | 8 | 0 | 38 | 310 | 320 | 355 | 0 | 0 | 146 | 8 | 0 | 78 | 30 | 0 | 18 | 172 | 17 | 75 | 182 | 33 | 0 | 0 | 12 | 7793 | 902 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 988 | 17 | 963.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 395 | 0 | 0 | 168 | 49 | 110 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 10 | 120 | 220 | 0 | 242 | 920 | 0 | 5955.23 | 13748.23
20:00 | 8 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 68 | 0 | 35 | 51 | 16 | 0 | 0 | 26 | 72 | 16 | 420 | 290 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 70 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 33 | 24 | 0 | 100 | 100 | 0 | 216 | 0 | 22 | 792 | 0 | 0 | 18 | 0 | 0 | 221 | 0 | 0 | 0 | 1082 | 0 | 51 | 0 | 8 | 0 | 356 | 340 | 50 | 184 | 20 | 17 | 0 | 157 | 38 | 16 | 43 | 34 | 8 | 0 | 38 | 315 | 320 | 350 | 0 | 0 | 153 | 8 | 0 | 78 | 30 | 0 | 18 | 172 | 17 | 75 | 182 | 33 | 0 | 0 | 12 | 7720 | 902 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 17 | 1008.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 377 | 0 | 0 | 166 | 49 | 115 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 11 | 120 | 220 | 0 | 271 | 972 | 0 | 6053.46 | 13773.46 | 97.13
21:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 158 | 0 | 35 | 34 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 307 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 33 | 24 | 0 | 100 | 100 | 0 | 216 | 0 | 25 | 782 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1050 | 0 | 51 | 0 | 33 | 0 | 320 | 340 | 52 | 201 | 20 | 17 | 0 | 180 | 39 | 16 | 50 | 34 | 8 | 0 | 38 | 305 | 320 | 385 | 0 | 0 | 147 | 8 | 0 | 79 | 30 | 0 | 18 | 172 | 17 | 75 | 183 | 33 | 0 | 0 | 12 | 7672 | 902 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 971 | 0 | 1034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 405 | 0 | 0 | 162 | 48 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 11 | 120 | 220 | 0 | 304 | 1110 | 0 | 6171 | 13843 | 97.15
22:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 373 | 0 | 35 | 34 | 0 | 0 | 0 | 0 | 14 | 0 | 350 | 288 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 52 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 33 | 24 | 0 | 100 | 100 | 0 | 216 | 0 | 28 | 752 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 990 | 0 | 51 | 0 | 35 | 0 | 356 | 340 | 51 | 192 | 20 | 17 | 50 | 177 | 38 | 16 | 43 | 36 | 8 | 0 | 37 | 310 | 320 | 346 | 0 | 0 | 141 | 8 | 0 | 79 | 30 | 0 | 18 | 172 | 17 | 75 | 183 | 33 | 0 | 0 | 12 | 7659 | 902 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 983 | 0 | 1011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 337 | 0 | 0 | 162 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 9 | 120 | 220 | 0 | 304 | 1050 | 0 | 5996 | 13655 | 97.17
23:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 407 | 0 | 35 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 296 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 52 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 33 | 2 | 0 | 36 | 60 | 0 | 216 | 0 | 30 | 779 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 950 | 0 | 51 | 0 | 35 | 0 | 356 | 340 | 51 | 202 | 20 | 44 | 50 | 173 | 39 | 19 | 47 | 34 | 8 | 0 | 32 | 315 | 320 | 386 | 0 | 0 | 142 | 8 | 0 | 79 | 30 | 0 | 18 | 172 | 17 | 75 | 184 | 33 | 0 | 0 | 8 | 7611 | 902 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 936 | 0 | 1031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 363 | 0 | 0 | 166 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 11 | 120 | 220 | 0 | 304 | 1000 | 0 | 5951 | 13562 | 97.19
Total KWH | 20304 | 684480 | 611040 | 0 | 0 | 0 | 0 | 0 | 9432000 | 0 | 6899640 | 25200 | 674640 | 601056 | 80160 | 0 | 0 | 387407 | 446400 | 20160 | 8001500 | 7199418 | 0 | 0 | 0 | 7134185 | 0 | 0 | 33594 | 391200 | 544200 | 521280 | 0 | 4700909.09 | 0 | 22582 | 0 | 0 | 734400 | 198931 | 88896 | 0 | 552960 | 606720 | 10059 | 5150707 | 0 | 433920 | 16160000 | 0 | 0 | 26880 | 0 | 0 | 5108592 | 0 | 0 | 0 | 19816361 | 109080 | 962804 | 80290 | 434909 | 0 | 8251000 | 7744000 | 982080 | 4897000 | 479952 | 536640 | 128680 | 2564160 | 384720 | 405150 | 687420 | 699840 | 73373 | 103082 | 212704 | 7450000 | 7554600 | 8572000 | 0 | 0 | 3449372.72 | 159264 | 0 | 1568640 | 685536 | 0 | 439000 | 4542830 | 428760 | 1220400 | 2536800 | 919680 | 6150 | 161000 | 294960 | 167045657.81 | 21758545 | 5011488 | 0 | 0 | 0 | 152000 | 0 | 0 | 0 | 0 | 0 | 96480 | 19483633 | 24480 | 21741818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211257 | 0 | 96752 | 0 | 0 | 3643664 | 0 | 3577364 | 0 | 8719927 | 0 | 8700 | 4260000 | 1174254 | 840957 | 138715 | 1217222 | 0 | 0 | 37676.4 | 810000 | 2005.5 | 0 | 4276000 | 171141 | 2834000 | 5345190 | 0 | 2807272 | 18881454.55 | 0 | 127321995.45 | 294367653.26

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 10-07-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12221.24 | MW | 12:00 Hr. | Energy Generated |  |  | 294.3677 |  | MKWHr.
| Day Peak Demand |  |  | 12221.24 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.086 |  | MKWHr.
| Evening Peak Generation |  |  | 13843 | MW | 21:00 Hr. | Energy Demand |  |  | 294.4537 |  | MKWHr.
| Evening Peak Demand |  |  | 13875.4 | MW | 21:00 Hr. | Maximum Temperature |  |  | 29.8 |  | °C
| Minimum Generation of the Day |  |  | 10433.57 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 962.59 |  | MMCFD
| Maximum Generation of the Day |  |  | 13843 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 5.4237 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 44.4331 | 0 | 3.942 | 0 | 0 | 0.033594 | 0 | 0 | 48.4088 | Gas | 138.9049 | Gas | 468484873.5605
| Chattogram Zone |  |  | 5.5425 | 35.9764 | 1.497 | 0 | 5.1507 | 0.11914 | 0 | 0.7344 | 49.0201 | Coal | 86.859 | Coal | 569075206.0125
| Cumilla Zone |  |  | 24.2856 | 0 | 4.5393 | 0 | 0 | 0.10308 | 0.69984 | 0 | 29.6278 | HFO | 16.5419 | HFO | 309472689.19
| Mymensingh Zone |  |  | 0.91968 | 0 | 4.4809 | 0 | 0 | 0.16715 | 0 | 0 | 5.5678 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 34.4212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.4212 | Hydro | 5.1507 | Hydro | 515070.7
| Khulna Zone |  |  | 5.0115 | 19.4836 | 0.02448 | 0 | 0 | 0.09648 | 21.9105 | 0 | 46.5266 | Solar | 1.8246 | Solar | 31353268.249
| Barishal Zone |  |  | 8.3503 | 25.9647 | 0 | 0 | 0 | 0.0020055 | 0 | 0 | 34.3171 | Import | 44.3522 | Import | 206919280.83
| Rajshahi Zone |  |  | 15.941 | 0 | 0 | 0 | 0 | 0.31671 | 21.7418 | 0 | 37.9995 | Wind | 0.7344 | Wind | 10751616
| Rangpur Zone |  |  | 0 | 5.4343 | 2.0582 | 0 | 0 | 0.98639 | 0 | 0 | 8.4788
| Total |  |  | 138.9049 | 86.859 | 16.5419 | 0 | 5.1507 | 1.8246 | 44.3522 | 0.7344 | 294.3677
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 468484873.5605 |  | Hydro | 515070.7
|  |  |  | Coal | 569075206.0125 |  | Solar | 31353268.249
|  |  |  | HFO | 309472689.19 |  | Import | 206919280.83
|  |  |  | HSD | 0 |  | Wind | 10751616
[5 empty] | Total: | 159,65,72,004 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.7585 | Peak Hr Flow | 902.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 33327554.25 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 21.7418 | Peak Hr Flow | 1034.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 494 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.69984 | Peak Hr Flow | 34.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 796 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 44.2002 | Peak Hr Flow | 1970.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4755
|  |  |  | Chattogram |  | 0 |  | 1353
|  |  |  | Cumilla |  | 0 |  | 1242
|  |  |  | Mymensingh |  | 0 |  | 1095
|  |  |  | Sylhet |  | 0 |  | 587
|  |  |  | Khulna |  | 0 |  | 1545
|  |  |  | Barishal |  | 0 |  | 395
|  |  |  | Rajshahi |  | 0 |  | 1351
|  |  |  | Rangpur |  | 31 |  | 1001
|  |  |  | Total |  | 31 |  | 13324
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[5 empty] | Total | 300 |  |  |  | Total | 476
|  |  |  | Total Unavailable Capacity |  |  |  | 776
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:35 | Chuadanga 132/33kV S/S 132kV Tr. T3 HT is restored.
|  | 08:36 | Chuadanga 132/33kV S/S 132kV Tr. T3 LT is restored.
| 09:28 | 11:08 | BIPTC S/S 10CF23 Forced S/D
| 11:18 |  | Tongi 230/132kV S/S Mid bay of 230kV Dia-1 was shutdown due to trip circuit
troubleshooting work by SPMD.
| 11:47 | 12:07 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Tripped showing General trip, Phase (R Y | [7 empty] | 46.0MW load
|  |  | B) LV-OC trip relays Due to Due to B.Ban 33 KV feeder . | [7 empty] | interrup.
| 12:00 |  | Day peak generation 12218 MW
| 13:09 | 15:33 | Barapukuria-Bogura 230 kV Ckt-1 Project Work S/D from Barapukuria 230/132/33kV end. and
from Bogura 400/230kV end Due to Maintenance work at Barapukuria 230kV Substation.
| 14:44 |  | Unique Meghnaghat Power Limited (UMPL) Shutdown with remarks:- ST
| 14:46 |  | Unique Meghnaghat Power Limited (UMPL) GT Shutdown with remarks:- CCPP is in shutdown
condition as per NLDC requirement due to Gas shortage
| 14:46 |  | Unique Meghnaghat Power 584 MW CCPP was shutdown due to gas shortage.
| 14:46 |  | Unique Meghnaghat Power Limited (UMPL) Shutdown with remarks:- GT
| 14:47 |  | Unique Meghnaghat Power Limited (UMPL) ST Shutdown with remarks:- None
| 15:33 | 17:03 | Kulaura 132/33kV S/S TR-1 AB LT Forced S/D Due to PBS feeder Red hot maintenance | [7 empty] | 30.0MW load
interrup.
| 15:34 | 17:02 | Kulaura 132/33kV S/S TR-1 AB HT Forced S/D Due to PBS feeder Red hot maintenance | [7 empty] | 30.0MW load
interrup.
| 15:56 |  | JERA Meghnaghat Power Limited 718 MW CCPP GT-11 was sync.
| 18:04 |  | JERA Meghnaghat Power Limited 718 MW CCPP tripped. | [7 empty] | 484MW generation
interrup.
| 19:09 |  | Matarbari 2*600 MW (CPGCBL), FGMO is OFF with remarks:-
| 19:21 |  | JERA Meghnaghat Power Limited 718 MW CCPP GT-11 and GT-12 was sync. at 19:21 hrs. and
19:32 hrs. respectively.
| 21:00 |  | Evening Peak Generation 13843 MW.
| 21:22 |  | Chandpur CCPP GT was sync.
| 21:27 |  | JERA Meghnaghat Power Limited 718 MW CCPP ST was sync.
| 01:51 |  | Bagerhat-Mongla 132 kV Ckt-1 Tripped from Bagerhat 132/33kV end showing Distance Relay.
relays Due to Unknown and from Mongla 132/33kV end showing Distance Realy relays Due to
line-1 tripped at 1:51 Distance Realy Showed 10.84 km
| 05:32 |  | Shahjibazar-Sreemangal 132kV Ckt-1 Scheduled S/D from Sreemongol 132/33kV end Due to Due
to the Roads and Highway project works in Shaistaganj. and from Shahjibazar 132/33kV end
Due to N/A
| 05:39 |  | Siddhirganj 230/132kV S/S MTR 1 HT Tripped showing Main 1 protection unit RET 670 relays
Due to PRV Trip ETR
| 07:00 |  | Min. Generation 10620 MW.
| 07:19 |  | Kushtia 132/33kV S/S T-3 LT Scheduled S/D Due to T-3, 33 kv bus Red Hot Maintenance | [7 empty] | 42.0MW load
interrup.
| 07:20 |  | Kushtia 132/33kV S/S T-3 HT Scheduled S/D | [7 empty] | 42.0MW load
interrup.
| 07:40 |  | Shahjibazar 132/33kV S/S TR-02 LT Scheduled S/D Due to Shutdown taken by PBS
| 07:40 |  | Shahjibazar 132/33kV S/S TR-06 LT Scheduled S/D Due to Shutdown taken by PBS
| 07:40 |  | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to Shutdown taken by PBS
| 07:42 |  | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to Shutdown taken by PBS
| 07:49 |  | Shahjibazar 132/33kV S/S TR-02 HT Scheduled S/D Due to Shutdown taken by PBS
| 07:53 |  | Matarbari 2*600 MW (CPGCBL), FGMO is ON with remarks:-
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 10-07-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 406 | 9432000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8001500 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 307 | 7199418 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7134185 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 20304 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 25200 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 80160 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 387407 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 25 | 544200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 521280 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 34 | 611040 | Engine Problem
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 34 | 601056 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 684480 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 20160 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 446400 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 33594 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 674640 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 4700909.09 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 158 | 6899640 | Gas shortage instructed by DS(Gen)
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 52 | 391200 | Engine Problem
Dhaka Area Total |  |  |  |  | 5939.724 | 1915 | 48408773.09
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 109080 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 26880 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 216 | 5150707 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 222 | 5108592 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 24 | 88896 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 33 | 198931 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 552960 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 25 | 433920 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 10059 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 22582 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 606720 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1050 | 19816361 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 22 | 734400 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 782 | 16160000 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.72 | 2574 | 49020088
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 201 | 4897000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 320 | 8251000 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 7744000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 20 | 479952 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 52 | 982080 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 33 | 434909 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 962804 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 80290 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 38 | 212704 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 128680 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 180 | 2564160 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 34 | 699840 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 73373 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 16 | 405150 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 50 | 687420 | Engine Problem
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 39 | 384720 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 17 | 536640 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 103082 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1399 | 29627804
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 33 | 919680 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 6150 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 183 | 2536800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 75 | 1220400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 161000 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 294960 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 428760 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 320 | 5567750
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | Gas shortage instructed by DS(Gen)
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 147 | 3449372.72 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 685536 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 1568640 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 172 | 4542830 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 439000 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 159264 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7450000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 385 | 8572000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7554600 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1464 | 34421242.72
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 902 | 21758545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 191 | 5011488 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 24480 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 96480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 971 | 19483633 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 152000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2064 | 46526626
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 304 | 2807272 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 11 | 171141 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2834000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1110 | 18881454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5345190 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 200 | 4276000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2005.5 | -
Barishal Area Total |  |  |  |  | 2236 | 1965 | 34317063.05
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 140 | 3643664 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 140 | 3577364 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 405 | 8719927 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 8700 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1034 | 21741818 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 96752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 211257 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 1719 | 37999482
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 48 | 1174254 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 162 | 4260000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 1217222 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 37676.4 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 840957 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 138715 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 810000 | -
Rangpur Area Total |  |  |  |  | 950 | 423 | 8478824.4
Eastern Grid Total |  |  |  |  | 16705.895 | 7672 | 167045657.81
Western Grid Total |  |  |  |  | 10378.16 | 6171 | 127321995.45
National Grid Total |  |  |  |  | 27084.055 | 13843 | 294367653.26
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 10-07-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9032.11 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4261.4 | MW
i) Dhaka area |  |  | 4754.99 |  | MW | i) Khulna area |  |  |  | 1545.2 | MW
ii) Chattogram area |  |  | 1353 |  | MW | ii) Barishal area |  |  |  | 395 | MW
iii) Cumilla area |  |  | 1242.12 |  | MW | iii) Rajshahi area |  |  |  | 1351.2 | MW
iv) Mymensingh area |  |  | 1095 |  | MW | iv) Rangpur area |  |  |  | 970 | MW
v) Sylhet area |  |  | 587 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13293.51 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 67 | 20:00 | 133 | Pabna | 111 | 19:30
2 | AKSML | 116 | 23:00 | 68 | Ishurdi | 73 | 19:30 | 134 | Palashbari | 98 | 19:00
3 | Aftabnagar | 34 | 13:00 | 69 | Jaldhaka | 86 | 19:30 | 135 | Panchagarh | 64 | 19:30
4 | Agargaon | 119 | 14:00 | 70 | Jamalpur | 116 | 20:00 | 136 | Patuakhali | 68 | 00:00
5 | Agrabad | 82 | 19:00 | 71 | Jashore | 124 | 19:30 | 137 | Payra | 28 | 01:00
6 | Amnura | 32 | 21:00 | 72 | Jhenaidah | 116 | 20:00 | 138 | Postogola | 55 | 13:00
7 | Ashuganj | 72 | 01:00 | 73 | Joydebpur | 131 | 13:00 | 139 | Purbachal | 18 | 22:00
8 | BSRM | 193 | 16:00 | 74 | Joypurhat | 58 | 22:00 | 140 | Purbasadipur | 135 | 20:00
9 | Bagerhat | 74 | 19:30 | 75 | Juldah | 13.5 | 00:00 | 141 | Rahanpur | 25 | 21:00
10 | Bajitpur | 66 | 22:00 | 76 | KSRM | 30 | 18:30 | 142 | Rahim | 38 | 18:00
11 | Bakulia | 81 | 19:30 | 77 | Kabirpur | 214 | 12:00 | 143 | Rajbari | 72 | 20:00
12 | Banani | 34 | 13:00 | 78 | Kachua | 80 | 21:00 | 144 | Rajendrapur | 125 | 20:00
13 | Bangabhaban | 15 | 12:00 | 79 | Kallyanpur | 105 | 13:00 | 145 | Rajshahi | 98 | 21:00
14 | Barapukuria | 62 | 21:00 | 80 | Kalurghat | 36 | 10:00 | 146 | Rajshahi-230 | 73 | 21:00
15 | Barguna | 20 | 22:00 | 81 | Kamrangirchar | 62.8 | 14:00 | 147 | Ramganj | 102 | 19:30
16 | Barishal | 87 | 22:00 | 82 | Kaptai | N/A | N/A | 148 | Rampur | 36 | 23:00
17 | Barishal-230 | 94 | 20:00 | 83 | Kasba | 31 | 19:00 | 149 | Rangamati | 16 | 19:00
18 | Baroaulia | 57 | 11:00 | 84 | Kazla | 93 | 12:00 | 150 | Rangpur | 140 | 19:00
19 | Baroirhat | 53 | 19:00 | 85 | Keranigonj | 86 | 19:30 | 151 | Ruppur | 6.8 | 10:00
20 | Bashundhara | 174 | 13:00 | 86 | Khagrachori | 26 | 19:00 | 152 | SSM | 5 | 01:00
21 | BashundharaCement | 7 | 01:00 | 87 | Khulna | 57 | 13:00 | 153 | Saidpur | 104 | 20:00
22 | Beanibazar | 74 | 22:00 | 88 | Khulshi | 141 | 14:00 | 154 | Satkhira | 110 | 19:30
23 | Benapole | 60 | 19:30 | 89 | Kishoreganj | 126 | 23:00 | 155 | Satmasjid | 76 | 13:00
24 | Bhaluka | 132 | 19:30 | 90 | Kodda | 303 | 19:00 | 156 | Savar | 218 | 12:00
25 | Bhandaria | 50 | 20:00 | 91 | Kulaura | 52 | 19:00 | 157 | SevenRings | 5.72 | 18:00
26 | Bhangura | 32 | 19:30 | 92 | Kurigram | 59 | 22:00 | 158 | ShahCement | 25 | 22:00
27 | Bheramara(GK) | 58 | 19:30 | 93 | Kushtia | 144 | 20:00 | 159 | Shahjadpur | 71 | 21:00
28 | Bhulta | 241 | 23:00 | 94 | Lakshmipur | 37 | 23:00 | 160 | Shahjibazar | 117 | 23:00
29 | Bog-Sherpur | 60 | 19:30 | 95 | Lalbag | 60 | 13:00 | 161 | Shahmirpur | 57 | 00:00
30 | Bogura | 165 | 20:00 | 96 | Lalmonirhat | 56 | 23:00 | 162 | Shariatpur | 77 | 22:00
31 | Borhanuddin | 75 | 00:00 | 97 | MI_Cement | 15 | 14:00 | 163 | Sherpur | 144 | 22:00
32 | Brahmanbaria | 122 | 22:00 | 98 | Madanganj | 44 | 00:00 | 164 | Shikalbaha | 15 | 12:00
33 | Cantonment | 140 | 13:00 | 99 | Madaripur | 94 | 22:00 | 165 | Shitalakhya | 76.7 | 12:00
34 | Chandina | 11.12 | 21:00 | 100 | Madartek | 72.64 | 20:00 | 166 | Sholosohor | 43 | 16:00
35 | Chandpur | 70 | 21:00 | 101 | Madunaghat | 47 | 21:00 | 167 | Shyampur | 148 | 02:00
36 | Chandraghona | 32 | 20:00 | 102 | Magura | 56 | 19:30 | 168 | Siddhirganj | 113 | 15:00
37 | Chapai | 60 | 22:00 | 103 | Mahasthangarh | 74 | 19:30 | 169 | Sirajganj | 90 | 20:00
38 | Charsaidpur | 25 | 13:00 | 104 | Maijdee | 12 | 21:00 | 170 | Sonargaon | 94 | 21:00
39 | Chauddagram | 61 | 23:00 | 105 | Manikganj | 111 | 19:30 | 171 | Sreemongol | 73 | 21:00
40 | Chhatak | 34 | 21:00 | 106 | Maniknagar | 78 | 13:00 | 172 | Sreepur | 93 | 19:30
41 | Chowmuhani | 164 | 21:00 | 107 | Matarbari | 46 | 22:00 | 173 | Srinagar | 39.74 | 22:00
42 | Chuadanga | 93 | 21:00 | 108 | Matuail | 62 | 16:00 | 174 | Sunamganj | 56 | 22:00
43 | Coxsbazar | 145 | 20:00 | 109 | Millgate | 102 | 12:00 | 175 | Sylhet | 47 | 21:00
44 | Cumilla(N) | 124 | 23:00 | 110 | Mirpur | 111 | 13:00 | 176 | Sylhet-132 | 113 | 19:00
45 | Cumilla(S) | 145 | 19:00 | 111 | Mirsorai | 9 | 12:00 | 177 | TK | 33 | 22:00
46 | Daganbhuiyan | 0 | 01:00 | 112 | Mirzapur | 41 | 19:30 | 178 | Tangail | 146 | 19:30
47 | Daudkandi | 137 | 21:00 | 113 | Mithapukur | 64 | 19:30 | 179 | Taraganj | 19 | 23:00
48 | Dhaka | 66 | 13:00 | 114 | Modern | N/A | N/A | 180 | Thakurgaon | 115 | 21:00
49 | Dhamrai | 112 | 15:00 | 115 | Mogbazar | 137 | 13:00 | 181 | Tongi | 136 | 12:00
50 | Dhanmondi | 134 | 13:00 | 116 | Mongla | 39 | 11:00 | 182 | Ullahpara | 33 | 20:00
51 | Dohazari | 93 | 19:00 | 117 | Motijheel | 38 | 13:00 | 183 | Ullon | 34 | 14:00
52 | Faridpur | 138 | 20:00 | 118 | Muktagacha | 33 | 19:00 | 184 | Uttara | 71 | 13:00
53 | Fatullah | 98 | 12:00 | 119 | Munshiganj | 96 | 00:00 | 185 | UttaraNew | 53 | 14:00
54 | Fenchuganj | 38 | 19:00 | 120 | Muradnagar | 38 | 21:00 | 186 | Zigatola | 68 | 13:00
55 | Feni | 92 | 20:00 | 121 | Mymensingh | 192 | 19:30
56 | GPH | 83 | 03:00 | 122 | Naogaon | 120 | 21:00
57 | Ghatail | 72 | 19:30 | 123 | Narail | 52 | 19:30
58 | Ghorashal | 14 | 10:00 | 124 | Narinda | 74 | 13:00
59 | Ghorashal-230 | 84 | 21:00 | 125 | Narshingdi | 171 | 23:00
60 | Goalpara | 33 | 19:30 | 126 | Natore | 131 | 20:00
61 | Gollamari | 84 | 20:00 | 127 | Nawabganj | 49 | 22:00
62 | Gopalganj | 88 | 20:00 | 128 | Netrakona | 126 | 19:30
63 | Gulshan | 112 | 13:00 | 129 | New | 58 | 12:00
64 | Halishahar | 74 | 10:00 | 130 | Niamatpur | 67 | 22:00
65 | HaripurSBU | 160 | 09:00 | 131 | Noapara | 40 | 19:30
66 | Hasnabad | 66 | 14:00 | 132 | PHP | 9 | 07:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 10-07-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 12621.86 | 0 |  | 12621.86
1:00 | 12189.53 | 0 |  | 12189.53
2:00 | 11370.94 | 0 |  | 11370.94
3:00 | 11394.4 | 0 |  | 11394.4
4:00 | 10968.68 | 0 |  | 10968.68
5:00 | 10701.97 | 0 |  | 10701.97
6:00 | 10433.57 | 0 |  | 10433.57
7:00 | 10575.11 | 0 |  | 10575.11
8:00 | 10805.81 | 0 |  | 10805.81
9:00 | 11167.83 | 0 |  | 11167.83
10:00 | 11511.57 | 0 |  | 11511.57
11:00 | 11827.11 | 0 |  | 11827.11
12:00 | 12221.24 | 0 |  | 12221.24
13:00 | 12573.18 | 0 |  | 12573.18
14:00 | 12420.27 | 0 |  | 12420.27
15:00 | 12368.07 | 0 |  | 12368.07
16:00 | 12224.52 | 0 |  | 12224.52
17:00 | 11979.89 | 0 |  | 11979.89
18:00 | 11885.79 | 0 |  | 11885.79
19:00 | 12788.34 | 0 |  | 12788.34
19:30 | 13748.23 | 31 |  | 13780.23
20:00 | 13773.46 | 31 |  | 13805.46
21:00 | 13843 | 31 |  | 13875.4
22:00 | 13655 | 24 |  | 13680
23:00 | 13562 | 0 |  | 13562
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 10-07-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7171 | 5450.86 | 12621.86 | DAILY GENERATION CURVE
00:30 | 7126.1 | 5279.595 | 12405.695
01:00 | 7081.2 | 5108.33 | 12189.53 | 10-07-2025
01:30 | 6928.7 | 4851.535 | 11780.235
02:00 | 6776.2 | 4594.74 | 11370.94
02:30 | 6716.7 | 4665.97 | 11382.67
03:00 | 6657.2 | 4737.2 | 11394.4
03:30 | 6483.7 | 4697.84 | 11181.54
04:00 | 6310.2 | 4658.48 | 10968.68
04:30 | 6185.7 | 4649.625 | 10835.325
05:00 | 6061.2 | 4640.77 | 10701.97
05:30 | 5968.365 | 4599.405 | 10567.77
06:00 | 5875.53 | 4558.04 | 10433.57
06:30 | 5920.625 | 4583.715 | 10504.34
07:00 | 5965.72 | 4609.39 | 10575.11
07:30 | 6007.205 | 4683.255 | 10690.46
08:00 | 6048.69 | 4757.12 | 10805.81
08:30 | 6180.12 | 4806.7 | 10986.82
09:00 | 6311.55 | 4856.28 | 11167.83
09:30 | 6460.335 | 4879.365 | 11339.7
10:00 | 6609.12 | 4902.45 | 11511.57
10:30 | 6736.93 | 4932.41 | 11669.34
11:00 | 6864.74 | 4962.37 | 11827.11
11:30 | 6922.57 | 5101.605 | 12024.175
12:00 | 6980.4 | 5240.84 | 12221.24
12:30 | 7032.395 | 5364.815 | 12397.21
13:00 | 7084.39 | 5488.79 | 12573.18
13:30 | 7058.6 | 5438.125 | 12496.725
14:00 | 7032.81 | 5387.46 | 12420.27
14:30 | 6957.25 | 5436.92 | 12394.17
15:00 | 6881.69 | 5486.38 | 12368.07
15:30 | 6870.58 | 5425.715 | 12296.295
16:00 | 6859.47 | 5365.05 | 12224.52
16:30 | 6830.75 | 5271.455 | 12102.205
17:00 | 6802.03 | 5177.86 | 11979.89
17:30 | 6834.88 | 5097.96 | 11932.84
18:00 | 6867.73 | 5018.06 | 11885.79
18:30 | 7136.865 | 5200.2 | 12337.065
19:00 | 7406 | 5382.34 | 12788.34
19:30 | 7793 | 5955.23 | 13748.23
20:00 | 7720 | 6053.46 | 13773.46
20:30 | 7696 | 6112.23 | 13808.23 |  | Executive Engineer
21:00 | 7672 | 6171 | 13843 |  | Network Operation Division
21:30 | 7665.5 | 6083.5 | 13749
22:00 | 7659 | 5996 | 13655
22:30 | 7635 | 5973.5 | 13608.5
23:00 | 7611 | 5951 | 13562

## En-Curve
QF-LDC-12
Date | 10-07-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3668 | 2214 | 901 | 38 | 32 | 962.86 | 214 | 3698 | 0 | 157 | 713 | 0 | 0 | 24 | 0 | DAILY ENERGY CURVE
00:30 | 3647 | 2211.1 | 901.5 | 38 | 31 | 910.595 | 214 | 3596.5 | 0 | 149 | 686.5 | 0 | 0 | 20.5 | 0 | 10-07-2025
01:00 | 3626 | 2208.2 | 902 | 38 | 30 | 858.33 | 214 | 3495 | 0 | 141 | 660 | 0 | 0 | 17 | 0
01:30 | 3564.5 | 2183.2 | 902 | 38 | 30 | 840.535 | 213.5 | 3274.5 | 0 | 87.5 | 628.5 | 0 | 0 | 18 | 0 | Energy Generated | 294.3677 |  | MKWHr
02:00 | 3503 | 2158.2 | 902 | 38 | 30 | 822.74 | 213 | 3054 | 0 | 34 | 597 | 0 | 0 | 19 | 0 | Energy not Served | 0.086 |  | MKWHr
02:30 | 3488.5 | 2154.2 | 902 | 19 | 30 | 823.97 | 212.5 | 3166 | 0 | 25 | 542 | 0 | 0 | 19.5 | 0 | Total Energy Requirement | 294.4537 |  | MKWHr
03:00 | 3474 | 2150.2 | 902 | 0 | 30 | 825.2 | 212 | 3278 | 0 | 16 | 487 | 0 | 0 | 20 | 0
03:30 | 3464 | 2118.7 | 899.5 | 0 | 30 | 823.84 | 212.5 | 3176 | 0 | 8 | 425.5 | 0 | 0 | 23.5 | 0
04:00 | 3454 | 2087.2 | 897 | 0 | 30 | 822.48 | 213 | 3074 | 0 | 0 | 364 | 0 | 0 | 27 | 0
04:30 | 3453.5 | 2055.7 | 897.5 | 0 | 28 | 823.125 | 213 | 3025 | 0 | 0 | 315.5 | 0 | 0 | 24 | 0
05:00 | 3453 | 2024.2 | 898 | 0 | 26 | 823.77 | 213 | 2976 | 0 | 0 | 267 | 0 | 0 | 21 | 0
05:30 | 3399.5 | 1982.7 | 897.5 | 0 | 27 | 825.715 | 213 | 2934.5 | 7.355 | 0 | 254.5 | 0 | 0 | 26 | 0
06:00 | 3346 | 1941.2 | 897 | 0 | 28 | 827.66 | 213 | 2893 | 14.71 | 0 | 242 | 0 | 0 | 31 | 0
06:30 | 3355.5 | 1950.2 | 897 | 0 | 26 | 824.75 | 213.5 | 2922 | 34.39 | 4 | 249.5 | 0 | 0 | 27.5 | 0
07:00 | 3365 | 1959.2 | 897 | 0 | 24 | 821.84 | 214 | 2951 | 54.07 | 8 | 257 | 0 | 0 | 24 | 0
07:30 | 3419 | 1944.7 | 899.5 | 0 | 21 | 824.78 | 214 | 2975.5 | 50.48 | 23 | 296 | 0 | 0 | 22.5 | 0
08:00 | 3473 | 1930.2 | 902 | 0 | 18 | 827.72 | 214 | 3000 | 46.89 | 38 | 335 | 0 | 0 | 21 | 0
08:30 | 3550 | 1969.2 | 902 | 0 | 23 | 827.48 | 214 | 3007.5 | 79.14 | 48.5 | 343 | 0 | 0 | 23 | 0
09:00 | 3627 | 2008.2 | 902 | 0 | 28 | 827.24 | 214 | 3015 | 111.39 | 59 | 351 | 0 | 0 | 25 | 0
09:30 | 3669.5 | 2034.1 | 902 | 0 | 28 | 841.285 | 214 | 3059 | 135.315 | 59 | 358 | 0 | 0 | 39.5 | 0
10:00 | 3712 | 2060 | 902 | 0 | 28 | 855.33 | 214 | 3103 | 159.24 | 59 | 365 | 0 | 0 | 54 | 0
10:30 | 3696.5 | 2098.5 | 902 | 0 | 28 | 835.285 | 214 | 3250.5 | 171.055 | 50.5 | 370 | 0 | 0 | 53 | 0
11:00 | 3681 | 2137 | 902 | 0 | 28 | 815.24 | 214 | 3398 | 182.87 | 42 | 375 | 0 | 0 | 52 | 0
11:30 | 3711.5 | 2151.5 | 902 | 0 | 30 | 858.195 | 215 | 3430.5 | 235.48 | 42 | 394 | 0 | 0 | 54 | 0
12:00 | 3742 | 2166 | 902 | 0 | 32 | 901.15 | 216 | 3463 | 288.09 | 42 | 413 | 0 | 0 | 56 | 0
12:30 | 3779.5 | 2160 | 901.5 | 19 | 32 | 957.925 | 216 | 3540 | 268.785 | 44.5 | 420 | 0 | 0 | 58 | 0
13:00 | 3817 | 2154 | 901 | 38 | 32 | 1014.7 | 216 | 3617 | 249.48 | 47 | 427 | 0 | 0 | 60 | 0
13:30 | 3777.5 | 2141 | 901.5 | 19 | 32 | 1017.485 | 216 | 3585.5 | 247.74 | 53 | 449 | 0 | 0 | 57 | 0
14:00 | 3738 | 2128 | 902 | 0 | 32 | 1020.27 | 216 | 3554 | 246 | 59 | 471 | 0 | 0 | 54 | 0
14:30 | 3772 | 2009.5 | 902 | 0 | 29 | 1028.5 | 216 | 3601 | 242.17 | 59 | 480 | 0 | 0 | 55 | 0
15:00 | 3806 | 1891 | 902 | 0 | 26 | 1036.73 | 216 | 3648 | 238.34 | 59 | 489 | 0 | 0 | 56 | 0
15:30 | 3800.5 | 1901.5 | 902 | 0 | 25 | 998.585 | 216 | 3666.5 | 191.71 | 59 | 490.5 | 0 | 0 | 45 | 0
16:00 | 3795 | 1912 | 902 | 0 | 24 | 960.44 | 216 | 3685 | 145.08 | 59 | 492 | 0 | 0 | 34 | 0
16:30 | 3768 | 1930.5 | 902 | 0 | 27 | 893.075 | 216 | 3650.5 | 130.13 | 63.5 | 494.5 | 0 | 0 | 27 | 0
17:00 | 3741 | 1949 | 902 | 0 | 30 | 825.71 | 216 | 3616 | 115.18 | 68 | 497 | 0 | 0 | 20 | 0
17:30 | 3720 | 2004.75 | 902 | 0 | 30 | 828.635 | 194 | 3577.5 | 81.455 | 73 | 504 | 0 | 0 | 17.5 | 0
18:00 | 3699 | 2060.5 | 902 | 0 | 30 | 831.56 | 172 | 3539 | 47.73 | 78 | 511 | 0 | 0 | 15 | 0
18:30 | 3726.5 | 1820.75 | 902 | 0 | 33 | 831.45 | 194 | 3821.5 | 23.865 | 172 | 795 | 0 | 0 | 17 | 0
19:00 | 3754 | 1581 | 902 | 0 | 36 | 831.34 | 216 | 4104 | 0 | 266 | 1079 | 0 | 0 | 19 | 0
19:30 | 3789 | 1680 | 902 | 0 | 28 | 963.23 | 216 | 4504 | 0 | 305 | 1337 | 0 | 0 | 24 | 31
20:00 | 3753 | 1752 | 902 | 0 | 34 | 1008.46 | 216 | 4592 | 0 | 285 | 1200 | 0 | 0 | 31 | 31
20:30 | 3775.5 | 1815.5 | 902 | 0 | 34 | 1021.23 | 216 | 4609.5 | 0 | 268 | 1140 | 0 | 0 | 26.5 | 31
21:00 | 3798 | 1879 | 902 | 0 | 34 | 1034 | 216 | 4627 | 0 | 251 | 1080 | 0 | 0 | 22 | 31
21:30 | 3754.5 | 1942.5 | 902 | 0 | 35 | 1022.5 | 216 | 4542 | 0 | 240.5 | 1073 | 0 | 0 | 21 | 27.5
22:00 | 3711 | 2006 | 902 | 0 | 36 | 1011 | 216 | 4457 | 0 | 230 | 1066 | 0 | 0 | 20 | 24
22:30 | 3746.5 | 2033.5 | 902 | 0 | 35 | 1021 | 216 | 4406.5 | 0 | 216.5 | 1014.5 | 0 | 0 | 17 | 12
23:00 | 3782 | 2061 | 902 | 0 | 34 | 1031 | 216 | 4356 | 0 | 203 | 963 | 0 | 0 | 14 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 10-07-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 389 | 06:00 | 372 | 21:00 | Payra | 417 | 05:00 | 409 | 21:00
Ashuganj | 390 | 06:00 | 385 | 12:00 | Rahanpur | 398 | 09:00 | 383 | 21:00
Bhulta | 400 | 04:00 | 380 | 12:00 | Rampal | 404 | 04:00 | 390 | 21:00
Bibiana | 389 | 01:00 | 382 | 22:00
BIPTC | 405 | 05:00 | 396 | 20:00
Bogura | 386 | 05:00 | 371 | 20:00
Gopalganj | 402 | 06:00 | 386 | 21:00
Kaliakoir | 379 | 05:00 | 364 | 21:00
Madunaghat | 396 | 06:00 | 388 | 21:00
Meghnaghat | 391 | 05:00 | 376 | 21:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 228 | 05:00 | 217 | 21:00 | Keranigonj | 227 | 06:00 | 216 | 21:00
AKSML | 232 | 07:00 | 225 | 18:00 | Khulna(S) | 231 | 04:00 | 218 | 21:00
Aminbazar | 229 | 05:00 | 219 | 12:00 | Madunaghat | 233 | 06:00 | 229 | 18:00
Ashuganj | 232 | 07:00 | 223 | 13:00 | Madunaghat-400 | 233 | 06:00 | 229 | 23:00
Ashuganj-400 | 232 | 07:00 | 223 | 13:00 | Maniknagar | 224 | 07:00 | 216 | 12:00
Baghabari | 234 | 05:00 | 225 | 20:00 | Meghnaghat | 232 | 12:00 | 222 | 16:00
Barapukuria | 224 | 18:30 | 215 | 15:00 | Meghnaghat-400 | 227 | 06:00 | 219 | 21:00
Barapukuria-230 | 224 | 18:30 | 215 | 15:00 | Mirsorai | 229 | 07:00 | 220 | 21:00
Barishal | 233 | 06:00 | 224 | 22:00 | Rajshahi | 234 | 18:30 | 221 | 21:00
Bheramara | 232 | 08:00 | 221 | 19:30 | Rampal | 232 | 06:00 | 220 | 20:00
Bhulta | 231 | 04:00 | 216 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 229 | 06:00 | 223 | 20:00 | Rampura | 230 | 04:00 | 215 | 12:00
BIPTC | 234 | 06:00 | 222 | 19:30 | Shikalbaha | 231 | 07:00 | 227 | 00:00
Bogura | 235 | 18:30 | 224 | 21:00 | Shyampur | 226 | 06:00 | 216 | 21:00
Bogura-400 | 234 | 06:00 | 225 | 20:00 | Siddhirganj | 225 | 05:00 | 218 | 11:00
Borhanuddin | 239 | 06:00 | 233 | 20:00 | Sirajgonj | 239 | 06:00 | 233 | 21:00
BSRM | 228 | 06:00 | 220 | 21:00 | Sreepur | 229 | 06:00 | 220 | 21:00
Cumilla(N) | 224 | 05:00 | 216 | 21:00 | Tongi | 228 | 04:00 | 218 | 12:00
Faridpur | 230 | 06:00 | 22 | 22:00
Fenchuganj | 230 | 05:00 | 224 | 20:00
Ghorashal | 235 | 04:00 | 230 | 00:00
Ghorashal-230 | 229 | 04:00 | 218 | 12:00
Gopalganj | 230 | 05:00 | 222 | 20:00
GPH | 231 | 06:00 | 225 | 13:00
Haripur | 225 | 06:00 | 216 | 21:00
Hasnabad | 226 | 06:00 | 55 | 17:00
Hathazari | 230 | 00:00 | 225 | 23:00
Ishurdi | 234 | 08:00 | 224 | 19:30
Jhenaidah | 232 | 08:00 | 218 | 19:30
Kaliakoir | 234 | 06:00 | 224 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 05:00 | 125 | 12:00 | Madanganj | 130 | 08:00 | 125 | 16:00
Agargaon | 135 | 06:00 | 127 | 21:00 | Madaripur | 136 | 05:00 | 130 | 21:00
Agrabad | 133 | 09:00 | 128 | 10:00 | Madartek | 135 | 07:00 | 125 | 12:00
AKS | 130 | 06:00 | 126 | 00:00 | Madunaghat | 132 | 06:00 | 129 | 18:00
Aminbazar | 135 | 05:00 | 127 | 12:00 | Magura | 135 | 05:00 | 125 | 21:00
Amnura | 136 | 09:00 | 126 | 01:00 | Mahasthangarh | 136 | 06:00 | 127 | 21:00
Ashuganj | 140 | 00:00 | 135 | 21:00 | Maijdee | 117 | 18:30 | 109 | 00:00
Bagerhat | 133 | 05:00 | 122 | 22:00 | Manikganj | 129 | 05:00 | 120 | 12:00
Bajitpur | 131 | 03:00 | 125 | 23:00 | Maniknagar | 134 | 06:00 | 127 | 12:00
Bakulia | 134 | 06:00 | 130 | 13:00 | Matarbari | 124 | 12:00 | 111 | 23:00
Banani | 136 | 06:00 | 124 | 12:00 | Matuail | 130 | 03:00 | 126 | 12:00
Bangabhaban | 133 | 03:00 | 127 | 12:00 | Millgate | 133 | 01:00 | 125 | 12:00
Barapukuria | 137 | 18:30 | 127 | 15:00 | Mirpur | 134 | 04:00 | 125 | 21:00
Barguna | 136 | 06:00 | 132 | 21:00 | Mirzapur | 131 | 08:00 | 125 | 21:00
Barishal | 136 | 04:00 | 129 | 23:00 | Mithapukur | 133 | 06:00 | 123 | 20:00
Barishal-230 | 137 | 06:00 | 130 | 20:00 | MI_Cement | 132 | 06:00 | 126 | 12:00
Baroaulia | 133 | 15:00 | 129 | 00:00 | Modern | 0 | 00:00 | 0 | 00:00
Baroirhat | 123 | 09:00 | 118 | 03:00 | Mogbazar | 136 | 04:00 | 125 | 12:00
Bashundhara | 135 | 03:00 | 124 | 12:00 | Mongla | 133 | 06:00 | 122 | 21:00
BashundharaCement | 132 | 01:00 | 125 | 16:00 | Motijheel | 133 | 03:00 | 127 | 12:00
Beanibazar | 129 | 05:00 | 124 | 21:00 | Muktagacha | 134 | 18:30 | 128 | 23:00
Benapole | 133 | 05:00 | 121 | 21:00 | Munshiganj | 131 | 06:00 | 125 | 12:00
Bhaluka | 130 | 08:00 | 12 | 17:00 | Muradnagar | 126 | 07:00 | 120 | 13:00
Bhandaria | 135 | 11:00 | 124 | 21:00 | Mymensingh | 135 | 18:30 | 116 | 21:00
Bhangura | 134 | 05:00 | 128 | 19:30 | Naogaon | 133 | 05:00 | 123 | 21:00
Bheramara | 137 | 08:00 | 132 | 19:30 | Narail | 137 | 05:00 | 125 | 19:30
Bheramara(GK) | 137 | 08:00 | 132 | 19:30 | Narinda | 134 | 06:00 | 127 | 12:00
Bhulta | 123 | 07:00 | 119 | 21:00 | Narshingdi | 132 | 05:00 | 122 | 12:00
Bog-Sherpur | 136 | 06:00 | 129 | 19:30 | Natore | 135 | 04:00 | 128 | 20:00
Bogura | 138 | 06:00 | 131 | 21:00 | Nawabganj | 136 | 05:00 | 128 | 21:00
Bogura-230 | 139 | 18:30 | 131 | 21:00 | Netrakona | 125 | 18:30 | 115 | 21:00
Brahmanbaria | 133 | 05:00 | 126 | 23:00 | New | 135 | 05:00 | 125 | 12:00
Cantonment | 135 | 04:00 | 127 | 12:00 | Niamatpur | 135 | 06:00 | 129 | 21:00
Chandina | 128 | 07:00 | 123 | 13:00 | Noapara | 137 | 05:00 | 125 | 21:00
Chandpur | 123 | 18:30 | 115 | 13:00 | Pabna | 135 | 06:00 | 129 | 19:30
Chandraghona | 133 | 07:00 | 131 | 12:00 | Palashbari | 132 | 09:00 | 121 | 22:00
Chapai | 132 | 06:00 | 126 | 22:00 | Panchagarh | 134 | 18:30 | 117 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 132 | 06:00 | 125 | 13:00 | Patuakhali | 135 | 05:00 | 132 | 21:00
Chauddagram | 122 | 07:00 | 118 | 00:00 | Payra | 137 | 09:00 | 134 | 20:00
Chhatak | 129 | 06:00 | 122 | 21:00 | PHP | 122 | 09:00 | 117 | 13:00
Chowmuhani | 120 | 18:30 | 113 | 00:00 | Postogola | 134 | 06:00 | 128 | 12:00
Chuadanga | 135 | 05:00 | 123 | 21:00 | Purbachal | 135 | 04:00 | 124 | 12:00
Coxsbazar | 123 | 07:00 | 111 | 23:00 | Purbasadipur | 131 | 18:30 | 117 | 15:00
Cumilla(N) | 127 | 06:00 | 123 | 22:00 | Rahanpur | 136 | 05:00 | 130 | 21:00
Cumilla(S) | 133 | 18:00 | 121 | 12:00 | Rahanpur-400 | 136 | 06:00 | 131 | 20:00
Daganbhuiyan | 119 | 10:00 | 114 | 13:00 | Rahim | 131 | 07:00 | 126 | 12:00
Daudkandi | 125 | 06:00 | 119 | 21:00 | Rajbari | 135 | 06:00 | 128 | 20:00
Dhaka | 135 | 03:00 | 124 | 12:00 | Rajendrapur | 132 | 02:00 | 124 | 13:00
Dhamrai | 133 | 04:00 | 127 | 12:00 | Rajshahi | 135 | 05:00 | 129 | 19:30
Dhanmondi | 136 | 06:00 | 127 | 12:00 | Rajshahi-230 | 135 | 05:00 | 120 | 21:00
Dohazari | 129 | 05:00 | 124 | 23:00 | Ramganj | 118 | 18:30 | 111 | 00:00
Faridpur | 136 | 06:00 | 130 | 21:00 | Rampur | 133 | 07:00 | 128 | 14:00
Fatullah | 133 | 06:00 | 127 | 12:00 | Rampura | 135 | 04:00 | 124 | 12:00
Fenchuganj | 136 | 06:00 | 132 | 20:00 | Rangamati | 132 | 06:00 | 130 | 00:00
Feni | 122 | 07:00 | 115 | 13:00 | Rangpur | 129 | 18:30 | 122 | 13:00
Ghatail | 131 | 18:30 | 124 | 22:00 | Ruppur | 138 | 07:00 | 132 | 19:30
Ghorashal | 140 | 19:00 | 131 | 12:00 | Saidpur | 134 | 18:30 | 120 | 14:00
Goalpara | 138 | 05:00 | 127 | 21:00 | Satkhira | 134 | 05:00 | 122 | 21:00
Gollamari | 138 | 05:00 | 128 | 22:00 | Satmasjid | 135 | 06:00 | 127 | 13:00
Gopalganj | 137 | 06:00 | 128 | 21:00 | Savar | 132 | 05:00 | 125 | 12:00
Gopalganj-400 | 138 | 06:00 | 132 | 19:30 | SevenRings | 138 | 07:00 | 131 | 12:00
Gulshan | 135 | 05:00 | 125 | 12:00 | ShahCement | 132 | 06:00 | 125 | 13:00
Halishahar | 133 | 06:00 | 128 | 10:00 | Shahjadpur | 138 | 03:00 | 132 | 15:00
Haripur | 131 | 05:00 | 127 | 12:00 | Shahjibazar | 133 | 01:00 | 127 | 21:00
HaripurSBU | 131 | 05:00 | 127 | 12:00 | Shahmirpur | 132 | 02:00 | 130 | 00:00
Hasnabad | 134 | 05:00 | 128 | 11:00 | Shariatpur | 135 | 06:00 | 128 | 23:00
Hathazari | 134 | 02:00 | 130 | 12:00 | Sherpur | 136 | 18:30 | 124 | 06:00
Ishurdi | 138 | 08:00 | 132 | 21:00 | Shikalbaha | 123 | 07:00 | 119 | 15:00
Jaldhaka | 128 | 18:30 | 119 | 14:00 | Shikalbaha-230 | 134 | 07:00 | 131 | 00:00
Jamalpur | 139 | 18:30 | 127 | 06:00 | Shitalakhya | 132 | 06:00 | 126 | 12:00
Jashore | 134 | 08:00 | 123 | 19:30 | Sholosohor | 132 | 06:00 | 129 | 13:00
Jhenaidah | 137 | 04:00 | 124 | 20:00 | Shyampur | 133 | 06:00 | 125 | 13:00
Jhenaidah-230 | 138 | 08:00 | 128 | 19:30 | Shyampur-230 | 133 | 06:00 | 126 | 16:00
Joydebpur | 137 | 18:30 | 130 | 16:00 | Siddhirganj | 131 | 03:00 | 127 | 12:00
Joypurhat | 132 | 05:00 | 122 | 21:00 | Sirajganj | 134 | 18:30 | 127 | 21:00
Juldah | 133 | 19:30 | 130 | 00:00 | Sonargaon | 129 | 05:00 | 123 | 21:00
Kabirpur | 131 | 07:00 | 122 | 12:00 | Sreemongol | 133 | 03:00 | 127 | 21:00
Kachua | 123 | 18:00 | 117 | 11:00 | Sreepur | 133 | 05:00 | 126 | 23:00
Kaliakoir | 135 | 06:00 | 129 | 12:00 | Srinagar | 137 | 06:00 | 129 | 12:00
Kallyanpur | 135 | 04:00 | 126 | 21:00 | SSM | 136 | 05:00 | 132 | 00:00
Kalurghat | 132 | 01:00 | 129 | 16:00 | Sunamganj | 127 | 08:00 | 121 | 22:00
Kamrangirchar | 137 | 05:00 | 128 | 12:00 | Sylhet | 131 | 07:00 | 125 | 21:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet-132 | 130 | 09:00 | 126 | 22:00
Kasba | 126 | 07:00 | 119 | 21:00 | Tangail | 129 | 09:00 | 123 | 21:00
Kazla | 133 | 04:00 | 126 | 13:00 | Taraganj | 128 | 00:00 | 121 | 14:00
Keranigonj | 137 | 06:00 | 129 | 21:00 | Thakurgaon | 133 | 18:30 | 115 | 13:00
Khagrachori | 132 | 04:00 | 129 | 18:00 | TK | 132 | 04:00 | 129 | 20:00
Khulna | 136 | 05:00 | 126 | 21:00 | Tongi | 135 | 04:00 | 127 | 12:00
Khulna(S) | 138 | 05:00 | 128 | 21:00 | Ullahpara | 135 | 05:00 | 129 | 20:00
Khulshi | 131 | 05:00 | 127 | 16:00 | Ullon | 135 | 06:00 | 124 | 12:00
Kishoreganj | 130 | 05:00 | 124 | 19:30 | Uttara | 135 | 06:00 | 126 | 12:00
Kodda | 132 | 07:00 | 122 | 13:00 | UttaraNew | 133 | 04:00 | 125 | 21:00
KSRM | 134 | 03:00 | 129 | 15:00 | Zigatola | 137 | 06:00 | 129 | 20:00
Kulaura | 134 | 03:00 | 130 | 21:00
Kurigram | 132 | 18:30 | 118 | 14:00
Kushtia | 134 | 04:00 | 128 | 19:30
Lakshmipur | 118 | 07:00 | 112 | 00:00
Lalbag | 136 | 05:00 | 128 | 21:00
Lalmonirhat | 127 | 09:00 | 119 | 14:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division