## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 15-07-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-07-2025 | during | 15-07-2025 | during | 15-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 0 | 0 | 0 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 288 | 291 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 199 | 204 | 208.13 | 208.13 | 208.13 | 208.13 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 35 | 49 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 48 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 25 | 24 | 33 | 33 | 26 | 26 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 43 | 43 | 52.19 | 52.19 | 42 | 42 | Engine Problem
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | -
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 52 | 70 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 70 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 30 | 104 | 104 | 50 | 50 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 108 | 54 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 11 | 0 | 17 | 0 | 17 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 54 | 55 | 55 | 35 | 35 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 311 | 348 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 108 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2035 | 2222 | 4695.45 | 4772.45 | 3267.46 | 3344.46
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 8 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 15 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 161 | 218 | 172 | 172 | 172 | 172 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 217 | 213 | 213 | 213 | 213 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 15 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 8 | 80 | 80 | 80 | 80 | Machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 67 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 60 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 4 | 15 | 2 | 25 | 2 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.32 | 0 | 4.57 | 0 | 4.57 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 14 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 48 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 580 | 550 | 612 | 1224 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 49 | 18 | 36 | 35 | 36 | 35 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 762 | 725 | 790 | 790 | 790 | 790 | FGMO
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1857.32 | 2045 | 3213.29 | 3832.72 | 3213.29 | 3220.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 203 | 183 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 350 | 356 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 340 | 340 | 340 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 19 | 19 | 46.7 | 46.7 | 19 | 19 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 47 | 47 | 55 | 55 | 50 | 50 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 63 | 107 | 195 | 195 | 185 | 185 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 115 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 30 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 80 | 160 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 30 | 26 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 8 | 20 | 17.75 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 32 | 99 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 29 | 113 | 113 | 18 | 37 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 91 | 82 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 54 | 0 | 40 | 0 | 40 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1419 | 1757 | 2434 | 2400.75 | 2185.55 | 2164.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-07-2025 | during | 15-07-2025 | during | 15-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 33 | 49 | 157.5 | 157.5 | 71 | 71 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 105 | 193 | 200 | 200 | 186 | 186 | Engine Problem
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 94 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 30.88 | 0 | 39 | 0 | 39 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 35 | 35 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 243.88 | 365 | 589.9 | 549 | 459.9 | 419
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 10 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 138 | 152 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 82 | 82 | 82 | 82 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 171 | 171 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 18 | 18 | 16 | 16 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 8 | 8 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 346 | 344 | 380 | 380 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | Aythority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1110 | 1132 | 1178 | 1178 | 1427 | 1427
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 890 | 889 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 207 | 214 | 410 | 410 | 307 | 307 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 60 | 60 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 20 | 0 | 30 | 0 | 30 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 505 | 545 | 617.1 | 617.1 | 1204 | 1204 | U1 under Force Majeure Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1660 | 1703 | 2965.1 | 2935.1 | 3404 | 3374
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 619 | 617 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 999 | 1070 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 220 | 268 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.27 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 2178.27 | 2295 | 2162 | 2161 | 2092 | 2091
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 181 | 220 | 220 | 193 | 193 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 140 | 220 | 220 | 201 | 201 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 377 | 331 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 67 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.33 | 0 | 4.6 | 0 | 4.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1062.02 | 1208.22 | 1435.88 | 1435.88 | 1355 | 1355 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 38.99 | 0 | 65 | 0 | 65 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 29 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 1790.34 | 2012.22 | 2983.47 | 2813.87 | 2814.8 | 2645.2
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 49 | 50 | 50 | 50 | 50 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 154 | 157 | 160 | 160 | 155 | 155 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 41 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 1.7 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 95 | 95 | 95 | 95 | 95
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 9 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 98 | 0 | 134.34 | 0 | 134.34 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 353.7 | 414 | 620.94 | 452 | 615.94 | 447
System Total |  |  |  |  | 28565.2 | 27084.055 | 12647.51 | 13945.22 | 20842.15 | 21094.89 | 19479.94 | 19132.93
Forecast Scenario (15-07-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15456 |  | 0 |  | 15456
|  |  |  | 1:00 | 15600 |  | 0 |  | 15600
|  |  |  | 2:00 | 15050 |  | 0 |  | 15050
|  |  |  | 3:00 | 14651 |  | 0 |  | 14651
|  |  |  | 4:00 | 14451 |  | 0 |  | 14451
|  |  |  | 5:00 | 14101 |  | 0 |  | 14101
|  |  |  | 6:00 | 13653 |  | 0 |  | 13653
|  |  |  | 7:00 | 13804 |  | 0 |  | 13804
|  |  |  | 8:00 | 13822 |  | 0 |  | 13822
|  |  |  | 9:00 | 14109 |  | 0 |  | 14109
|  |  |  | 10:00 | 14262 |  | 0 |  | 14262
|  |  |  | 11:00 | 14632 |  | 0 |  | 14632
|  |  |  | 12:00 | 14717 |  | 0 |  | 14717
|  |  |  | 13:00 | 14911 |  | 0 |  | 14911
|  |  |  | 14:00 | 14497 |  | 0 |  | 14497
|  |  |  | 15:00 | 14268 |  | 0 |  | 14268
|  |  |  | 16:00 | 13636 |  | 0 |  | 13636
|  |  |  | 17:00 | 13144 |  | 0 |  | 13144
|  |  |  | 18:00 | 12978 |  | 0 |  | 12978
|  |  |  | 18:30 | 13500 |  | 0 |  | 13500
|  |  |  | 19:00 | 14486 |  | 0 |  | 14486
|  |  |  | 19:30 | 15360 |  | 0 |  | 15360
|  |  |  | 20:00 | 15290 |  | 0 |  | 15290
|  |  |  | 21:00 | 15680 |  | 0 |  | 15680
|  |  |  | 22:00 | 15480 |  | 0 |  | 15480
|  |  |  | 23:00 | 15460 |  | 0 |  | 15460
Probable Maximum Temperature: |  |  | 30.60°C
Probable Maximum Demand at Day Peak: |  |  | 14717.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15680.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12863.91 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 310.38335 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:05 hrs on 15-07-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 14-07-2025 | [28 empty] | Date: | 14-07-2025 | [28 empty] | Date: | 14-07-2025 | [28 empty] | Date: | 14-07-2025 | [28 empty] | Date: | 14-07-2025 | [11 empty] | Date: | 14-07-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [11 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 725 | 54 | 35 | 64 | 62 | 15 | 0 | 55 | 149 | 51 | 380 | 299 | 0 | 0 | 35 | 300 | 136 | 0 | 0 | 108 | 25 | 14 | 0 | 0 | 0 | 45 | 0 | 0 | 55 | 65 | 40 | 0 | 100 | 100 | 0 | 220 | 30 | 14 | 751 | 0 | 0 | 40 | 8 | 96 | 221 | 0 | 0 | 0 | 576 | 0 | 51 | 145 | 138 | 0 | 349 | 340 | 49 | 189 | 19 | 115 | 45 | 200 | 14 | 19 | 114 | 46 | 52.2 | 0 | 30 | 0 | 320 | 388 | 0 | 0 | 156 | 8 | 0 | 82 | 30 | 0 | 16 | 171 | 17 | 101 | 164 | 62 | 0 | 0 | 12 | 8457.2 | 892 | 214 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 594 | 34 | 1176.07 | 0 | 49 | 0 | 35 | 0 | 65 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 183 | 0 | 184 | 0 | 403 | 0 | 0 | 155 | 49 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 120 | 220 | 0 | 618 | 1180 | 35 | 6791.07 | 15248.27 | 98.47
01:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 724 | 54 | 35 | 46 | 0 | 0 | 0 | 55 | 152 | 38 | 380 | 294 | 0 | 0 | 35 | 300 | 137 | 0 | 0 | 70 | 25 | 21 | 0 | 0 | 0 | 45 | 0 | 0 | 42 | 65 | 40 | 0 | 100 | 100 | 0 | 204 | 31 | 16 | 748 | 0 | 0 | 40 | 0 | 97 | 220 | 0 | 0 | 0 | 572 | 0 | 51 | 145 | 127 | 0 | 353 | 340 | 50 | 172 | 17 | 92 | 45 | 200 | 17 | 19 | 114 | 46 | 0 | 0 | 30 | 0 | 320 | 372 | 0 | 0 | 155 | 8 | 0 | 82 | 30 | 0 | 16 | 171 | 17 | 84 | 164 | 63 | 0 | 0 | 12 | 8145 | 892 | 212 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 594 | 34 | 1175.52 | 0 | 49 | 0 | 35 | 0 | 65 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 182 | 0 | 183 | 0 | 383 | 0 | 0 | 157 | 49 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 120 | 220 | 0 | 618 | 1180 | 35 | 6767.52 | 14912.52 | 98.48
02:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 724 | 54 | 35 | 34 | 0 | 0 | 0 | 0 | 108 | 16 | 380 | 302 | 0 | 0 | 0 | 300 | 137 | 0 | 0 | 70 | 25 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 100 | 100 | 0 | 204 | 0 | 24 | 760 | 0 | 0 | 0 | 0 | 65 | 220 | 0 | 0 | 0 | 575 | 0 | 51 | 110 | 61 | 0 | 351 | 340 | 50 | 194 | 17 | 90 | 50 | 200 | 9 | 19 | 114 | 44 | 0 | 0 | 30 | 0 | 320 | 388 | 0 | 0 | 156 | 8 | 0 | 82 | 30 | 0 | 16 | 171 | 17 | 85 | 165 | 68 | 0 | 0 | 12 | 7631 | 892 | 213 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 592 | 0 | 1175.59 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 183 | 0 | 401 | 0 | 0 | 156 | 49 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 120 | 220 | 0 | 618 | 1175 | 0 | 6569.59 | 14200.59 | 98.49
03:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 724 | 17 | 35 | 34 | 0 | 0 | 0 | 0 | 52 | 16 | 380 | 294 | 0 | 0 | 0 | 300 | 134 | 0 | 0 | 70 | 25 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 100 | 100 | 0 | 156 | 0 | 26 | 737 | 0 | 0 | 0 | 0 | 33 | 220 | 0 | 0 | 0 | 574 | 0 | 51 | 20 | 61 | 0 | 355 | 335 | 50 | 208 | 17 | 90 | 50 | 199 | 9 | 19 | 114 | 42 | 0 | 0 | 30 | 0 | 320 | 386 | 0 | 0 | 157 | 8 | 0 | 82 | 30 | 0 | 16 | 171 | 17 | 95 | 175 | 69 | 0 | 0 | 12 | 7329 | 892 | 212 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 601 | 0 | 1176.97 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 183 | 0 | 386 | 0 | 0 | 154 | 49 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 120 | 220 | 0 | 618 | 1180 | 0 | 6533.97 | 13862.97 | 98.5
04:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 724 | 0 | 35 | 23 | 0 | 0 | 0 | 0 | 0 | 16 | 380 | 302 | 0 | 0 | 0 | 300 | 135 | 0 | 0 | 52 | 25 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 12 | 36 | 0 | 156 | 0 | 34 | 740 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 575 | 0 | 51 | 0 | 63 | 0 | 353 | 340 | 50 | 212 | 17 | 92 | 50 | 120 | 9 | 19 | 114 | 40 | 0 | 0 | 0 | 0 | 320 | 388 | 0 | 0 | 157 | 8 | 0 | 82 | 30 | 0 | 16 | 171 | 17 | 65 | 175 | 69 | 0 | 0 | 12 | 6905 | 892 | 211 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 0 | 1176.46 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 183 | 0 | 399 | 0 | 0 | 155 | 49 | 95 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 120 | 220 | 0 | 618 | 1175 | 0 | 6439.46 | 13344.46 | 98.51
05:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 724 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 380 | 289 | 0 | 0 | 0 | 300 | 136 | 0 | 0 | 52 | 25 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 12 | 0 | 156 | 0 | 34 | 714 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 541 | 0 | 51 | 0 | 63 | 0 | 353 | 335 | 50 | 217 | 17 | 82 | 50 | 120 | 9 | 19 | 49 | 40 | 0 | 0 | 0 | 0 | 320 | 364 | 0 | 0 | 151 | 8 | 0 | 81 | 30 | 0 | 16 | 173 | 17 | 45 | 135 | 69 | 0 | 0 | 12 | 6636 | 892 | 212 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 0 | 1156.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 183 | 0 | 364 | 0 | 0 | 155 | 50 | 95 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 120 | 220 | 0 | 618 | 1120 | 0 | 6206.89 | 12842.89 | 98.82
06:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 724 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 340 | 297 | 0 | 0 | 0 | 300 | 135 | 0 | 1 | 52 | 25 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0.16 | 156 | 0 | 35 | 724 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 425 | 0 | 51 | 0 | 63 | 0 | 355 | 340 | 50 | 217 | 17 | 61 | 50 | 119 | 9 | 19 | 50 | 38 | 0 | 3 | 0 | 0 | 320 | 385 | 0 | 0 | 134 | 8 | 0 | 81 | 30 | 0 | 16 | 173 | 17 | 45 | 105 | 69 | 0 | 1.07 | 12 | 6417.23 | 892 | 216 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 438 | 0 | 999.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 181 | 0 | 183 | 0 | 350 | 0 | 0.07 | 155 | 50 | 95 | 0 | 110 | 0 | 0 | 0.2 | 0 | 0.01 | 0 | 173 | 120 | 220 | 0 | 617 | 920 | 0 | 5759.45 | 12176.68 | 98.53
07:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 724 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 308 | 0 | 0 | 0 | 300 | 134 | 0 | 3 | 17 | 25 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0.14 | 156 | 0 | 30 | 762 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 422 | 0 | 51 | 0 | 63 | 0 | 350 | 340 | 50 | 216 | 17 | 64 | 50 | 85 | 9 | 20 | 33 | 34 | 0 | 5 | 0 | 0 | 320 | 395 | 0 | 0 | 146 | 8 | 0 | 81 | 30 | 0 | 16 | 173 | 17 | 45 | 85 | 69 | 0 | 6.15 | 12 | 6426.29 | 892 | 217 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1.35 | 398 | 0 | 887.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 9.45 | 0 | 0 | 181 | 0 | 183 | 0 | 414 | 0 | 0.67 | 157 | 50 | 95 | 0 | 104 | 0 | 0 | 1.1 | 2 | 0.04 | 0 | 174 | 120 | 220 | 0 | 619 | 800 | 0 | 5573.64 | 11999.93 | 98.54
08:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 292 | 0 | 0 | 0 | 335 | 199 | 0 | 4 | 17 | 26 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0.25 | 156 | 0 | 6 | 729 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 484 | 0 | 51 | 0 | 63 | 0 | 319 | 340 | 50 | 217 | 17 | 62 | 50 | 81 | 9 | 20 | 33 | 32 | 0 | 36 | 0 | 0 | 320 | 360 | 0 | 0 | 152 | 8 | 0 | 78 | 30 | 0 | 16 | 173 | 17 | 45 | 85 | 61 | 0 | 5.9 | 12 | 5951.15 | 890 | 218 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4.56 | 426 | 0 | 981.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 12.85 | 0 | 0 | 191 | 0 | 193 | 0 | 387 | 0 | 1.3 | 153 | 50 | 95 | 1 | 106 | 0 | 0 | 1.2 | 9 | 0.06 | 0 | 233 | 120 | 220 | 0 | 620 | 820 | 0 | 5797.21 | 11748.36 | 98.55
09:00 | 0 | 17 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 35 | 19 | 0 | 0 | 0 | 13 | 0 | 0 | 450 | 292 | 0 | 0 | 0 | 335 | 199 | 0 | 6 | 35 | 26 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0.32 | 161 | 0 | 6 | 720 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 562 | 0 | 51 | 0 | 63 | 0 | 300 | 340 | 47 | 194 | 19 | 64 | 50 | 80 | 9 | 20 | 30 | 30 | 0 | 26 | 0 | 0 | 320 | 326 | 0 | 0 | 137 | 8 | 0 | 78 | 30 | 0 | 16 | 173 | 17 | 45 | 105 | 62 | 1 | 6.24 | 12 | 6026.56 | 890 | 213 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9.63 | 454 | 0 | 953.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 29.59 | 0 | 0 | 192 | 0 | 197 | 0 | 385 | 0 | 1.52 | 154 | 50 | 50 | 3 | 113 | 0 | 0 | 2.1 | 23 | 0.3 | 0 | 218 | 120 | 220 | 0 | 619 | 838 | 0 | 5784.72 | 11811.28 | 98.56
10:00 | 0 | 17 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 35 | 47 | 0 | 0 | 0 | 35 | 5 | 0 | 450 | 302 | 0 | 0 | 0 | 335 | 198 | 0 | 10 | 35 | 26 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 7 | 24 | 0.87 | 161 | 0 | 2 | 775 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 580 | 5 | 43 | 0 | 63 | 0 | 326 | 340 | 47 | 207 | 19 | 64 | 50 | 80 | 9 | 20 | 32 | 28 | 0 | 21 | 0 | 0 | 320 | 340 | 0 | 0 | 138 | 8 | 0 | 79 | 30 | 0 | 16 | 173 | 17 | 45 | 105 | 61 | 1 | 15.8 | 12 | 6245.67 | 890 | 210 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12.73 | 453 | 0 | 973.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 36.42 | 0 | 0 | 190 | 0 | 196 | 0 | 385 | 0 | 2.77 | 158 | 50 | 0 | 9 | 70 | 0 | 0 | 0.6 | 94 | 0.4 | 0 | 223 | 120 | 220 | 0 | 619 | 838 | 0 | 5836.73 | 12082.4 | 98.57
11:00 | 0 | 17 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 35 | 52 | 0 | 0 | 0 | 35 | 35 | 0 | 450 | 296 | 0 | 0 | 0 | 335 | 198 | 0 | 6 | 35 | 25 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 12 | 24 | 0 | 161 | 0 | 2 | 735 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 580 | 14 | 43 | 0 | 63 | 0 | 353 | 340 | 48 | 200 | 19 | 65 | 50 | 79 | 10 | 20 | 30 | 30 | 0 | 2 | 0 | 0 | 320 | 340 | 0 | 0 | 137 | 8 | 0 | 81 | 30 | 0 | 16 | 172 | 17 | 45 | 105 | 28 | 1 | 2.72 | 12 | 6200.72 | 890 | 206 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 28 | 447 | 0 | 1063.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 27.26 | 0 | 0 | 164 | 0 | 140 | 0 | 364 | 0 | 2.61 | 154 | 50 | 0 | 18 | 49 | 0 | 0 | 1.8 | 175 | 0.36 | 0 | 221 | 120 | 220 | 0 | 617 | 955 | 0 | 6037.73 | 12238.45 | 98.58
12:00 | 0 | 52 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311 | 35 | 35 | 52 | 0 | 0 | 0 | 35 | 108 | 0 | 450 | 288 | 0 | 0 | 0 | 335 | 199 | 0 | 11 | 35 | 25 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 24 | 48 | 2.32 | 161 | 0 | 4 | 762 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 580 | 8 | 43 | 0 | 63 | 0 | 350 | 340 | 47 | 203 | 19 | 91 | 50 | 80 | 9 | 8 | 32 | 30 | 0 | 54 | 0 | 0 | 320 | 346 | 0 | 0 | 138 | 8 | 0 | 81 | 30 | 0 | 16 | 171 | 17 | 45 | 105 | 33 | 1 | 30.88 | 12 | 6665.2 | 890 | 207 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 20 | 505 | 0 | 1062.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 38.99 | 0 | 0 | 140 | 0 | 140 | 0 | 377 | 0 | 3.33 | 154 | 50 | 0 | 9 | 41 | 0 | 0 | 1.7 | 98 | 0.27 | 0 | 220 | 120 | 220 | 0 | 619 | 999 | 0 | 5982.31 | 12647.51 | 98.59
13:00 | 0 | 52 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 54 | 35 | 52 | 0 | 0 | 0 | 35 | 155 | 0 | 450 | 299 | 0 | 0 | 0 | 335 | 200 | 0 | 16 | 17 | 25 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 24 | 48 | 3.97 | 161 | 0 | 9 | 721 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 572 | 8 | 51 | 10 | 63 | 0 | 300 | 280 | 48 | 198 | 19 | 96 | 50 | 91 | 9 | 8 | 33 | 34 | 0 | 35 | 0 | 0 | 320 | 366 | 0 | 0 | 154 | 8 | 0 | 80 | 30 | 0 | 16 | 171 | 17 | 45 | 105 | 33 | 2 | 26.57 | 12 | 6619.54 | 890 | 209 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 8 | 522 | 0 | 1069.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 40.46 | 0 | 0 | 140 | 0 | 140 | 0 | 356 | 0 | 5.87 | 153 | 50 | 35 | 22 | 64 | 0 | 0 | 4.7 | 211 | 0.26 | 0 | 171 | 120 | 220 | 0 | 619 | 1075 | 0 | 6208.37 | 12827.91 | 98.6
14:00 | 0 | 52 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 54 | 35 | 52 | 0 | 0 | 0 | 35 | 162 | 0 | 450 | 306 | 0 | 0 | 0 | 335 | 136 | 0 | 7 | 17 | 25 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 31 | 0 | 24 | 48 | 0.36 | 201 | 0 | 9 | 743 | 0 | 0 | 0 | 6 | 0 | 221 | 0 | 0 | 0 | 578 | 11 | 51 | 0 | 63 | 0 | 300 | 280 | 48 | 201 | 19 | 103 | 45 | 100 | 9 | 12 | 46 | 34 | 0 | 15 | 0 | 0 | 320 | 371 | 0 | 0 | 139 | 0 | 0 | 80 | 30 | 0 | 16 | 171 | 17 | 45 | 105 | 33 | 2 | 45.54 | 12 | 6678.9 | 890 | 208 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 509 | 0 | 1068.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 31.55 | 0 | 0 | 140 | 0 | 140 | 0 | 364 | 0 | 2.67 | 153 | 50 | 35 | 13 | 70 | 0 | 0 | 4.9 | 113 | 0.41 | 0 | 172 | 120 | 180 | 0 | 619 | 1100 | 0 | 6082.43 | 12761.33 | 98.61
15:00 | 0 | 52 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 54 | 35 | 52 | 0 | 0 | 0 | 35 | 155 | 0 | 450 | 309 | 0 | 0 | 0 | 331 | 135 | 0 | 4 | 17 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 37 | 0 | 24 | 48 | 1.59 | 195 | 0 | 3 | 740 | 0 | 0 | 0 | 8 | 0 | 220 | 0 | 0 | 0 | 578 | 8 | 51 | 0 | 63 | 0 | 300 | 280 | 47 | 204 | 19 | 101 | 45 | 100 | 9 | 20 | 48 | 34 | 0 | 15 | 28 | 0 | 320 | 380 | 0 | 0 | 139 | 8 | 0 | 77 | 30 | 0 | 16 | 171 | 17 | 45 | 85 | 33 | 0 | 15.35 | 12 | 6665.94 | 890 | 208 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 506 | 0 | 1069.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 13.06 | 0 | 0 | 140 | 0 | 140 | 0 | 376 | 0 | 0 | 149 | 49 | 35 | 20 | 70 | 0 | 0 | 5.9 | 79 | 0.24 | 0 | 172 | 120 | 180 | 0 | 618 | 1096 | 0 | 5999.96 | 12665.9 | 98.62
16:00 | 0 | 52 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 54 | 35 | 52 | 0 | 0 | 0 | 47 | 152 | 0 | 450 | 304 | 0 | 0 | 0 | 330 | 135 | 0 | 7 | 17 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 62 | 0 | 24 | 48 | 0.94 | 195 | 0 | 6 | 727 | 0 | 0 | 0 | 8 | 0 | 219 | 0 | 0 | 0 | 577 | 7 | 51 | 0 | 63 | 0 | 300 | 280 | 45 | 199 | 19 | 101 | 45 | 100 | 9 | 20 | 47 | 26 | 0 | 3 | 29 | 0 | 320 | 365 | 0 | 0 | 140 | 8 | 0 | 77 | 30 | 0 | 16 | 171 | 17 | 45 | 85 | 33 | 1 | 12.82 | 12 | 6636.76 | 890 | 208 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9 | 500 | 0 | 1062.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 22.03 | 0 | 0 | 140 | 0 | 140 | 0 | 354 | 0 | 1.67 | 154 | 48 | 35 | 19 | 70 | 0 | 0 | 5 | 62 | 0.13 | 0 | 172 | 120 | 180 | 0 | 618 | 1060 | 0 | 5926.39 | 12563.15 | 98.63
17:00 | 0 | 52 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 54 | 35 | 52 | 0 | 0 | 0 | 53 | 90 | 0 | 450 | 300 | 0 | 0 | 0 | 331 | 135 | 0 | 4 | 17 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 70 | 0 | 24 | 48 | 0.29 | 195 | 0 | 12 | 720 | 0 | 0 | 0 | 8 | 0 | 219 | 0 | 0 | 0 | 520 | 2 | 51 | 0 | 63 | 0 | 351 | 340 | 43 | 197 | 19 | 68 | 50 | 100 | 12 | 20 | 48 | 22 | 0 | 1 | 29 | 0 | 320 | 359 | 0 | 10 | 144 | 8 | 0 | 80 | 30 | 0 | 16 | 171 | 17 | 45 | 75 | 33 | 0 | 11.3 | 12 | 6586.59 | 890 | 208 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4 | 427 | 0 | 910.01 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 9.47 | 0 | 0 | 140 | 0 | 140 | 0 | 348 | 0 | 0.96 | 155 | 48 | 35 | 0 | 70 | 0 | 0 | 2.7 | 19 | 0.09 | 0 | 170 | 120 | 220 | 0 | 617 | 900 | 0 | 5528.23 | 12114.82 | 98.64
18:00 | 0 | 52 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 54 | 36 | 52 | 0 | 0 | 0 | 53 | 83 | 0 | 400 | 306 | 0 | 0 | 0 | 300 | 136 | 0 | 1 | 17 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 78 | 0 | 24 | 48 | 0.1 | 206 | 0 | 14 | 730 | 0 | 0 | 0 | 8 | 0 | 219 | 0 | 0 | 0 | 533 | 0 | 51 | 0 | 63 | 0 | 352 | 340 | 44 | 200 | 19 | 65 | 50 | 100 | 28 | 20 | 47 | 26 | 0 | 0 | 29 | 0 | 320 | 312 | 0 | 10 | 153 | 8 | 0 | 80 | 30 | 0 | 16 | 171 | 17 | 45 | 78 | 33 | 0 | 1.22 | 12 | 6490.32 | 890 | 211 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 400 | 0 | 923.65 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.92 | 0 | 0 | 140 | 0 | 140 | 0 | 354 | 0 | 0.15 | 156 | 48 | 35 | 0 | 70 | 0 | 0 | 1 | 7 | 0.03 | 0 | 172 | 100 | 220 | 0 | 617 | 850 | 0 | 5423.75 | 11914.07 | 98.65
19:00 | 0 | 70 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 54 | 54 | 55 | 62 | 0 | 0 | 53 | 80 | 10 | 350 | 302 | 0 | 0 | 17 | 328 | 136 | 0 | 0 | 108 | 19 | 22 | 0 | 0 | 0 | 15 | 0 | 0 | 26 | 67 | 76 | 0 | 24 | 100 | 0 | 206 | 4 | 16 | 758 | 0 | 0 | 3 | 8 | 7 | 218 | 0 | 0 | 0 | 550 | 0 | 51 | 35 | 63 | 0 | 300 | 340 | 44 | 206 | 19 | 67 | 50 | 110 | 27 | 20 | 101 | 28 | 25 | 0 | 29 | 0 | 320 | 366 | 0 | 10 | 155 | 8 | 0 | 81 | 30 | 0 | 16 | 171 | 17 | 102 | 125 | 49 | 0 | 0 | 12 | 7118 | 890 | 215 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 6 | 1054.56 | 0 | 48 | 0 | 8 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 376 | 0 | 0 | 154 | 49 | 90 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 224 | 100 | 180 | 0 | 617 | 890 | 0 | 5797.56 | 12915.56 | 98.66
19:30 | 0 | 70 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 54 | 54 | 70 | 62 | 0 | 0 | 53 | 79 | 24 | 420 | 301 | 0 | 0 | 17 | 335 | 201 | 0 | 0 | 108 | 20 | 22 | 0 | 0 | 0 | 15 | 0 | 0 | 33 | 67 | 76 | 0 | 60 | 100 | 0 | 218 | 15 | 12 | 715 | 0 | 0 | 14 | 8 | 14 | 217 | 0 | 0 | 0 | 567 | 0 | 51 | 115 | 90 | 0 | 354 | 340 | 44 | 194 | 19 | 85 | 50 | 165 | 27 | 20 | 100 | 26 | 43 | 0 | 30 | 0 | 320 | 356 | 0 | 10 | 154 | 8 | 0 | 81 | 30 | 0 | 16 | 171 | 17 | 92 | 181 | 49 | 0 | 0 | 12 | 7614 | 890 | 215 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 492 | 17 | 1124.87 | 0 | 50 | 0 | 35 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 140 | 0 | 345 | 0 | 0 | 158 | 50 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 100 | 220 | 0 | 617 | 1040 | 0 | 6241.87 | 13855.87
20:00 | 0 | 70 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 49 | 54 | 70 | 48 | 0 | 0 | 35 | 54 | 30 | 420 | 291 | 0 | 0 | 17 | 335 | 204 | 0 | 0 | 108 | 24 | 22 | 0 | 0 | 0 | 15 | 0 | 0 | 18 | 67 | 8 | 0 | 60 | 100 | 0 | 218 | 14 | 15 | 725 | 0 | 0 | 15 | 8 | 15 | 217 | 0 | 0 | 0 | 550 | 0 | 51 | 115 | 107 | 0 | 356 | 340 | 47 | 183 | 19 | 82 | 50 | 160 | 29 | 20 | 99 | 26 | 43 | 0 | 30 | 0 | 320 | 344 | 0 | 10 | 152 | 8 | 0 | 81 | 30 | 0 | 16 | 171 | 17 | 94 | 193 | 49 | 0 | 0 | 12 | 7521 | 889 | 214 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 545 | 17 | 1208.22 | 0 | 50 | 0 | 35 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 140 | 0 | 331 | 0 | 0 | 157 | 49 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 268 | 120 | 220 | 0 | 617 | 1070 | 0 | 6424.22 | 13945.22 | 98.67
21:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 17 | 35 | 55 | 32 | 0 | 0 | 0 | 17 | 32 | 450 | 313 | 0 | 0 | 0 | 332 | 199 | 0 | 0 | 108 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 66 | 0 | 0 | 60 | 60 | 0 | 213 | 0 | 22 | 770 | 0 | 0 | 0 | 8 | 0 | 217 | 0 | 0 | 0 | 583 | 0 | 51 | 30 | 108 | 0 | 352 | 340 | 48 | 209 | 19 | 68 | 50 | 178 | 29 | 20 | 102 | 26 | 52.2 | 0 | 31 | 0 | 320 | 396 | 0 | 10 | 152 | 8 | 0 | 81 | 30 | 0 | 16 | 171 | 17 | 65 | 165 | 49 | 0 | 0 | 12 | 7305.2 | 890 | 216 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 584 | 0 | 1233 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 140 | 0 | 414 | 0 | 0 | 157 | 49 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 120 | 220 | 0 | 617 | 1100 | 0 | 6517 | 13822.2 | 98.68
22:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 35 | 52 | 32 | 0 | 0 | 0 | 17 | 23 | 450 | 312 | 0 | 0 | 0 | 335 | 201 | 0 | 0 | 108 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 65 | 0 | 0 | 60 | 60 | 0 | 214 | 0 | 22 | 740 | 0 | 0 | 0 | 8 | 0 | 217 | 0 | 0 | 0 | 575 | 0 | 51 | 0 | 108 | 0 | 353 | 335 | 48 | 193 | 19 | 67 | 50 | 189 | 29 | 20 | 104 | 28 | 52.2 | 0 | 31 | 0 | 320 | 388 | 0 | 10 | 160 | 8 | 0 | 81 | 30 | 0 | 16 | 171 | 17 | 65 | 165 | 49 | 0 | 0 | 12 | 7200.2 | 890 | 187 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 573 | 0 | 1219 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 140 | 0 | 414 | 0 | 0 | 160 | 50 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 120 | 220 | 0 | 617 | 1180 | 0 | 6542 | 13742.2 | 98.69
23:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 35 | 52 | 32 | 0 | 0 | 0 | 52 | 16 | 450 | 312 | 0 | 0 | 0 | 335 | 199 | 0 | 0 | 108 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 60 | 0 | 0 | 60 | 60 | 0 | 214 | 0 | 22 | 770 | 0 | 0 | 0 | 8 | 0 | 217 | 0 | 0 | 0 | 579 | 0 | 51 | 0 | 61 | 0 | 351 | 335 | 48 | 208 | 19 | 68 | 45 | 182 | 29 | 20 | 111 | 26 | 52.2 | 0 | 31 | 0 | 320 | 390 | 0 | 10 | 159 | 8 | 0 | 81 | 30 | 0 | 16 | 171 | 17 | 65 | 165 | 50 | 0 | 0 | 12 | 7236.2 | 890 | 188 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 582 | 0 | 1227 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 140 | 0 | 414 | 0 | 0 | 160 | 50 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 120 | 220 | 0 | 617 | 1244 | 0 | 6625 | 13861.2 | 98.7
Total KWH | 0 | 1213440 | 838080 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10420490 | 583920 | 905040 | 1044864 | 262080 | 8029 | 0 | 579278 | 1658880 | 250560 | 9886000 | 7297775 | 0 | 0 | 90143 | 7759158 | 4144000 | 0 | 82180 | 1312800 | 587400 | 436680 | 0 | 0 | 0 | 95345 | 0 | 0 | 730560 | 402859 | 426144 | 0 | 2676480 | 1202880 | 11086 | 4343882 | 90300 | 397920 | 17883636.36 | 0 | 0 | 83520 | 96721.2 | 291055 | 5132487 | 0 | 0 | 0 | 13270907 | 67095 | 1188623 | 580436 | 1756363 | 0 | 8458800 | 7990000 | 1141920 | 4938000 | 452160 | 1930560 | 1172430 | 3142080 | 354480 | 429080 | 1656420 | 770880 | 290160 | 197173 | 351328 | 0 | 7667500 | 9124000 | 0 | 65520 | 3573573 | 169728 | 0 | 1915200 | 719136 | 0 | 392000 | 3529540 | 427680 | 1437600 | 3050400 | 1143360 | 9200 | 183910 | 298800 | 167071714.56 | 21557818 | 5143104 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 100080 | 12356360 | 66240 | 26049219 | 0 | 420010 | 0 | 281472 | 0 | 248528 | 0 | 33097 | 0 | 325730 | 48165 | 259496 | 0 | 0 | 4343900 | 0 | 4156900 | 0 | 9134764 | 0 | 20340 | 3797000 | 1154181 | 1594461 | 128190 | 2291568 | 0 | 0 | 32087.64 | 935280 | 2353 | 0 | 5345000 | 2840000 | 5374640 | 0 | 14843636 | 25435636.36 | 58800 | 149290056 | 316361770.56

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 14-07-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12647.51 | MW | 12:00 Hr. | Energy Generated |  |  | 316.3618 |  | MKWHr.
| Day Peak Demand |  |  | 12647.51 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.386 |  | MKWHr.
| Evening Peak Generation |  |  | 13945.22 | MW | 20:00 Hr. | Energy Demand |  |  | 316.7478 |  | MKWHr.
| Evening Peak Demand |  |  | 13945.22 | MW | 20:00 Hr. | Maximum Temperature |  |  | 31.6 |  | °C
| Minimum Generation of the Day |  |  | 11748.36 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 958.17 |  | MMCFD
| Maximum Generation of the Day |  |  | 15248.27 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.9302 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.5315 | 0 | 8.7471 | 0 | 0 | 0.08218 | 0 | 0 | 49.3608 | Gas | 132.8822 | Gas | 452372462.3
| Chattogram Zone |  |  | 5.5304 | 31.1545 | 5.3653 | 0 | 4.3439 | 0.078181 | 0 | 0.73056 | 47.2029 | Coal | 94.0864 | Coal | 532607694.948
| Cumilla Zone |  |  | 27.5274 | 0 | 8.3055 | 0 | 0 | 0.19717 | 0.77088 | 0 | 36.8009 | HFO | 32.6747 | HFO | 605241936.044
| Mymensingh Zone |  |  | 1.1434 | 0 | 5.2145 | 0 | 0 | 0.19311 | 0 | 0 | 6.551 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.1562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.1562 | Hydro | 4.3439 | Hydro | 434388.2
| Khulna Zone |  |  | 5.1431 | 12.3564 | 0.06624 | 0 | 0 | 0.10008 | 22.4698 | 0 | 40.1356 | Solar | 2.3542 | Solar | 38965301.7004
| Barishal Zone |  |  | 8.2146 | 45.6243 | 0.0588 | 0 | 0 | 0.002353 | 0 | 0 | 53.9001 | Import | 49.2899 | Import | 235768176.84
| Rajshahi Zone |  |  | 17.6356 | 0 | 1.0313 | 0 | 0 | 0.60557 | 26.0492 | 0 | 45.3216 | Wind | 0.73056 | Wind | 10695398.4
| Rangpur Zone |  |  | 0 | 4.9512 | 3.886 | 0 | 0 | 1.0956 | 0 | 0 | 9.9328
| Total |  |  | 132.8822 | 94.0864 | 32.6747 | 0 | 4.3439 | 2.3542 | 49.2899 | 0.73056 | 316.3618
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 452372462.3 |  | Hydro | 434388.2
|  |  |  | Coal | 532607694.948 |  | Solar | 38965301.7004
|  |  |  | HFO | 605241936.044 |  | Import | 235768176.84
|  |  |  | HSD | 0 |  | Wind | 10695398.4
[5 empty] | Total: | 187,60,85,358 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5578 | Peak Hr Flow | 889.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 51374581.92 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.0492 | Peak Hr Flow | 1208.22 MW at 20:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 964 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.77088 | Peak Hr Flow | 26.00 MW at 20:00 hrs.
Maximum Power Flow: |  |  | MW: | 1032 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 48.3779 | Peak Hr Flow | 2123.22 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5007
|  |  |  | Chattogram |  | 0 |  | 1361
|  |  |  | Cumilla |  | 0 |  | 1266
|  |  |  | Mymensingh |  | 0 |  | 1163
|  |  |  | Sylhet |  | 0 |  | 644
|  |  |  | Khulna |  | 0 |  | 1319
|  |  |  | Barishal |  | 0 |  | 422
|  |  |  | Rajshahi |  | 0 |  | 1329
|  |  |  | Rangpur |  | 0 |  | 934
|  |  |  | Total |  | 0 |  | 13445
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Bibiana-II 341 MW CCPP (Summit) GT |  |  | 222 | 3 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
|  | 4 | Bibiana-II 341 MW CCPP (Summit) ST |  |  | 119
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 641 |  |  |  | Total | 476
|  |  |  | Total Unavailable Capacity |  |  |  | 1117
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:19 | 13:59 | Bogura 132/33kV S/S Transformer-3 LT Scheduled S/D Due to Junction point temperature high | [7 empty] | 15.0MW load
|  |  | (red hot) | [7 empty] | interrup.
| 08:19 | 13:59 | Bogura 132/33kV S/S Transformer-3 HT Scheduled S/D Due to Junction point temperature high | [7 empty] | 15.0MW load
|  |  | (red hot) | [7 empty] | interrup.
| 08:42 | 08:48 | Palashbari 132/33kV S/S TR1-414T LT Tripped showing MiCOM P142 relays Due to ডুগডুগি ৩৩ | [7 empty] | 46.0MW load
|  |  | কেভি ফিডার চালু করার সময় T-1 & T-2 ৩৩ কেভি ইনকামার-১ এবং ইনকামার-২ ট্রিপ করে। | [7 empty] | interrup.
| 08:42 | 08:48 | Palashbari 132/33kV S/S TR2-404T LT Tripped showing MiCOM P142 relays Due to ডুগডুগি ৩৩ | [7 empty] | 46.0MW load
|  |  | কেভি ফিডার চালু করার সময় T-1 & T-2 ৩৩ কেভি ইনকামার-১ এবং ইনকামার-২ ট্রিপ করে। | [7 empty] | interrup.
| 08:45 | 09:39 | Purbasadipur 132/33kV S/S T-3 Transformer (423T) LT Scheduled S/D Due to B ph boosing | [7 empty] | 20.0MW load
|  |  | redhot LT side | [7 empty] | interrup.
| 08:45 | 09:39 | Purbasadipur 132/33kV S/S T-3 Transformer (423T) HT Scheduled S/D Due to Red hot LT side | [7 empty] | 20.0MW load
|  |  | B ph | [7 empty] | interrup.
| 10:12 |  | Bibiana 400/230kV S/S Summit STG Scheduled S/D
| 10:38 | 18:27 | Bogura 400/230kV S/S ATR-01 HT Scheduled S/D Due to Painting work by STGEP project.
| 10:38 | 18:27 | Bogura 400/230kV S/S ATR-01 LT Scheduled S/D Due to Painting work by STGEP project
| 12:00 |  | Day Peak Generation: 12644 MW.
| 12:38 | 20:18 | Shahjibazar 132/33kV S/S TR-02 LT Scheduled S/D Due to Tr-02 Tripping fault maintenance
| 12:40 | 20:16 | Shahjibazar 132/33kV S/S TR-02 HT Scheduled S/D Due to Tr-02 Tripping fault maintenance
| 12:56 | 14:40 | Khulna (C) S/S Tr-2 415 T HT Tripped showing No Relay pickup relays Due to Due to 33kv
Shiromoni-2 faulty
| 12:56 | 14:41 | Khulna (C) S/S Tr-2 415 T LT Tripped showing 50G ( inst E/F) But Not Trip relays Due to
Due to 33kv Shiromoni-2 Faulty
| 13:14 |  | Raozan 25 MW PP Synchronized
| 15:20 |  | Rampal 400/230kV S/S Generator Transformer-1 (GT-1) HT Project Work S/D Due to Permit
taken Against PTW 19555
| 15:25 | 18:36 | Jashore 132/33kV S/S T-1 LT Tripped showing O/C, E/F relays Due to Trip
|  | 17:50 | Mahasthangar-Palashbari 132kV Ckt-1 is restored.
|  | 17:50 | Mithapukur-Palashbari 132kV Ckt-1 is restored.
|  | 17:50 | Mithapukur-Palashbari 132kV Ckt-2 is restored.
|  | 17:56 | Shahjibazar-Sreemangal 132kV Ckt-2 is restored.
| 19:03 | 22:59 | Mahasthangar-Palashbari 132kV Ckt-2 Project Work S/D from Mahasthangarh 132/33kV end Due
to Line Load test of project work .
| 19:36 | 00:15 | Chapai 132/33kV S/S T-2 (415T) LT Forced S/D Due to Red hot maintenance.
| 20:00 |  | Evening Peak Generation 13945 MW.
| 20:20 | 00:13 | Chapai 132/33kV S/S T-2 (415T) HT Forced S/D Due to Red hot maintenance.
| 21:48 | 23:05 | Jaldhaka 132/33kV S/S 406T-1 LT Forced S/D Due to 33 KV Domar-2 feeder red hot | [7 empty] | 25.0MW load
|  |  | maintenance work. | [7 empty] | interrup.
| 21:50 | 23:03 | Jaldhaka 132/33kV S/S 406T-1 HT Forced S/D Due to 33 kv Domar-2 feeder red hot | [7 empty] | 25.0MW load
|  |  | maintenance work. | [7 empty] | interrup.
| 02:28 |  | Raozan 25 MW PP Shutdown
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 14-07-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9886000 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 291 | 7297775 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 204 | 4144000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7759158 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 49 | 583920 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 48 | 262080 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 579278 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 90143 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 24 | 587400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 436680 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 43 | 838080 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 8029 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 70 | 1044864 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1213440 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 30 | 250560 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 1658880 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 82180 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 905040 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 348 | 10420490 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 1312800 | Engine Problem
Dhaka Area Total |  |  |  |  | 5939.724 | 2222 | 49360797
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 96721.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 67095 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 15 | 83520 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 218 | 4343882 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5132487 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 15 | 291055 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 8 | 426144 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 67 | 402859 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 60 | 2676480 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 15 | 397920 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 11086 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 95345 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 14 | 90300 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1202880 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 550 | 13270907 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 18 | 730560 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 725 | 17883636.36 | FGMO
Chattogram Area Total |  |  |  |  | 4895.72 | 2045 | 47202877.56
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 183 | 4938000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 356 | 8458800 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 7990000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 19 | 452160 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 47 | 1141920 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 107 | 1756363 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1188623 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 115 | 580436 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 30 | 351328 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1172430 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 160 | 3142080 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 26 | 770880 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 290160 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 429080 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 99 | 1656420 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 29 | 354480 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 82 | 1930560 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 197173 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1757 | 36800893
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 49 | 1143360 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9200 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 193 | 3050400 | Engine Problem
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 94 | 1437600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 183910 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 298800 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 427680 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 365 | 6550950
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 10 | 65520 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3573573 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 719136 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1915200 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 171 | 3529540 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 392000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 169728 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | -
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 344 | 9124000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7667500 | Aythority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2325 | 1132 | 27156197
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 889 | 21557818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 214 | 5143104 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 66240 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 100080 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 545 | 12356360 | U1 under Force Majeure Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1703 | 40135602
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 617 | 14843636 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2840000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1070 | 25435636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5374640 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 58800 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 268 | 5345000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2353 | -
Barishal Area Total |  |  |  |  | 2236 | 2295 | 53900065.36
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 420010 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 33097 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 181 | 4343900 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 140 | 4156900 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 331 | 9134764 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 48165 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 67 | 248528 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 281472 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 20340 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1208.22 | 26049219 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 259496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 325730 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2012.22 | 45321621
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 49 | 1154181 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 157 | 3797000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 2291568 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 32087.64 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 1594461 | Schedule Maintenance
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 128190 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 935280 | -
Rangpur Area Total |  |  |  |  | 950 | 414 | 9932767.64
Eastern Grid Total |  |  |  |  | 16705.895 | 7521 | 167071714.56
Western Grid Total |  |  |  |  | 10378.16 | 6424.22 | 149290056
National Grid Total |  |  |  |  | 27084.055 | 13945.22 | 316361770.56
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 14-07-2025
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9441.44 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4004.1 | MW
i) Dhaka area |  |  | 5007.43 |  | MW | i) Khulna area |  |  |  | 1319 | MW
ii) Chattogram area |  |  | 1361 |  | MW | ii) Barishal area |  |  |  | 422.1 | MW
iii) Cumilla area |  |  | 1266.01 |  | MW | iii) Rajshahi area |  |  |  | 1329 | MW
iv) Mymensingh area |  |  | 1163 |  | MW | iv) Rangpur area |  |  |  | 934 | MW
v) Sylhet area |  |  | 644 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13445.54 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 77 | 00:00 | 133 | Pabna | 118 | 00:00
2 | AKSML | 138 | 17:00 | 68 | Ishurdi | 79 | 00:00 | 134 | Palashbari | 128 | 00:00
3 | Aftabnagar | 36 | 00:00 | 69 | Jaldhaka | 82 | 02:00 | 135 | Panchagarh | 61 | 22:00
4 | Agargaon | 125 | 12:00 | 70 | Jamalpur | 141 | 00:00 | 136 | Patuakhali | 62.4 | 21:00
5 | Agrabad | 88 | 16:00 | 71 | Jashore | 122 | 00:00 | 137 | Payra | 30 | 22:00
6 | Amnura | 43 | 00:00 | 72 | Jhenaidah | 112 | 00:00 | 138 | Postogola | 57 | 12:00
7 | Ashuganj | 103 | 00:00 | 73 | Joydebpur | 135 | 09:00 | 139 | Purbachal | 21 | 00:00
8 | BSRM | 184 | 07:00 | 74 | Joypurhat | 72 | 00:00 | 140 | Purbasadipur | 140 | 20:00
9 | Bagerhat | 77 | 00:00 | 75 | Juldah | 16 | 00:00 | 141 | Rahanpur | 30 | 00:00
10 | Bajitpur | 60 | 00:00 | 76 | KSRM | 29 | 21:00 | 142 | Rahim | 28 | 11:00
11 | Bakulia | 90 | 19:00 | 77 | Kabirpur | 228 | 11:00 | 143 | Rajbari | 78 | 00:00
12 | Banani | 36 | 12:00 | 78 | Kachua | 88 | 00:00 | 144 | Rajendrapur | 135 | 00:00
13 | Bangabhaban | 16 | 10:00 | 79 | Kallyanpur | 117 | 00:00 | 145 | Rajshahi | 117 | 23:00
14 | Barapukuria | 66 | 22:00 | 80 | Kalurghat | 38 | 15:00 | 146 | Rajshahi-230 | 91 | 00:00
15 | Barguna | 22 | 22:00 | 81 | Kamrangirchar | 70.3 | 13:00 | 147 | Ramganj | 108 | 00:00
16 | Barishal | 109 | 14:00 | 82 | Kaptai | N/A | N/A | 148 | Rampur | 41 | 00:00
17 | Barishal-230 | 88 | 19:00 | 83 | Kasba | 34 | 00:00 | 149 | Rangamati | 16 | 19:00
18 | Baroaulia | 59 | 14:00 | 84 | Kazla | 94 | 15:00 | 150 | Rangpur | 149 | 21:00
19 | Baroirhat | 60 | 00:00 | 85 | Keranigonj | 90 | 00:00 | 151 | Ruppur | 7 | 10:00
20 | Bashundhara | 186 | 12:00 | 86 | Khagrachori | 32 | 20:00 | 152 | SSM | 14 | 01:00
21 | BashundharaCement | 13 | 09:00 | 87 | Khulna | 66 | 13:00 | 153 | Saidpur | 116 | 00:00
22 | Beanibazar | 90 | 00:00 | 88 | Khulshi | 146 | 20:00 | 154 | Satkhira | 120 | 00:00
23 | Benapole | 63 | 00:00 | 89 | Kishoreganj | 135 | 22:00 | 155 | Satmasjid | 82 | 00:00
24 | Bhaluka | 147 | 00:00 | 90 | Kodda | 315 | 11:00 | 156 | Savar | 225 | 16:00
25 | Bhandaria | 59 | 00:00 | 91 | Kulaura | 54 | 00:00 | 157 | SevenRings | 11.29 | 17:00
26 | Bhangura | 38 | 00:00 | 92 | Kurigram | 62 | 20:00 | 158 | ShahCement | 16 | 00:00
27 | Bheramara(GK) | 67 | 00:00 | 93 | Kushtia | 150 | 00:00 | 159 | Shahjadpur | 85 | 00:00
28 | Bhulta | 253 | 23:00 | 94 | Lakshmipur | 31 | 00:00 | 160 | Shahjibazar | 126 | 00:00
29 | Bog-Sherpur | 76 | 00:00 | 95 | Lalbag | 56 | 12:00 | 161 | Shahmirpur | 64 | 00:00
30 | Bogura | 173 | 21:00 | 96 | Lalmonirhat | 60 | 22:00 | 162 | Shariatpur | 84 | 00:00
31 | Borhanuddin | 84 | 22:00 | 97 | MI_Cement | 14.8 | 03:00 | 163 | Sherpur | 174 | 00:00
32 | Brahmanbaria | 134 | 00:00 | 98 | Madanganj | 38 | 00:00 | 164 | Shikalbaha | 16 | 17:00
33 | Cantonment | 146 | 11:00 | 99 | Madaripur | 105 | 00:00 | 165 | Shitalakhya | 81.9 | 12:00
34 | Chandina | 13.41 | 14:00 | 100 | Madartek | 91.65 | 00:00 | 166 | Sholosohor | 43 | 12:00
35 | Chandpur | 78 | 00:00 | 101 | Madunaghat | 54 | 00:00 | 167 | Shyampur | 140 | 00:00
36 | Chandraghona | 35 | 19:30 | 102 | Magura | 58 | 00:00 | 168 | Siddhirganj | 110 | 12:00
37 | Chapai | 69 | 00:00 | 103 | Mahasthangarh | 96 | 00:00 | 169 | Sirajganj | 111 | 01:00
38 | Charsaidpur | 39 | 00:00 | 104 | Maijdee | 14 | 00:00 | 170 | Sonargaon | 107 | 00:00
39 | Chauddagram | 72 | 00:00 | 105 | Manikganj | 120 | 22:00 | 171 | Sreemongol | 88 | 00:00
40 | Chhatak | 46 | 00:00 | 106 | Maniknagar | 80 | 13:00 | 172 | Sreepur | 102 | 12:00
41 | Chowmuhani | 180 | 00:00 | 107 | Matarbari | 48 | 19:30 | 173 | Srinagar | 46 | 00:00
42 | Chuadanga | 104 | 00:00 | 108 | Matuail | 63 | 10:00 | 174 | Sunamganj | 65 | 23:00
43 | Coxsbazar | 128 | 22:00 | 109 | Millgate | 88 | 15:00 | 175 | Sylhet | 56 | 00:00
44 | Cumilla(N) | 142 | 00:00 | 110 | Mirpur | 117 | 15:00 | 176 | Sylhet-132 | 141 | 19:00
45 | Cumilla(S) | 168 | 00:00 | 111 | Mirsorai | 10 | 15:00 | 177 | TK | 35 | 00:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirzapur | 43 | 00:00 | 178 | Tangail | 186 | 00:00
47 | Daudkandi | 142 | 00:00 | 113 | Mithapukur | 70 | 04:00 | 179 | Taraganj | 23 | 04:00
48 | Dhaka | 70 | 12:00 | 114 | Modern | N/A | N/A | 180 | Thakurgaon | 110 | 03:00
49 | Dhamrai | 124 | 00:00 | 115 | Mogbazar | 148 | 13:00 | 181 | Tongi | 116 | 15:00
50 | Dhanmondi | 136 | 12:00 | 116 | Mongla | 30 | 00:00 | 182 | Ullahpara | 39 | 00:00
51 | Dohazari | 108 | 00:00 | 117 | Motijheel | 41 | 12:00 | 183 | Ullon | 40 | 00:00
52 | Faridpur | 160 | 00:00 | 118 | Muktagacha | 36 | 01:00 | 184 | Uttara | 77 | 12:00
53 | Fatullah | 94 | 15:00 | 119 | Munshiganj | 110 | 00:00 | 185 | UttaraNew | 61 | 00:00
54 | Fenchuganj | 48 | 00:00 | 120 | Muradnagar | 40 | 00:00 | 186 | Zigatola | 74 | 00:00
55 | Feni | 114 | 00:00 | 121 | Mymensingh | 198 | 19:00
56 | GPH | 10 | 03:00 | 122 | Naogaon | 143 | 00:00
57 | Ghatail | 84 | 01:00 | 123 | Narail | 50 | 19:30
58 | Ghorashal | 14 | 01:00 | 124 | Narinda | 72 | 16:00
59 | Ghorashal-230 | 82 | 23:00 | 125 | Narshingdi | 180 | 00:00
60 | Goalpara | 39 | 00:00 | 126 | Natore | 181 | 00:00
61 | Gollamari | 82 | 00:00 | 127 | Nawabganj | 56.2 | 00:00
62 | Gopalganj | 97.2 | 00:00 | 128 | Netrakona | 137 | 20:00
63 | Gulshan | 120 | 14:00 | 129 | New | 89.1 | 12:00
64 | Halishahar | 73.5 | 12:00 | 130 | Niamatpur | 89 | 00:00
65 | HaripurSBU | 172 | 13:00 | 131 | Noapara | 42 | 00:00
66 | Hasnabad | 67 | 00:00 | 132 | PHP | 9 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 14-07-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15248.27 | 107 |  | 15360.27
1:00 | 14912.52 | 103 |  | 15020.52
2:00 | 14200.59 | 96 |  | 14300.59
3:00 | 13862.97 | 46 |  | 13910.97
4:00 | 13344.46 | 34 |  | 13380.46
5:00 | 12842.89 | 0 |  | 12842.89
6:00 | 12176.68 | 0 |  | 12176.68
7:00 | 11999.93 | 0 |  | 11999.93
8:00 | 11748.36 | 0 |  | 11748.36
9:00 | 11811.28 | 0 |  | 11811.28
10:00 | 12082.4 | 0 |  | 12082.4
11:00 | 12238.45 | 0 |  | 12238.45
12:00 | 12647.51 | 0 |  | 12647.51
13:00 | 12827.91 | 0 |  | 12827.91
14:00 | 12761.33 | 0 |  | 12761.33
15:00 | 12665.9 | 0 |  | 12665.9
16:00 | 12563.15 | 0 |  | 12563.15
17:00 | 12114.82 | 0 |  | 12114.82
18:00 | 11914.07 | 0 |  | 11914.07
19:00 | 12915.56 | 0 |  | 12915.56
19:30 | 13855.87 | 0 |  | 13855.87
20:00 | 13945.22 | 0 |  | 13945.22
21:00 | 13822.2 | 0 |  | 13822.2
22:00 | 13742.2 | 0 |  | 13742.2
23:00 | 13861.2 | 0 |  | 13861.2
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 14-07-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8457.2 | 6791.07 | 15248.27 | DAILY GENERATION CURVE
00:30 | 8301.1 | 6779.295 | 15080.395
01:00 | 8145 | 6767.52 | 14912.52 | 14-07-2025
01:30 | 7888 | 6668.555 | 14556.555
02:00 | 7631 | 6569.59 | 14200.59
02:30 | 7480 | 6551.78 | 14031.78
03:00 | 7329 | 6533.97 | 13862.97
03:30 | 7117 | 6486.715 | 13603.715
04:00 | 6905 | 6439.46 | 13344.46
04:30 | 6770.5 | 6323.175 | 13093.675
05:00 | 6636 | 6206.89 | 12842.89
05:30 | 6526.615 | 5983.17 | 12509.785
06:00 | 6417.23 | 5759.45 | 12176.68
06:30 | 6421.76 | 5666.545 | 12088.305
07:00 | 6426.29 | 5573.64 | 11999.93
07:30 | 6188.72 | 5685.425 | 11874.145
08:00 | 5951.15 | 5797.21 | 11748.36
08:30 | 5988.855 | 5790.965 | 11779.82
09:00 | 6026.56 | 5784.72 | 11811.28
09:30 | 6136.115 | 5810.725 | 11946.84
10:00 | 6245.67 | 5836.73 | 12082.4
10:30 | 6223.195 | 5937.23 | 12160.425
11:00 | 6200.72 | 6037.73 | 12238.45
11:30 | 6432.96 | 6010.02 | 12442.98
12:00 | 6665.2 | 5982.31 | 12647.51
12:30 | 6642.37 | 6095.34 | 12737.71
13:00 | 6619.54 | 6208.37 | 12827.91
13:30 | 6649.22 | 6145.4 | 12794.62
14:00 | 6678.9 | 6082.43 | 12761.33
14:30 | 6672.42 | 6041.195 | 12713.615
15:00 | 6665.94 | 5999.96 | 12665.9
15:30 | 6651.35 | 5963.175 | 12614.525
16:00 | 6636.76 | 5926.39 | 12563.15
16:30 | 6611.675 | 5727.31 | 12338.985
17:00 | 6586.59 | 5528.23 | 12114.82
17:30 | 6538.455 | 5475.99 | 12014.445
18:00 | 6490.32 | 5423.75 | 11914.07
18:30 | 6804.16 | 5610.655 | 12414.815
19:00 | 7118 | 5797.56 | 12915.56
19:30 | 7614 | 6241.87 | 13855.87
20:00 | 7521 | 6424.22 | 13945.22
20:30 | 7413.1 | 6470.61 | 13883.71 |  | Executive Engineer
21:00 | 7305.2 | 6517 | 13822.2 |  | Network Operation Division
21:30 | 7252.7 | 6529.5 | 13782.2
22:00 | 7200.2 | 6542 | 13742.2
22:30 | 7218.2 | 6583.5 | 13801.7
23:00 | 7236.2 | 6625 | 13861.2

## En-Curve
QF-LDC-12
Date | 14-07-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3690 | 2180 | 892 | 38 | 46 | 1176.07 | 220 | 4202 | 0 | 626 | 2123.2 | 0 | 0 | 55 | 107 | DAILY ENERGY CURVE
00:30 | 3663 | 2176 | 892 | 38 | 46 | 1175.795 | 212 | 4199 | 0 | 576 | 2054.1 | 0 | 0 | 48.5 | 105 | 14-07-2025
01:00 | 3636 | 2172 | 892 | 38 | 46 | 1175.52 | 204 | 4196 | 0 | 526 | 1985 | 0 | 0 | 42 | 103
01:30 | 3668 | 2147.5 | 892 | 38 | 45 | 1175.555 | 204 | 4200 | 0 | 377 | 1771 | 0 | 0 | 38.5 | 99.5 | Energy Generated | 316.3618 |  | MKWHr
02:00 | 3700 | 2123 | 892 | 38 | 44 | 1175.59 | 204 | 4204 | 0 | 228 | 1557 | 0 | 0 | 35 | 96 | Energy not Served | 0.386 |  | MKWHr
02:30 | 3697 | 2117 | 892 | 38 | 43 | 1176.28 | 180 | 4198 | 0 | 198 | 1459 | 0 | 0 | 33.5 | 71 | Total Energy Requirement | 316.7478 |  | MKWHr
03:00 | 3694 | 2111 | 892 | 38 | 42 | 1176.97 | 156 | 4192 | 0 | 168 | 1361 | 0 | 0 | 32 | 46
03:30 | 3704.5 | 2120 | 892 | 38 | 41 | 1176.715 | 156 | 4143 | 0 | 135 | 1163.5 | 0 | 0 | 34 | 40
04:00 | 3715 | 2129 | 892 | 38 | 40 | 1176.46 | 156 | 4094 | 0 | 102 | 966 | 0 | 0 | 36 | 34
04:30 | 3687.5 | 2119 | 892 | 38 | 40 | 1166.675 | 156 | 3993.5 | 0 | 102 | 858 | 0 | 0 | 41 | 17
05:00 | 3660 | 2109 | 892 | 38 | 40 | 1156.89 | 156 | 3893 | 0 | 102 | 750 | 0 | 0 | 46 | 0
05:30 | 3669 | 2085 | 892 | 38 | 39 | 1078.43 | 156 | 3697.5 | 3.355 | 93.5 | 720 | 0 | 0 | 38 | 0
06:00 | 3678 | 2061 | 892 | 38 | 38 | 999.97 | 156 | 3502 | 6.71 | 85 | 690 | 0 | 0 | 30 | 0
06:30 | 3712 | 2094 | 892 | 38 | 36 | 943.5 | 156 | 3442 | 22.805 | 72 | 645.5 | 0 | 0 | 34.5 | 0
07:00 | 3746 | 2127 | 892 | 38 | 34 | 887.03 | 156 | 3382 | 38.9 | 59 | 601 | 0 | 0 | 39 | 0
07:30 | 3757.5 | 1842 | 891 | 38 | 33 | 934.135 | 156 | 3448.5 | 70.51 | 59 | 599 | 0 | 0 | 45.5 | 0
08:00 | 3769 | 1557 | 890 | 38 | 32 | 981.24 | 156 | 3515 | 102.12 | 59 | 597 | 0 | 0 | 52 | 0
08:30 | 3731 | 1582 | 890 | 38 | 31 | 967.41 | 158.5 | 3565 | 110.91 | 77 | 594.5 | 0 | 0 | 34.5 | 0
09:00 | 3693 | 1607 | 890 | 38 | 30 | 953.58 | 161 | 3615 | 119.7 | 95 | 592 | 0 | 0 | 17 | 0
09:30 | 3714.5 | 1607 | 890 | 38 | 29 | 963.695 | 161 | 3655.5 | 188.145 | 95 | 589.5 | 0 | 0 | 15.5 | 0
10:00 | 3736 | 1607 | 890 | 38 | 28 | 973.81 | 161 | 3696 | 256.59 | 95 | 587 | 0 | 0 | 14 | 0
10:30 | 3675 | 1605 | 890 | 38 | 29 | 1018.755 | 161 | 3727.5 | 310.67 | 95 | 596 | 0 | 0 | 14.5 | 0
11:00 | 3614 | 1603 | 890 | 38 | 30 | 1063.7 | 161 | 3759 | 364.75 | 95 | 605 | 0 | 0 | 15 | 0
11:30 | 3614.5 | 1655 | 890 | 38 | 30 | 1062.86 | 161 | 3824 | 336.12 | 112.5 | 687 | 0 | 0 | 32 | 0
12:00 | 3615 | 1707 | 890 | 38 | 30 | 1062.02 | 161 | 3889 | 307.49 | 130 | 769 | 0 | 0 | 49 | 0
12:30 | 3558.5 | 1747 | 890 | 38 | 32 | 1065.55 | 161 | 3886 | 368.16 | 121.5 | 844.5 | 0 | 0 | 25.5 | 0
13:00 | 3502 | 1787 | 890 | 38 | 34 | 1069.08 | 161 | 3883 | 428.83 | 113 | 920 | 0 | 0 | 2 | 0
13:30 | 3476 | 1761 | 890 | 38 | 34 | 1068.99 | 181 | 3903.5 | 367.63 | 128 | 939 | 0 | 0 | 7.5 | 0
14:00 | 3450 | 1735 | 890 | 38 | 34 | 1068.9 | 201 | 3924 | 306.43 | 143 | 958 | 0 | 0 | 13 | 0
14:30 | 3459 | 1739 | 890 | 38 | 34 | 1069.33 | 198 | 3916 | 246.785 | 160 | 945.5 | 0 | 0 | 18 | 0
15:00 | 3468 | 1743 | 890 | 38 | 34 | 1069.76 | 195 | 3908 | 187.14 | 177 | 933 | 0 | 0 | 23 | 0
15:30 | 3446 | 1741.5 | 890 | 38 | 30 | 1066.16 | 195 | 3882 | 177.865 | 190 | 937 | 0 | 0 | 21 | 0
16:00 | 3424 | 1740 | 890 | 38 | 26 | 1062.56 | 195 | 3856 | 168.59 | 203 | 941 | 0 | 0 | 19 | 0
16:30 | 3480.5 | 1763.5 | 890 | 38 | 24 | 986.285 | 195 | 3706.5 | 116.2 | 230.5 | 893.5 | 0 | 0 | 15 | 0
17:00 | 3537 | 1787 | 890 | 38 | 22 | 910.01 | 195 | 3557 | 63.81 | 258 | 846 | 0 | 0 | 11 | 0
17:30 | 3495 | 1746 | 890 | 38 | 24 | 916.83 | 200.5 | 3531.5 | 39.115 | 262 | 850.5 | 0 | 0 | 21 | 0
18:00 | 3453 | 1705 | 890 | 38 | 26 | 923.65 | 206 | 3506 | 14.42 | 266 | 855 | 0 | 0 | 31 | 0
18:30 | 3491.5 | 1658 | 890 | 38 | 27 | 989.105 | 206 | 3573 | 7.21 | 418 | 1088.5 | 0 | 0 | 28.5 | 0
19:00 | 3530 | 1611 | 890 | 38 | 28 | 1054.56 | 206 | 3640 | 0 | 570 | 1322 | 0 | 0 | 26 | 0
19:30 | 3623 | 1743 | 890 | 38 | 26 | 1124.87 | 218 | 3913 | 0 | 573 | 1674 | 0 | 0 | 33 | 0
20:00 | 3630 | 1806 | 889 | 38 | 26 | 1208.22 | 218 | 3981 | 0 | 491 | 1640 | 0 | 0 | 18 | 0
20:30 | 3715 | 1824 | 889.5 | 38 | 26 | 1220.61 | 215.5 | 4061 | 0 | 440.5 | 1425.1 | 0 | 0 | 28.5 | 0
21:00 | 3800 | 1842 | 890 | 38 | 26 | 1233 | 213 | 4141 | 0 | 390 | 1210.2 | 0 | 0 | 39 | 0
21:30 | 3773 | 1845.5 | 890 | 38 | 27 | 1226 | 213.5 | 4157 | 0 | 389.5 | 1186.7 | 0 | 0 | 36 | 0
22:00 | 3746 | 1849 | 890 | 38 | 28 | 1219 | 214 | 4173 | 0 | 389 | 1163.2 | 0 | 0 | 33 | 0
22:30 | 3751 | 1836.5 | 890 | 38 | 27 | 1223 | 214 | 4227 | 0 | 386.5 | 1177.7 | 0 | 0 | 31 | 0
23:00 | 3756 | 1824 | 890 | 38 | 26 | 1227 | 214 | 4281 | 0 | 384 | 1192.2 | 0 | 0 | 29 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 14-07-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 382 | 06:00 | 367 | 11:00 | Payra | 414 | 06:00 | 405 | 23:00
Ashuganj | 400 | 6:00 | 379 | 15:00 | Rahanpur | 400 | 18:00 | 374 | 00:00
Bhulta | 396 | 06:00 | 374 | 15:00 | Rampal | 402 | 06:00 | 383 | 22:00
Bibiana | 384 | 06:00 | 376 | 11:00
BIPTC | 405 | 06:00 | 397 | 00:00
Bogura | 387 | 18:00 | 363 | 00:00
Gopalganj | 395 | 06:00 | 378 | 23:00
Kaliakoir | 373 | 07:00 | 358 | 11:00
Madunaghat | 393 | 00:00 | 384 | 13:00
Meghnaghat | 385 | 06:00 | 370 | 23:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 223 | 06:00 | 213 | 11:00 | Keranigonj | 221 | 06:00 | 211 | 11:00
AKSML | 229 | 00:00 | 223 | 12:00 | Khulna(S) | 234 | 06:00 | 216 | 23:00
Aminbazar | 223 | 04:00 | 215 | 15:00 | Madunaghat | 233 | 00:00 | 226 | 13:00
Ashuganj | 231 | 07:00 | 220 | 15:00 | Madunaghat-400 | 234 | 00:00 | 226 | 13:00
Ashuganj-400 | 230 | 6:00 | 218 | 15:00 | Maniknagar | 219 | 04:00 | 210 | 11:00
Baghabari | 234 | 06:00 | 225 | 00:00 | Meghnaghat | 227 | 05:00 | 219 | 11:00
Barapukuria | 226 | 18:00 | 215 | 00:00 | Meghnaghat-400 | 223 | 06:00 | 215 | 11:00
Barapukuria-230 | 226 | 18:00 | 216 | 23:00 | Mirsorai | 226 | 08:00 | 219 | 15:00
Barishal | 231 | 06:00 | 221 | 22:00 | Rajshahi | 235 | 07:00 | 221 | 23:00
Bheramara | 233 | 17:00 | 222 | 00:00 | Rampal | 232 | 06:00 | 216 | 23:00
Bhulta | 228 | 06:00 | 210 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 225 | 18:30 | 220 | 16:00 | Rampura | 226 | 06:00 | 212 | 15:00
BIPTC | 236 | 06:00 | 223 | 00:00 | Shikalbaha | 232 | 00:00 | 222 | 13:00
Bogura | 234 | 07:00 | 221 | 00:00 | Shyampur | 221 | 06:00 | 212 | 11:00
Bogura-400 | 234 | 08:00 | 221 | 00:00 | Siddhirganj | 219 | 04:00 | 212 | 10:00
Borhanuddin | 236 | 09:00 | 229 | 21:00 | Sirajgonj | 238 | 06:00 | 232 | 02:00
BSRM | 225 | 00:00 | 219 | 13:00 | Sreepur | 227 | 06:00 | 219 | 15:00
Cumilla(N) | 221 | 07:00 | 214 | 15:00 | Tongi | 222 | 00:00 | 214 | 12:00
Faridpur | 227 | 06:00 | 215 | 23:00
Fenchuganj | 227 | 18:30 | 222 | 23:00
Ghorashal | 230 | 00:00 | 225 | 08:00
Ghorashal-230 | 226 | 06:00 | 215 | 11:00
Gopalganj | 228 | 06:00 | 217 | 22:00
GPH | 228 | 00:00 | 222 | 13:00
Haripur | 219 | 07:00 | 212 | 12:00
Hasnabad | 221 | 06:00 | 213 | 12:00
Hathazari | 230 | 00:00 | 220 | 14:00
Ishurdi | 235 | 06:00 | 225 | 00:00
Jhenaidah | 232 | 06:00 | 217 | 00:00
Kaliakoir | 229 | 06:00 | 219 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 07:00 | 126 | 15:00 | Madanganj | 127 | 04:00 | 122 | 11:00
Agargaon | 131 | 06:00 | 123 | 11:00 | Madaripur | 136 | 05:00 | 129 | 23:00
Agrabad | 133 | 00:00 | 125 | 13:00 | Madartek | 135 | 06:00 | 127 | 10:00
AKS | 131 | 01:00 | 125 | 13:00 | Madunaghat | 132 | 00:00 | 128 | 13:00
Aminbazar | 130 | 00:00 | 125 | 21:00 | Magura | 135 | 17:00 | 121 | 00:00
Amnura | 137 | 19:00 | 121 | 00:00 | Mahasthangarh | 137 | 18:00 | 125 | 00:00
Ashuganj | 140 | 06:00 | 136 | 15:00 | Maijdee | 118 | 20:00 | 110 | 05:00
Bagerhat | 139 | 06:00 | 120 | 23:00 | Manikganj | 125 | 00:00 | 119 | 11:00
Bajitpur | 132 | 05:00 | 124 | 23:00 | Maniknagar | 130 | 03:00 | 123 | 11:00
Bakulia | 135 | 00:00 | 126 | 13:00 | Matarbari | 129 | 07:00 | 112 | 13:00
Banani | 136 | 06:00 | 127 | 10:00 | Matuail | 128 | 03:00 | 122 | 11:00
Bangabhaban | 129 | 04:00 | 124 | 11:00 | Millgate | 131 | 05:00 | 122 | 15:00
Barapukuria | 138 | 18:00 | 127 | 21:00 | Mirpur | 129 | 00:00 | 122 | 11:00
Barguna | 136 | 07:00 | 129 | 21:00 | Mirzapur | 129 | 08:00 | 126 | 07:00
Barishal | 137 | 05:00 | 127 | 23:00 | Mithapukur | 135 | 07:00 | 123 | 01:00
Barishal-230 | 137 | 06:00 | 128 | 23:00 | MI_Cement | 128 | 05:00 | 122 | 11:00
Baroaulia | 132 | 00:00 | 126 | 14:00 | Modern | N/A | N/A | N/A | N/A
Baroirhat | 123 | 18:00 | 118 | 13:00 | Mogbazar | 137 | 05:00 | 128 | 15:00
Bashundhara | 135 | 05:00 | 120 | 15:00 | Mongla | 140 | 05:00 | 122 | 23:00
BashundharaCement | 127 | 04:00 | 122 | 11:00 | Motijheel | 129 | 04:00 | 124 | 11:00
Beanibazar | 126 | 15:00 | 122 | 00:00 | Muktagacha | 134 | 19:00 | 126 | 18:00
Benapole | 137 | 05:00 | 123 | 23:00 | Munshiganj | 127 | 06:00 | 121 | 11:00
Bhaluka | 129 | 07:00 | 123 | 15:00 | Muradnagar | 124 | 18:00 | 120 | 11:00
Bhandaria | 135 | 10:00 | 120 | 00:00 | Mymensingh | 135 | 20:00 | 116 | 23:00
Bhangura | 134 | 17:00 | 127 | 00:00 | Naogaon | 134 | 16:00 | 121 | 02:00
Bheramara | 139 | 18:00 | 132 | 00:00 | Narail | 136 | 17:00 | 120 | 00:00
Bheramara(GK) | 138 | 17:00 | 131 | 00:00 | Narinda | 130 | 3:00 | 123 | 11:00
Bhulta | 121 | 01:00 | 116 | 11:00 | Narshingdi | 135 | 18:30 | 117 | 23:00
Bog-Sherpur | 136 | 18:00 | 126 | 00:00 | Natore | 135 | 07:00 | 127 | 00:00
Bogura | 138 | 07:00 | 128 | 00:00 | Nawabganj | 132 | 05:00 | 126 | 11:00
Bogura-230 | 138 | 07:00 | 129 | 00:00 | Netrakona | 126 | 06:00 | 115 | 02:00
Brahmanbaria | 134 | 06:00 | 129 | 23:00 | New | 131 | 02:00 | 123 | 15:00
Cantonment | 131 | 07:00 | 124 | 11:00 | Niamatpur | 135 | 09:00 | 127 | 21:00
Chandina | 127 | 19:30 | 122 | 15:00 | Noapara | 140 | 05:00 | 125 | 23:00
Chandpur | 126 | 00:00 | 122 | 05:00 | Pabna | 136 | 18:30 | 128 | 00:00
Chandraghona | 133 | 00:00 | 129 | 13:00 | Palashbari | 133 | 07:00 | 120 | 00:00
Chapai | 135 | 07:00 | 122 | 00:00 | Panchagarh | 140 | 18:30 | 118 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 128 | 06:00 | 122 | 11:00 | Patuakhali | 135 | 01:00 | 130 | 19:30
Chauddagram | 122 | 19:30 | 117 | 13:00 | Payra | 136 | 07:00 | 133 | 21:00
Chhatak | 125 | 05:00 | 119 | 01:00 | PHP | 123 | 20:00 | 117 | 05:00
Chowmuhani | 119 | 18:00 | 112 | 15:00 | Postogola | 130 | 06:00 | 124 | 11:00
Chuadanga | 138 | 17:00 | 120 | 00:00 | Purbachal | 136 | 05:00 | 122 | 15:00
Coxsbazar | 124 | 07:00 | 113 | 13:00 | Purbasadipur | 134 | 18:30 | 117 | 12:00
Cumilla(N) | 127 | 20:00 | 121 | 15:00 | Rahanpur | 137 | 17:00 | 127 | 00:00
Cumilla(S) | 133 | 04:00 | 120 | 15:00 | Rahanpur-400 | 137 | 17:00 | 127 | 00:00
Daganbhuiyan | 120 | 20:00 | 113 | 04:00 | Rahim | 128 | 18:30 | 123 | 11:00
Daudkandi | 123 | 06:00 | 117 | 11:00 | Rajbari | 135 | 06:00 | 125 | 23:00
Dhaka | 136 | 05:00 | 127 | 16:00 | Rajendrapur | 132 | 18:30 | 123 | 09:00
Dhamrai | 129 | 05:00 | 123 | 11:00 | Rajshahi | 135 | 07:00 | 128 | 22:00
Dhanmondi | 136 | 06:00 | 127 | 15:00 | Rajshahi-230 | 136 | 07:00 | 114 | 00:00
Dohazari | 130 | 01:00 | 121 | 13:00 | Ramganj | 120 | 17:00 | 115 | 23:00
Faridpur | 135 | 08:00 | 128 | 00:00 | Rampur | 132 | 00:00 | 125 | 13:00
Fatullah | 129 | 05:00 | 124 | 11:00 | Rampura | 136 | 06:00 | 126 | 15:00
Fenchuganj | 134 | 18:00 | 130 | 23:00 | Rangamati | 132 | 01:00 | 128 | 13:00
Feni | 123 | 00:00 | 115 | 15:00 | Rangpur | 134 | 18:00 | 121 | 12:00
Ghatail | 130 | 05:00 | 124 | 11:00 | Ruppur | 138 | 17:00 | 131 | 00:00
Ghorashal | 135 | 05:00 | 131 | 11:00 | Saidpur | 134 | 07:00 | 120 | 12:00
Goalpara | 140 | 06:00 | 127 | 22:00 | Satkhira | 140 | 08:00 | 122 | 23:00
Gollamari | 141 | 06:00 | 127 | 23:00 | Satmasjid | 131 | 06:00 | 123 | 11:00
Gopalganj | 136 | 06:00 | 127 | 23:00 | Savar | 131 | 00:00 | 122 | 11:00
Gopalganj-400 | 137 | 06:00 | 130 | 22:00 | SevenRings | 135 | 06:00 | 130 | 11:00
Gulshan | 136 | 06:00 | 127 | 10:00 | ShahCement | 128 | 06:00 | 122 | 11:00
Halishahar | 135 | 00:00 | 125 | 13:00 | Shahjadpur | 138 | 17:00 | 131 | 00:00
Haripur | 127 | 00:00 | 122 | 11:00 | Shahjibazar | 134 | 07:00 | 128 | 00:00
HaripurSBU | 127 | 00:00 | 123 | 11:00 | Shahmirpur | 135 | 00:00 | 128 | 13:00
Hasnabad | 130 | 01:00 | 124 | 11:00 | Shariatpur | 135 | 07:00 | 127 | 22:00
Hathazari | 133 | 00:00 | 128 | 15:00 | Sherpur | 135 | 03:00 | 125 | 15:00
Ishurdi | 139 | 18:00 | 132 | 00:00 | Shikalbaha | 122 | 01:00 | 118 | 16:00
Jaldhaka | 133 | 18:30 | 118 | 12:00 | Shikalbaha-230 | 135 | 00:00 | 128 | 13:00
Jamalpur | 139 | 03:00 | 127 | 15:00 | Shitalakhya | 128 | 05:00 | 122 | 11:00
Jashore | 142 | 05:00 | 120 | 00:00 | Sholosohor | 132 | 01:00 | 127 | 13:00
Jhenaidah | 137 | 17:00 | 123 | 00:00 | Shyampur | 130 | 06:00 | 124 | 11:00
Jhenaidah-230 | 139 | 17:00 | 126 | 00:00 | Shyampur-230 | 130 | 06:00 | 123 | 13:00
Joydebpur | 132 | 18:00 | 123 | 15:00 | Siddhirganj | 128 | 04:00 | 123 | 11:00
Joypurhat | 131 | 07:00 | 118 | 00:00 | Sirajganj | 133 | 10:00 | 126 | 00:00
Juldah | 135 | 00:00 | 128 | 11:00 | Sonargaon | 126 | 00:00 | 121 | 11:00
Kabirpur | 131 | 02:00 | 119 | 15:00 | Sreemongol | 132 | 18:00 | 127 | 00:00
Kachua | 125 | 19:30 | 120 | 23:00 | Sreepur | 132 | 06:00 | 126 | 15:00
Kaliakoir | 132 | 05:00 | 125 | 11:00 | Srinagar | 132 | 06:00 | 126 | 11:00
Kallyanpur | 130 | 00:00 | 123 | 11:00 | SSM | 135 | 00:00 | 126 | 14:00
Kalurghat | 133 | 00:00 | 127 | 13:00 | Sunamganj | 123 | 18:00 | 117 | 01:00
Kamrangirchar | 132 | 05:00 | 125 | 11:00 | Sylhet | 127 | 06:00 | 123 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet-132 | 128 | 06:00 | 125 | 00:00
Kasba | 123 | 18:00 | 118 | 15:00 | Tangail | 127 | 04:00 | 121 | 21:00
Kazla | 130 | 07:00 | 123 | 12:00 | Taraganj | 134 | 07:00 | 120 | 12:00
Keranigonj | 132 | 06:00 | 126 | 11:00 | Thakurgaon | 138 | 18:30 | 116 | 12:00
Khagrachori | 131 | 00:00 | 127 | 13:00 | TK | 132 | 00:00 | 127 | 13:00
Khulna | 139 | 05:00 | 125 | 23:00 | Tongi | 132 | 04:00 | 125 | 15:00
Khulna(S) | 141 | 06:00 | 128 | 23:00 | Ullahpara | 135 | 18:30 | 128 | 00:00
Khulshi | 132 | 00:00 | 125 | 13:00 | Ullon | 136 | 06:00 | 126 | 15:00
Kishoreganj | 129 | 06:00 | 120 | 23:00 | Uttara | 129 | 00:00 | 123 | 05:00
Kodda | 131 | 18:00 | 117 | 11:00 | UttaraNew | 129 | 00:00 | 122 | 11:00
KSRM | 133 | 00:00 | 127 | 11:00 | Zigatola | 132 | 07:00 | 126 | 12:00
Kulaura | 132 | 07:00 | 129 | 00:00
Kurigram | 133 | 18:00 | 119 | 03:00
Kushtia | 138 | 18:00 | 127 | 00:00
Lakshmipur | 118 | 17:00 | 112 | 05:00
Lalbag | 132 | 06:00 | 125 | 11:00
Lalmonirhat | 134 | 18:00 | 120 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division