## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 16-07-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 15-07-2025 | during | 16-07-2025 | during | 16-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 0 | 0 | 0 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 302 | 310 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 196 | 200 | 208.13 | 208.13 | 201 | 201 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 327 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 46.08 | 28 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 15 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 17 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 17 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23 | 15 | 33 | 33 | 26 | 26 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 13 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 33 | 33 | 52.19 | 52.19 | 42 | 42 | Engine Problem
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 95 | 15 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 52 | 56 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 88 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 39 | 16 | 104 | 104 | 50 | 50 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 86 | 150 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 9 | 0 | 18 | 0 | 18 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 54 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 471 | 550 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 90 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2388.08 | 2418 | 4711.65 | 4787.65 | 2711.33 | 2806.33
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 6 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 10 | 0 | 8 | 0 | 8 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 216 | 207 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 217 | 213 | 213 | 213 | 213 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 32 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 46 | 80 | 80 | 80 | 80 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 60 | 76 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 21 | 2 | 25 | 2 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.72 | 0 | 0.54 | 0 | 0.54 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 30 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 14 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 88 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 580 | 580 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 7 | 14 | 10 | 10 | 10 | 10 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 679 | 703 | 790 | 790 | 790 | 790 | FGMO
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1954.72 | 2039 | 3831.26 | 3845.72 | 3831.26 | 3845.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 204 | 199 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 330 | 354 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 300 | 340 | 340 | 340 | 340 | 340 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 16 | 19 | 46.7 | 46.7 | 19 | 19 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 43 | 48 | 55 | 55 | 50 | 50 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 35 | 108 | 195 | 195 | 108 | 108 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 70 | 70 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 30 | 31 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 96 | 164 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 26 | 30 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 45 | 105 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 26 | 113 | 113 | 9 | 37 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 90 | 114 | 115 | 115 | 115 | 115 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 52 | 0 | 68 | 0 | 68 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1451 | 1781.2 | 2468.75 | 2400.75 | 2111.55 | 2071.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 15-07-2025 | during | 16-07-2025 | during | 16-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 44 | 50 | 157.5 | 157.5 | 51 | 51 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 125 | 200 | 200 | 200 | 186 | 186 | Engine Problem
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 55 | 45 | 115 | 115 | 105 | 105 | Engine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 25.22 | 0 | 37 | 0 | 37 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 35 | 35 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 279.22 | 324 | 588 | 549 | 428 | 389
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 10 | 20 | 10 | 10 | 10 | 10 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 138 | 144 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 84 | 83 | 83 | 82 | 82 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 170 | 171 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 8 | 8 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 380 | 366 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | Aythority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1151 | 1161 | 1196 | 1196 | 1148 | 1148
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 884 | 885 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 210 | 205 | 410 | 410 | 218 | 218 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 60 | 60 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 32.16 | 0 | 20 | 0 | 20 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 447 | 611 | 1234.2 | 1234.2 | 617.1 | 617.1 | U#1 Under Reserve shut down
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1611.16 | 1756 | 3572.2 | 3552.2 | 2718.1 | 2698.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 617 | 618 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1000 | 1110 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 173 | 278 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.11 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 2130.11 | 2346 | 2162 | 2161 | 2102 | 2101
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 170 | 204 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 203 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 360 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 32 | 32 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 41 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.04 | 0 | 5.2 | 0 | 5.2 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 875.77 | 1211 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 21.06 | 0 | 62 | 0 | 62 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 63 | 0 | 65 | 0 | 65 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 1631.87 | 2138 | 3160.07 | 3027.87 | 3118.69 | 2986.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 49 | 49 | 50 | 50 | 50 | 50 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 156 | 154 | 150 | 150 | 155 | 155 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 108 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 1.8 | 0 | 5.4 | 0 | 5.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 95 | 95 | 95 | 95 | 95 | Schedule Maintenance
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 7 | 0 | 22 | 0 | 22 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 15 | 0 | 80.61 | 0 | 80.61 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 262.8 | 406 | 550.01 | 442 | 555.01 | 447
System Total |  |  |  |  | 28565.2 | 27084.055 | 12859.96 | 14369.2 | 22239.94 | 21962.19 | 18723.94 | 18493.19
Forecast Scenario (16-07-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14090 |  | 0 |  | 14090
|  |  |  | 1:00 | 13810 |  | 0 |  | 13810
|  |  |  | 2:00 | 13330 |  | 0 |  | 13330
|  |  |  | 3:00 | 13040 |  | 0 |  | 13040
|  |  |  | 4:00 | 12690 |  | 0 |  | 12690
|  |  |  | 5:00 | 12370 |  | 0 |  | 12370
|  |  |  | 6:00 | 12050 |  | 0 |  | 12050
|  |  |  | 7:00 | 12210 |  | 0 |  | 12210
|  |  |  | 8:00 | 12290 |  | 0 |  | 12290
|  |  |  | 9:00 | 12590 |  | 0 |  | 12590
|  |  |  | 10:00 | 12870 |  | 0 |  | 12870
|  |  |  | 11:00 | 13110 |  | 0 |  | 13110
|  |  |  | 12:00 | 12990 |  | 0 |  | 12990
|  |  |  | 13:00 | 13000 |  | 0 |  | 13000
|  |  |  | 14:00 | 12840 |  | 0 |  | 12840
|  |  |  | 15:00 | 12630 |  | 0 |  | 12630
|  |  |  | 16:00 | 12540 |  | 0 |  | 12540
|  |  |  | 17:00 | 12460 |  | 0 |  | 12460
|  |  |  | 18:00 | 12530 |  | 0 |  | 12530
|  |  |  | 18:30 | 13150 |  | 0 |  | 13150
|  |  |  | 19:00 | 13730 |  | 0 |  | 13730
|  |  |  | 19:30 | 14560 |  | 0 |  | 14560
|  |  |  | 20:00 | 14550 |  | 0 |  | 14550
|  |  |  | 21:00 | 14610 |  | 0 |  | 14610
|  |  |  | 22:00 | 14560 |  | 0 |  | 14560
|  |  |  | 23:00 | 14600 |  | 0 |  | 14600
Probable Maximum Temperature: |  |  | 31.60°C
Probable Maximum Demand at Day Peak: |  |  | 13110.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14610.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14610.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 315.49 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:41 hrs on 16-07-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 15-07-2025 | [28 empty] | Date: | 15-07-2025 | [28 empty] | Date: | 15-07-2025 | [28 empty] | Date: | 15-07-2025 | [28 empty] | Date: | 15-07-2025 | [11 empty] | Date: | 15-07-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [11 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 35 | 52 | 32 | 0 | 0 | 0 | 81 | 16 | 450 | 300 | 0 | 0 | 0 | 335 | 202 | 0 | 0 | 108 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 65 | 0 | 0 | 100 | 100 | 0 | 214 | 0 | 24 | 715 | 0 | 0 | 0 | 8 | 0 | 217 | 0 | 0 | 0 | 572 | 0 | 51 | 0 | 26 | 0 | 355 | 335 | 48 | 216 | 19 | 81 | 45 | 185 | 11 | 19 | 102 | 28 | 52.2 | 0 | 31 | 0 | 320 | 370 | 0 | 10 | 157 | 8 | 0 | 81 | 30 | 0 | 18 | 171 | 17 | 65 | 165 | 50 | 0 | 0 | 12 | 7224.2 | 891 | 187 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 0 | 1223 | 0 | 50 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 140 | 0 | 394 | 0 | 0 | 158 | 50 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 120 | 220 | 0 | 617 | 1244 | 0 | 6618 | 13842.2 | 98.71
01:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 35 | 52 | 32 | 0 | 0 | 0 | 83 | 16 | 450 | 302 | 0 | 0 | 0 | 335 | 201 | 0 | 0 | 108 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 65 | 0 | 0 | 100 | 100 | 0 | 214 | 0 | 32 | 735 | 0 | 0 | 0 | 8 | 0 | 220 | 0 | 0 | 0 | 572 | 0 | 51 | 0 | 8 | 0 | 355 | 300 | 48 | 197 | 19 | 98 | 45 | 176 | 8 | 20 | 102 | 26 | 52.2 | 0 | 31 | 0 | 320 | 379 | 0 | 10 | 156 | 8 | 0 | 82 | 30 | 0 | 18 | 172 | 17 | 65 | 165 | 51 | 0 | 0 | 12 | 7206.2 | 885 | 184 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 566 | 0 | 1181 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 140 | 0 | 353 | 0 | 0 | 157 | 50 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 120 | 220 | 0 | 617 | 1120 | 0 | 6358 | 13564.2 | 98.72
02:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 35 | 52 | 16 | 0 | 0 | 0 | 32 | 0 | 450 | 301 | 0 | 0 | 0 | 335 | 200 | 0 | 0 | 90 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 65 | 0 | 0 | 60 | 100 | 0 | 216 | 0 | 32 | 716 | 0 | 0 | 0 | 8 | 0 | 221 | 0 | 0 | 0 | 567 | 0 | 51 | 0 | 8 | 0 | 355 | 300 | 49 | 195 | 19 | 96 | 45 | 170 | 9 | 20 | 100 | 26 | 52.2 | 0 | 31 | 0 | 320 | 371 | 0 | 10 | 152 | 8 | 0 | 81 | 30 | 0 | 18 | 172 | 17 | 65 | 165 | 50 | 0 | 0 | 12 | 7014.7 | 885 | 187 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 557 | 0 | 1148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 140 | 0 | 349 | 0 | 0 | 158 | 50 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 120 | 220 | 0 | 618 | 1070 | 0 | 6069 | 13083.7 | 98.73
03:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 35 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 302 | 0 | 0 | 0 | 335 | 201 | 0 | 0 | 70 | 21.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 33 | 0 | 0 | 60 | 72 | 0 | 212 | 0 | 32 | 729 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 573 | 0 | 51 | 0 | 8 | 0 | 355 | 300 | 48 | 196 | 19 | 96 | 50 | 175 | 9 | 20 | 102 | 24 | 52.2 | 0 | 30 | 0 | 320 | 386 | 0 | 10 | 152 | 8 | 0 | 82 | 30 | 0 | 18 | 172 | 17 | 65 | 165 | 50 | 0 | 0 | 12 | 6862.7 | 885 | 189 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 561 | 0 | 1088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 140 | 0 | 350 | 0 | 0 | 159 | 50 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 120 | 220 | 0 | 618 | 1040 | 0 | 5929 | 12791.7 | 98.74
04:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 17 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 303 | 0 | 0 | 0 | 334 | 200 | 0 | 0 | 52 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 33 | 0 | 0 | 36 | 48 | 0 | 212 | 0 | 29 | 731 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 523 | 0 | 51 | 0 | 8 | 0 | 355 | 300 | 48 | 197 | 19 | 97 | 50 | 165 | 9 | 20 | 83 | 24 | 25 | 0 | 30 | 0 | 320 | 368 | 0 | 10 | 154 | 8 | 0 | 81 | 30 | 0 | 18 | 172 | 17 | 65 | 165 | 50 | 0 | 0 | 12 | 6637.5 | 884 | 197 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 523 | 0 | 1025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 140 | 0 | 353 | 0 | 0 | 157 | 50 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 120 | 220 | 0 | 618 | 1045 | 0 | 5808 | 12445.5 | 98.75
05:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 309 | 0 | 0 | 0 | 333 | 200 | 0 | 0 | 52 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 33 | 0 | 0 | 36 | 48 | 0 | 211 | 0 | 27 | 667 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 464 | 0 | 51 | 0 | 8 | 0 | 320 | 300 | 49 | 209 | 19 | 101 | 50 | 136 | 9 | 20 | 65 | 24 | 0 | 0 | 30 | 0 | 320 | 393 | 0 | 10 | 156 | 8 | 0 | 81 | 30 | 0 | 18 | 172 | 17 | 65 | 135 | 50 | 0 | 0 | 12 | 6410.5 | 884 | 201 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 471 | 0 | 1023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 140 | 0 | 387 | 0 | 0 | 156 | 50 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 120 | 220 | 0 | 618 | 960 | 0 | 5711 | 12121.5 | 98.76
06:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 300 | 0 | 0 | 0 | 334 | 200 | 0 | 1 | 52 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 3 | 0 | 0 | 36 | 48 | 0.04 | 211 | 0 | 0 | 657 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 454 | 1 | 51 | 0 | 8 | 0 | 320 | 300 | 48 | 196 | 19 | 98 | 50 | 132 | 9 | 20 | 48 | 22 | 0 | 1 | 30 | 0 | 320 | 386 | 0 | 10 | 155 | 8 | 0 | 81 | 30 | 0 | 18 | 172 | 17 | 65 | 125 | 50 | 0 | 0.57 | 12 | 6270.11 | 885 | 205 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4 | 440 | 0 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.34 | 0 | 0 | 198 | 0 | 140 | 0 | 352 | 0 | 0.1 | 156 | 50 | 0 | 0 | 55 | 0 | 0 | 0.2 | 3 | 0.04 | 0 | 172 | 120 | 220 | 0 | 617 | 950 | 0 | 5531.68 | 11801.79 | 98.77
07:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 17 | 18 | 12 | 0 | 0 | 0 | 0 | 0 | 450 | 309 | 0 | 0 | 0 | 331 | 198 | 0 | 1 | 52 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 36 | 48 | 0.74 | 211 | 0 | 14 | 690 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 500 | 2 | 51 | 0 | 8 | 0 | 349 | 300 | 48 | 205 | 19 | 105 | 50 | 100 | 8 | 20 | 49 | 22 | 0 | 12 | 30 | 0 | 320 | 390 | 0 | 10 | 158 | 8 | 0 | 81 | 30 | 0 | 18 | 172 | 17 | 65 | 125 | 50 | 0 | 6.48 | 12 | 6412.72 | 884 | 210 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 24 | 455 | 0 | 877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8.09 | 0 | 0 | 198 | 0 | 140 | 0 | 376 | 0 | 0.73 | 154 | 50 | 0 | 2 | 34 | 0 | 0 | 0.9 | 14 | 0.17 | 0 | 172 | 120 | 220 | 0 | 619 | 950 | 0 | 5554.89 | 11967.61 | 98.78
08:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 21 | 34 | 15 | 0 | 0 | 2 | 0 | 0 | 450 | 308 | 0 | 0 | 0 | 332 | 198 | 0 | 6 | 52 | 21.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 36 | 48 | 1.97 | 213 | 0 | 4 | 720 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 500 | 3 | 51 | 0 | 8 | 0 | 351 | 300 | 48 | 200 | 16 | 92 | 50 | 96 | 9 | 20 | 51 | 22 | 0 | 25 | 30 | 0 | 320 | 389 | 0 | 10 | 157 | 8 | 0 | 78 | 30 | 0 | 18 | 172 | 17 | 55 | 125 | 50 | 0 | 23.37 | 12 | 6451.84 | 885 | 210 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 450 | 0 | 876.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 14.37 | 0 | 0 | 202 | 0 | 140 | 0 | 359 | 0 | 1.02 | 158 | 50 | 35 | 17 | 34 | 0 | 0 | 1.4 | 40 | 0.42 | 0 | 173 | 120 | 220 | 0 | 617 | 942 | 0 | 5597.26 | 12049.1 | 98.79
09:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 35 | 34 | 15 | 0 | 0 | 35 | 0 | 0 | 450 | 302 | 0 | 0 | 0 | 330 | 197 | 0 | 29 | 52 | 20.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 36 | 48 | 1.83 | 213 | 0 | 2 | 656 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 500 | 6 | 51 | 0 | 8 | 0 | 347 | 340 | 47 | 201 | 16 | 91 | 50 | 95 | 8 | 20 | 51 | 22 | 0 | 63 | 30 | 0 | 320 | 389 | 0 | 10 | 158 | 8 | 0 | 77 | 30 | 0 | 18 | 170 | 17 | 55 | 125 | 49 | 1 | 19.79 | 12 | 6534.12 | 884 | 211 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 8 | 462 | 0 | 873.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 15.37 | 0 | 0 | 201 | 0 | 140 | 0 | 414 | 0 | 1.49 | 158 | 50 | 35 | 19 | 34 | 0 | 0 | 2.8 | 135 | 0.38 | 0 | 173 | 120 | 220 | 0 | 617 | 945 | 0 | 5809.49 | 12343.61 | 98.8
10:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 17.64 | 35 | 43 | 15 | 70 | 0 | 36 | 17 | 18 | 450 | 303 | 0 | 0 | 17 | 330 | 196 | 0 | 16 | 70 | 20 | 15 | 0 | 0 | 0 | 30 | 0 | 0 | 14 | 0 | 0 | 0 | 60 | 88 | 3.17 | 220 | 5 | 2 | 663 | 0 | 0 | 2 | 0 | 17 | 217 | 0 | 0 | 0 | 570 | 8 | 43 | 11 | 31 | 0 | 342 | 330 | 45 | 198 | 16 | 90 | 50 | 100 | 9 | 13 | 48 | 24 | 0 | 7 | 30 | 0 | 320 | 362 | 0 | 10 | 155 | 8 | 0 | 74 | 30 | 0 | 18 | 169 | 17 | 55 | 125 | 44 | 0 | 19.5 | 12 | 6840.31 | 884 | 210 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 40.37 | 456 | 0 | 876.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 23.03 | 0 | 0 | 196 | 0 | 140 | 0 | 382 | 0 | 2.93 | 158 | 49 | 35 | 25 | 34 | 0 | 0 | 1.7 | 40 | 0.27 | 0 | 167 | 120 | 220 | 0 | 615 | 990 | 0 | 5781.75 | 12622.06 | 98.81
11:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 471 | 46.08 | 35 | 52 | 15 | 95 | 0 | 55 | 86 | 39 | 450 | 302 | 0 | 0 | 35 | 327 | 196 | 0 | 9 | 70 | 23 | 15 | 0 | 0 | 0 | 30 | 0 | 0 | 7 | 0 | 0 | 0 | 60 | 88 | 1.72 | 216 | 14 | 2 | 679 | 0 | 0 | 18 | 0 | 32 | 217 | 0 | 0 | 0 | 580 | 10 | 43 | 70 | 35 | 0 | 330 | 300 | 43 | 204 | 16 | 90 | 50 | 96 | 8 | 13 | 45 | 26 | 0 | 52 | 30 | 0 | 320 | 380 | 0 | 10 | 138 | 8 | 0 | 77 | 30 | 0 | 18 | 170 | 17 | 55 | 125 | 44 | 1 | 25.22 | 12 | 7224.02 | 884 | 210 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 32.16 | 447 | 0 | 875.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 21.06 | 0 | 0 | 170 | 0 | 140 | 0 | 360 | 0 | 2.04 | 156 | 49 | 0 | 7 | 34 | 0 | 0 | 1.8 | 15 | 0.11 | 0 | 173 | 120 | 220 | 0 | 617 | 1000 | 0 | 5635.94 | 12859.96 | 98.82
12:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 48.96 | 35 | 69 | 15 | 95 | 0 | 48 | 85 | 50 | 450 | 298 | 0 | 0 | 0 | 325 | 195 | 0 | 12 | 70 | 23.5 | 15 | 0 | 0 | 0 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 60 | 88 | 4.01 | 212 | 16 | 3 | 686 | 0 | 0 | 19 | 0 | 32 | 217 | 0 | 0 | 0 | 580 | 11 | 43 | 90 | 35 | 0 | 342 | 330 | 43 | 206 | 16 | 90 | 50 | 97 | 8 | 13 | 50 | 28 | 0 | 60 | 30 | 0 | 320 | 384 | 0 | 10 | 144 | 8 | 0 | 77 | 30 | 0 | 18 | 170 | 17 | 55 | 125 | 44 | 0 | 23.37 | 12 | 7062.84 | 885 | 209 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2.15 | 461 | 0 | 881.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 2.01 | 0 | 0 | 170 | 0 | 160 | 0 | 410 | 0 | 0.31 | 157 | 49 | 0 | 9 | 34 | 0 | 0 | 4.7 | 20 | 0.1 | 0 | 184 | 120 | 220 | 0 | 618 | 1003 | 0 | 5680.2 | 12743.04 | 98.83
13:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 47.16 | 35 | 69 | 15 | 95 | 0 | 53 | 122 | 50 | 450 | 280 | 0 | 0 | 0 | 270 | 203 | 0 | 1 | 52 | 24 | 14 | 0 | 0 | 0 | 65 | 0 | 0 | 10 | 0 | 0 | 0 | 76 | 100 | 4.42 | 212 | 32 | 7 | 653 | 0 | 0 | 19 | 0 | 74 | 216 | 0 | 0 | 0 | 520 | 18 | 43 | 112 | 80 | 0 | 300 | 280 | 42 | 191 | 18 | 88 | 45 | 93 | 8 | 20 | 46 | 30 | 0 | 30 | 30 | 0 | 320 | 353 | 0 | 10 | 133 | 8 | 0 | 79 | 30 | 0 | 16 | 170 | 17 | 55 | 105 | 43 | 0 | 21.11 | 12 | 7085.69 | 885 | 207 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2.17 | 490 | 0 | 959.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 7.73 | 0 | 0 | 170 | 0 | 160 | 0 | 337 | 0 | 1.09 | 155 | 47 | 0 | 5 | 34 | 0 | 0 | 0 | 9 | 0.5 | 0 | 216 | 100 | 180 | 0 | 618 | 1007 | 0 | 5667.18 | 12752.87 | 98.84
14:00 | 0 | 17 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 35.64 | 7 | 51 | 0 | 95 | 0 | 20 | 108 | 50 | 450 | 305 | 0 | 0 | 17 | 270 | 199 | 0 | 1 | 52 | 24 | 21 | 0 | 0 | 0 | 65 | 0 | 0 | 23 | 0 | 0 | 0 | 76 | 100 | 4.82 | 214 | 48 | 6 | 682 | 0 | 0 | 19 | 0 | 97 | 215 | 0 | 0 | 0 | 476 | 8 | 51 | 120 | 81 | 0 | 300 | 280 | 42 | 206 | 19 | 88 | 45 | 96 | 8 | 0 | 49 | 30 | 0 | 43 | 0 | 0 | 320 | 336 | 0 | 10 | 141 | 8 | 0 | 80 | 30 | 0 | 16 | 170 | 17 | 55 | 105 | 32 | 0 | 0.17 | 12 | 6987.63 | 885 | 204 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7.05 | 462 | 0 | 976.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 3.3 | 0 | 0 | 170 | 0 | 160 | 0 | 370 | 0 | 0.09 | 155 | 49 | 0 | 6 | 34 | 0 | 0 | 0 | 8 | 0.14 | 0 | 219 | 100 | 180 | 0 | 618 | 950 | 0 | 5611.03 | 12598.66 | 98.84
15:00 | 0 | 17 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 17 | 51 | 0 | 15 | 0 | 19 | 104 | 50 | 450 | 282 | 0 | 0 | 0 | 335 | 137 | 0 | 3 | 17 | 24 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 2 | 0 | 87 | 100 | 0.64 | 169 | 0 | 2 | 674 | 0 | 0 | 20 | 0 | 51 | 214 | 0 | 0 | 0 | 540 | 16 | 51 | 113 | 81 | 0 | 339 | 280 | 41 | 196 | 19 | 91 | 45 | 102 | 8 | 13 | 56 | 30 | 0 | 48 | 0 | 0 | 320 | 309 | 0 | 20 | 153 | 8 | 0 | 79 | 30 | 0 | 16 | 170 | 17 | 55 | 85 | 33 | 0 | 1.29 | 12 | 6678.93 | 885 | 200 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 10.2 | 473 | 0 | 1008.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 12.18 | 0 | 0 | 160 | 0 | 140 | 0 | 341 | 0 | 0.9 | 154 | 49 | 0 | 5 | 34 | 0 | 0 | 1.1 | 6 | 0.16 | 0 | 213 | 120 | 220 | 0 | 618 | 975 | 0 | 5704.13 | 12383.06 | 98.85
16:00 | 0 | 17 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 34 | 49 | 0 | 0 | 0 | 53 | 35 | 52 | 380 | 310 | 0 | 0 | 0 | 333 | 135 | 0 | 3 | 0 | 19 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 16 | 0 | 87 | 100 | 2.35 | 165 | 0 | 2 | 695 | 0 | 0 | 41 | 0 | 0 | 214 | 0 | 0 | 0 | 558 | 10 | 51 | 10 | 80 | 0 | 344 | 280 | 39 | 213 | 19 | 110 | 45 | 136 | 8 | 8 | 88 | 30 | 16 | 32 | 0 | 0 | 320 | 352 | 0 | 20 | 147 | 8 | 0 | 79 | 20 | 0 | 16 | 170 | 0 | 55 | 85 | 33 | 0 | 1.67 | 12 | 6569.02 | 884 | 200 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14.67 | 490 | 0 | 1032.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 9.99 | 0 | 0 | 140 | 0 | 140 | 0 | 400 | 0 | 0.91 | 155 | 49 | 0 | 1 | 0 | 0 | 0 | 1.6 | 16 | 0.1 | 0 | 177 | 120 | 220 | 0 | 618 | 1000 | 0 | 5728.87 | 12297.89 | 98.85
17:00 | 0 | 17 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 15 | 35 | 34 | 0 | 0 | 0 | 55 | 33 | 52 | 420 | 300 | 0 | 0 | 0 | 335 | 135 | 0 | 2 | 0 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 16 | 0 | 76 | 100 | 0.55 | 164 | 0 | 6 | 640 | 0 | 0 | 50 | 0 | 0 | 214 | 0 | 0 | 0 | 550 | 2 | 51 | 6 | 81 | 0 | 353 | 340 | 43 | 197 | 19 | 115 | 50 | 136 | 12 | 19 | 76 | 28 | 16 | 14 | 0 | 0 | 320 | 315 | 0 | 20 | 157 | 5 | 0 | 82 | 20 | 0 | 16 | 170 | 0 | 55 | 86 | 33 | 0 | 1.35 | 12 | 6551.9 | 884 | 198 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 11.67 | 495 | 0 | 1013.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 5.14 | 0 | 0 | 140 | 0 | 140 | 0 | 350 | 0 | 0.55 | 155 | 49 | 0 | 1 | 0 | 0 | 0 | 1.6 | 14 | 0.08 | 0 | 171 | 120 | 220 | 0 | 617 | 1020 | 0 | 5665.53 | 12217.43 | 98.86
18:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 16 | 35 | 36 | 0 | 0 | 0 | 55 | 31 | 52 | 420 | 312 | 0 | 0 | 0 | 280 | 137 | 0 | 1 | 17 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 17 | 0 | 76 | 100 | 0.12 | 163 | 0 | 10 | 690 | 0 | 0 | 50 | 0 | 0 | 215 | 0 | 0 | 0 | 512 | 1 | 51 | 6 | 81 | 0 | 348 | 340 | 45 | 213 | 19 | 115 | 50 | 136 | 26 | 19 | 85 | 26 | 16 | 3 | 4 | 0 | 320 | 384 | 0 | 20 | 144 | 8 | 0 | 84 | 30 | 0 | 16 | 171 | 11 | 75 | 125 | 33 | 0 | 0.61 | 12 | 6707.73 | 884 | 202 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4.52 | 466 | 0 | 952.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 2.53 | 0 | 0 | 140 | 0 | 140 | 0 | 396 | 0 | 0.3 | 155 | 49 | 0 | 1 | 0 | 0 | 0 | 0.7 | 4 | 0.03 | 0 | 177 | 120 | 180 | 0 | 618 | 1040 | 0 | 5575.92 | 12283.65 | 98.86
19:00 | 0 | 60 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 26 | 35 | 52 | 16 | 40 | 0 | 55 | 120 | 52 | 420 | 305 | 0 | 0 | 10 | 333 | 201 | 0 | 0 | 76 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 33 | 28 | 0 | 76 | 100 | 0 | 209 | 0 | 10 | 735 | 0 | 0 | 50 | 0 | 0 | 215 | 0 | 0 | 0 | 570 | 0 | 51 | 41 | 81 | 0 | 349 | 340 | 47 | 211 | 19 | 115 | 50 | 155 | 26 | 19 | 104 | 30 | 16 | 0 | 24 | 0 | 320 | 392 | 0 | 20 | 147 | 8 | 0 | 84 | 30 | 0 | 16 | 171 | 17 | 76 | 155 | 33 | 0 | 0 | 12 | 7442 | 884 | 204 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 461 | 10 | 1129.25 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 392 | 0 | 0 | 156 | 49 | 90 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 120 | 220 | 0 | 618 | 1050 | 0 | 6041.25 | 13483.25 | 98.87
19:30 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 46 | 35 | 58 | 16 | 90 | 0 | 55 | 145 | 52 | 450 | 283 | 0 | 0 | 35 | 335 | 201 | 0 | 0 | 90 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 33 | 0 | 76 | 100 | 0 | 209 | 0 | 12 | 688 | 0 | 0 | 50 | 0 | 0 | 216 | 0 | 0 | 0 | 575 | 0 | 51 | 120 | 104 | 0 | 355 | 340 | 49 | 196 | 19 | 115 | 50 | 156 | 26 | 19 | 100 | 28 | 30 | 0 | 30 | 0 | 320 | 353 | 0 | 20 | 155 | 8 | 0 | 84 | 30 | 0 | 18 | 171 | 17 | 77 | 190 | 33 | 0 | 0 | 12 | 7846 | 884 | 205 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 519 | 17 | 1216.97 | 0 | 0 | 0 | 36 | 0 | 58 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 174 | 0 | 175 | 0 | 407 | 0 | 0 | 156 | 50 | 92 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 120 | 220 | 0 | 618 | 1110 | 0 | 6472.97 | 14318.97
20:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 45 | 35 | 65 | 16 | 60 | 0 | 55 | 142 | 16 | 450 | 279 | 0 | 0 | 17 | 335 | 201 | 0 | 0 | 90 | 23 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50 | 40 | 0 | 76 | 100 | 0 | 215 | 0 | 17 | 685 | 0 | 0 | 50 | 0 | 0 | 216 | 0 | 0 | 0 | 560 | 0 | 51 | 127 | 108 | 0 | 357 | 340 | 48 | 190 | 19 | 114 | 50 | 168 | 26 | 20 | 95 | 28 | 43 | 0 | 31 | 0 | 320 | 309 | 0 | 20 | 143 | 8 | 0 | 84 | 30 | 0 | 18 | 171 | 17 | 65 | 200 | 50 | 0 | 0 | 12 | 7748 | 885 | 207 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 568 | 17 | 1201.74 | 0 | 0 | 0 | 42 | 0 | 75 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 200 | 0 | 200 | 0 | 338 | 0 | 0 | 154 | 49 | 94 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 120 | 220 | 0 | 618 | 1120 | 0 | 6558.74 | 14306.74 | 98.87
21:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 28 | 35 | 56 | 0 | 15 | 0 | 17 | 150 | 16 | 450 | 310 | 0 | 0 | 17 | 335 | 200 | 0 | 0 | 90 | 15 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 50 | 46 | 0 | 76 | 100 | 0 | 207 | 0 | 21 | 703 | 0 | 0 | 19 | 6 | 0 | 217 | 0 | 0 | 0 | 580 | 0 | 51 | 70 | 108 | 0 | 354 | 340 | 48 | 199 | 19 | 114 | 50 | 164 | 26 | 20 | 105 | 30 | 52.2 | 0 | 31 | 0 | 320 | 366 | 0 | 20 | 144 | 8 | 0 | 84 | 30 | 0 | 18 | 171 | 17 | 45 | 200 | 50 | 0 | 0 | 12 | 7723.2 | 885 | 205 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 611 | 17 | 1211 | 0 | 0 | 0 | 35 | 0 | 41 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 204 | 0 | 203 | 0 | 414 | 0 | 0 | 154 | 49 | 95 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 120 | 220 | 0 | 618 | 1110 | 0 | 6646 | 14369.2 | 98.88
22:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 15 | 35 | 52 | 0 | 15 | 0 | 17 | 146 | 16 | 450 | 307 | 0 | 0 | 17 | 335 | 200 | 0 | 0 | 90 | 23.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 50 | 46 | 0 | 88 | 100 | 0 | 208 | 0 | 25 | 737 | 0 | 0 | 19 | 8 | 0 | 218 | 0 | 0 | 0 | 575 | 0 | 51 | 70 | 53 | 0 | 355 | 335 | 48 | 197 | 19 | 114 | 50 | 174 | 27 | 20 | 100 | 30 | 25 | 0 | 31 | 0 | 320 | 370 | 0 | 20 | 153 | 8 | 0 | 84 | 30 | 0 | 18 | 171 | 17 | 45 | 200 | 50 | 0 | 0 | 12 | 7690.5 | 885 | 202 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 604 | 17 | 1211 | 0 | 0 | 0 | 35 | 0 | 41 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 199 | 0 | 200 | 0 | 409 | 0 | 0 | 156 | 50 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 120 | 220 | 0 | 619 | 1100 | 0 | 6621 | 14311.5 | 98.88
23:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 15 | 35 | 51 | 0 | 0 | 0 | 17 | 108 | 16 | 450 | 306 | 0 | 0 | 17 | 335 | 200 | 0 | 0 | 90 | 23.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 50 | 43 | 0 | 88 | 100 | 0 | 208 | 0 | 29 | 730 | 0 | 0 | 19 | 8 | 0 | 219 | 0 | 0 | 0 | 575 | 0 | 51 | 30 | 53 | 0 | 355 | 340 | 48 | 189 | 19 | 115 | 40 | 168 | 27 | 20 | 102 | 32 | 31 | 0 | 31 | 0 | 320 | 386 | 0 | 20 | 155 | 8 | 0 | 84 | 30 | 0 | 18 | 171 | 17 | 45 | 184 | 49 | 0 | 0 | 12 | 7581.5 | 882 | 202 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 608 | 17 | 1214 | 0 | 0 | 0 | 35 | 0 | 41 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 199 | 0 | 204 | 0 | 414 | 0 | 0 | 157 | 50 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 120 | 220 | 0 | 619 | 1100 | 0 | 6634 | 14215.5 | 98.89
Total KWH | 0 | 1141440 | 745440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9553050 | 374760 | 750240 | 1115424 | 198240 | 643080 | 0 | 624088 | 1565280 | 566400 | 10319000 | 7279709 | 0 | 0 | 194303 | 7825440 | 4770000 | 0 | 69517 | 1474800 | 528000 | 437760 | 0 | 0 | 0 | 228327 | 0 | 0 | 364800 | 520554 | 271200 | 0 | 1595520 | 2024640 | 27117 | 4940204 | 162300 | 348960 | 16741818.2 | 0 | 0 | 430080 | 53418.6 | 348764 | 5097443 | 0 | 0 | 0 | 12981817 | 88290 | 1160587 | 1020363 | 1087272 | 0 | 8591800 | 7678000 | 1097760 | 4922000 | 449712 | 2424000 | 1134040 | 3294720 | 327600 | 406830 | 1843380 | 640320 | 445325 | 426755 | 552800 | 0 | 7658200 | 9253000 | 0 | 340000 | 3618736 | 176376 | 0 | 1937280 | 686688 | 0 | 428000 | 4524970 | 398160 | 1441200 | 3384000 | 994560 | 3800 | 145280 | 299520 | 169194257.8 | 21411637 | 4939776 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 183600 | 12370910 | 88800 | 24288364 | 0 | 4536 | 0 | 294720 | 0 | 232736 | 0 | 0 | 0 | 402570 | 134515 | 112504 | 0 | 0 | 4621327 | 0 | 3999127 | 0 | 9121382 | 0 | 10440 | 3856000 | 1144145 | 825054 | 90187 | 1418198 | 0 | 0 | 21048 | 313920 | 3181 | 0 | 5040000 | 2774000 | 5365380 | 0 | 14783976 | 25297454.55 | 0 | 144061487.55 | 313255745.35

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 15-07-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12859.96 | MW | 11:00 Hr. | Energy Generated |  |  | 313.2557 |  | MKWHr.
| Day Peak Demand |  |  | 12859.96 | MW | 11:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 14369.2 | MW | 21:00 Hr. | Energy Demand |  |  | 313.2557 |  | MKWHr.
| Evening Peak Demand |  |  | 14369.2 | MW | 21:00 Hr. | Maximum Temperature |  |  | 31.8 |  | °C
| Minimum Generation of the Day |  |  | 11801.79 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 977.6 |  | MMCFD
| Maximum Generation of the Day |  |  | 14369.2 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 5.9223 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.713 | 0 | 9.3935 | 0 | 0 | 0.069517 | 0 | 0 | 50.176 | Gas | 133.1262 | Gas | 457724831.15
| Chattogram Zone |  |  | 5.4464 | 29.7236 | 5.6348 | 0 | 4.9402 | 0.11541 | 0 | 0.3648 | 46.2253 | Coal | 92.2161 | Coal | 520444812.6325
| Cumilla Zone |  |  | 26.528 | 0 | 9.9082 | 0 | 0 | 0.42675 | 0.64032 | 0 | 37.5033 | HFO | 33.4579 | HFO | 619643244.832
| Mymensingh Zone |  |  | 0.99456 | 0 | 5.5229 | 0 | 0 | 0.14908 | 0 | 0 | 6.6665 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.6232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.6232 | Hydro | 4.9402 | Hydro | 494020.4
| Khulna Zone |  |  | 4.9398 | 12.3709 | 0.0888 | 0 | 0 | 0.1836 | 22.3236 | 0 | 39.9067 | Solar | 1.8982 | Solar | 29123535.54
| Barishal Zone |  |  | 8.1394 | 45.1214 | 0 | 0 | 0 | 0.003181 | 0 | 0 | 53.264 | Import | 47.2523 | Import | 222430412.19
| Rajshahi Zone |  |  | 17.7418 | 0 | 0.66651 | 0 | 0 | 0.52551 | 24.2884 | 0 | 43.2222 | Wind | 0.3648 | Wind | 5340672
| Rangpur Zone |  |  | 0 | 5.0001 | 2.2433 | 0 | 0 | 0.42516 | 0 | 0 | 7.6686
| Total |  |  | 133.1262 | 92.2161 | 33.4579 | 0 | 4.9402 | 1.8982 | 47.2523 | 0.3648 | 313.2557
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 457724831.15 |  | Hydro | 494020.4
|  |  |  | Coal | 520444812.6325 |  | Solar | 29123535.54
|  |  |  | HFO | 619643244.832 |  | Import | 222430412.19
|  |  |  | HSD | 0 |  | Wind | 5340672
[5 empty] | Total: | 185,52,01,528 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.4116 | Peak Hr Flow | 885.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 46373381.91 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.2884 | Peak Hr Flow | 1211.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 810 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.64032 | Peak Hr Flow | 30.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 948 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 46.3403 | Peak Hr Flow | 2126.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4838
|  |  |  | Chattogram |  | 0 |  | 1411
|  |  |  | Cumilla |  | 0 |  | 1394
|  |  |  | Mymensingh |  | 0 |  | 1126
|  |  |  | Sylhet |  | 0 |  | 661
|  |  |  | Khulna |  | 0 |  | 1605
|  |  |  | Barishal |  | 0 |  | 468
|  |  |  | Rajshahi |  | 0 |  | 1326
|  |  |  | Rangpur |  | 0 |  | 947
|  |  |  | Total |  | 0 |  | 13776
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Bibiana-II 341 MW CCPP (Summit) GT |  |  | 222 | 3 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
|  | 4 | Bibiana-II 341 MW CCPP (Summit) ST |  |  | 119
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 641 |  |  |  | Total | 476
|  |  |  | Total Unavailable Capacity |  |  |  | 1117
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:53 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is OFF with remarks:- Gas Shortage
| 09:34 |  | Ashuganj-Ghorasal 132kV Ckt-2 Project Work S/D from Ashuganj 230/132/33kV end Due to GIS
project work
| 10:30 | 12:43 | Khulna (C) S/S Tr-2 415 T LT Forced S/D Due to Due to 33kv seromoni 2 feeder faulty
| 10:31 | 12:42 | Khulna (C) S/S Tr-2 415 T HT Forced S/D Due to Due to 33 kv seromoni-2 feeder faulty
| 11:00 |  | Day peak generation 12857 MW
| 11:58 | 12:39 | Gollamari 132/33kV S/S Tr-1 LT Tripped showing Backup relay 1 relays Due to due to Khulna | [7 empty] | 32.0MW load
|  |  | Sadar (PBS) Feeder fault. | [7 empty] | interrup.
| 11:58 | 12:40 | Gollamari 132/33kV S/S Tr-2 LT Tripped showing Backup protection-1 relay relays Due to | [7 empty] | 32.0MW load
|  |  | Due to Khulna sadar (PBS) | [7 empty] | interrup.
| 13:15 | 14:04 | Niamatpur 132/33kV S/S Transformer-3(426T) LT Tripped showing OC/ EF & OPTD relays Due | [7 empty] | 6.0MW load
|  |  | to Finding… (আবহাওয়া জনিত কারনে T-3, ৩৩ কেভি বাসে সংযুক্ত পবিস Rajshahi-2, ফিডার Relay | [7 empty] | interrup.
তে O/C, E/F DMT Signal দেখায় কিন্তু তাদের ব্রেকার ট্রিপ না করে গ্রিড এর 33kV Breaker (T-3
transformer) ট্রিপ করে।)
|  | 13:57 | Munshiganj 132/33kV S/S Transformer-2 LT is restored.
| 14:22 |  | Ishwardi- Sathia 132kV circuit and Sathia- Baghabari 132kV circuit were switched ON at
14:22 hrs. and 14:26 hrs. respectively. Also, Sathia 132/33kV T-1 and T-2 transformers
were switched ON with no load for the first time at 14:38 hrs. and 14:40
hrs. respectively.
| 14:37 | 14:57 | Munshiganj 132/33kV S/S Transformer-1 LT Tripped showing DIR E/F Trip relays. | [7 empty] | 41.0MW load
interrup.
| 14:37 |  | Munshiganj 132/33kV S/S Transformer-2 LT Tripped showing DIR E/F Trip relays Due to None | [7 empty] | 41.0MW load
interrup.
| 16:48 | 18:02 | Goalpara 132/33kV S/S T1 LT Scheduled S/D Due to Khulna PBS taken Shutdown due to remove | [7 empty] | 8.0MW load
|  |  | red hot on Therokhada feeder | [7 empty] | interrup.
| 16:49 | 18:01 | Goalpara 132/33kV S/S T1 HT Scheduled S/D Due to Khulna PBS taken Shutdown due to remove | [7 empty] | 8.0MW load
|  |  | red hot on Therokhada feeder | [7 empty] | interrup.
| 16:50 | 18:00 | Goalpara 132/33kV S/S T-5 LT Scheduled S/D Due to Khulna PBS taken Shutdown due to remove | [7 empty] | 8.0MW load
|  |  | red hot on Therokhada feeder | [7 empty] | interrup.
| 16:51 | 17:59 | Goalpara 132/33kV S/S T-5 HT Scheduled S/D Due to Khulna PBS taken Shutdown due to remove | [7 empty] | 8.0MW load
|  |  | red hot on Therokhada feeder | [7 empty] | interrup.
| 16:53 | 17:58 | Goalpara 132/33kV S/S T-6 LT Scheduled S/D Due to Khulna PBS taken Shutdown due to remove | [7 empty] | 8.0MW load
|  |  | red hot on Therokhada feeder | [7 empty] | interrup.
| 16:54 | 17:57 | Goalpara 132/33kV S/S T-6 HT Scheduled S/D Due to Khulna PBS taken Shutdown due to remove | [7 empty] | 8.0MW load
|  |  | red hot on Therokhada feeder | [7 empty] | interrup.
| 20:08 |  | Raozan 25 MW PP Synchronized
| 21:00 |  | Evening Peak Generation: 14369 MW.
| 23:26 |  | Bhola 225 MW CCPP tripped due to gas booster trip.
| 23:47 |  | Bashkhali SS Power Unit-2 was sync.
| 03:04 |  | Raozan 25 MW PP Shutdown
| 06:00 |  | Minimum Generation 12108 MW.
| 06:30 |  | Kishoreganj 132/33kV S/S Tr-3 (424T) LT Scheduled S/D Due to 33 kv T-3 bus Shutdown,Due | [7 empty] | 30.0MW load
|  |  | to pakundia feeder hotspot maintenance work | [7 empty] | interrup.
| 06:31 |  | Kishoreganj 132/33kV S/S Tr-3 (424T) HT Scheduled S/D Due to 33 kv Bus Shutdown, pakundia | [7 empty] | 30.0MW load
|  |  | feeder hotspot maintenance work. | [7 empty] | interrup.
| 06:54 |  | Kishoreganj 132/33kV S/S Tr-1 (404T) LT Scheduled S/D Due to 33kv bus shutdown due to | [7 empty] | 10.0MW load
|  |  | 33kv t-4 hotspot maintenance | [7 empty] | interrup.
| 06:55 |  | Kishoreganj 132/33kV S/S Tr-1 (404T) HT Scheduled S/D Due to 33 kv bus Shutdown,due to | [7 empty] | 10.0MW load
|  |  | PBD feeder hotspot maintenance work | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 15-07-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10319000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 310 | 7279709 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 200 | 4770000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7825440 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 28 | 374760 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 198240 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 624088 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 194303 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 15 | 528000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 13 | 437760 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 33 | 745440 | Engine Problem
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | -
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 15 | 643080 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 56 | 1115424 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1141440 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 566400 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 150 | 1565280 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 69517 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 750240 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 550 | 9553050 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 90 | 1474800 | Engine Problem
Dhaka Area Total |  |  |  |  | 5939.724 | 2418 | 50175971
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 6 | 53418.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 88290 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 430080 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 207 | 4940204 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5097443 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 348764 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 46 | 271200 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 520554 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 76 | 1595520 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 21 | 348960 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 27117 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 228327 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 162300 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2024640 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 580 | 12981817 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 14 | 364800 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 703 | 16741818.2 | FGMO
Chattogram Area Total |  |  |  |  | 4895.72 | 2039 | 46225252.8
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 199 | 4922000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 354 | 8591800 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 7678000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 19 | 449712 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 48 | 1097760 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 108 | 1087272 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1160587 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 70 | 1020363 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 31 | 552800 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1134040 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 164 | 3294720 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 30 | 640320 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 445325 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 406830 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 105 | 1843380 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 26 | 327600 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 114 | 2424000 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 426755 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1781.2 | 37503264
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 50 | 994560 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 3800 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 200 | 3384000 | Engine Problem
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 45 | 1441200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 145280 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 299520 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 398160 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 324 | 6666520
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 20 | 340000 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 144 | 3618736 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 686688 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1937280 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 171 | 4524970 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 428000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 176376 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 366 | 9253000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7658200 | Aythority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2325 | 1161 | 28623250
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 885 | 21411637 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 205 | 4939776 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 88800 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 183600 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 611 | 12370910 | U#1 Under Reserve shut down
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1756 | 39906723
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 618 | 14783976 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2774000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1110 | 25297454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5365380 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 278 | 5040000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3181 | -
Barishal Area Total |  |  |  |  | 2236 | 2346 | 53263991.55
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 4536 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 204 | 4621327 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 203 | 3999127 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9121382 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 134515 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 41 | 232736 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 294720 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 10440 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1211 | 24288364 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 112504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 402570 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2138 | 43222221
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 49 | 1144145 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 154 | 3856000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 108 | 1418198 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 21048 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 825054 | Schedule Maintenance
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 90187 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 313920 | -
Rangpur Area Total |  |  |  |  | 950 | 406 | 7668552
Eastern Grid Total |  |  |  |  | 16705.895 | 7723.2 | 169194257.8
Western Grid Total |  |  |  |  | 10378.16 | 6646 | 144061487.55
National Grid Total |  |  |  |  | 27084.055 | 14369.2 | 313255745.35
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 15-07-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9430.55 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4346.4 | MW
i) Dhaka area |  |  | 4838.3 |  | MW | i) Khulna area |  |  |  | 1605.3 | MW
ii) Chattogram area |  |  | 1411.1 |  | MW | ii) Barishal area |  |  |  | 468.5 | MW
iii) Cumilla area |  |  | 1394.15 |  | MW | iii) Rajshahi area |  |  |  | 1325.6 | MW
iv) Mymensingh area |  |  | 1126 |  | MW | iv) Rangpur area |  |  |  | 947 | MW
v) Sylhet area |  |  | 661 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13776.95 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 85 | 19:00 | 133 | Pabna | 115 | 19:30
2 | AKSML | 138.9 | 15:00 | 68 | Ishurdi | 75 | 19:30 | 134 | Palashbari | 106 | 00:00
3 | Aftabnagar | 38 | 12:00 | 69 | Jaldhaka | 80 | 22:00 | 135 | Panchagarh | 67 | 19:30
4 | Agargaon | 124 | 13:00 | 70 | Jamalpur | 127 | 20:00 | 136 | Patuakhali | 72 | 22:00
5 | Agrabad | 96 | 15:00 | 71 | Jashore | 124 | 20:00 | 137 | Payra | 36 | 22:00
6 | Amnura | 32 | 21:00 | 72 | Jhenaidah | 109 | 21:00 | 138 | Postogola | 58 | 12:00
7 | Ashuganj | 97 | 23:00 | 73 | Joydebpur | 139 | 11:00 | 139 | Purbachal | 19 | 12:00
8 | BSRM | 198 | 02:00 | 74 | Joypurhat | 62 | 00:00 | 140 | Purbasadipur | 136 | 00:00
9 | Bagerhat | 77 | 19:30 | 75 | Juldah | 16 | 00:00 | 141 | Rahanpur | 26 | 21:00
10 | Bajitpur | 59 | 20:00 | 76 | KSRM | 30 | 13:00 | 142 | Rahim | 23 | 09:00
11 | Bakulia | 97 | 19:30 | 77 | Kabirpur | 225 | 10:00 | 143 | Rajbari | 74 | 19:30
12 | Banani | 36.8 | 12:00 | 78 | Kachua | 92 | 22:00 | 144 | Rajendrapur | 127 | 00:00
13 | Bangabhaban | 17 | 10:00 | 79 | Kallyanpur | 105 | 11:00 | 145 | Rajshahi | 107 | 00:00
14 | Barapukuria | 64 | 00:00 | 80 | Kalurghat | 40 | 12:00 | 146 | Rajshahi-230 | 70 | 21:00
15 | Barguna | 22 | 19:00 | 81 | Kamrangirchar | 71.6 | 12:00 | 147 | Ramganj | 118 | 22:00
16 | Barishal | 111 | 20:00 | 82 | Kaptai | N/A | N/A | 148 | Rampur | 42 | 23:00
17 | Barishal-230 | 98 | 21:00 | 83 | Kasba | 38 | 22:00 | 149 | Rangamati | 18 | 19:00
18 | Baroaulia | 69 | 15:00 | 84 | Kazla | 100 | 13:00 | 150 | Rangpur | 137 | 00:00
19 | Baroirhat | 63 | 20:00 | 85 | Keranigonj | 100 | 19:30 | 151 | Ruppur | 7.2 | 15:00
20 | Bashundhara | 187 | 12:00 | 86 | Khagrachori | 32 | 19:00 | 152 | SSM | 14 | 00:00
21 | BashundharaCement | 9 | 11:00 | 87 | Khulna | 81 | 21:00 | 153 | Saidpur | 101 | 12:00
22 | Beanibazar | 86 | 23:00 | 88 | Khulshi | 142 | 19:00 | 154 | Satkhira | 124 | 22:00
23 | Benapole | 51 | 20:00 | 89 | Kishoreganj | 131 | 00:00 | 155 | Satmasjid | 84 | 13:00
24 | Bhaluka | 142 | 12:00 | 90 | Kodda | 317 | 12:00 | 156 | Savar | 231 | 10:00
25 | Bhandaria | 56 | 22:00 | 91 | Kulaura | 54 | 19:00 | 157 | SevenRings | 9.46 | 06:00
26 | Bhangura | 32 | 21:00 | 92 | Kurigram | 60 | 00:00 | 158 | ShahCement | 20 | 10:00
27 | Bheramara(GK) | 58 | 19:30 | 93 | Kushtia | 146 | 20:00 | 159 | Shahjadpur | 70 | 19:30
28 | Bhulta | 247 | 02:00 | 94 | Lakshmipur | 32 | 23:00 | 160 | Shahjibazar | 130 | 22:00
29 | Bog-Sherpur | 66 | 00:00 | 95 | Lalbag | 58 | 13:00 | 161 | Shahmirpur | 60 | 00:00
30 | Bogura | 160 | 00:00 | 96 | Lalmonirhat | 60 | 19:00 | 162 | Shariatpur | 83 | 23:00
31 | Borhanuddin | 98 | 22:00 | 97 | MI_Cement | 11.8 | 12:00 | 163 | Sherpur | 146 | 00:00
32 | Brahmanbaria | 131 | 21:00 | 98 | Madanganj | 40 | 10:00 | 164 | Shikalbaha | 14 | 12:00
33 | Cantonment | 146 | 12:00 | 99 | Madaripur | 97 | 23:00 | 165 | Shitalakhya | 87.2 | 12:00
34 | Chandina | 20.08 | 14:00 | 100 | Madartek | 83 | 00:00 | 166 | Sholosohor | 47 | 15:00
35 | Chandpur | 77 | 22:00 | 101 | Madunaghat | 56 | 14:00 | 167 | Shyampur | 170 | 12:00
36 | Chandraghona | 37 | 19:00 | 102 | Magura | 57 | 20:00 | 168 | Siddhirganj | 115 | 15:00
37 | Chapai | 62 | 21:00 | 103 | Mahasthangarh | 84 | 00:00 | 169 | Sirajganj | 102 | 21:00
38 | Charsaidpur | 26 | 00:00 | 104 | Maijdee | 15 | 19:30 | 170 | Sonargaon | 105 | 00:00
39 | Chauddagram | 71 | 22:00 | 105 | Manikganj | 118 | 22:00 | 171 | Sreemongol | 83 | 23:00
40 | Chhatak | 45 | 22:00 | 106 | Maniknagar | 80 | 12:00 | 172 | Sreepur | 97 | 12:00
41 | Chowmuhani | 185 | 19:00 | 107 | Matarbari | 53 | 19:30 | 173 | Srinagar | 42.98 | 22:00
42 | Chuadanga | 100 | 19:30 | 108 | Matuail | 68 | 12:00 | 174 | Sunamganj | 66 | 22:00
43 | Coxsbazar | 134 | 21:00 | 109 | Millgate | 91 | 12:00 | 175 | Sylhet | 54 | 21:00
44 | Cumilla(N) | 138 | 21:00 | 110 | Mirpur | 120 | 12:00 | 176 | Sylhet-132 | 139 | 19:30
45 | Cumilla(S) | 149 | 19:30 | 111 | Mirsorai | 11 | 10:00 | 177 | TK | 34 | 23:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirzapur | 44 | 19:00 | 178 | Tangail | 162 | 00:00
47 | Daudkandi | 139 | 22:00 | 113 | Mithapukur | 70 | 00:00 | 179 | Taraganj | 21 | 00:00
48 | Dhaka | 70 | 11:00 | 114 | Modern | N/A | N/A | 180 | Thakurgaon | 110 | 21:00
49 | Dhamrai | 122 | 10:00 | 115 | Mogbazar | 136.2 | 10:00 | 181 | Tongi | 127 | 11:00
50 | Dhanmondi | 117.6 | 13:00 | 116 | Mongla | 32 | 10:00 | 182 | Ullahpara | 32 | 19:30
51 | Dohazari | 112 | 22:00 | 117 | Motijheel | 41 | 11:00 | 183 | Ullon | 37 | 20:00
52 | Faridpur | 147 | 21:00 | 118 | Muktagacha | 34 | 19:30 | 184 | Uttara | 75 | 11:00
53 | Fatullah | 99 | 12:00 | 119 | Munshiganj | 102 | 00:00 | 185 | UttaraNew | 58 | 12:00
54 | Fenchuganj | 44 | 19:30 | 120 | Muradnagar | 45 | 19:30 | 186 | Zigatola | 69 | 11:00
55 | Feni | 119 | 19:00 | 121 | Mymensingh | 208 | 21:00
56 | GPH | 17 | 14:00 | 122 | Naogaon | 122 | 00:00
57 | Ghatail | 76 | 00:00 | 123 | Narail | 52 | 19:30
58 | Ghorashal | 14 | 00:00 | 124 | Narinda | 74 | 12:00
59 | Ghorashal-230 | 86 | 22:00 | 125 | Narshingdi | 175 | 22:00
60 | Goalpara | 36 | 13:00 | 126 | Natore | 135 | 20:00
61 | Gollamari | 70 | 00:00 | 127 | Nawabganj | 50 | 21:00
62 | Gopalganj | 100 | 20:00 | 128 | Netrakona | 135 | 20:00
63 | Gulshan | 124 | 12:00 | 129 | New | 92.8 | 12:00
64 | Halishahar | 71 | 14:00 | 130 | Niamatpur | 62 | 01:00
65 | HaripurSBU | 163 | 11:00 | 131 | Noapara | 40 | 19:30
66 | Hasnabad | 67 | 12:00 | 132 | PHP | 8 | 09:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 15-07-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13842.2 | 0 |  | 13842.2
1:00 | 13564.2 | 0 |  | 13564.2
2:00 | 13083.7 | 0 |  | 13083.7
3:00 | 12791.7 | 0 |  | 12791.7
4:00 | 12445.5 | 0 |  | 12445.5
5:00 | 12121.5 | 0 |  | 12121.5
6:00 | 11801.79 | 0 |  | 11801.79
7:00 | 11967.61 | 0 |  | 11967.61
8:00 | 12049.1 | 0 |  | 12049.1
9:00 | 12343.61 | 0 |  | 12343.61
10:00 | 12622.06 | 0 |  | 12622.06
11:00 | 12859.96 | 0 |  | 12859.96
12:00 | 12743.04 | 0 |  | 12743.04
13:00 | 12752.87 | 0 |  | 12752.87
14:00 | 12598.66 | 0 |  | 12598.66
15:00 | 12383.06 | 0 |  | 12383.06
16:00 | 12297.89 | 0 |  | 12297.89
17:00 | 12217.43 | 0 |  | 12217.43
18:00 | 12283.65 | 0 |  | 12283.65
19:00 | 13483.25 | 0 |  | 13483.25
19:30 | 14318.97 | 0 |  | 14318.97
20:00 | 14306.74 | 0 |  | 14306.74
21:00 | 14369.2 | 0 |  | 14369.2
22:00 | 14311.5 | 0 |  | 14311.5
23:00 | 14215.5 | 0 |  | 14215.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 15-07-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7224.2 | 6618 | 13842.2 | DAILY GENERATION CURVE
00:30 | 7215.2 | 6488 | 13703.2
01:00 | 7206.2 | 6358 | 13564.2 | 15-07-2025
01:30 | 7110.45 | 6213.5 | 13323.95
02:00 | 7014.7 | 6069 | 13083.7
02:30 | 6938.7 | 5999 | 12937.7
03:00 | 6862.7 | 5929 | 12791.7
03:30 | 6750.1 | 5868.5 | 12618.6
04:00 | 6637.5 | 5808 | 12445.5
04:30 | 6524 | 5759.5 | 12283.5
05:00 | 6410.5 | 5711 | 12121.5
05:30 | 6340.305 | 5621.34 | 11961.645
06:00 | 6270.11 | 5531.68 | 11801.79
06:30 | 6341.415 | 5543.285 | 11884.7
07:00 | 6412.72 | 5554.89 | 11967.61
07:30 | 6432.28 | 5576.075 | 12008.355
08:00 | 6451.84 | 5597.26 | 12049.1
08:30 | 6492.98 | 5703.375 | 12196.355
09:00 | 6534.12 | 5809.49 | 12343.61
09:30 | 6687.215 | 5795.62 | 12482.835
10:00 | 6840.31 | 5781.75 | 12622.06
10:30 | 7032.165 | 5708.845 | 12741.01
11:00 | 7224.02 | 5635.94 | 12859.96
11:30 | 7143.43 | 5658.07 | 12801.5
12:00 | 7062.84 | 5680.2 | 12743.04
12:30 | 7074.265 | 5673.69 | 12747.955
13:00 | 7085.69 | 5667.18 | 12752.87
13:30 | 7036.66 | 5639.105 | 12675.765
14:00 | 6987.63 | 5611.03 | 12598.66
14:30 | 6833.28 | 5657.58 | 12490.86
15:00 | 6678.93 | 5704.13 | 12383.06
15:30 | 6623.975 | 5716.5 | 12340.475
16:00 | 6569.02 | 5728.87 | 12297.89
16:30 | 6560.46 | 5697.2 | 12257.66
17:00 | 6551.9 | 5665.53 | 12217.43
17:30 | 6629.815 | 5620.725 | 12250.54
18:00 | 6707.73 | 5575.92 | 12283.65
18:30 | 7074.865 | 5808.585 | 12883.45
19:00 | 7442 | 6041.25 | 13483.25
19:30 | 7846 | 6472.97 | 14318.97
20:00 | 7748 | 6558.74 | 14306.74
20:30 | 7735.6 | 6602.37 | 14337.97 |  | Executive Engineer
21:00 | 7723.2 | 6646 | 14369.2 |  | Network Operation Division
21:30 | 7706.85 | 6633.5 | 14340.35
22:00 | 7690.5 | 6621 | 14311.5
22:30 | 7636 | 6627.5 | 14263.5
23:00 | 7581.5 | 6634 | 14215.5

## En-Curve
QF-LDC-12
Date | 15-07-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3732 | 1780 | 891 | 38 | 28 | 1223 | 214 | 4206 | 0 | 389 | 1320.2 | 0 | 0 | 21 | 0 | DAILY ENERGY CURVE
00:30 | 3688 | 1776.5 | 888 | 38 | 27 | 1202 | 214 | 4151 | 0 | 364 | 1331.2 | 0 | 0 | 23.5 | 0 | 15-07-2025
01:00 | 3644 | 1773 | 885 | 38 | 26 | 1181 | 214 | 4096 | 0 | 339 | 1342.2 | 0 | 0 | 26 | 0
01:30 | 3638 | 1769.25 | 885 | 38 | 26 | 1164.5 | 215 | 4030.5 | 0 | 322 | 1210.2 | 0 | 0 | 25.5 | 0 | Energy Generated | 313.2557 |  | MKWHr
02:00 | 3632 | 1765.5 | 885 | 38 | 26 | 1148 | 216 | 3965 | 0 | 305 | 1078.2 | 0 | 0 | 25 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3644.5 | 1762.5 | 885 | 38 | 25 | 1118 | 214 | 3933 | 0 | 257 | 1043.2 | 0 | 0 | 17.5 | 0 | Total Energy Requirement | 313.2557 |  | MKWHr
03:00 | 3657 | 1759.5 | 885 | 38 | 24 | 1088 | 212 | 3901 | 0 | 209 | 1008.2 | 0 | 0 | 10 | 0
03:30 | 3653.5 | 1762.5 | 884.5 | 38 | 24 | 1056.5 | 212 | 3860 | 0 | 191.5 | 925.1 | 0 | 0 | 11 | 0
04:00 | 3650 | 1765.5 | 884 | 38 | 24 | 1025 | 212 | 3819 | 0 | 174 | 842 | 0 | 0 | 12 | 0
04:30 | 3670.5 | 1767.5 | 884 | 38 | 24 | 1024 | 211.5 | 3690 | 0 | 174 | 785 | 0 | 0 | 15 | 0
05:00 | 3691 | 1769.5 | 884 | 38 | 24 | 1023 | 211 | 3561 | 0 | 174 | 728 | 0 | 0 | 18 | 0
05:30 | 3666 | 1751 | 884.5 | 38 | 23 | 974 | 211 | 3528.5 | 6.145 | 159 | 703.5 | 0 | 0 | 17 | 0
06:00 | 3641 | 1732.5 | 885 | 38 | 22 | 925 | 211 | 3496 | 12.29 | 144 | 679 | 0 | 0 | 16 | 0
06:30 | 3673 | 1745.5 | 884.5 | 38 | 22 | 901 | 211 | 3543 | 46.2 | 148.5 | 656.5 | 0 | 0 | 15.5 | 0
07:00 | 3705 | 1758.5 | 884 | 38 | 22 | 877 | 211 | 3590 | 80.11 | 153 | 634 | 0 | 0 | 15 | 0
07:30 | 3695.5 | 1747.5 | 884.5 | 38 | 22 | 876.525 | 212 | 3600 | 113.83 | 154.5 | 650.5 | 0 | 0 | 13.5 | 0
08:00 | 3686 | 1736.5 | 885 | 38 | 22 | 876.05 | 213 | 3610 | 147.55 | 156 | 667 | 0 | 0 | 12 | 0
08:30 | 3728.5 | 1741.5 | 884.5 | 38 | 22 | 874.75 | 213 | 3585.5 | 251.105 | 156 | 689 | 0 | 0 | 12.5 | 0
09:00 | 3771 | 1746.5 | 884 | 38 | 22 | 873.45 | 213 | 3561 | 354.66 | 156 | 711 | 0 | 0 | 13 | 0
09:30 | 3725.5 | 1762.75 | 884 | 38 | 23 | 874.95 | 216.5 | 3614.5 | 309.815 | 169 | 851.32 | 0 | 0 | 13.5 | 0
10:00 | 3680 | 1779 | 884 | 38 | 24 | 876.45 | 220 | 3668 | 264.97 | 182 | 991.64 | 0 | 0 | 14 | 0
10:30 | 3646 | 1809.5 | 884 | 38 | 25 | 876.11 | 218 | 3684.5 | 253.04 | 182 | 1114.36 | 0 | 0 | 10.5 | 0
11:00 | 3612 | 1840 | 884 | 38 | 26 | 875.77 | 216 | 3701 | 241.11 | 182 | 1237.08 | 0 | 0 | 7 | 0
11:30 | 3669 | 1719.75 | 884.5 | 38 | 27 | 878.85 | 214 | 3719.5 | 215.88 | 182 | 1245.52 | 0 | 0 | 7.5 | 0
12:00 | 3726 | 1599.5 | 885 | 38 | 28 | 881.93 | 212 | 3738 | 190.65 | 182 | 1253.96 | 0 | 0 | 8 | 0
12:30 | 3582.5 | 1681.75 | 885 | 38 | 29 | 920.81 | 212 | 3722 | 164.335 | 173 | 1330.56 | 0 | 0 | 9 | 0
13:00 | 3439 | 1764 | 885 | 38 | 30 | 959.69 | 212 | 3706 | 138.02 | 164 | 1407.16 | 0 | 0 | 10 | 0
13:30 | 3445.5 | 1780.5 | 885 | 38 | 30 | 968.07 | 213 | 3658.5 | 117.795 | 133 | 1389.9 | 0 | 0 | 16.5 | 0
14:00 | 3452 | 1797 | 885 | 38 | 30 | 976.45 | 214 | 3611 | 97.57 | 102 | 1372.64 | 0 | 0 | 23 | 0
14:30 | 3438 | 1803.5 | 885 | 38 | 30 | 992.52 | 191.5 | 3653.5 | 121.02 | 85.5 | 1229.82 | 0 | 0 | 22.5 | 0
15:00 | 3424 | 1810 | 885 | 38 | 30 | 1008.59 | 169 | 3696 | 144.47 | 69 | 1087 | 0 | 0 | 22 | 0
15:30 | 3469 | 1766.5 | 884.5 | 38 | 30 | 1020.595 | 167 | 3719 | 129.38 | 67.5 | 1029 | 0 | 0 | 20 | 0
16:00 | 3514 | 1723 | 884 | 38 | 30 | 1032.6 | 165 | 3742 | 114.29 | 66 | 971 | 0 | 0 | 18 | 0
16:30 | 3499.5 | 1752 | 884 | 38 | 29 | 1023.045 | 164.5 | 3719.5 | 94.615 | 66 | 967.5 | 0 | 0 | 20 | 0
17:00 | 3485 | 1781 | 884 | 38 | 28 | 1013.49 | 164 | 3697 | 74.94 | 66 | 964 | 0 | 0 | 22 | 0
17:30 | 3529.5 | 1759 | 884 | 38 | 27 | 983.165 | 163.5 | 3702 | 49.375 | 85.5 | 1011 | 0 | 0 | 18.5 | 0
18:00 | 3574 | 1737 | 884 | 38 | 26 | 952.84 | 163 | 3707 | 23.81 | 105 | 1058 | 0 | 0 | 15 | 0
18:30 | 3635 | 1772.5 | 884 | 38 | 28 | 1041.045 | 186 | 3767 | 11.905 | 211 | 1298 | 0 | 0 | 11 | 0
19:00 | 3696 | 1808 | 884 | 38 | 30 | 1129.25 | 209 | 3827 | 0 | 317 | 1538 | 0 | 0 | 7 | 0
19:30 | 3738 | 1980 | 884 | 38 | 28 | 1216.97 | 209 | 3958 | 0 | 425 | 1838 | 0 | 0 | 4 | 0
20:00 | 3691 | 1973 | 885 | 38 | 28 | 1201.74 | 215 | 4026 | 0 | 450 | 1794 | 0 | 0 | 5 | 0
20:30 | 3763 | 2007.5 | 885 | 38 | 29 | 1206.37 | 211 | 4064.5 | 0 | 429.5 | 1694.6 | 0 | 0 | 9.5 | 0
21:00 | 3835 | 2042 | 885 | 38 | 30 | 1211 | 207 | 4103 | 0 | 409 | 1595.2 | 0 | 0 | 14 | 0
21:30 | 3826.5 | 2027.25 | 885 | 38 | 30 | 1211 | 207.5 | 4110.5 | 0 | 409 | 1583.6 | 0 | 0 | 12 | 0
22:00 | 3818 | 2012.5 | 885 | 38 | 30 | 1211 | 208 | 4118 | 0 | 409 | 1572 | 0 | 0 | 10 | 0
22:30 | 3824 | 2015.5 | 883.5 | 38 | 31 | 1212.5 | 208 | 4116.5 | 0 | 407.5 | 1518.5 | 0 | 0 | 8.5 | 0
23:00 | 3830 | 2018.5 | 882 | 38 | 32 | 1214 | 208 | 4115 | 0 | 406 | 1465 | 0 | 0 | 7 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 15-07-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 377 | 06:00 | 369 | 00:00 | Payra | 411 | 06:00 | 406 | 00:00
Ashuganj | 402 | 5:00 | 373 | 19:00 | Rahanpur | 398 | 10:00 | 380 | 00:00
Bhulta | 395 | 04:00 | 381 | 09:00 | Rampal | 396 | 06:00 | 382 | 23:00
Bibiana | 382 | 06:00 | 376 | 23:00
BIPTC | 405 | 04:00 | 393 | 20:00
Bogura | 387 | 10:00 | 368 | 00:00
Gopalganj | 390 | 06:00 | 380 | 00:00
Kaliakoir | 370 | 06:00 | 362 | 00:00
Madunaghat | 389 | 14:00 | 385 | 00:00
Meghnaghat | 378 | 05:00 | 373 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 220 | 06:00 | 215 | 10:00 | Keranigonj | 218 | 05:00 | 213 | 00:00
AKSML | 230 | 18:00 | 224 | 04:00 | Khulna(S) | 236 | 07:00 | 218 | 00:00
Aminbazar | 221 | 05:00 | 216 | 23:00 | Madunaghat | 230 | 03:00 | 228 | 00:00
Ashuganj | 230 | 20:00 | 224 | 00:00 | Madunaghat-400 | 231 | 14:00 | 228 | 00:00
Ashuganj-400 | 230 | 20:00 | 224 | 00:00 | Maniknagar | 216 | 05:00 | 211 | 10:00
Baghabari | 233 | 05:00 | 225 | 21:00 | Meghnaghat | 224 | 06:00 | 219 | 23:00
Barapukuria | 224 | 19:00 | 217 | 00:00 | Meghnaghat-400 | 221 | 06:00 | 216 | 00:00
Barapukuria-230 | 224 | 19:00 | 217 | 00:00 | Mirsorai | 225 | 07:00 | 220 | 00:00
Barishal | 228 | 14:00 | 220 | 23:00 | Rajshahi | 231 | 06:00 | 219 | 22:00
Bheramara | 231 | 06:00 | 221 | 22:00 | Rampal | 226 | 06:00 | 217 | 00:00
Bhulta | 228 | 04:00 | 212 | 09:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 224 | 06:00 | 220 | 23:00 | Rampura | 227 | 04:00 | 217 | 09:00
BIPTC | 234 | 06:00 | 222 | 22:00 | Shikalbaha | 229 | 18:00 | 224 | 23:00
Bogura | 234 | 10:00 | 225 | 00:00 | Shyampur | 219 | 06:00 | 213 | 10:00
Bogura-400 | 234 | 10:00 | 224 | 02:00 | Siddhirganj | 218 | 07:00 | 213 | 09:00
Borhanuddin | 233 | 14:00 | 226 | 23:00 | Sirajgonj | 238 | 13:00 | 233 | 00:00
BSRM | 225 | 18:00 | 220 | 00:00 | Sreepur | 226 | 06:00 | 220 | 00:00
Cumilla(N) | 221 | 18:30 | 214 | 23:00 | Tongi | 225 | 05:00 | 217 | 23:00
Faridpur | 223 | 06:00 | 216 | 00:00
Fenchuganj | 228 | 18:00 | 222 | 01:00
Ghorashal | 230 | 01:00 | 225 | 00:00
Ghorashal-230 | 226 | 03:00 | 218 | 11:00
Gopalganj | 224 | 06:00 | 217 | 23:00
GPH | 227 | 18:00 | 224 | 00:00
Haripur | 218 | 06:00 | 213 | 10:00
Hasnabad | 218 | 04:00 | 214 | 09:00
Hathazari | 228 | 18:00 | 221 | 00:00
Ishurdi | 233 | 06:00 | 224 | 22:00
Jhenaidah | 229 | 06:00 | 217 | 19:30
Kaliakoir | 227 | 04:00 | 221 | 09:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 04:00 | 129 | 09:00 | Madanganj | 127 | 19:30 | 123 | 09:00
Agargaon | 130 | 06:00 | 124 | 15:00 | Madaripur | 134 | 06:00 | 129 | 00:00
Agrabad | 132 | 18:00 | 128 | 07:00 | Madartek | 138 | 04:00 | 129 | 09:00
AKS | 129 | 01:00 | 126 | 11:00 | Madunaghat | 131 | 03:00 | 129 | 00:00
Aminbazar | 130 | 04:00 | 127 | 00:00 | Magura | 133 | 10:00 | 125 | 19:30
Amnura | 135 | 10:00 | 126 | 23:00 | Mahasthangarh | 135 | 10:00 | 128 | 00:00
Ashuganj | 140 | 08:00 | 136 | 00:00 | Maijdee | 119 | 18:00 | 109 | 14:00
Bagerhat | 131 | 06:00 | 121 | 00:00 | Manikganj | 126 | 06:00 | 121 | 00:00
Bajitpur | 132 | 15:00 | 125 | 00:00 | Maniknagar | 129 | 05:00 | 125 | 10:00
Bakulia | 133 | 18:00 | 130 | 00:00 | Matarbari | 121 | 11:00 | 109 | 19:00
Banani | 137 | 03:00 | 131 | 09:00 | Matuail | 127.5 | 19:00 | 123 | 10:00
Bangabhaban | 130 | 06:00 | 124 | 11:00 | Millgate | 131 | 03:00 | 124 | 09:00
Barapukuria | 137 | 19:00 | 128 | 07:00 | Mirpur | 129 | 04:00 | 124 | 09:00
Barguna | 133 | 14:00 | 129 | 23:00 | Mirzapur | 129 | 13:00 | 124 | 00:00
Barishal | 133 | 09:00 | 126 | 23:00 | Mithapukur | 133 | 19:00 | 124 | 02:00
Barishal-230 | 134 | 14:00 | 128 | 22:00 | MI_Cement | 127.4 | 06:00 | 123 | 10:00
Baroaulia | 132 | 18:00 | 127 | 15:00 | Modern | 0 | 00:00 | 0 | 00:00
Baroirhat | 125 | 18:30 | 118 | 14:00 | Mogbazar | 137 | 01:00 | 130 | 10:00
Bashundhara | 136 | 01:00 | 123 | 16:00 | Mongla | 131 | 13:00 | 120 | 19:30
BashundharaCement | 127 | 19:30 | 123 | 09:00 | Motijheel | 130 | 06:00 | 124 | 11:00
Beanibazar | 127 | 17:00 | 122 | 00:00 | Muktagacha | 134 | 14:00 | 127 | 00:00
Benapole | 134 | 20:00 | 122 | 19:30 | Munshiganj | 127 | 19:00 | 123 | 00:00
Bhaluka | 131 | 11:00 | 124 | 00:00 | Muradnagar | 124 | 17:00 | 118 | 23:00
Bhandaria | 130 | 14:00 | 119 | 22:00 | Mymensingh | 135 | 14:00 | 116 | 22:00
Bhangura | 134 | 08:00 | 128 | 20:00 | Naogaon | 134 | 09:00 | 125 | 00:00
Bheramara | 137 | 06:00 | 131 | 22:00 | Narail | 132 | 06:00 | 123 | 19:00
Bheramara(GK) | 136 | 05:00 | 131 | 22:00 | Narinda | 129 | 05:00 | 125 | 10:00
Bhulta | 120 | 04:00 | 117 | 10:00 | Narshingdi | 134 | 05:00 | 117 | 23:00
Bog-Sherpur | 136 | 09:00 | 129 | 21:00 | Natore | 135 | 06:00 | 128 | 22:00
Bogura | 139 | 09:00 | 131 | 00:00 | Nawabganj | 131 | 05:00 | 126 | 10:00
Bogura-230 | 138 | 09:00 | 132 | 00:00 | Netrakona | 127 | 15:00 | 114 | 22:00
Brahmanbaria | 134 | 15:00 | 129 | 00:00 | New | 132 | 06:00 | 126 | 09:00
Cantonment | 130 | 05:00 | 125 | 09:00 | Niamatpur | 136 | 08:00 | 128 | 00:00
Chandina | 127 | 18:30 | 122 | 14:00 | Noapara | 133 | 06:00 | 124 | 19:30
Chandpur | 128 | 18:00 | 119 | 13:00 | Pabna | 134 | 06:00 | 128 | 22:00
Chandraghona | 132 | 02:00 | 130 | 00:00 | Palashbari | 131 | 10:00 | 123 | 00:00
Chapai | 135 | 10:00 | 128 | 00:00 | Panchagarh | 133 | 19:00 | 117 | 07:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 128 | 19:00 | 123 | 10:00 | Patuakhali | 133 | 03:00 | 129 | 22:00
Chauddagram | 123 | 18:00 | 116 | 13:00 | Payra | 135 | 05:00 | 132 | 00:00
Chhatak | 126 | 08:00 | 119 | 00:00 | PHP | 124 | 18:30 | 116 | 23:00
Chowmuhani | 121 | 18:30 | 109 | 14:00 | Postogola | 129 | 03:00 | 125 | 12:00
Chuadanga | 134 | 06:00 | 120 | 19:30 | Purbachal | 137 | 02:00 | 125 | 09:00
Coxsbazar | 121 | 11:00 | 112 | 21:00 | Purbasadipur | 131 | 18:30 | 119 | 07:00
Cumilla(N) | 126 | 17:00 | 121 | 23:00 | Rahanpur | 136 | 10:00 | 130 | 22:00
Cumilla(S) | 133 | 03:00 | 120 | 14:00 | Rahanpur-400 | 137 | 10:00 | 130 | 23:00
Daganbhuiyan | 121 | 18:00 | 111 | 23:00 | Rahim | 127 | 05:00 | 123 | 10:00
Daudkandi | 122 | 00:00 | 117 | 23:00 | Rajbari | 132 | 10:00 | 126 | 00:00
Dhaka | 136 | 01:00 | 130 | 09:00 | Rajendrapur | 132 | 14:00 | 124 | 01:00
Dhamrai | 129 | 04:00 | 123 | 09:00 | Rajshahi | 134 | 05:00 | 128 | 21:00
Dhanmondi | 137.5 | 04:00 | 130.6 | 09:00 | Rajshahi-230 | 133 | 06:00 | 127 | 22:00
Dohazari | 127 | 05:00 | 123 | 19:00 | Ramganj | 122 | 18:30 | 111 | 23:00
Faridpur | 133 | 06:00 | 128 | 00:00 | Rampur | 131 | 18:00 | 128 | 23:00
Fatullah | 128 | 04:00 | 124 | 12:00 | Rampura | 137 | 03:00 | 130 | 09:00
Fenchuganj | 135 | 18:30 | 131 | 00:00 | Rangamati | 131 | 07:00 | 128 | 19:00
Feni | 123 | 08:00 | 115 | 22:00 | Rangpur | 131 | 19:00 | 124 | 00:00
Ghatail | 130 | 13:00 | 124 | 00:00 | Ruppur | 137 | 04:00 | 131 | 22:00
Ghorashal | 135 | 15:00 | 131 | 00:00 | Saidpur | 132 | 19:00 | 123 | 07:00
Goalpara | 134 | 08:00 | 127 | 00:00 | Satkhira | 132 | 13:00 | 121 | 19:30
Gollamari | 135 | 12:00 | 128 | 02:00 | Satmasjid | 130 | 05:00 | 125 | 10:00
Gopalganj | 133 | 06:00 | 127 | 19:30 | Savar | 131 | 20:00 | 16 | 10:00
Gopalganj-400 | 134 | 04:00 | 130 | 00:00 | SevenRings | 139 | 20:00 | 130 | 09:00
Gulshan | 137 | 06:00 | 129 | 09:00 | ShahCement | 128 | 19:00 | 123 | 10:00
Halishahar | 133 | 18:00 | 128 | 09:00 | Shahjadpur | 136 | 15:00 | 133 | 00:00
Haripur | 128 | 19:00 | 123 | 10:00 | Shahjibazar | 134 | 15:00 | 128 | 00:00
HaripurSBU | 128 | 19:00 | 123 | 10:00 | Shahmirpur | 133 | 18:00 | 130 | 08:00
Hasnabad | 129 | 04:00 | 126 | 00:00 | Shariatpur | 135 | 14:00 | 126 | 23:00
Hathazari | 133 | 18:00 | 129 | 00:00 | Sherpur | 138 | 14:00 | 126 | 00:00
Ishurdi | 137 | 07:00 | 131 | 22:00 | Shikalbaha | 122 | 18:00 | 118 | 02:00
Jaldhaka | 130 | 19:00 | 119 | 07:00 | Shikalbaha-230 | 133 | 17:00 | 131 | 02:00
Jamalpur | 139 | 14:00 | 129 | 01:00 | Shitalakhya | 127.6 | 19:00 | 123 | 10:00
Jashore | 135 | 05:00 | 122 | 19:30 | Sholosohor | 131 | 18:00 | 129 | 00:00
Jhenaidah | 135 | 05:00 | 12 | 12:00 | Shyampur | 128 | 06:00 | 125 | 00:00
Jhenaidah-230 | 135 | 06:00 | 127 | 19:30 | Shyampur-230 | 130 | 06:00 | 124 | 00:00
Joydebpur | 134 | 13:00 | 123 | 08:00 | Siddhirganj | 128 | 19:00 | 124 | 10:00
Joypurhat | 133 | 10:00 | 123 | 00:00 | Sirajganj | 134 | 10:00 | 127 | 21:00
Juldah | 133 | 10:00 | 130 | 07:00 | Sonargaon | 126 | 19:00 | 121 | 22:00
Kabirpur | 130 | 13:00 | 122 | 10:00 | Sreemongol | 132 | 08:00 | 126 | 23:00
Kachua | 125 | 17:00 | 117 | 23:00 | Sreepur | 132 | 13:00 | 127 | 00:00
Kaliakoir | 139 | 23:00 | 127 | 09:00 | Srinagar | 131 | 06:00 | 127 | 00:00
Kallyanpur | 130 | 13:00 | 125 | 10:00 | SSM | 132 | 00:00 | 130 | 10:00
Kalurghat | 131 | 18:00 | 129 | 00:00 | Sunamganj | 126 | 17:00 | 117 | 21:00
Kamrangirchar | 131 | 05:00 | 126 | 09:00 | Sylhet | 128 | 07:00 | 123 | 21:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet-132 | 128 | 05:00 | 125 | 00:00
Kasba | 124 | 18:00 | 118 | 22:00 | Tangail | 128 | 03:00 | 123 | 00:00
Kazla | 129 | 05:00 | 124 | 11:00 | Taraganj | 132 | 19:00 | 122 | 07:00
Keranigonj | 131 | 05:00 | 127 | 00:00 | Thakurgaon | 137 | 19:00 | 114 | 07:00
Khagrachori | 130 | 07:00 | 127 | 19:00 | TK | 131 | 19:00 | 129 | 00:00
Khulna | 132 | 05:00 | 125 | 19:00 | Tongi | 134 | 05:00 | 128 | 10:00
Khulna(S) | 135 | 09:00 | 128 | 00:00 | Ullahpara | 135 | 10:00 | 129 | 21:00
Khulshi | 130 | 18:00 | 127 | 15:00 | Ullon | 137 | 04:00 | 130 | 09:00
Kishoreganj | 130 | 15:00 | 123 | 00:00 | Uttara | 129 | 06:00 | 124 | 09:00
Kodda | 130 | 01:00 | 121 | 15:00 | UttaraNew | 129 | 20:00 | 124 | 09:00
KSRM | 132 | 17:00 | 128 | 15:00 | Zigatola | 131 | 05:00 | 127 | 00:00
Kulaura | 133 | 07:00 | 129 | 00:00
Kurigram | 128 | 10:00 | 120 | 02:00
Kushtia | 135 | 06:00 | 126 | 22:00
Lakshmipur | 121 | 18:30 | 109 | 23:00
Lalbag | 130 | 04:00 | 126 | 10:00
Lalmonirhat | 130 | 09:00 | 123 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division