## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 17-07-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-07-2025 | during | 17-07-2025 | during | 17-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 0 | 0 | 0 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 305 | 311 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 4 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 195 | 201 | 208.13 | 208.13 | 203 | 203 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 333 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 39.24 | 48 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 28 | 48 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23 | 23 | 33 | 33 | 25 | 25 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 20 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 33 | 34 | 52.19 | 52.19 | 42 | 42 | Engine Problem
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | -
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 60 | 145 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 70 | 70 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 70 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 13 | 50 | 104 | 104 | 50 | 50 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 97 | 154 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 11 | 0 | 29 | 0 | 29 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 553 | 500 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 90 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2421.24 | 2673 | 4722.65 | 4787.65 | 3307.33 | 3372.33
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 211 | 206 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 217 | 213 | 213 | 213 | 213 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 16 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 39 | 80 | 80 | 80 | 80 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 65 | 65 | 65 | 68 | 68 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 36 | 63 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 20 | 2 | 25 | 2 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.91 | 0 | 4.01 | 0 | 4.01 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 15 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 50 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1058 | 1150 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 15 | 0 | 3 | 2 | 3 | 2 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 705 | 667 | 790 | 790 | 790 | 790 | FGMO
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 2311.91 | 2590 | 3829.73 | 3837.72 | 3832.73 | 3840.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 210 | 209 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 339 | 330 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 340 | 340 | 340 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 19 | 17 | 46.7 | 46.7 | 19 | 19 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 43 | 49 | 55 | 55 | 48 | 48 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 60 | 16 | 195 | 195 | 108 | 108 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 143 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 38 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 40 | 45 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 176 | 149 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 28 | 32 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 43 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 19 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 97 | 97 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 27 | 113 | 113 | 18 | 37 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 73 | 106 | 115 | 115 | 115 | 115 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 37 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1573 | 1702 | 2460.75 | 2400.75 | 2110.55 | 2069.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-07-2025 | during | 17-07-2025 | during | 17-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 31 | 33 | 157.5 | 157.5 | 51 | 51 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 119 | 180 | 200 | 200 | 186 | 186 | Engine Problem
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 85 | 115 | 115 | 105 | 105 | Engine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 21.48 | 0 | 44.15 | 0 | 44.15 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 35 | 17 | 54.5 | 54.5 | 35 | 35 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 263.48 | 327 | 595.05 | 549 | 435.05 | 389
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 50 | 30 | 30 | 20 | 20 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 157 | 148 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 84 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 173 | 171 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 8 | 8 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 390 | 360 | 380 | 380 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1198 | 1189 | 1212 | 1212 | 1160 | 1160
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 885 | 893 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 266 | 270 | 410 | 410 | 266 | 266 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 34 | 105 | 105 | 60 | 60 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 32 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 13 | 0 | 40 | 0 | 40 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 462 | 581 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1664 | 1848 | 3592.2 | 3552.2 | 3403.2 | 3363.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 616 | 488 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 0 | 0 | 65 | 65 | 65 | 65 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 860 | 1240 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 173 | 278 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.51 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1869.51 | 2226 | 2097 | 2096 | 2047 | 2046
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 204 | 200 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 206 | 198 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 392 | 393 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 52 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.52 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 931 | 1073.01 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 27.84 | 0 | 65 | 0 | 65 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 93 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 1856.36 | 1946.01 | 2983.47 | 2812.87 | 2942.09 | 2771.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 49 | 49 | 50 | 50 | 50 | 50 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 196 | 158 | 150 | 150 | 155 | 155 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 0.5 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 95 | 95 | 95 | 95 | 95 | Schedule Maintenance
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 7 | 0 | 24 | 0 | 24 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 112 | 0 | 89.21 | 0 | 89.21 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 433.5 | 415 | 561.81 | 442 | 566.81 | 447
System Total |  |  |  |  | 28565.2 | 27084.055 | 13591 | 14916.01 | 22054.66 | 21690.19 | 19804.76 | 19459.29
Forecast Scenario (17-07-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14550 |  | 0 |  | 14550
|  |  |  | 1:00 | 14100 |  | 0 |  | 14100
|  |  |  | 2:00 | 13730 |  | 0 |  | 13730
|  |  |  | 3:00 | 13340 |  | 0 |  | 13340
|  |  |  | 4:00 | 13150 |  | 0 |  | 13150
|  |  |  | 5:00 | 12830 |  | 0 |  | 12830
|  |  |  | 6:00 | 12600 |  | 0 |  | 12600
|  |  |  | 7:00 | 12670 |  | 0 |  | 12670
|  |  |  | 8:00 | 12880 |  | 0 |  | 12880
|  |  |  | 9:00 | 13100 |  | 0 |  | 13100
|  |  |  | 10:00 | 13430 |  | 0 |  | 13430
|  |  |  | 11:00 | 13850 |  | 0 |  | 13850
|  |  |  | 12:00 | 14090 |  | 0 |  | 14090
|  |  |  | 13:00 | 14360 |  | 0 |  | 14360
|  |  |  | 14:00 | 14020 |  | 0 |  | 14020
|  |  |  | 15:00 | 13930 |  | 0 |  | 13930
|  |  |  | 16:00 | 13630 |  | 0 |  | 13630
|  |  |  | 17:00 | 13330 |  | 0 |  | 13330
|  |  |  | 18:00 | 13150 |  | 0 |  | 13150
|  |  |  | 18:30 | 13800 |  | 0 |  | 13800
|  |  |  | 19:00 | 14340 |  | 0 |  | 14340
|  |  |  | 19:30 | 15250 |  | 0 |  | 15250
|  |  |  | 20:00 | 15280 |  | 0 |  | 15280
|  |  |  | 21:00 | 15410 |  | 0 |  | 15410
|  |  |  | 22:00 | 15300 |  | 0 |  | 15300
|  |  |  | 23:00 | 15200 |  | 0 |  | 15200
Probable Maximum Temperature: |  |  | 31.70°C
Probable Maximum Demand at Day Peak: |  |  | 14090.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15410.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15410.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 332.27 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:09 hrs on 17-07-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 16-07-2025 | [28 empty] | Date: | 16-07-2025 | [28 empty] | Date: | 16-07-2025 | [28 empty] | Date: | 16-07-2025 | [28 empty] | Date: | 16-07-2025 | [11 empty] | Date: | 16-07-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [11 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 16 | 35 | 53 | 0 | 0 | 0 | 17 | 103 | 0 | 450 | 305 | 0 | 0 | 17 | 335 | 200 | 0 | 0 | 90 | 23.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 47 | 43 | 0 | 88 | 100 | 0 | 208 | 0 | 31 | 690 | 0 | 0 | 19 | 8 | 0 | 219 | 0 | 0 | 0 | 655 | 0 | 51 | 30 | 8 | 0 | 355 | 340 | 46 | 216 | 19 | 93 | 40 | 182 | 12 | 20 | 102 | 32 | 52.2 | 0 | 31 | 0 | 320 | 366 | 0 | 20 | 155 | 8 | 0 | 84 | 30 | 0 | 18 | 170 | 23 | 45 | 192 | 50 | 0 | 0 | 12 | 7558.7 | 882 | 202 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 604 | 25 | 1206 | 0 | 0 | 0 | 35 | 0 | 41 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 199 | 0 | 208 | 0 | 373 | 0 | 0 | 157 | 50 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 0 | 220 | 0 | 619 | 1120 | 0 | 6494 | 14052.7 | 98.89
01:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 35 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 304 | 0 | 0 | 0 | 335 | 130 | 0 | 0 | 70 | 23.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 50 | 8 | 0 | 88 | 88 | 0 | 208 | 0 | 31 | 696 | 0 | 0 | 0 | 8 | 0 | 219 | 0 | 0 | 0 | 800 | 0 | 51 | 0 | 8 | 0 | 354 | 340 | 48 | 199 | 19 | 91 | 40 | 171 | 8 | 20 | 101 | 28 | 52.2 | 0 | 31 | 0 | 320 | 375 | 0 | 20 | 134 | 8 | 0 | 84 | 30 | 0 | 18 | 170 | 35 | 45 | 145 | 50 | 0 | 0 | 8 | 7212.7 | 883 | 205 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 597 | 17 | 1215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 208 | 0 | 356 | 0 | 0 | 158 | 49 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 246 | 0 | 220 | 0 | 619 | 1244 | 0 | 6394 | 13606.7 | 98.9
02:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 314 | 0 | 0 | 0 | 335 | 130 | 0 | 0 | 70 | 23.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 50 | 0 | 0 | 48 | 88 | 0 | 208 | 0 | 31 | 720 | 0 | 0 | 0 | 8 | 0 | 220 | 0 | 0 | 0 | 870 | 0 | 51 | 0 | 8 | 0 | 352 | 340 | 48 | 204 | 19 | 90 | 40 | 176 | 8 | 20 | 106 | 28 | 52.2 | 0 | 31 | 0 | 320 | 392 | 0 | 20 | 138 | 8 | 0 | 84 | 30 | 0 | 18 | 170 | 35 | 45 | 145 | 50 | 0 | 0 | 7 | 7214.7 | 883 | 210 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 534 | 0 | 1115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204 | 0 | 208 | 0 | 377 | 0 | 0 | 156 | 49 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 220 | 0 | 619 | 1100 | 0 | 6019 | 13233.7 | 98.9
03:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 305 | 0 | 0 | 0 | 335 | 130 | 0 | 0 | 70 | 23.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 50 | 0 | 0 | 48 | 48 | 0 | 208 | 0 | 33 | 681 | 0 | 0 | 0 | 8 | 0 | 220 | 0 | 0 | 0 | 870 | 0 | 51 | 0 | 8 | 0 | 355 | 340 | 48 | 195 | 19 | 87 | 50 | 178 | 8 | 20 | 86 | 26 | 52.2 | 0 | 31 | 0 | 320 | 369 | 0 | 20 | 139 | 8 | 0 | 84 | 30 | 0 | 18 | 171 | 35 | 45 | 145 | 50 | 0 | 0 | 12 | 7072.7 | 883 | 212 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 496 | 0 | 1107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 208 | 0 | 349 | 0 | 0 | 155 | 49 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 220 | 0 | 619 | 1000 | 0 | 5775 | 12847.7 | 98.91
04:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 313 | 0 | 0 | 0 | 335 | 130 | 0 | 0 | 52 | 23.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 50 | 0 | 0 | 12 | 48 | 0 | 208 | 0 | 33 | 695 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 910 | 0 | 51 | 0 | 8 | 0 | 353 | 340 | 48 | 198 | 19 | 73 | 50 | 174 | 8 | 20 | 83 | 26 | 52.2 | 0 | 31 | 0 | 320 | 385 | 0 | 20 | 136 | 8 | 0 | 84 | 30 | 0 | 18 | 171 | 35 | 45 | 145 | 50 | 0 | 0 | 12 | 7063.7 | 883 | 220 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 426 | 0 | 1029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209 | 0 | 208 | 0 | 356 | 0 | 0 | 156 | 49 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 220 | 0 | 619 | 970 | 0 | 5589 | 12652.7 | 98.91
05:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 311 | 0 | 0 | 0 | 335 | 130 | 0 | 0 | 35 | 23.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 50 | 0 | 0 | 12 | 24 | 0 | 208 | 0 | 33 | 671 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 895 | 0 | 51 | 0 | 8 | 0 | 356 | 340 | 47 | 194 | 18 | 72 | 50 | 172 | 8 | 20 | 83 | 26 | 25 | 0 | 31 | 0 | 320 | 360 | 0 | 20 | 134 | 8 | 0 | 84 | 30 | 0 | 18 | 172 | 35 | 45 | 125 | 50 | 0 | 0 | 12 | 6886.5 | 883 | 224 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 388 | 0 | 1007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209 | 0 | 208 | 0 | 348 | 0 | 0 | 156 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 220 | 0 | 618 | 930 | 0 | 5447 | 12333.5 | 98.92
06:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 312 | 0 | 0 | 0 | 335 | 130 | 0 | 1 | 17 | 23.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16 | 0 | 0 | 12 | 24 | 0.09 | 208 | 0 | 33 | 700 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 900 | 1 | 51 | 0 | 8 | 0 | 300 | 340 | 46 | 199 | 18 | 36 | 50 | 166 | 9 | 20 | 87 | 24 | 0 | 4 | 0 | 0 | 320 | 383 | 0 | 20 | 130 | 8 | 0 | 84 | 30 | 0 | 18 | 172 | 35 | 46 | 105 | 50 | 0 | 1.22 | 10 | 6714.81 | 883 | 226 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 377 | 0 | 986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1.43 | 0 | 0 | 209 | 0 | 208 | 0 | 358 | 0 | 0.2 | 156 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0.02 | 0 | 173 | 0 | 220 | 0 | 618 | 880 | 0 | 5394.65 | 12109.46 | 98.92
07:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 313 | 0 | 0 | 0 | 330 | 130 | 0 | 3 | 17 | 23.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 12 | 24 | 0.39 | 208 | 0 | 17 | 702 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 910 | 0 | 51 | 0 | 8 | 0 | 300 | 340 | 46 | 208 | 18 | 37 | 50 | 181 | 8 | 20 | 95 | 24 | 0 | 13 | 0 | 0 | 320 | 395 | 0 | 20 | 145 | 8 | 0 | 84 | 30 | 0 | 18 | 171 | 35 | 65 | 107 | 50 | 0 | 5.2 | 8 | 6836.09 | 883 | 232 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14 | 407 | 0 | 931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 8.07 | 0 | 0 | 208 | 0 | 208 | 0 | 390 | 0 | 0.9 | 156 | 50 | 0 | 4 | 0 | 0 | 0 | 0 | 28 | 0.1 | 0 | 175 | 0 | 220 | 0 | 619 | 750 | 0 | 5341.07 | 12177.16 | 98.93
08:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 515 | 0 | 25 | 24 | 0 | 0 | 0 | 2 | 0 | 0 | 420 | 309 | 0 | 0 | 0 | 330 | 130 | 0 | 11 | 17 | 25 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 1.08 | 208 | 0 | 6 | 700 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1000 | 7 | 51 | 0 | 8 | 0 | 300 | 340 | 47 | 200 | 18 | 36 | 50 | 178 | 8 | 20 | 100 | 24 | 0 | 28 | 0 | 0 | 320 | 362 | 0 | 20 | 136 | 8 | 0 | 84 | 30 | 0 | 18 | 171 | 35 | 75 | 125 | 49 | 1 | 9.95 | 12 | 6937.03 | 883 | 248 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 20 | 400 | 0 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 13.63 | 0 | 0 | 209 | 0 | 211 | 0 | 347 | 0 | 1.58 | 156 | 50 | 35 | 8 | 0 | 0 | 0 | 0.1 | 69 | 0.16 | 0 | 171 | 0 | 220 | 0 | 618 | 780 | 0 | 5443.47 | 12380.5 | 98.93
09:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 35 | 33 | 16 | 0 | 0 | 17 | 0 | 0 | 400 | 300 | 0 | 0 | 0 | 331 | 198 | 0 | 15 | 35 | 23 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 12 | 24 | 2.31 | 212 | 0 | 2 | 700 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1009 | 11 | 51 | 0 | 8 | 0 | 343 | 340 | 48 | 202 | 16 | 42 | 45 | 179 | 9 | 20 | 98 | 24 | 3 | 32 | 0 | 0 | 320 | 368 | 0 | 20 | 152 | 8 | 0 | 82 | 30 | 0 | 18 | 172 | 35 | 45 | 125 | 44 | 1 | 17.84 | 12 | 7085.15 | 883 | 249 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 38 | 397 | 0 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 31.35 | 0 | 0 | 206 | 0 | 210 | 0 | 365 | 0 | 2.67 | 156 | 49 | 35 | 8 | 27 | 0 | 0 | 0.6 | 79 | 0.3 | 0 | 171 | 0 | 220 | 0 | 619 | 785 | 0 | 5523.92 | 12609.07 | 98.93
10:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 35 | 39 | 16 | 0 | 0 | 23 | 8 | 0 | 420 | 306 | 0 | 0 | 0 | 329 | 196 | 0 | 21 | 35 | 23 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 48 | 3.86 | 214 | 0 | 2 | 700 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 1011 | 14 | 51 | 0 | 8 | 0 | 343 | 300 | 42 | 208 | 18 | 69 | 40 | 173 | 8 | 17 | 97 | 24 | 16 | 49 | 0 | 0 | 320 | 390 | 0 | 20 | 155 | 8 | 0 | 81 | 30 | 0 | 18 | 173 | 35 | 45 | 125 | 44 | 2 | 30.35 | 12 | 7278.21 | 883 | 249 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 49 | 392 | 0 | 947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 15.27 | 0 | 0 | 206 | 0 | 209 | 0 | 389 | 0 | 3.23 | 155 | 50 | 35 | 9 | 42 | 0 | 0 | 1.1 | 130 | 0.42 | 0 | 174 | 0 | 220 | 0 | 618 | 787 | 0 | 5658.02 | 12936.23 | 98.93
11:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 1.8 | 35 | 70 | 16 | 30 | 0 | 35 | 47 | 2 | 450 | 297 | 0 | 0 | 0 | 330 | 196 | 0 | 14 | 70 | 23 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 36 | 48 | 2.78 | 214 | 0 | 2 | 700 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 1000 | 14 | 43 | 0 | 42 | 0 | 345 | 300 | 42 | 199 | 19 | 72 | 40 | 181 | 8 | 17 | 97 | 26 | 22 | 52 | 0 | 0 | 320 | 374 | 0 | 20 | 157 | 8 | 0 | 83 | 30 | 0 | 18 | 172 | 35 | 45 | 120 | 43 | 2 | 37.53 | 12 | 7495.11 | 882 | 260 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 96 | 440 | 0 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 0 | 66.11 | 0 | 0 | 204 | 0 | 207 | 0 | 351 | 0 | 5.98 | 155 | 50 | 35 | 10 | 34 | 0 | 0 | 1.3 | 165 | 0.15 | 0 | 166 | 0 | 220 | 0 | 618 | 825 | 0 | 5855.54 | 13350.65 | 98.93
12:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553 | 39.24 | 35 | 70 | 28 | 60 | 4 | 35 | 97 | 13 | 450 | 305 | 0 | 0 | 0 | 330 | 195 | 0 | 11 | 70 | 23 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 36 | 50 | 1.91 | 211 | 0 | 2 | 705 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1058 | 18 | 43 | 0 | 60 | 0 | 339 | 340 | 43 | 210 | 19 | 73 | 40 | 176 | 8 | 17 | 97 | 28 | 43 | 37 | 0 | 0 | 320 | 390 | 0 | 20 | 157 | 8 | 0 | 82 | 30 | 0 | 18 | 173 | 35 | 45 | 119 | 31 | 0 | 21.48 | 12 | 7767.63 | 885 | 266 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 13 | 462 | 0 | 931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 27.84 | 0 | 0 | 204 | 0 | 206 | 0 | 392 | 0 | 2.52 | 196 | 49 | 35 | 7 | 34 | 0 | 0 | 0.5 | 112 | 0.51 | 0 | 173 | 0 | 220 | 0 | 616 | 860 | 0 | 5823.37 | 13591 | 98.93
13:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 546 | 49.32 | 35 | 70 | 31 | 95 | 15 | 35 | 122 | 16 | 450 | 285 | 0 | 0 | 0 | 330 | 196 | 0 | 7 | 70 | 23 | 14 | 0 | 0 | 0 | 15 | 0 | 0 | 3 | 0 | 0 | 0 | 36 | 50 | 4.31 | 211 | 0 | 2 | 680 | 0 | 0 | 4 | 0 | 10 | 215 | 0 | 0 | 0 | 1094 | 18 | 43 | 10 | 107 | 0 | 342 | 340 | 44 | 191 | 18 | 69 | 40 | 173 | 8 | 17 | 97 | 32 | 52.2 | 36 | 0 | 0 | 320 | 360 | 0 | 20 | 154 | 8 | 0 | 80 | 30 | 0 | 16 | 173 | 35 | 65 | 123 | 31 | 1 | 12.22 | 12 | 7874.05 | 885 | 262 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 8 | 500 | 0 | 1116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 27 | 0 | 0 | 206 | 0 | 209 | 0 | 336 | 0 | 2.32 | 142 | 50 | 35 | 2 | 44 | 0 | 0 | 2 | 105 | 0.07 | 0 | 163 | 0 | 220 | 0 | 618 | 970 | 0 | 5995.39 | 13869.44 | 98.93
14:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 44 | 35 | 70 | 15 | 95 | 15 | 35 | 142 | 16 | 450 | 290 | 0 | 0 | 0 | 327 | 194 | 0 | 3 | 70 | 23 | 21 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 50 | 3.38 | 211 | 0 | 2 | 692 | 0 | 0 | 18 | 0 | 14 | 215 | 0 | 0 | 0 | 1050 | 15 | 43 | 24 | 108 | 0 | 300 | 340 | 44 | 198 | 19 | 85 | 40 | 169 | 8 | 20 | 97 | 32 | 52.2 | 22 | 0 | 0 | 320 | 371 | 0 | 40 | 132 | 8 | 0 | 81 | 30 | 0 | 18 | 173 | 35 | 45 | 85 | 32 | 1 | 6.59 | 12 | 7740.17 | 885 | 258 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 28 | 483 | 0 | 1108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 18.11 | 0 | 0 | 160 | 0 | 160 | 0 | 348 | 0 | 1.71 | 153 | 50 | 35 | 1 | 49 | 0 | 0 | 2.2 | 3 | 0.39 | 0 | 169 | 0 | 220 | 0 | 618 | 960 | 0 | 5782.41 | 13522.58 | 98.93
15:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 47 | 35 | 62 | 15 | 95 | 15 | 35 | 150 | 16 | 450 | 290 | 0 | 0 | 0 | 326 | 194 | 0 | 4 | 70 | 23 | 21 | 0 | 0 | 0 | 15 | 0 | 0 | 1 | 0 | 0 | 0 | 36 | 50 | 3.29 | 210 | 0 | 2 | 680 | 0 | 0 | 19 | 0 | 15 | 215 | 0 | 0 | 0 | 1050 | 10 | 43 | 24 | 108 | 0 | 300 | 340 | 41 | 196 | 19 | 89 | 40 | 177 | 8 | 19 | 97 | 30 | 43 | 22 | 0 | 0 | 320 | 364 | 0 | 40 | 137 | 8 | 0 | 79 | 30 | 0 | 18 | 173 | 35 | 45 | 85 | 33 | 0 | 0.02 | 8 | 7708.31 | 884 | 260 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 494 | 0 | 1105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 3.47 | 0 | 0 | 160 | 0 | 160 | 0 | 348 | 0 | 0.13 | 158 | 49 | 35 | 1 | 49 | 0 | 0 | 1.5 | 8 | 0.14 | 0 | 168 | 0 | 220 | 0 | 618 | 940 | 0 | 5727.24 | 13435.55 | 98.93
16:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 37 | 35 | 69 | 0 | 45 | 0 | 35 | 108 | 19 | 450 | 292 | 0 | 0 | 0 | 333 | 198 | 0 | 3 | 35 | 18 | 21 | 0 | 0 | 0 | 15 | 0 | 0 | 7 | 0 | 0 | 0 | 36 | 50 | 0.63 | 208 | 0 | 2 | 694 | 0 | 0 | 19 | 0 | 15 | 215 | 0 | 0 | 0 | 1050 | 7 | 35 | 0 | 108 | 0 | 300 | 340 | 42 | 200 | 17 | 88 | 40 | 174 | 8 | 19 | 97 | 30 | 43 | 26 | 0 | 0 | 320 | 390 | 0 | 40 | 134 | 8 | 0 | 79 | 30 | 0 | 18 | 171 | 21 | 45 | 85 | 33 | 0 | 0.39 | 6 | 7531.02 | 884 | 260 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 25 | 483 | 0 | 1033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.31 | 0 | 0 | 160 | 0 | 160 | 0 | 354 | 0 | 0.24 | 162 | 49 | 0 | 1 | 34 | 0 | 0 | 1.6 | 4 | 0.08 | 0 | 172 | 0 | 220 | 0 | 618 | 945 | 0 | 5606.23 | 13137.25 | 98.93
17:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 31 | 35 | 70 | 0 | 45 | 0 | 35 | 96 | 32 | 450 | 284 | 0 | 0 | 0 | 332 | 200 | 0 | 4 | 17 | 18 | 17 | 0 | 0 | 0 | 15 | 0 | 0 | 2 | 0 | 0 | 0 | 36 | 50 | 0.66 | 206 | 0 | 7 | 675 | 0 | 0 | 19 | 0 | 15 | 215 | 0 | 0 | 0 | 941 | 3 | 51 | 0 | 108 | 0 | 300 | 340 | 44 | 191 | 17 | 99 | 40 | 170 | 8 | 19 | 97 | 30 | 34 | 20 | 15 | 0 | 320 | 387 | 0 | 40 | 136 | 8 | 0 | 83 | 30 | 0 | 18 | 171 | 17 | 45 | 88 | 33 | 0 | 1.87 | 6 | 7384.53 | 884 | 265 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7 | 411 | 0 | 980 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3.02 | 0 | 0 | 160 | 0 | 160 | 0 | 339 | 0 | 0.26 | 159 | 49 | 0 | 2 | 34 | 0 | 0 | 1.8 | 9 | 0.04 | 0 | 165 | 0 | 220 | 0 | 618 | 940 | 0 | 5446.12 | 12830.65 | 98.93
18:00 | 0 | 51 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 32 | 35 | 70 | 16 | 45 | 0 | 35 | 99 | 32 | 380 | 306 | 0 | 0 | 0 | 333 | 200 | 0 | 1 | 17 | 18 | 21 | 0 | 0 | 0 | 15 | 0 | 0 | 1 | 0 | 0 | 0 | 36 | 50 | 0.31 | 205 | 0 | 5 | 673 | 0 | 0 | 19 | 0 | 16 | 215 | 0 | 0 | 0 | 958 | 1 | 51 | 0 | 108 | 0 | 300 | 340 | 43 | 210 | 19 | 104 | 40 | 150 | 23 | 19 | 97 | 28 | 34 | 6 | 15 | 0 | 320 | 385 | 0 | 40 | 140 | 8 | 0 | 41 | 30 | 0 | 18 | 171 | 17 | 65 | 105 | 33 | 0 | 0.54 | 3 | 7311.85 | 885 | 266 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 432 | 0 | 988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 2.17 | 0 | 0 | 140 | 0 | 140 | 0 | 392 | 0 | 0.19 | 159 | 49 | 0 | 1 | 34 | 0 | 0 | 1.4 | 6 | 0 | 0 | 176 | 0 | 220 | 0 | 502 | 900 | 0 | 5337.76 | 12649.61 | 98.93
19:00 | 0 | 54 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 485 | 33 | 35 | 70 | 44 | 85 | 0 | 37 | 144 | 41 | 420 | 307 | 0 | 0 | 20 | 331 | 198 | 0 | 0 | 70 | 18 | 21 | 0 | 0 | 10 | 15 | 0 | 0 | 0 | 47 | 32 | 0 | 50 | 50 | 0 | 205 | 9 | 10 | 686 | 0 | 0 | 23 | 0 | 16 | 216 | 0 | 0 | 0 | 1104 | 0 | 51 | 38 | 111 | 0 | 330 | 340 | 45 | 188 | 19 | 109 | 40 | 155 | 27 | 19 | 97 | 32 | 34 | 0 | 16 | 0 | 320 | 393 | 0 | 40 | 148 | 8 | 0 | 84 | 30 | 0 | 18 | 171 | 17 | 65 | 113 | 33 | 0 | 0 | 6 | 8016 | 885 | 272 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 495 | 12 | 1087 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 178 | 0 | 170 | 0 | 394 | 0 | 0 | 156 | 49 | 50 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 220 | 0 | 488 | 935 | 0 | 5832 | 13848 | 98.93
19:30 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 46 | 35 | 70 | 48 | 145 | 0 | 55 | 144 | 50 | 450 | 306 | 0 | 0 | 35 | 330 | 198 | 0 | 0 | 70 | 21 | 21 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 48 | 39 | 0 | 50 | 50 | 0 | 205 | 16 | 12 | 695 | 0 | 0 | 50 | 0 | 16 | 216 | 0 | 0 | 0 | 1145 | 0 | 51 | 120 | 90 | 0 | 330 | 340 | 49 | 167 | 19 | 111 | 40 | 155 | 28 | 19 | 97 | 32 | 34 | 0 | 34 | 0 | 320 | 390 | 0 | 40 | 157 | 8 | 0 | 84 | 30 | 0 | 18 | 171 | 17 | 85 | 179 | 33 | 0 | 0 | 6 | 8504 | 887 | 272 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 17 | 1083 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 196 | 0 | 197 | 0 | 414 | 0 | 0 | 156 | 50 | 91 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 220 | 0 | 488 | 1120 | 0 | 6249 | 14753
20:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 48 | 35 | 70 | 48 | 145 | 0 | 55 | 155 | 50 | 450 | 294 | 0 | 0 | 35 | 332 | 201 | 0 | 0 | 70 | 24 | 21 | 0 | 0 | 16 | 15 | 0 | 0 | 1 | 48 | 39 | 0 | 63 | 50 | 0 | 205 | 15 | 18 | 693 | 0 | 0 | 50 | 0 | 16 | 216 | 0 | 0 | 0 | 1115 | 0 | 51 | 123 | 55 | 0 | 330 | 340 | 49 | 166 | 17 | 109 | 40 | 155 | 27 | 19 | 97 | 32 | 34 | 0 | 38 | 0 | 320 | 395 | 0 | 50 | 157 | 8 | 0 | 84 | 30 | 0 | 18 | 171 | 17 | 85 | 180 | 33 | 0 | 0 | 6 | 8493 | 888 | 272 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 581 | 22 | 1041 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 198 | 0 | 197 | 0 | 402 | 0 | 0 | 159 | 50 | 95 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 0 | 220 | 0 | 488 | 1155 | 0 | 6296 | 14789 | 98.93
21:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 48 | 35 | 70 | 48 | 145 | 0 | 55 | 154 | 50 | 450 | 311 | 0 | 0 | 35 | 333 | 201 | 0 | 0 | 90 | 23 | 21 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 65 | 39 | 0 | 63 | 50 | 0 | 206 | 15 | 20 | 667 | 0 | 0 | 50 | 0 | 16 | 217 | 0 | 0 | 0 | 1150 | 0 | 51 | 143 | 16 | 0 | 330 | 340 | 49 | 209 | 17 | 106 | 45 | 149 | 27 | 19 | 97 | 32 | 34 | 0 | 38 | 0 | 320 | 360 | 0 | 50 | 148 | 8 | 0 | 84 | 30 | 0 | 18 | 171 | 17 | 85 | 180 | 33 | 0 | 0 | 12 | 8481 | 893 | 270 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 581 | 34 | 1073.01 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 200 | 0 | 198 | 0 | 393 | 0 | 0 | 158 | 49 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 220 | 0 | 488 | 1240 | 0 | 6435.01 | 14916.01 | 98.93
22:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 46 | 35 | 62 | 32 | 30 | 0 | 43 | 145 | 50 | 450 | 307 | 0 | 0 | 0 | 333 | 202 | 0 | 0 | 90 | 23 | 14 | 0 | 0 | 14 | 15 | 0 | 0 | 2 | 65 | 39 | 0 | 63 | 50 | 0 | 208 | 14 | 25 | 671 | 0 | 0 | 26 | 1 | 15 | 219 | 0 | 0 | 0 | 1140 | 0 | 51 | 147 | 8 | 0 | 330 | 340 | 49 | 195 | 17 | 96 | 40 | 146 | 27 | 19 | 97 | 32 | 34 | 0 | 38 | 0 | 320 | 385 | 0 | 50 | 153 | 8 | 0 | 84 | 30 | 0 | 18 | 172 | 17 | 85 | 164 | 33 | 0 | 0 | 11 | 8229 | 893 | 266 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 784 | 42 | 1060.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 198 | 0 | 414 | 0 | 0 | 159 | 50 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 220 | 0 | 487 | 1244 | 0 | 6571.79 | 14800.79 | 98.93
23:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 46 | 35 | 51 | 32 | 0 | 0 | 35 | 147 | 50 | 450 | 311 | 0 | 0 | 0 | 335 | 200 | 0 | 0 | 90 | 23 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 65 | 39 | 0 | 63 | 50 | 0 | 209 | 0 | 29 | 687 | 0 | 0 | 26 | 8 | 0 | 219 | 0 | 0 | 0 | 1150 | 0 | 51 | 70 | 8 | 0 | 330 | 340 | 49 | 199 | 17 | 88 | 35 | 144 | 26 | 19 | 98 | 32 | 40 | 0 | 38 | 0 | 320 | 388 | 0 | 50 | 155 | 8 | 0 | 84 | 30 | 0 | 18 | 172 | 17 | 85 | 164 | 33 | 0 | 0 | 6 | 8090 | 887 | 264 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 810 | 17 | 1067.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 198 | 0 | 414 | 0 | 0 | 157 | 50 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 0 | 220 | 0 | 486 | 1244 | 0 | 6537.85 | 14627.85 | 98.93
Total KWH | 0 | 1106880 | 692160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12476620 | 565200 | 782640 | 1176048 | 366720 | 921087 | 60946 | 594398 | 1824480 | 439680 | 9928500 | 7279709 | 0 | 0 | 104545 | 7983931 | 4402000 | 0 | 102503 | 1339200 | 532800 | 455760 | 0 | 0 | 61473 | 155564 | 0 | 0 | 108960 | 586765 | 225744 | 0 | 958080 | 1180800 | 25246 | 5039773 | 68600 | 399840 | 16901818.18 | 0 | 0 | 327360 | 42750 | 167273 | 5127443 | 0 | 0 | 0 | 23950907 | 112050 | 1127116 | 695854 | 1053818 | 0 | 8260300 | 8156000 | 1099200 | 4844000 | 440928 | 1959360 | 1022670 | 4055520 | 314160 | 432500 | 2298240 | 678720 | 834696 | 371555 | 392464 | 0 | 7685200 | 9471000 | 0 | 686960 | 3468191 | 170712 | 0 | 1927680 | 716352 | 0 | 435000 | 3542540 | 705960 | 1411200 | 3120000 | 901440 | 7250 | 168530 | 233520 | 181264889.18 | 21422545 | 6078528 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 83952 | 307440 | 12516368 | 204000 | 24877455 | 0 | 0 | 0 | 10848 | 0 | 167296 | 0 | 0 | 0 | 454675 | 73594 | 216000 | 0 | 0 | 4882727 | 0 | 4922627 | 0 | 8969163 | 0 | 19860 | 3843000 | 1154182 | 921721 | 55714 | 1271568 | 0 | 0 | 14540.04 | 768960 | 2923 | 0 | 4844000 | 0 | 5409710 | 0 | 14085864 | 24369454.55 | 0 | 142860714.59 | 324125603.77

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 16-07-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13591 | MW | 12:00 Hr. | Energy Generated |  |  | 324.1256 |  | MKWHr.
| Day Peak Demand |  |  | 13591 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.059 |  | MKWHr.
| Evening Peak Generation |  |  | 14916.01 | MW | 21:00 Hr. | Energy Demand |  |  | 324.1846 |  | MKWHr.
| Evening Peak Demand |  |  | 14916.01 | MW | 21:00 Hr. | Maximum Temperature |  |  | 33.3 |  | °C
| Minimum Generation of the Day |  |  | 12109.46 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 977.57 |  | MMCFD
| Maximum Generation of the Day |  |  | 14916.01 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 5.8113 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 43.0593 | 0 | 9.974 | 0 | 0 | 0.1025 | 0 | 0 | 53.1358 | Gas | 134.291 | Gas | 450759827.97
| Chattogram Zone |  |  | 5.5273 | 40.8527 | 3.7744 | 0 | 5.0398 | 0.1373 | 0 | 0.10896 | 55.4404 | Coal | 101.6656 | Coal | 553735710.0163
| Cumilla Zone |  |  | 26.4365 | 0 | 10.5503 | 0 | 0 | 0.37156 | 0.67872 | 0 | 38.0371 | HFO | 32.5023 | HFO | 597456929.04
| Mymensingh Zone |  |  | 0.90144 | 0 | 5.4707 | 0 | 0 | 0.17578 | 0 | 0 | 6.5479 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.1036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.1036 | Hydro | 5.0398 | Hydro | 503977.3
| Khulna Zone |  |  | 6.0785 | 12.5164 | 0.28795 | 0 | 0 | 0.30744 | 22.3345 | 0 | 41.5248 | Solar | 2.6272 | Solar | 41869412.1644
| Barishal Zone |  |  | 5.4097 | 43.2993 | 0 | 0 | 0 | 0.002923 | 0 | 0 | 48.712 | Import | 47.8907 | Import | 237683191.1
| Rajshahi Zone |  |  | 18.7745 | 0 | 0.25174 | 0 | 0 | 0.69054 | 24.8775 | 0 | 44.5942 | Wind | 0.10896 | Wind | 1595174.4
| Rangpur Zone |  |  | 0 | 4.9972 | 2.1933 | 0 | 0 | 0.83921 | 0 | 0 | 8.0297
| Total |  |  | 134.291 | 101.6656 | 32.5023 | 0 | 5.0398 | 2.6272 | 47.8907 | 0.10896 | 324.1256
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 450759827.97 |  | Hydro | 503977.3
|  |  |  | Coal | 553735710.0163 |  | Solar | 41869412.1644
|  |  |  | HFO | 597456929.04 |  | Import | 237683191.1
|  |  |  | HSD | 0 |  | Wind | 1595174.4
[5 empty] | Total: | 188,36,04,221 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.4225 | Peak Hr Flow | 893.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 37161945.54 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.8775 | Peak Hr Flow | 1073.01 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 774 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.67872 | Peak Hr Flow | 32.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 970 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 46.9787 | Peak Hr Flow | 1998.01 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5063
|  |  |  | Chattogram |  | 0 |  | 1538
|  |  |  | Cumilla |  | 0 |  | 1416
|  |  |  | Mymensingh |  | 0 |  | 1167
|  |  |  | Sylhet |  | 0 |  | 659
|  |  |  | Khulna |  | 0 |  | 1705
|  |  |  | Barishal |  | 0 |  | 477
|  |  |  | Rajshahi |  | 0 |  | 1401
|  |  |  | Rangpur |  | 0 |  | 933
|  |  |  | Total |  | 0 |  | 14359
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Bibiana-II 341 MW CCPP (Summit) GT |  |  | 222 | 3 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
|  | 4 | Bibiana-II 341 MW CCPP (Summit) ST |  |  | 119
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 641 |  |  |  | Total | 476
|  |  |  | Total Unavailable Capacity |  |  |  | 1117
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:18 | 08:48 | Gopalganj 132/33kV S/S T1 LT Tripped showing O/c+u/f relays Due to Bpbs-1+REB-8 feeder | [7 empty] | 35.0MW load
|  |  | fault | [7 empty] | interrup.
| 08:40 | 19:26 | Bogura 400/230kV S/S ATR-01 HT Scheduled S/D Due to ATR-01 Painting.
| 08:40 | 19:26 | Bogura 400/230kV S/S ATR-01 LT Scheduled S/D Due to ATR-01 Painting.
| 08:43 | 17:55 | Feni-PHP 132kV Ckt-1 Scheduled S/D from Feni 132/33kV end Due to For Sub-station
Maintenance at PHP End
| 08:45 | 17:41 | Baroirhat-PHP 132 kV Ckt-1 Forced S/D from Baroirhat 132/33kV end Due to PHP SS S/D
| 08:54 | 09:18 | Purbasadipur 132/33kV S/S T-1 Transformer (403T) LT Tripped showing ALSTOM (MCGG) relays. | [7 empty] | 6.0MW load
interrup.
|  | 09:07 | Kishoreganj 132/33kV S/S Tr-1 (404T) HT is restored.
|  | 09:08 | Kishoreganj 132/33kV S/S Tr-1 (404T) LT is restored.
| 09:08 | 10:35 | Aminbazar-Meghnaghat 400kV Ckt-1 Scheduled S/D from Meghnaghat 400/230kV end Due to
Aminbazar ckt -1 shutdown for changing nut-bolts of 410-CT junction point
| 09:15 | 16:03 | Brahmanbaria-Narsinghdi 132 kV Ckt-1 Project Work S/D from Brahmanbaria 132/33kV end Due
to relocation of 6nos. tower
| 09:15 | 16:03 | Brahmanbaria-Narsinghdi 132 kV Ckt-2 Project Work S/D from Brahmanbaria 132/33kV end Due
to relocation of 6 nos. tower
| 09:26 | 10:03 | Bhandaria 132/33kV S/S Transformer-1 LT Forced S/D Due to 33 kV Incoming Meter
Replacement work by EAUD, BPDB Barishal.
| 09:27 | 10:02 | Bhandaria 132/33kV S/S Transformer-1 HT Forced S/D Due to 33 kV Incoming Meter
Replacement work by EAUD, BPDB Barishal.
| 09:42 | 13:25 | Mahasthangar-Palashbari 132kV Ckt-1 Project Work S/D from Palashbari 132/33kV end Due to
Project work and from Mahasthangarh 132/33kVend.
|  | 09:56 | Kishoreganj 132/33kV S/S Tr-3 (424T) HT is restored.
|  | 09:57 | Kishoreganj 132/33kV S/S Tr-3 (424T) LT is restored.
| 10:01 | 12:51 | Mahasthangarh 132/33kV S/S 132KVMain bus 2 Project Work S/D
| 10:18 | 11:06 | Bhandaria 132/33kV S/S Transformer-2 LT Forced S/D Due to 33 kV Incoming Meter
Replacement work by EAUD, BPDB Barishal.
| 10:20 | 11:05 | Bhandaria 132/33kV S/S Transformer-2 HT Forced S/D Due to 33 kV Incoming Meter
Replacement work by EAUD, BPDB Barishal.
| 10:31 | 20:59 | Kalurghat 132/33kV S/S TRFO-01(506T) LT Scheduled S/D Due to Upgrading by BPDB
| 12:00 |  | Day peak Generation is 13587 MW
| 12:29 | 12:44 | Bogura 230/132kV S/S T-01 HT Tripped showing General trip , Backup trip lockout relay
relays.
| 12:29 | 12:44 | Bogura 230/132kV S/S T-01 LT Tripped showing N/A relays.
|  | 12:34 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-2 is restored.
| 13:32 |  | Mahasthangar-Palashbari 132kV Ckt-2 Project Work S/D from Mahasthangarh 132/33kV end Due
to Mahasthangarh-Palashbari Ckt-2 Reconducting work by STGE project. and from Palashbari
132/33kV end Due to Reconducting work
| 16:05 | 18:39 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T LT Scheduled S/D Due to Red hot | [7 empty] | 30.0MW load
|  |  | maintenance of moddhapara feeder (R- phase) | [7 empty] | interrup.
| 16:06 | 18:34 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T HT Scheduled S/D Due to Red hot | [7 empty] | 30.0MW load
|  |  | maintenance at NESCO switching, moddhopara feeder | [7 empty] | interrup.
| 16:07 | 16:53 | Kodda-Rajendrapur 132kV Ckt-1 Tripped from Kodda 132/33kV end showing Distance Relay | [7 empty] | 12.0MW load
|  |  | relays Due to Extreme weather | [7 empty] | interrup. Kodda
132/33kV end
| 16:21 | 16:53 | Kodda-Rajendrapur 132kV Ckt-1 Tripped from Rajendrapur 132/33kV end showing Distance
relays Due to Earth fault at R-Phase shown at Kodda end , there is no relay/breaker
operated at Rajendrapur end.
| 17:49 |  | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-2 Forced S/D Due to Line VT( Y-Phase)
Unwanted noise rechecking work finish.Line VT Problem.
| 17:55 | 20:50 | Madanganj 132/33kV S/S GT-2 LT Tripped showing O/E fault relays. | [7 empty] | 30.0MW load
interrup.
| 17:55 | 19:55 | Madanganj 132/33kV S/S GT-1 HT Tripped showing O/E fault relay relays. | [7 empty] | 8.0MW load
interrup.
| 17:55 | 19:55 | Madanganj 132/33kV S/S GT-1 LT Tripped showing O/E fault relay relays. | [7 empty] | 8.0MW load
interrup.
| 17:55 | 20:50 | Madanganj 132/33kV S/S GT-2 HT Tripped showing Back up protection relays. | [7 empty] | 30.0MW load
interrup.
| 18:01 | 22:21 | Madanganj 132/33kV S/S Madanganj -Bashundhara 132 kv Ckt Tripped showing Line | [7 empty] | 6.0MW load
|  |  | Differential relay relays. | [7 empty] | interrup.
| 21:00 |  | peak generation 14916 MW
| 21:04 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U1
| 21:49 |  | Raozan 25 MW PP Synchronized
| 22:17 | 00:01 | Mirzapur 132/33kV S/S Transformer-01(E05) LT Forced S/D Due to Tr-01 S/D taken due to red | [7 empty] | 26.0MW load
|  |  | hot at 33 kV side B-phase. | [7 empty] | interrup.
| 22:18 | 00:00 | Mirzapur 132/33kV S/S Transformer-01(E05) HT Forced S/D Due to Tr-01 S/D taken due to red | [7 empty] | 26.0MW load
|  |  | hot at 33 kV side B-phase. | [7 empty] | interrup.
| 01:44 |  | Raozan 25 MW PP Shutdown
| 06:26 |  | Dhamrai 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Work by PBS. | [7 empty] | 60.0MW load
interrup.
| 06:26 |  | Dhamrai 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Work by PBS. | [7 empty] | 60.0MW load
interrup.
| 06:45 |  | Borhanuddin 230/33kV S/S Tr-Load LT Scheduled S/D Due to Red hot maintenance at 33 KV | [7 empty] | 75.0MW load
|  |  | busbar and DS. | [7 empty] | interrup.
| 06:45 |  | Borhanuddin 230/33kV S/S Tr-Load HT Scheduled S/D Due to Red hot maintenance at 33 KV | [7 empty] | 75.0MW load
|  |  | busbar and DS. | [7 empty] | interrup.
| 07:00 |  | Minimum Generation: 12235 MW.
| 07:25 | 07:50 | Bhaluka-Mymensingh 132 kV Ckt-1 Tripped from Bhaluka 132/33kV end showing Distance relay
R phase relays Due to Bad weather. and from Mymensingh 132/33kV end showing Distance
(21) relays Due to Due to Heavy Thunderstorm
| 07:25 | 07:50 | Bhaluka-Mymensingh 132 kV Ckt-2 Tripped from Bhaluka 132/33kV end showing Distance relay
R Y B Phase relays Due to Bad weather and from Mymensingh 132/33kV end showing Distance
(21)) relays Due to Due to heavy thunderstorm
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 16-07-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9928500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 311 | 7279709 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 60946 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 201 | 4402000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 333 | 7983931 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 48 | 565200 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 48 | 366720 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 594398 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 104545 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23 | 532800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 455760 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 34 | 692160 | Engine Problem
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 921087 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 70 | 1176048 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1106880 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 50 | 439680 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 154 | 1824480 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 102503 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 782640 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 500 | 12476620 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 90 | 1339200 | Engine Problem
Dhaka Area Total |  |  |  |  | 5939.724 | 2673 | 53135807
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 42750 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 112050 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 327360 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 206 | 5039773 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5127443 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 16 | 167273 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 39 | 225744 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 586765 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 63 | 958080 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 20 | 399840 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 25246 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 155564 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 15 | 68600 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 1180800 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 61473 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1150 | 23950907 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 108960 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 667 | 16901818.18 | FGMO
Chattogram Area Total |  |  |  |  | 4895.72 | 2590 | 55440446.18
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 209 | 4844000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 330 | 8260300 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 8156000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 17 | 440928 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 49 | 1099200 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 16 | 1053818 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1127116 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 143 | 695854 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 38 | 392464 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 45 | 1022670 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 149 | 4055520 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 32 | 678720 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 34 | 834696 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 432500 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 97 | 2298240 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 314160 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 106 | 1959360 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 371555 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1702 | 38037101
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 33 | 901440 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7250 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 180 | 3120000 | Engine Problem
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 85 | 1411200 | Engine Problem
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 168530 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 233520 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 705960 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 327 | 6547900
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 50 | 686960 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 148 | 3468191 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 716352 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1927680 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 171 | 3542540 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 435000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 170712 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under Maintenance
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 360 | 9471000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7685200 | Aythority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2325 | 1189 | 28103635
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 893 | 21422545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 270 | 6078528 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 34 | 204000 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 32 | 83952 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 307440 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 581 | 12516368 | U#1 Under Reserve shut down
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1848 | 41524833
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 488 | 14085864 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 0 | 0 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1240 | 24369454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5409710 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 278 | 4844000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2923 | -
Barishal Area Total |  |  |  |  | 2236 | 2226 | 48711951.55
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 200 | 4882727 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 198 | 4922627 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 393 | 8969163 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 73594 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 52 | 167296 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 10848 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 19860 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1073.01 | 24877455 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 216000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 454675 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 1946.01 | 44594245
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 49 | 1154182 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 158 | 3843000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1271568 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 14540.04 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 921721 | Schedule Maintenance
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 55714 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 768960 | -
Rangpur Area Total |  |  |  |  | 950 | 415 | 8029685.04
Eastern Grid Total |  |  |  |  | 16705.895 | 8481 | 181264889.18
Western Grid Total |  |  |  |  | 10378.16 | 6435.01 | 142860714.59
National Grid Total |  |  |  |  | 27084.055 | 14916.01 | 324125603.77
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 16-07-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9842.87 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4516.4 | MW
i) Dhaka area |  |  | 5062.99 |  | MW | i) Khulna area |  |  |  | 1705 | MW
ii) Chattogram area |  |  | 1537.9 |  | MW | ii) Barishal area |  |  |  | 477 | MW
iii) Cumilla area |  |  | 1415.98 |  | MW | iii) Rajshahi area |  |  |  | 1401.4 | MW
iv) Mymensingh area |  |  | 1167 |  | MW | iv) Rangpur area |  |  |  | 933 | MW
v) Sylhet area |  |  | 659 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14359.27 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 85 | 22:00 | 133 | PHP | 6 | 02:00
2 | AKSML | 149.7 | 15:00 | 68 | Ishurdi | 77 | 13:00 | 134 | Pabna | 117 | 20:00
3 | Aftabnagar | 38 | 13:00 | 69 | Jaldhaka | 80 | 19:00 | 135 | Palashbari | 110 | 20:00
4 | Agargaon | 130 | 15:00 | 70 | Jamalpur | 116 | 20:00 | 136 | Panchagarh | 60 | 00:00
5 | Agrabad | 96 | 14:00 | 71 | Jashore | 130 | 19:30 | 137 | Patuakhali | 77 | 22:00
6 | Amnura | 35 | 21:00 | 72 | Jhenaidah | 124 | 22:00 | 138 | Payra | 38 | 22:00
7 | Ashuganj | 94 | 02:00 | 73 | Joydebpur | 145 | 15:00 | 139 | Postogola | 61 | 13:00
8 | BSRM | 199 | 21:00 | 74 | Joypurhat | 58 | 23:00 | 140 | Purbachal | 20 | 19:30
9 | Bagerhat | 83 | 19:00 | 75 | Juldah | 17.5 | 23:00 | 141 | Purbasadipur | 126 | 00:00
10 | Bajitpur | 59 | 19:30 | 76 | KSRM | 23 | 03:00 | 142 | Rahanpur | 28 | 22:00
11 | Bakulia | 96 | 19:30 | 77 | Kabirpur | 220 | 09:00 | 143 | Rahim | 28 | 16:00
12 | Banani | 38.2 | 13:00 | 78 | Kachua | 90 | 22:00 | 144 | Rajbari | 82 | 19:30
13 | Bangabhaban | 17 | 10:00 | 79 | Kallyanpur | 108 | 15:00 | 145 | Rajendrapur | 132 | 15:00
14 | Barapukuria | 69 | 19:30 | 80 | Kalurghat | 39 | 17:00 | 146 | Rajshahi | 129 | 21:00
15 | Barguna | 24 | 22:00 | 81 | Kamrangirchar | 77 | 12:00 | 147 | Rajshahi-230 | 72 | 00:00
16 | Barishal | 118 | 22:00 | 82 | Kaptai | N/A | N/A | 148 | Ramganj | 116 | 19:00
17 | Barishal-230 | 94 | 23:00 | 83 | Kasba | 36 | 21:00 | 149 | Rampur | 41 | 19:00
18 | Baroaulia | 73 | 14:00 | 84 | Kazla | 98 | 13:00 | 150 | Rangamati | 16 | 19:00
19 | Baroirhat | 65 | 19:00 | 85 | Keranigonj | 101 | 13:00 | 151 | Rangpur | 134 | 21:00
20 | Bashundhara | 185 | 14:00 | 86 | Khagrachori | 32 | 21:00 | 152 | Ruppur | 7.6 | 10:00
21 | BashundharaCement | 9 | 15:00 | 87 | Khulna | 84 | 13:00 | 153 | SSM | 14 | 01:00
22 | Beanibazar | 86 | 19:30 | 88 | Khulshi | 155 | 16:00 | 154 | Saidpur | 101 | 19:30
23 | Benapole | 58 | 21:00 | 89 | Kishoreganj | 141 | 21:00 | 155 | Satkhira | 129 | 22:00
24 | Bhaluka | 140 | 21:00 | 90 | Kodda | 320 | 19:30 | 156 | Satmasjid | 89 | 13:00
25 | Bhandaria | 58 | 22:00 | 91 | Kulaura | 49 | 19:00 | 157 | Savar | 224 | 12:00
26 | Bhangura | 34 | 19:30 | 92 | Kurigram | 64 | 20:00 | 158 | SevenRings | 8.87 | 23:00
27 | Bheramara(GK) | 62 | 21:00 | 93 | Kushtia | 144 | 21:00 | 159 | ShahCement | 22 | 20:00
28 | Bhulta | 244 | 23:00 | 94 | Laksam | N/A | N/A | 160 | Shahjadpur | 86 | 21:00
29 | Bog-Sherpur | 60 | 19:00 | 95 | Lakshmipur | 32 | 19:30 | 161 | Shahjibazar | 132 | 21:00
30 | Bogura | 157 | 23:00 | 96 | Lalbag | 58 | 13:00 | 162 | Shahmirpur | 62 | 00:00
31 | Borhanuddin | 93 | 20:00 | 97 | Lalmonirhat | 60 | 20:00 | 163 | Shariatpur | 85 | 22:00
32 | Brahmanbaria | 135 | 22:00 | 98 | MI_Cement | 11.2 | 01:00 | 164 | Sherpur | 146 | 21:00
33 | Cantonment | 158 | 13:00 | 99 | Madanganj | 42 | 08:00 | 165 | Shikalbaha | 10 | 18:30
34 | Chandina | 15.1 | 15:00 | 100 | Madaripur | 112 | 22:00 | 166 | Shitalakhya | 85.1 | 12:00
35 | Chandpur | 80 | 23:00 | 101 | Madartek | 85 | 21:00 | 167 | Sholosohor | 46 | 15:00
36 | Chandraghona | 43 | 10:00 | 102 | Madunaghat | 56 | 19:00 | 168 | Shyampur | 164 | 13:00
37 | Chapai | 63 | 21:00 | 103 | Magura | 62 | 19:30 | 169 | Siddhirganj | 118 | 12:00
38 | Charsaidpur | 40 | 05:00 | 104 | Mahasthangarh | 72 | 23:00 | 170 | Sirajganj | 108 | 21:00
39 | Chauddagram | 75 | 23:00 | 105 | Maijdee | 16 | 01:00 | 171 | Sonargaon | 108 | 23:00
40 | Chhatak | 45 | 00:00 | 106 | Manikganj | 122 | 21:00 | 172 | Sreemongol | 92 | 19:30
41 | Chowmuhani | 187 | 19:30 | 107 | Maniknagar | 82 | 13:00 | 173 | Sreepur | 104 | 12:00
42 | Chuadanga | 107 | 21:00 | 108 | Matarbari | 51 | 20:00 | 174 | Srinagar | 45.39 | 22:00
43 | Coxsbazar | 145 | 19:00 | 109 | Matuail | 66 | 15:00 | 175 | Sunamganj | 63 | 00:00
44 | Cumilla(N) | 146 | 22:00 | 110 | Millgate | 103 | 14:00 | 176 | Sylhet | 54 | 00:00
45 | Cumilla(S) | 151 | 15:00 | 111 | Mirpur | 124 | 12:00 | 177 | Sylhet-132 | 140 | 19:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 11 | 09:00 | 178 | TK | 45 | 23:00
47 | Daudkandi | 142 | 21:00 | 113 | Mirzapur | 44 | 22:00 | 179 | Tangail | 162 | 21:00
48 | Dhaka | 80 | 13:00 | 114 | Mithapukur | 68 | 19:30 | 180 | Taraganj | 21 | 19:30
49 | Dhamrai | 128 | 11:00 | 115 | Modern | N/A | N/A | 181 | Thakurgaon | 101 | 00:00
50 | Dhanmondi | 148 | 13:00 | 116 | Mogbazar | 154.6 | 15:00 | 182 | Tongi | 122 | 11:00
51 | Dohazari | 113 | 21:00 | 117 | Mongla | 40 | 10:00 | 183 | Ullahpara | 34 | 20:00
52 | Faridpur | 160 | 21:00 | 118 | Motijheel | 44 | 13:00 | 184 | Ullon | 38 | 21:00
53 | Fatullah | 102 | 12:00 | 119 | Muktagacha | 33 | 00:00 | 185 | Uttara | 80 | 13:00
54 | Fenchuganj | 44 | 00:00 | 120 | Munshiganj | 109 | 00:00 | 186 | UttaraNew | 59 | 14:00
55 | Feni | 120 | 19:30 | 121 | Muradnagar | 42 | 21:00 | 187 | Zigatola | 72 | 13:00
56 | GPH | 78 | 18:00 | 122 | Mymensingh | 193 | 00:00
57 | Ghatail | 72 | 22:00 | 123 | Naogaon | 122 | 21:00
58 | Ghorashal | 14 | 16:00 | 124 | Narail | 57 | 20:00
59 | Ghorashal-230 | 88 | 22:00 | 125 | Narinda | 81 | 13:00
60 | Goalpara | 33 | 22:00 | 126 | Narshingdi | 181 | 21:00
61 | Gollamari | 76 | 23:00 | 127 | Natore | 132 | 00:00
62 | Gopalganj | 99 | 19:30 | 128 | Nawabganj | 55 | 22:00
63 | Gulshan | 130 | 13:00 | 129 | Netrakona | 146 | 20:00
64 | Halishahar | 73.5 | 15:00 | 130 | New | 90 | 12:00
65 | HaripurSBU | 160 | 12:00 | 131 | Niamatpur | 66 | 21:00
66 | Hasnabad | 55 | 19:00 | 132 | Noapara | 41 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 16-07-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14052.7 | 32 |  | 14085.7
1:00 | 13606.7 | 0 |  | 13606.7
2:00 | 13233.7 | 0 |  | 13233.7
3:00 | 12847.7 | 0 |  | 12847.7
4:00 | 12652.7 | 0 |  | 12652.7
5:00 | 12333.5 | 0 |  | 12333.5
6:00 | 12109.46 | 0 |  | 12109.46
7:00 | 12177.16 | 0 |  | 12177.16
8:00 | 12380.5 | 0 |  | 12380.5
9:00 | 12609.07 | 0 |  | 12609.07
10:00 | 12936.23 | 0 |  | 12936.23
11:00 | 13350.65 | 0 |  | 13350.65
12:00 | 13591 | 0 |  | 13591
13:00 | 13869.44 | 0 |  | 13869.44
14:00 | 13522.58 | 0 |  | 13522.58
15:00 | 13435.55 | 0 |  | 13435.55
16:00 | 13137.25 | 0 |  | 13137.25
17:00 | 12830.65 | 0 |  | 12830.65
18:00 | 12649.61 | 0 |  | 12649.61
19:00 | 13848 | 0 |  | 13848
19:30 | 14753 | 0 |  | 14753
20:00 | 14789 | 0 |  | 14789
21:00 | 14916.01 | 0 |  | 14916.01
22:00 | 14800.79 | 0 |  | 14800.79
23:00 | 14627.85 | 27 |  | 14656.07
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 16-07-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7558.7 | 6494 | 14052.7 | DAILY GENERATION CURVE
00:30 | 7385.7 | 6444 | 13829.7
01:00 | 7212.7 | 6394 | 13606.7 | 16-07-2025
01:30 | 7213.7 | 6206.5 | 13420.2
02:00 | 7214.7 | 6019 | 13233.7
02:30 | 7143.7 | 5897 | 13040.7
03:00 | 7072.7 | 5775 | 12847.7
03:30 | 7068.2 | 5682 | 12750.2
04:00 | 7063.7 | 5589 | 12652.7
04:30 | 6975.1 | 5518 | 12493.1
05:00 | 6886.5 | 5447 | 12333.5
05:30 | 6800.655 | 5420.825 | 12221.48
06:00 | 6714.81 | 5394.65 | 12109.46
06:30 | 6775.45 | 5367.86 | 12143.31
07:00 | 6836.09 | 5341.07 | 12177.16
07:30 | 6886.56 | 5392.27 | 12278.83
08:00 | 6937.03 | 5443.47 | 12380.5
08:30 | 7011.09 | 5483.695 | 12494.785
09:00 | 7085.15 | 5523.92 | 12609.07
09:30 | 7181.68 | 5590.97 | 12772.65
10:00 | 7278.21 | 5658.02 | 12936.23
10:30 | 7386.66 | 5756.78 | 13143.44
11:00 | 7495.11 | 5855.54 | 13350.65
11:30 | 7631.37 | 5839.455 | 13470.825
12:00 | 7767.63 | 5823.37 | 13591
12:30 | 7820.84 | 5909.38 | 13730.22
13:00 | 7874.05 | 5995.39 | 13869.44
13:30 | 7807.11 | 5888.9 | 13696.01
14:00 | 7740.17 | 5782.41 | 13522.58
14:30 | 7724.24 | 5754.825 | 13479.065
15:00 | 7708.31 | 5727.24 | 13435.55
15:30 | 7619.665 | 5666.735 | 13286.4
16:00 | 7531.02 | 5606.23 | 13137.25
16:30 | 7457.775 | 5526.175 | 12983.95
17:00 | 7384.53 | 5446.12 | 12830.65
17:30 | 7348.19 | 5391.94 | 12740.13
18:00 | 7311.85 | 5337.76 | 12649.61
18:30 | 7663.925 | 5584.88 | 13248.805
19:00 | 8016 | 5832 | 13848
19:30 | 8504 | 6249 | 14753
20:00 | 8493 | 6296 | 14789
20:30 | 8487 | 6365.505 | 14852.505 |  | Executive Engineer
21:00 | 8481 | 6435.01 | 14916.01 |  | Network Operation Division
21:30 | 8355 | 6503.4 | 14858.4
22:00 | 8229 | 6571.79 | 14800.79
22:30 | 8159.5 | 6554.82 | 14714.32
23:00 | 8090 | 6537.85 | 14627.85

## En-Curve
QF-LDC-12
Date | 16-07-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3680 | 1972.5 | 882 | 38 | 32 | 1206 | 208 | 4172 | 0 | 386 | 1467.2 | 0 | 0 | 9 | 32 | DAILY ENERGY CURVE
00:30 | 3633.5 | 1962.5 | 882.5 | 38 | 30 | 1210.5 | 208 | 4290.5 | 0 | 298 | 1264.7 | 0 | 0 | 11.5 | 16 | 16-07-2025
01:00 | 3587 | 1952.5 | 883 | 38 | 28 | 1215 | 208 | 4409 | 0 | 210 | 1062.2 | 0 | 0 | 14 | 0
01:30 | 3613 | 1924.5 | 883 | 38 | 28 | 1165 | 208 | 4329 | 0 | 206 | 1013.7 | 0 | 0 | 12 | 0 | Energy Generated | 324.1256 |  | MKWHr
02:00 | 3639 | 1896.5 | 883 | 38 | 28 | 1115 | 208 | 4249 | 0 | 202 | 965.2 | 0 | 0 | 10 | 0 | Energy not Served | 0.059 |  | MKWHr
02:30 | 3619 | 1893.5 | 883 | 38 | 27 | 1111 | 208 | 4158 | 0 | 193.5 | 901.7 | 0 | 0 | 8 | 0 | Total Energy Requirement | 324.1846 |  | MKWHr
03:00 | 3599 | 1890.5 | 883 | 38 | 26 | 1107 | 208 | 4067 | 0 | 185 | 838.2 | 0 | 0 | 6 | 0
03:30 | 3616 | 1893 | 883 | 38 | 26 | 1068 | 208 | 4032 | 0 | 176 | 805.7 | 0 | 0 | 4.5 | 0
04:00 | 3633 | 1895.5 | 883 | 38 | 26 | 1029 | 208 | 3997 | 0 | 167 | 773.2 | 0 | 0 | 3 | 0
04:30 | 3617.5 | 1893 | 883 | 38 | 26 | 1018 | 208 | 3936.5 | 0 | 158.5 | 710.1 | 0 | 0 | 4.5 | 0
05:00 | 3602 | 1890.5 | 883 | 38 | 26 | 1007 | 208 | 3876 | 0 | 150 | 647 | 0 | 0 | 6 | 0
05:30 | 3594 | 1888.5 | 883 | 38 | 25 | 996.5 | 208 | 3865.5 | 9.48 | 108.5 | 597 | 0 | 0 | 8 | 0
06:00 | 3586 | 1886.5 | 883 | 38 | 24 | 986 | 208 | 3855 | 18.96 | 67 | 547 | 0 | 0 | 10 | 0
06:30 | 3612 | 1906.5 | 883 | 38 | 24 | 958.5 | 208 | 3812 | 57.31 | 67.5 | 568 | 0 | 0 | 8.5 | 0
07:00 | 3638 | 1926.5 | 883 | 38 | 24 | 931 | 208 | 3769 | 95.66 | 68 | 589 | 0 | 0 | 7 | 0
07:30 | 3605 | 1898.25 | 883 | 38 | 24 | 928 | 208 | 3822 | 153.08 | 76 | 640 | 0 | 0 | 3.5 | 0
08:00 | 3572 | 1870 | 883 | 38 | 24 | 925 | 208 | 3875 | 210.5 | 84 | 691 | 0 | 0 | 0 | 0
08:30 | 3633.5 | 1849 | 883 | 38 | 24 | 920 | 210 | 3880.5 | 244.285 | 101 | 711 | 0 | 0 | 0.5 | 0
09:00 | 3695 | 1828 | 883 | 38 | 24 | 915 | 212 | 3886 | 278.07 | 118 | 731 | 0 | 0 | 1 | 0
09:30 | 3696.5 | 1862.5 | 883 | 38 | 24 | 931 | 213 | 3886.5 | 331.15 | 118 | 788.5 | 0 | 0 | 0.5 | 0
10:00 | 3698 | 1897 | 883 | 38 | 24 | 947 | 214 | 3887 | 384.23 | 118 | 846 | 0 | 0 | 0 | 0
10:30 | 3670 | 1925.5 | 882.5 | 38 | 25 | 931 | 214 | 3920.5 | 481.04 | 143.5 | 905.9 | 0 | 0 | 6.5 | 0
11:00 | 3642 | 1954 | 882 | 38 | 26 | 915 | 214 | 3954 | 577.85 | 169 | 965.8 | 0 | 0 | 13 | 0
11:30 | 3690 | 1968.5 | 883.5 | 38 | 27 | 923 | 212.5 | 4036.5 | 461.805 | 175 | 1041.02 | 0 | 0 | 14 | 0
12:00 | 3738 | 1983 | 885 | 38 | 28 | 931 | 211 | 4119 | 345.76 | 181 | 1116.24 | 0 | 0 | 15 | 0
12:30 | 3686.5 | 1988 | 885 | 38 | 30 | 1023.5 | 211 | 4168 | 312.84 | 182.5 | 1195.88 | 0 | 0 | 9 | 0
13:00 | 3635 | 1993 | 885 | 38 | 32 | 1116 | 211 | 4217 | 279.92 | 184 | 1275.52 | 0 | 0 | 3 | 0
13:30 | 3589 | 1967.5 | 885 | 38 | 32 | 1112 | 211 | 4196 | 209.65 | 176 | 1278.36 | 0 | 0 | 1.5 | 0
14:00 | 3543 | 1942 | 885 | 38 | 32 | 1108 | 211 | 4175 | 139.38 | 168 | 1281.2 | 0 | 0 | 0 | 0
14:30 | 3539.5 | 1941.5 | 884.5 | 38 | 31 | 1106.5 | 210.5 | 4166 | 109.965 | 168 | 1283.1 | 0 | 0 | 0.5 | 0
15:00 | 3536 | 1941 | 884 | 38 | 30 | 1105 | 210 | 4157 | 80.55 | 168 | 1285 | 0 | 0 | 1 | 0
15:30 | 3557.5 | 1934.5 | 884 | 38 | 30 | 1069 | 209 | 4165 | 75.9 | 135 | 1184.5 | 0 | 0 | 4 | 0
16:00 | 3579 | 1928 | 884 | 38 | 30 | 1033 | 208 | 4173 | 71.25 | 102 | 1084 | 0 | 0 | 7 | 0
16:30 | 3568.5 | 1936.5 | 884 | 38 | 30 | 1006.5 | 207 | 4065.5 | 62.45 | 100.5 | 1080.5 | 0 | 0 | 4.5 | 0
17:00 | 3558 | 1945 | 884 | 38 | 30 | 980 | 206 | 3958 | 53.65 | 99 | 1077 | 0 | 0 | 2 | 0
17:30 | 3575 | 1867.5 | 884.5 | 38 | 29 | 984 | 205.5 | 3903.5 | 39.63 | 115.5 | 1096.5 | 0 | 0 | 1.5 | 0
18:00 | 3592 | 1790 | 885 | 38 | 28 | 988 | 205 | 3849 | 25.61 | 132 | 1116 | 0 | 0 | 1 | 0
18:30 | 3636.5 | 1868.5 | 885 | 38 | 30 | 1037.5 | 205 | 3996.5 | 12.805 | 250 | 1288.5 | 0 | 0 | 0.5 | 0
19:00 | 3681 | 1947 | 885 | 38 | 32 | 1087 | 205 | 4144 | 0 | 368 | 1461 | 0 | 0 | 0 | 0
19:30 | 3721 | 2038 | 887 | 38 | 32 | 1083 | 205 | 4485 | 0 | 425 | 1839 | 0 | 0 | 0 | 0
20:00 | 3728 | 2010 | 888 | 38 | 32 | 1041 | 205 | 4514 | 0 | 461 | 1871 | 0 | 0 | 1 | 0
20:30 | 3731.5 | 1965 | 890.5 | 38 | 32 | 1057.005 | 205.5 | 4562.5 | 0 | 479.5 | 1890.5 | 0 | 0 | 0.5 | 0
21:00 | 3735 | 1920 | 893 | 38 | 32 | 1073.01 | 206 | 4611 | 0 | 498 | 1910 | 0 | 0 | 0 | 0
21:30 | 3748.5 | 1915.5 | 893 | 38 | 32 | 1066.9 | 207 | 4711 | 0 | 449 | 1796.5 | 0 | 0 | 1 | 0
22:00 | 3762 | 1911 | 893 | 38 | 32 | 1060.79 | 208 | 4811 | 0 | 400 | 1683 | 0 | 0 | 2 | 0
22:30 | 3762 | 1919.5 | 890 | 38 | 32 | 1064.32 | 208.5 | 4836 | 0 | 384 | 1578.5 | 0 | 0 | 1.5 | 13.5
23:00 | 3762 | 1928 | 887 | 38 | 32 | 1067.85 | 209 | 4861 | 0 | 368 | 1474 | 0 | 0 | 1 | 27
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 16-07-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 376 | 06:00 | 366 | 12:00 | Payra | 413 | 18:00 | 405 | 00:00
Ashuganj | 400 | 5:00 | 375 | 12:00 | Rahanpur | 397 | 09:00 | 380 | 01:00
Bhulta | 396 | 05:00 | 371 | 12:00 | Rampal | 398 | 18:30 | 380 | 01:00
Bibiana | 382 | 06:00 | 376 | 00:00
BIPTC | 402 | 06:00 | 394 | 22:00
Bogura | 384 | 09:00 | 368 | 01:00
Gopalganj | 391 | 18:30 | 379 | 00:00
Kaliakoir | 368 | 05:00 | 357 | 10:00
Madunaghat | 389 | 10:00 | 384 | 01:00
Meghnaghat | 379 | 04:00 | 371 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 220 | 06:00 | 212 | 10:00 | Keranigonj | 217 | 04:00 | 210 | 10:00
AKSML | 228 | 06:00 | 222 | 15:00 | Khulna(S) | 229 | 06:00 | 216 | 19:30
Aminbazar | 220 | 05:00 | 212 | 10:00 | Madunaghat | 230 | 18:30 | 225 | 15:00
Ashuganj | 229 | 05:00 | 212 | 15:00 | Madunaghat-400 | 230 | 19:00 | 227 | 00:00
Ashuganj-400 | 229 | 05:00 | 212 | 15:00 | Maniknagar | 216 | 03:00 | 209 | 10:00
Baghabari | 233 | 17:00 | 225 | 00:00 | Meghnaghat | 223 | 07:00 | 218 | 11:00
Barapukuria | 224 | 15:00 | 217 | 01:00 | Meghnaghat-400 | 221 | 04:00 | 214 | 12:00
Barapukuria-230 | 224 | 15:00 | 217 | 01:00 | Mirsorai | 225 | 18:30 | 218 | 01:00
Barishal | 230 | 03:00 | 218 | 00:00 | Rajshahi | 230 | 17:00 | 221 | 00:00
Bheramara | 230 | 17:00 | 222 | 00:00 | Rampal | 227 | 18:30 | 216 | 19:30
Bhulta | 228 | 04:00 | 209 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 224 | 06:00 | 220 | 00:00 | Rampura | 227 | 05:00 | 211 | 12:00
BIPTC | 233 | 17:00 | 222 | 01:00 | Shikalbaha | 226 | 05:00 | 222 | 23:00
Bogura | 233 | 17:00 | 224 | 01:00 | Shyampur | 217 | 04:00 | 211 | 10:00
Bogura-400 | 232 | 17:00 | 224 | 01:00 | Siddhirganj | 217 | 19:00 | 212 | 10:00
Borhanuddin | 232 | 03:00 | 222 | 00:00 | Sirajgonj | 239 | 06:00 | 232 | 19:30
BSRM | 224 | 18:30 | 218 | 01:00 | Sreepur | 227 | 17:00 | 219 | 10:00
Cumilla(N) | 221 | 18:30 | 214 | 00:00 | Tongi | 223 | 07:00 | 213 | 11:00
Faridpur | 223 | 08:00 | 215 | 00:00
Fenchuganj | 227 | 18:30 | 220 | 01:00
Ghorashal | 230 | 00:00 | 220 | 13:00
Ghorashal-230 | 225 | 04:00 | 213 | 12:00
Gopalganj | 224 | 18:00 | 216 | 00:00
GPH | 226 | 00:00 | 221 | 14:00
Haripur | 217 | 05:00 | 211 | 11:00
Hasnabad | 218 | 18:00 | 211 | 10:00
Hathazari | 225 | 01:00 | 220 | 21:00
Ishurdi | 233 | 17:00 | 225 | 00:00
Jhenaidah | 227 | 18:00 | 216 | 19:30
Kaliakoir | 227 | 05:00 | 218 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 04:00 | 127 | 14:00 | Lalmonirhat | 127 | 16:00 | 120 | 19:30
Agargaon | 129 | 04:00 | 120 | 18:30 | Madanganj | 126 | 05:00 | 121 | 10:00
Agrabad | 129 | 07:00 | 125 | 12:00 | Madaripur | 134 | 17:00 | 128 | 01:00
AKS | 128 | 06:00 | 124 | 13:00 | Madartek | 137 | 05:00 | 124 | 12:00
Aminbazar | 130 | 18:30 | 124 | 10:00 | Madunaghat | 130 | 06:00 | 127 | 15:00
Amnura | 135 | 18:00 | 126 | 01:00 | Magura | 133 | 17:00 | 124 | 19:30
Ashuganj | 140 | 18:30 | 135 | 01:00 | Mahasthangarh | 134 | 11:00 | 129 | 00:00
Bagerhat | 130 | 15:00 | 120 | 19:30 | Maijdee | 119 | 18:30 | 107 | 01:00
Bajitpur | 132 | 17:00 | 124 | 23:00 | Manikganj | 126 | 06:00 | 117 | 15:00
Bakulia | 131 | 03:00 | 126 | 15:00 | Maniknagar | 129 | 05:00 | 122 | 13:00
Banani | 137 | 04:00 | 126 | 12:00 | Matarbari | 115 | 08:00 | 107 | 19:00
Bangabhaban | 128 | 03:00 | 123 | 12:00 | Matuail | 127 | 18:30 | 122 | 10:00
Barapukuria | 137 | 15:00 | 129 | 07:00 | Millgate | 130 | 05:00 | 122 | 10:00
Barguna | 133 | 07:00 | 128 | 23:00 | Mirpur | 128 | 18:00 | 122 | 10:00
Barishal | 132 | 07:00 | 126 | 00:00 | Mirzapur | 128 | 13:00 | 123 | 10:00
Barishal-230 | 132 | 06:00 | 126 | 00:00 | Mithapukur | 132 | 15:00 | 124 | 07:00
Baroaulia | 131 | 06:00 | 127 | 07:00 | MI_Cement | 127 | 18:00 | 122 | 11:00
Baroirhat | 123 | 18:00 | 115 | 01:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 137 | 03:00 | 120 | 15:00 | Mogbazar | 138 | 04:00 | 125 | 12:00
BashundharaCement | 126 | 04:00 | 121 | 10:00 | Mongla | 131 | 09:00 | 124 | 00:00
Beanibazar | 128 | 04:00 | 121 | 01:00 | Motijheel | 128 | 03:00 | 123 | 12:00
Benapole | 131 | 09:00 | 122 | 00:00 | Muktagacha | 134 | 13:00 | 128 | 02:00
Bhaluka | 131 | 01:00 | 123 | 10:00 | Munshiganj | 126 | 18:00 | 121 | 10:00
Bhandaria | 127 | 09:00 | 118 | 00:00 | Muradnagar | 124 | 18:30 | 117 | 23:00
Bhangura | 133 | 17:00 | 127 | 20:00 | Mymensingh | 135 | 12:00 | 117 | 00:00
Bheramara | 136 | 17:00 | 131 | 00:00 | Naogaon | 132 | 17:00 | 126 | 01:00
Bheramara(GK) | 135 | 09:00 | 131 | 00:00 | Narail | 133 | 08:00 | 124 | 19:30
Bhulta | 122 | 02:00 | 116 | 14:00 | Narinda | 129 | 05:00 | 122 | 13:00
Bog-Sherpur | 135 | 17:00 | 129 | 01:00 | Narshingdi | 134 | 18:30 | 114 | 22:00
Bogura | 136 | 08:00 | 132 | 00:00 | Natore | 134 | 17:00 | 128 | 01:00
Bogura-230 | 137 | 15:00 | 132 | 01:00 | Nawabganj | 130 | 04:00 | 123 | 12:00
Brahmanbaria | 133 | 07:00 | 127 | 12:00 | Netrakona | 127 | 15:00 | 114 | 23:00
Cantonment | 129 | 04:00 | 122 | 12:00 | New | 131 | 04:00 | 122 | 12:00
Chandina | 127 | 18:30 | 121 | 01:00 | Niamatpur | 136 | 09:00 | 129 | 00:00
Chandpur | 129 | 18:00 | 118 | 23:00 | Noapara | 133 | 15:00 | 125 | 19:30
Chandraghona | 131 | 08:00 | 129 | 00:00 | Pabna | 133 | 06:00 | 129 | 00:00
Chapai | 135 | 07:00 | 128 | 00:00 | Palashbari | 131 | 09:00 | 122 | 19:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 127 | 07:00 | 122 | 10:00 | Panchagarh | 137 | 19:00 | 124 | 03:00
Chauddagram | 123 | 18:30 | 115 | 21:00 | Patuakhali | 133 | 17:00 | 130 | 01:00
Chhatak | 126 | 06:00 | 119 | 00:00 | Payra | 135 | 06:00 | 132 | 00:00
Chowmuhani | 115 | 09:00 | 109 | 23:00 | PHP | 123 | 18:30 | 114 | 21:00
Chuadanga | 131 | 09:00 | 120 | 00:00 | Postogola | 128 | 04:00 | 124 | 10:00
Coxsbazar | 116 | 09:00 | 107 | 18:30 | Purbachal | 138 | 03:00 | 122 | 12:00
Cumilla(N) | 127 | 18:30 | 121 | 00:00 | Purbasadipur | 131 | 14:00 | 125 | 07:00
Cumilla(S) | 133 | 05:00 | 119 | 15:00 | Rahanpur | 137 | 09:00 | 130 | 00:00
Daganbhuiyan | 120 | 18:00 | 110 | 21:00 | Rahanpur-400 | 137 | 09:00 | 131 | 00:00
Daudkandi | 122 | 18:00 | 115 | 00:00 | Rahim | 126 | 03:00 | 122 | 11:00
Dhaka | 138 | 04:00 | 126 | 12:00 | Rajbari | 131 | 08:00 | 125 | 00:00
Dhamrai | 129 | 04:00 | 122 | 10:00 | Rajendrapur | 132 | 18:30 | 122 | 12:00
Dhanmondi | 139 | 05:00 | 125 | 12:00 | Rajshahi | 133 | 17:00 | 128 | 00:00
Dohazari | 125 | 06:00 | 120 | 19:00 | Rajshahi-230 | 133 | 17:00 | 127 | 00:00
Faridpur | 132 | 09:00 | 127 | 00:00 | Ramganj | 118 | 18:30 | 110 | 00:00
Fatullah | 128 | 05:00 | 123 | 10:00 | Rampur | 130 | 00:00 | 125 | 12:00
Fenchuganj | 134 | 09:00 | 130 | 01:00 | Rampura | 138 | 06:00 | 125 | 15:00
Feni | 125 | 18:00 | 113 | 00:00 | Rangamati | 130 | 05:00 | 127 | 15:00
Ghatail | 130 | 14:00 | 121 | 01:00 | Rangpur | 132 | 15:00 | 123 | 08:00
Ghorashal | 140 | 17:00 | 130 | 13:00 | Ruppur | 136 | 08:00 | 131 | 00:00
Goalpara | 136 | 08:00 | 126 | 01:00 | Saidpur | 132 | 14:00 | 125 | 07:00
Gollamari | 135 | 08:00 | 127 | 19:30 | Satkhira | 132 | 15:00 | 121 | 19:30
Gopalganj | 133 | 08:00 | 127 | 00:00 | Satmasjid | 129 | 04:00 | 122 | 13:00
Gopalganj-400 | 135 | 18:30 | 130 | 00:00 | Savar | 130 | 19:00 | 122 | 10:00
Gulshan | 137 | 05:00 | 126 | 12:00 | SevenRings | 137 | 06:00 | 128 | 12:00
Halishahar | 130 | 00:00 | 125 | 12:00 | ShahCement | 128 | 19:30 | 122 | 10:00
Haripur | 127 | 18:00 | 122 | 11:00 | Shahjadpur | 137 | 03:00 | 132 | 21:00
HaripurSBU | 127 | 03:00 | 123 | 12:00 | Shahjibazar | 133 | 08:00 | 126 | 23:00
Hasnabad | 129 | 04:00 | 123 | 13:00 | Shahmirpur | 131 | 01:00 | 128 | 12:00
Hathazari | 132 | 01:00 | 130 | 00:00 | Shariatpur | 132 | 08:00 | 126 | 00:00
Ishurdi | 136 | 09:00 | 132 | 00:00 | Sherpur | 136 | 14:00 | 124 | 01:00
Jaldhaka | 131 | 15:00 | 123 | 07:00 | Shikalbaha | 124 | 00:00 | 117 | 12:00
Jamalpur | 139 | 13:00 | 128 | 01:00 | Shikalbaha-230 | 131 | 06:00 | 128 | 12:00
Jashore | 130 | 17:00 | 121 | 19:30 | Shitalakhya | 127 | 18:00 | 122 | 11:00
Jhenaidah | 134 | 17:00 | 122 | 00:00 | Sholosohor | 129 | 10:00 | 127 | 15:00
Jhenaidah-230 | 134 | 09:00 | 126 | 19:30 | Shyampur | 127 | 02:00 | 123 | 10:00
Joydebpur | 135 | 17:00 | 124 | 01:00 | Shyampur-230 | 128 | 18:30 | 123 | 10:00
Joypurhat | 131 | 17:00 | 123 | 01:00 | Siddhirganj | 127 | 03:00 | 123 | 10:00
Juldah | 130 | 00:00 | 128 | 09:00 | Sirajganj | 133 | 07:00 | 127 | 19:30
Kabirpur | 129 | 19:30 | 118 | 12:00 | Sonargaon | 126 | 18:00 | 119 | 10:00
Kachua | 126 | 18:30 | 116 | 23:00 | Sreemongol | 131 | 07:00 | 126 | 00:00
Kaliakoir | 131 | 05:00 | 125 | 10:00 | Sreepur | 133 | 17:00 | 126 | 10:00
Kallyanpur | 129 | 18:00 | 124 | 09:00 | Srinagar | 130 | 05:00 | 124 | 12:00
Kalurghat | 130 | 05:00 | 128 | 07:00 | SSM | 132 | 00:00 | 130 | 04:00
Kamrangirchar | 131 | 06:00 | 123 | 12:00 | Sunamganj | 124 | 07:00 | 117 | 00:00
Kaptai | 133 | 4:00 | 131 | 16:00 | Sylhet | 128 | 05:00 | 123 | 00:00
Kasba | 123 | 18:00 | 117 | 01:00 | Sylhet-132 | 128 | 06:00 | 125 | 00:00
Kazla | 128 | 05:00 | 122 | 13:00 | Tangail | 128 | 14:00 | 120 | 01:00
Keranigonj | 130 | 04:00 | 124 | 12:00 | Taraganj | 131 | 14:00 | 125 | 07:00
Khagrachori | 129 | 06:00 | 126 | 15:00 | Thakurgaon | 136 | 19:00 | 121 | 03:00
Khulna | 133 | 15:00 | 125 | 00:00 | TK | 130 | 01:00 | 128 | 11:00
Khulna(S) | 135 | 08:00 | 127 | 19:30 | Tongi | 132 | 04:00 | 124 | 11:00
Khulshi | 128 | 02:00 | 124 | 15:00 | Ullahpara | 133 | 05:00 | 129 | 01:00
Kishoreganj | 131 | 17:00 | 120 | 00:00 | Ullon | 137 | 04:00 | 125 | 12:00
Kodda | 132 | 18:30 | 120 | 10:00 | Uttara | 128 | 05:00 | 123 | 09:00
KSRM | 131 | 03:00 | 126 | 15:00 | UttaraNew | 128 | 00:00 | 122 | 10:00
Kulaura | 133 | 08:00 | 129 | 23:00 | Zigatola | 130 | 05:00 | 124 | 11:00
Kurigram | 133 | 15:00 | 122 | 19:30
Kushtia | 133 | 18:00 | 127 | 00:00
Laksam | N/A | N/A | N/A | N/A
Lakshmipur | 120 | 18:30 | 108 | 00:00
Lalbag | 131 | 07:00 | 124 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division