## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 17-07-2025 | [28 empty] | Date: | 17-07-2025 | [28 empty] | Date: | 17-07-2025 | [28 empty] | Date: | 17-07-2025 | [28 empty] | Date: | 17-07-2025 | [11 empty] | Date: | 17-07-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [11 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 44 | 35 | 51 | 16 | 0 | 0 | 35 | 151 | 50 | 450 | 296 | 0 | 0 | 0 | 335 | 202 | 0 | 0 | 90 | 23 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 39 | 0 | 36 | 50 | 0 | 210 | 0 | 30 | 690 | 0 | 0 | 26 | 8 | 0 | 219 | 0 | 0 | 0 | 1125 | 0 | 51 | 0 | 8 | 0 | 354 | 340 | 48 | 197 | 17 | 99 | 35 | 174 | 10 | 19 | 98 | 34 | 52.2 | 0 | 38 | 0 | 320 | 364 | 0 | 50 | 149 | 8 | 0 | 84 | 30 | 0 | 18 | 172 | 17 | 85 | 192 | 33 | 0 | 0 | 10 | 8007.2 | 892 | 262 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 898 | 17 | 1168.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 198 | 0 | 352 | 0 | 0 | 157 | 50 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 0 | 220 | 0 | 488 | 1200 | 0 | 6604.05 | 14611.25 | 98.93
01:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 35 | 51 | 16 | 0 | 0 | 0 | 54 | 26 | 450 | 297 | 0 | 0 | 0 | 335 | 200 | 0 | 0 | 90 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 18 | 0 | 36 | 50 | 0 | 210 | 0 | 22 | 660 | 0 | 0 | 26 | 8 | 0 | 219 | 0 | 0 | 0 | 1140 | 0 | 51 | 0 | 8 | 0 | 354 | 340 | 48 | 198 | 17 | 102 | 35 | 177 | 8 | 19 | 98 | 32 | 52.2 | 0 | 38 | 0 | 320 | 332 | 0 | 50 | 137 | 8 | 0 | 84 | 30 | 0 | 18 | 173 | 17 | 85 | 192 | 33 | 0 | 0 | 12 | 7654.2 | 892 | 261 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 931 | 0 | 1168.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 199 | 0 | 355 | 0 | 0 | 154 | 51 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0.19 | 0 | 173 | 0 | 220 | 0 | 487 | 1120 | 0 | 6457.24 | 14111.44 | 98.92
02:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 35 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 293 | 0 | 0 | 0 | 335 | 130 | 0 | 0 | 90 | 24 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 36 | 50 | 0 | 210 | 0 | 22 | 670 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1135 | 0 | 51 | 0 | 8 | 0 | 354 | 340 | 48 | 195 | 17 | 94 | 35 | 181 | 0 | 19 | 97 | 30 | 52.2 | 0 | 38 | 0 | 320 | 310 | 0 | 50 | 133 | 8 | 0 | 84 | 30 | 0 | 18 | 173 | 17 | 65 | 192 | 46 | 0 | 0 | 9 | 7380.2 | 902 | 261 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 862 | 0 | 1148.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 199 | 0 | 349 | 0 | 0 | 158 | 50 | 50 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 220 | 0 | 487 | 1105 | 0 | 6313.13 | 13693.33 | 98.92
03:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 35 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 298 | 0 | 0 | 0 | 335 | 133 | 0 | 0 | 90 | 24.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 12 | 50 | 0 | 209 | 0 | 22 | 697 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1050 | 0 | 51 | 0 | 8 | 0 | 354 | 340 | 48 | 200 | 17 | 86 | 40 | 181 | 0 | 19 | 97 | 28 | 52.2 | 0 | 38 | 0 | 320 | 330 | 0 | 50 | 132 | 8 | 0 | 84 | 30 | 0 | 18 | 173 | 17 | 45 | 192 | 46 | 0 | 0 | 12 | 7253.7 | 903 | 261 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 778 | 0 | 1118.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 200 | 0 | 361 | 0 | 0 | 159 | 50 | 35 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 220 | 0 | 487 | 1080 | 0 | 6156.13 | 13409.83 | 98.92
04:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 35 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 295 | 0 | 0 | 0 | 332 | 133 | 0 | 0 | 52 | 24.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 12 | 24 | 0 | 208 | 0 | 22 | 681 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 960 | 0 | 51 | 0 | 8 | 0 | 354 | 340 | 48 | 196 | 17 | 91 | 45 | 181 | 0 | 19 | 98 | 28 | 52.2 | 0 | 32 | 0 | 320 | 331 | 0 | 50 | 139 | 8 | 0 | 84 | 30 | 0 | 18 | 173 | 17 | 45 | 163 | 46 | 0 | 0 | 12 | 7056.7 | 902 | 264 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 807 | 0 | 1051.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 201 | 0 | 351 | 0 | 0 | 160 | 50 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 220 | 0 | 487 | 1042 | 0 | 6036.22 | 13092.92 | 98.92
05:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 293 | 0 | 0 | 0 | 333 | 133 | 0 | 0 | 52 | 24.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 12 | 24 | 0 | 208 | 0 | 27 | 675 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 835 | 0 | 51 | 0 | 8 | 0 | 354 | 335 | 48 | 196 | 17 | 90 | 45 | 182 | 0 | 19 | 98 | 28 | 52.2 | 0 | 38 | 0 | 320 | 314 | 0 | 50 | 137 | 8 | 0 | 84 | 30 | 0 | 18 | 173 | 17 | 45 | 154 | 50 | 0 | 0 | 12 | 6890.7 | 902 | 267 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 819 | 0 | 907.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 201 | 0 | 353 | 0 | 0 | 159 | 47 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 220 | 0 | 487 | 1041 | 0 | 5885.16 | 12775.86 | 98.91
06:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 297 | 0 | 0 | 0 | 332 | 133 | 0 | 1 | 17 | 24.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 0.24 | 208 | 0 | 27 | 679 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 840 | 1 | 5 | 0 | 8 | 0 | 354 | 340 | 48 | 196 | 17 | 88 | 45 | 180 | 0 | 19 | 98 | 26 | 52.2 | 2 | 38 | 0 | 320 | 326 | 0 | 50 | 134 | 8 | 0 | 84 | 30 | 0 | 18 | 173 | 17 | 45 | 142 | 50 | 0 | 0 | 12 | 6755.94 | 902 | 270 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2.45 | 804 | 0 | 864.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0.83 | 0 | 0 | 200 | 0 | 201 | 0 | 353 | 0 | 0.07 | 156 | 48 | 0 | 1 | 49 | 0 | 0 | 0.2 | 4 | 0.1 | 0 | 172 | 0 | 220 | 0 | 487 | 799 | 0 | 5575.33 | 12331.27 | 98.91
07:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 35 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 304 | 0 | 0 | 0 | 330 | 133 | 0 | 2 | 0 | 23 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 1.26 | 207 | 0 | 20 | 696 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 850 | 2 | 5 | 0 | 8 | 0 | 349 | 340 | 48 | 202 | 17 | 91 | 40 | 181 | 5 | 19 | 98 | 24 | 16 | 11 | 0 | 0 | 320 | 333 | 0 | 50 | 140 | 8 | 0 | 84 | 30 | 0 | 18 | 174 | 17 | 52 | 142 | 50 | 0 | 0 | 12 | 6605.26 | 902 | 273 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14.21 | 825 | 0 | 878.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 3.48 | 0 | 0 | 200 | 0 | 150 | 0 | 370 | 0 | 0.28 | 157 | 49 | 0 | 3 | 49 | 0 | 0 | 1.2 | 34 | 0.2 | 0 | 173 | 0 | 220 | 0 | 488 | 795 | 0 | 5631.42 | 12236.68 | 98.91
08:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 35 | 68 | 0 | 0 | 0 | 1 | 0 | 0 | 400 | 301 | 0 | 0 | 0 | 300 | 132 | 0 | 4 | 0 | 23 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 1.69 | 207 | 0 | 2 | 695 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 853 | 5 | 5 | 0 | 8 | 0 | 352 | 335 | 48 | 200 | 17 | 91 | 35 | 182 | 10 | 19 | 80 | 24 | 16 | 37 | 0 | 0 | 320 | 331 | 0 | 50 | 136 | 8 | 0 | 82 | 30 | 0 | 18 | 172 | 17 | 85 | 85 | 45 | 0 | 0 | 12 | 6609.69 | 902 | 275 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 58.3 | 803 | 0 | 871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 4.99 | 0 | 0 | 200 | 0 | 150 | 0 | 358 | 0 | 0.31 | 154 | 49 | 0 | 12 | 67 | 0 | 0 | 2.6 | 32 | 0.11 | 0 | 173 | 0 | 220 | 0 | 488 | 795 | 0 | 5662.31 | 12272 | 98.91
09:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 35 | 68 | 0 | 0 | 0 | 19 | 0 | 6 | 400 | 307 | 0 | 0 | 0 | 280 | 201 | 0 | 4 | 0 | 22 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 48 | 1.41 | 210 | 0 | 2 | 718 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 854 | 6 | 5 | 0 | 8 | 0 | 351 | 340 | 48 | 206 | 17 | 93 | 35 | 180 | 8 | 19 | 70 | 24 | 16 | 30 | 0 | 0 | 320 | 336 | 0 | 50 | 156 | 8 | 0 | 79 | 30 | 0 | 18 | 172 | 17 | 85 | 65 | 45 | 0 | 0.54 | 12 | 6752.95 | 891 | 280 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 50.62 | 847 | 0 | 876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 2.64 | 0 | 0 | 200 | 0 | 150 | 0 | 379 | 0 | 0.23 | 158 | 50 | 0 | 13 | 70 | 0 | 0 | 1.4 | 80 | 0.2 | 0 | 174 | 0 | 220 | 0 | 488 | 800 | 0 | 5795.09 | 12548.04 | 98.9
10:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 35 | 68 | 0 | 15 | 0 | 35 | 13 | 16 | 400 | 305 | 0 | 0 | 0 | 332 | 200 | 0 | 7 | 0 | 22 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 50 | 1.95 | 210 | 0 | 2 | 650 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 850 | 9 | 5 | 0 | 33 | 0 | 355 | 340 | 49 | 204 | 19 | 92 | 35 | 181 | 9 | 19 | 70 | 24 | 16 | 45 | 0 | 0 | 320 | 333 | 0 | 50 | 159 | 8 | 0 | 79 | 30 | 0 | 18 | 172 | 17 | 57 | 65 | 31 | 0 | 3.12 | 12 | 6800.07 | 891 | 273 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 73 | 1022 | 0 | 876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 1.42 | 0 | 0 | 205 | 0 | 200 | 0 | 374 | 0 | 0.24 | 155 | 49 | 0 | 29 | 70 | 0 | 0 | 3.9 | 60 | 0.21 | 0 | 173 | 0 | 220 | 0 | 487 | 800 | 0 | 6043.77 | 12843.84 | 98.9
11:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 4 | 35 | 70 | 0 | 40 | 0 | 35 | 39 | 16 | 420 | 289 | 0 | 0 | 0 | 335 | 201 | 0 | 12 | 0 | 22 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 50 | 2.89 | 210 | 0 | 4 | 688 | 0 | 0 | 1 | 0 | 0 | 218 | 0 | 0 | 0 | 854 | 13 | 15 | 0 | 61 | 0 | 356 | 340 | 46 | 198 | 18 | 97 | 40 | 180 | 9 | 19 | 70 | 26 | 16 | 55 | 0 | 0 | 320 | 330 | 0 | 50 | 157 | 7 | 0 | 79 | 30 | 0 | 18 | 172 | 17 | 65 | 65 | 33 | 0 | 14.73 | 12 | 7106.62 | 891 | 273 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 43 | 1153 | 0 | 874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 5.35 | 0 | 0 | 202 | 0 | 209 | 0 | 353 | 0 | 0.7 | 157 | 49 | 0 | 29 | 70 | 0 | 0 | 3.9 | 42 | 0.23 | 0 | 174 | 0 | 220 | 0 | 485 | 800 | 0 | 6107.18 | 13213.8 | 98.9
12:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 548 | 16 | 35 | 53 | 15 | 70 | 0 | 35 | 80 | 16 | 420 | 302 | 0 | 0 | 0 | 335 | 200 | 0 | 9 | 0 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 50 | 3.13 | 210 | 0 | 2 | 670 | 0 | 0 | 18 | 0 | 0 | 218 | 0 | 0 | 0 | 900 | 5 | 43 | 0 | 92 | 0 | 354 | 340 | 45 | 197 | 18 | 93 | 35 | 181 | 9 | 19 | 70 | 26 | 16 | 11 | 0 | 0 | 320 | 380 | 0 | 50 | 159 | 7 | 0 | 81 | 30 | 0 | 18 | 172 | 17 | 65 | 65 | 30 | 1 | 21.56 | 12 | 7340.69 | 891 | 268 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 45 | 1224 | 0 | 987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 18.17 | 0 | 0 | 205 | 0 | 208 | 0 | 414 | 0 | 1.8 | 158 | 49 | 35 | 30 | 69 | 0 | 0 | 7.7 | 9 | 0.19 | 0 | 173 | 0 | 220 | 0 | 485 | 800 | 0 | 6371.86 | 13712.55 | 98.89
13:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 26 | 35 | 50 | 15 | 95 | 0 | 35 | 96 | 22 | 420 | 304 | 0 | 0 | 0 | 335 | 199 | 0 | 12 | 17 | 22 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 27 | 25 | 1.96 | 211 | 0 | 10 | 675 | 0 | 0 | 30 | 0 | 0 | 220 | 0 | 0 | 0 | 945 | 13 | 43 | 8 | 108 | 0 | 356 | 340 | 45 | 196 | 18 | 86 | 30 | 181 | 9 | 17 | 63 | 28 | 16 | 76 | 20 | 0 | 320 | 371 | 0 | 50 | 162 | 7 | 0 | 81 | 30 | 0 | 18 | 172 | 17 | 75 | 65 | 27 | 1 | 31.37 | 12 | 7549.33 | 900 | 260 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 8 | 1197 | 0 | 1136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 41.43 | 0 | 0 | 208 | 0 | 170 | 0 | 349 | 0 | 3.8 | 156 | 49 | 35 | 9 | 70 | 0 | 0 | 6.1 | 25 | 0.29 | 0 | 173 | 0 | 200 | 0 | 487 | 788 | 0 | 6340.62 | 13889.95 | 98.89
14:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 46 | 35 | 50 | 15 | 95 | 0 | 35 | 115 | 16 | 420 | 304 | 0 | 0 | 0 | 331 | 199 | 0 | 9 | 35 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 29 | 25 | 1.81 | 211 | 0 | 5 | 670 | 0 | 0 | 40 | 0 | 0 | 219 | 0 | 0 | 0 | 947 | 12 | 43 | 24 | 108 | 0 | 355 | 340 | 46 | 196 | 18 | 86 | 30 | 181 | 9 | 17 | 64 | 28 | 16 | 24 | 26 | 0 | 320 | 374 | 0 | 50 | 138 | 7 | 0 | 81 | 30 | 0 | 18 | 172 | 17 | 75 | 65 | 27 | 1 | 49.62 | 5 | 7532.43 | 901 | 256 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 16 | 952 | 0 | 1112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 30.15 | 0 | 0 | 205 | 0 | 170 | 0 | 347 | 0 | 3.58 | 157 | 47 | 35 | 10 | 113 | 0 | 0 | 7.8 | 85 | 0.21 | 0 | 173 | 0 | 200 | 0 | 487 | 800 | 0 | 6184.74 | 13717.17 | 98.89
15:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 48 | 35 | 50 | 16 | 95 | 0 | 35 | 119 | 16 | 420 | 310 | 0 | 0 | 0 | 331 | 196 | 0 | 9 | 35 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 30 | 25 | 3.35 | 211 | 0 | 3 | 703 | 0 | 0 | 40 | 0 | 0 | 215 | 0 | 0 | 0 | 961 | 8 | 51 | 24 | 60 | 0 | 348 | 340 | 48 | 182 | 18 | 88 | 40 | 180 | 9 | 13 | 68 | 28 | 16 | 19 | 31 | 0 | 320 | 390 | 0 | 60 | 141 | 7 | 0 | 79 | 30 | 0 | 18 | 172 | 17 | 75 | 65 | 28 | 2 | 35.36 | 10 | 7577.71 | 900 | 253 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 26 | 917 | 0 | 1136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 28.98 | 0 | 0 | 205 | 0 | 170 | 0 | 394 | 0 | 2.45 | 157 | 47 | 35 | 12 | 113 | 0 | 0 | 5.6 | 120 | 0.18 | 0 | 177 | 0 | 200 | 0 | 486 | 800 | 0 | 6282.21 | 13859.92 | 98.88
16:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 504 | 51 | 35 | 50 | 16 | 95 | 0 | 35 | 123 | 16 | 420 | 302 | 0 | 0 | 0 | 333 | 197 | 0 | 9 | 35 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 32 | 25 | 2.86 | 211 | 0 | 7 | 692 | 0 | 0 | 40 | 0 | 0 | 216 | 0 | 0 | 0 | 950 | 2 | 51 | 24 | 8 | 0 | 354 | 340 | 48 | 199 | 18 | 94 | 40 | 180 | 9 | 20 | 62 | 26 | 16 | 12 | 24 | 0 | 320 | 385 | 0 | 60 | 157 | 7 | 0 | 83 | 30 | 0 | 18 | 171 | 17 | 75 | 65 | 32 | 1 | 25.86 | 12 | 7522.72 | 900 | 252 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 30 | 912 | 0 | 1115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 23.92 | 0 | 0 | 204 | 0 | 170 | 0 | 350 | 0 | 2.91 | 159 | 48 | 35 | 17 | 113 | 0 | 0 | 4.6 | 87 | 0.19 | 0 | 173 | 0 | 220 | 0 | 486 | 800 | 0 | 6212.62 | 13735.34 | 98.88
17:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 46 | 35 | 50 | 16 | 95 | 0 | 35 | 72 | 16 | 420 | 297 | 0 | 0 | 0 | 333 | 198 | 0 | 5 | 35 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 25 | 1.14 | 211 | 0 | 8 | 680 | 0 | 0 | 40 | 0 | 0 | 215 | 0 | 0 | 0 | 940 | 2 | 51 | 10 | 8 | 0 | 352 | 340 | 48 | 211 | 18 | 87 | 40 | 180 | 9 | 20 | 58 | 26 | 16 | 6 | 32 | 0 | 320 | 367 | 0 | 60 | 152 | 7 | 0 | 83 | 30 | 0 | 18 | 171 | 17 | 75 | 65 | 32 | 0 | 16.37 | 12 | 7378.51 | 890 | 247 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 28 | 863 | 0 | 1021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 11.65 | 0 | 0 | 206 | 0 | 170 | 0 | 339 | 0 | 1.02 | 157 | 46 | 35 | 4 | 113 | 0 | 0 | 2.1 | 58 | 0.14 | 0 | 168 | 0 | 220 | 0 | 485 | 800 | 0 | 5937.91 | 13316.42 | 98.88
18:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 45 | 35 | 50 | 16 | 95 | 0 | 35 | 64 | 16 | 350 | 289 | 0 | 0 | 0 | 332 | 134 | 0 | 2 | 50 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 25 | 0.12 | 211 | 0 | 10 | 693 | 0 | 0 | 40 | 0 | 0 | 216 | 0 | 0 | 0 | 840 | 1 | 51 | 10 | 8 | 0 | 300 | 300 | 49 | 198 | 18 | 84 | 35 | 189 | 9 | 20 | 62 | 26 | 16 | 4 | 38 | 0 | 320 | 358 | 0 | 60 | 143 | 7 | 0 | 85 | 30 | 0 | 18 | 171 | 17 | 75 | 65 | 32 | 0 | 3.25 | 12 | 7043.37 | 900 | 248 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 8 | 789 | 0 | 1029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 1.73 | 0 | 0 | 160 | 0 | 150 | 0 | 348 | 0 | 0.14 | 158 | 47 | 35 | 3 | 113 | 0 | 0 | 0.7 | 12 | 0 | 0 | 173 | 0 | 220 | 0 | 485 | 780 | 0 | 5707.57 | 12750.94 | 98.87
19:00 | 0 | 73 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 47 | 35 | 85 | 80 | 95 | 0 | 35 | 69 | 16 | 350 | 304 | 0 | 0 | 17 | 325 | 197 | 0 | 0 | 108 | 22 | 22 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 65 | 32 | 0 | 36 | 25 | 0 | 211 | 4 | 20 | 725 | 0 | 0 | 40 | 0 | 8 | 215 | 0 | 0 | 0 | 1050 | 0 | 51 | 38 | 8 | 0 | 347 | 330 | 50 | 213 | 18 | 96 | 35 | 199 | 8 | 20 | 78 | 28 | 16 | 0 | 38 | 0 | 320 | 387 | 0 | 60 | 138 | 8 | 0 | 85 | 30 | 0 | 18 | 171 | 17 | 92 | 87 | 32 | 0 | 0 | 12 | 7889 | 900 | 248 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 808 | 3 | 1104 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 163 | 0 | 153 | 0 | 390 | 0 | 0 | 158 | 48 | 90 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 220 | 0 | 487 | 770 | 0 | 5979 | 13868 | 98.87
19:30 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 46 | 0 | 105 | 80 | 95 | 0 | 35 | 67 | 16 | 450 | 310 | 0 | 0 | 17 | 332 | 198 | 0 | 0 | 108 | 23 | 21 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 65 | 40 | 0 | 36 | 25 | 0 | 211 | 16 | 18 | 730 | 0 | 0 | 40 | 0 | 15 | 218 | 0 | 0 | 0 | 1050 | 0 | 51 | 100 | 8 | 0 | 348 | 340 | 50 | 208 | 18 | 90 | 35 | 199 | 9 | 19 | 97 | 28 | 45 | 0 | 38 | 0 | 320 | 390 | 0 | 60 | 148 | 8 | 0 | 85 | 30 | 0 | 18 | 171 | 17 | 100 | 132 | 33 | 0 | 0 | 12 | 8227 | 899 | 247 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 965 | 17 | 1203 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 184 | 0 | 183 | 0 | 414 | 0 | 0 | 157 | 49 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 0 | 220 | 0 | 499 | 970 | 0 | 6600 | 14827
20:00 | 0 | 102 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 509 | 50 | 0 | 105 | 80 | 95 | 0 | 47 | 70 | 16 | 450 | 299 | 0 | 0 | 17 | 335 | 201 | 0 | 0 | 108 | 23 | 18 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 65 | 40 | 0 | 36 | 25 | 0 | 220 | 15 | 22 | 735 | 0 | 0 | 40 | 0 | 16 | 217 | 0 | 0 | 0 | 1034 | 0 | 51 | 100 | 8 | 0 | 356 | 340 | 50 | 190 | 18 | 98 | 35 | 198 | 9 | 17 | 97 | 28 | 52.2 | 0 | 38 | 0 | 320 | 349 | 0 | 60 | 155 | 8 | 0 | 85 | 30 | 0 | 18 | 171 | 17 | 102 | 132 | 33 | 0 | 0 | 12 | 8207.2 | 900 | 247 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1027 | 19 | 1211 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 182 | 0 | 187 | 0 | 385 | 0 | 0 | 156 | 48 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 0 | 220 | 0 | 521 | 1040 | 0 | 6754 | 14961.2 | 98.87
21:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 509 | 47 | 0 | 101 | 80 | 0 | 0 | 27 | 35 | 16 | 450 | 314 | 0 | 0 | 0 | 332 | 198 | 0 | 0 | 108 | 23 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 65 | 40 | 0 | 36 | 25 | 0 | 210 | 14 | 22 | 793 | 0 | 0 | 40 | 0 | 31 | 217 | 0 | 0 | 0 | 1097 | 0 | 51 | 50 | 8 | 0 | 350 | 340 | 50 | 208 | 18 | 90 | 35 | 199 | 9 | 19 | 97 | 28 | 52.2 | 0 | 38 | 0 | 320 | 349 | 0 | 60 | 156 | 8 | 0 | 85 | 30 | 0 | 18 | 171 | 17 | 102 | 132 | 32 | 0 | 0 | 12 | 8089.2 | 894 | 247 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1099 | 51 | 1226 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 190 | 0 | 190 | 0 | 414 | 0 | 0 | 158 | 49 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 220 | 0 | 437 | 1110 | 0 | 6903 | 14992.2 | 98.86
22:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 46 | 0 | 80 | 64 | 0 | 0 | 17 | 31 | 16 | 450 | 302 | 0 | 0 | 0 | 335 | 200 | 0 | 0 | 108 | 23 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 65 | 40 | 0 | 36 | 25 | 0 | 210 | 14 | 25 | 744 | 0 | 0 | 40 | 0 | 31 | 217 | 0 | 0 | 0 | 1090 | 0 | 51 | 50 | 8 | 0 | 356 | 340 | 50 | 196 | 18 | 91 | 35 | 199 | 9 | 19 | 97 | 28 | 52.2 | 0 | 38 | 0 | 320 | 369 | 0 | 60 | 153 | 8 | 0 | 84 | 30 | 0 | 18 | 172 | 17 | 101 | 132 | 33 | 0 | 0 | 12 | 7979.2 | 891 | 248 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1135 | 34 | 1214.4 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 190 | 0 | 190 | 0 | 400 | 0 | 0 | 156 | 48 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 220 | 0 | 441 | 1113 | 0 | 6888.4 | 14867.6 | 98.86
23:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 45 | 0 | 70 | 64 | 0 | 0 | 17 | 30 | 0 | 450 | 302 | 0 | 0 | 0 | 335 | 201 | 0 | 0 | 108 | 23 | 12 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 50 | 39 | 0 | 36 | 25 | 0 | 210 | 15 | 29 | 745 | 0 | 0 | 40 | 0 | 30 | 222 | 0 | 0 | 0 | 1090 | 0 | 51 | 50 | 8 | 0 | 356 | 340 | 50 | 196 | 18 | 90 | 0 | 200 | 0 | 19 | 98 | 30 | 52.2 | 0 | 38 | 0 | 320 | 373 | 0 | 60 | 152 | 8 | 0 | 84 | 30 | 0 | 18 | 172 | 17 | 102 | 132 | 33 | 0 | 0 | 12 | 7906.2 | 891 | 242 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1139 | 34 | 1215.57 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 22 | 0 | 12 | 0 | 190 | 0 | 190 | 0 | 407 | 0 | 0 | 158 | 48 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 0 | 220 | 0 | 441 | 1111 | 0 | 6906.57 | 14812.77 | 98.86
Total KWH | 0 | 1300800 | 606720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11507520 | 572760 | 688680 | 1414368 | 495840 | 846818 | 0 | 512610 | 1139040 | 265920 | 10108000 | 7273018 | 0 | 0 | 34050 | 7943367 | 4400000 | 0 | 86132 | 1220400 | 501600 | 461520 | 0 | 0 | 0 | 95345 | 0 | 0 | 16800 | 679639 | 248928 | 0 | 690240 | 772800 | 23844 | 5042569 | 85309 | 382560 | 16916363.64 | 0 | 0 | 480480 | 12335.4 | 153054 | 5119913 | 0 | 0 | 0 | 23187271 | 83295 | 968544 | 508509 | 602182 | 0 | 8733000 | 8178000 | 1161600 | 4866000 | 440712 | 2201280 | 835650 | 4464960 | 161280 | 423310 | 1991580 | 653760 | 804677 | 320327 | 628976 | 0 | 7664600 | 8876000 | 0 | 1258200 | 3534055 | 183024 | 0 | 1991040 | 719520 | 0 | 432000 | 4610770 | 426960 | 1788000 | 2769600 | 826560 | 7450 | 200810 | 284160 | 178887005.04 | 21715636 | 6374016 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 411840 | 22814540 | 195840 | 25309091 | 0 | 0 | 0 | 0 | 0 | 330000 | 0 | 0 | 0 | 413230 | 123028 | 199496 | 29273 | 0 | 4961664 | 0 | 4665845 | 0 | 8957454 | 0 | 18840 | 3853000 | 1134109 | 1006536 | 166519 | 2274240 | 0 | 0 | 47451.6 | 690480 | 2023 | 0 | 4713000 | 0 | 5426120 | 0 | 11598840 | 22750545.45 | 0 | 151094657.05 | 329981662.09

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 18-07-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-07-2025 | during | 18-07-2025 | during | 18-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 0 | 0 | 0 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 302 | 314 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 200 | 198 | 208.13 | 208.13 | 202 | 202 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 332 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 16 | 47 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 15 | 80 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 27 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21 | 23 | 33 | 33 | 25 | 25 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 15 | 22 | 22 | 21 | 21 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 42 | 42 | Engine Problem
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 70 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 53 | 101 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 70 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 16 | 16 | 104 | 104 | 50 | 50 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 80 | 35 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 9 | 0 | 29 | 0 | 29 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 0 | 55 | 55 | 35 | 35 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 548 | 509 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 108 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2251 | 2350 | 4722.65 | 4787.65 | 3305.33 | 3370.33
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 5 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 40 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 210 | 210 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 218 | 217 | 213 | 213 | 221 | 221 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 31 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 40 | 56 | 70 | 80 | 80 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 65 | 65 | 65 | 68 | 68 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 36 | 36 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 22 | 35 | 40 | 35 | 40 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.13 | 0 | 1.9 | 0 | 1.9 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 14 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 25 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 900 | 1097 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 1 | 0 | 1 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 670 | 793 | 790 | 790 | 790 | 790 | FGMO
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 2112.13 | 2605 | 3834.62 | 3840.72 | 3869.62 | 3861.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 197 | 208 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 354 | 350 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 340 | 340 | 340 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 18 | 18 | 46.7 | 46.7 | 19 | 19 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 45 | 50 | 55 | 55 | 49 | 49 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 92 | 8 | 195 | 195 | 111 | 111 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 50 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 38 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 35 | 35 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 181 | 199 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 26 | 28 | 0 | 0 | 0 | 0 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 70 | 97 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 9 | 113 | 113 | 18 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 93 | 90 | 115 | 115 | 115 | 115 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 11 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1549 | 1642.2 | 2295.75 | 2240.75 | 1949.55 | 1914.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-07-2025 | during | 18-07-2025 | during | 18-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 30 | 32 | 157.5 | 157.5 | 50 | 50 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.4 | 0 | 1.4 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 65 | 132 | 200 | 200 | 186 | 186 | Engine Problem
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 65 | 102 | 115 | 115 | 105 | 105 | Engine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 21.56 | 0 | 35 | 0 | 35 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 35 | 35 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 211.56 | 295 | 585.4 | 549 | 424.4 | 388
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 50 | 60 | 50 | 50 | 50 | 50 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 159 | 156 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 85 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 172 | 171 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 7 | 8 | 25 | 25 | 8 | 8 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | Plant Shutdown as per schedule HGPI work
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 380 | 349 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1217 | 1197 | 1235 | 1235 | 1174 | 1174
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 891 | 894 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 268 | 247 | 410 | 410 | 280 | 280 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 51 | 105 | 105 | 60 | 60 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 45 | 0 | 50 | 0 | 50 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1224 | 1099 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2466 | 2329 | 3564.2 | 3514.2 | 3387.2 | 3337.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 485 | 437 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 0 | 0 | 65 | 65 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 800 | 1110 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 173 | 280 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.19 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1678.19 | 2047 | 2097 | 2096 | 2112 | 2111
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 0 | 0 | 220 | 220 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 205 | 190 | 220 | 220 | 209 | 209 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 208 | 190 | 220 | 220 | 211 | 211 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 62 | 95 | 95 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.8 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 987 | 1226 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 18.17 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 36 | 0 | 59 | 0 | 59 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 1869.97 | 2112 | 2937.47 | 2811.87 | 3097.09 | 2971.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 49 | 49 | 50 | 50 | 50 | 50 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 158 | 158 | 150 | 150 | 155 | 155 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 69 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.7 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 95 | 115 | 115 | 95 | 95 | Engine Problem
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 20.5 | 0 | 20.5 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 9 | 0 | 125.3 | 0 | 125.3 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 357.7 | 415 | 614.4 | 462 | 599.4 | 447
System Total |  |  |  |  | 28565.2 | 27084.055 | 13712.55 | 14992.2 | 21886.49 | 21537.19 | 19918.59 | 19575.29
Forecast Scenario (18-07-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14340 |  | 0 |  | 14340
|  |  |  | 1:00 | 13950 |  | 0 |  | 13950
|  |  |  | 2:00 | 13610 |  | 0 |  | 13610
|  |  |  | 3:00 | 13100 |  | 0 |  | 13100
|  |  |  | 4:00 | 12700 |  | 0 |  | 12700
|  |  |  | 5:00 | 12300 |  | 0 |  | 12300
|  |  |  | 6:00 | 11620 |  | 0 |  | 11620
|  |  |  | 7:00 | 11620 |  | 0 |  | 11620
|  |  |  | 8:00 | 11490 |  | 0 |  | 11490
|  |  |  | 9:00 | 11480 |  | 0 |  | 11480
|  |  |  | 10:00 | 11580 |  | 0 |  | 11580
|  |  |  | 11:00 | 12030 |  | 0 |  | 12030
|  |  |  | 12:00 | 12860 |  | 0 |  | 12860
|  |  |  | 13:00 | 13630 |  | 0 |  | 13630
|  |  |  | 14:00 | 13180 |  | 0 |  | 13180
|  |  |  | 15:00 | 13280 |  | 0 |  | 13280
|  |  |  | 16:00 | 12890 |  | 0 |  | 12890
|  |  |  | 17:00 | 12370 |  | 0 |  | 12370
|  |  |  | 18:00 | 12070 |  | 0 |  | 12070
|  |  |  | 18:30 | 12700 |  | 0 |  | 12700
|  |  |  | 19:00 | 13470 |  | 0 |  | 13470
|  |  |  | 19:30 | 14600 |  | 0 |  | 14600
|  |  |  | 20:00 | 14890 |  | 0 |  | 14890
|  |  |  | 21:00 | 14800 |  | 0 |  | 14800
|  |  |  | 22:00 | 14700 |  | 0 |  | 14700
|  |  |  | 23:00 | 14600 |  | 0 |  | 14600
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 12860.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 14890.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14890.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 312.56 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:27 hrs on 18-07-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 17-07-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13712.55 | MW | 12:00 Hr. | Energy Generated |  |  | 329.9817 |  | MKWHr.
| Day Peak Demand |  |  | 13712.55 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.281 |  | MKWHr.
| Evening Peak Generation |  |  | 14992.2 | MW | 21:00 Hr. | Energy Demand |  |  | 330.2627 |  | MKWHr.
| Evening Peak Demand |  |  | 15030.2 | MW | 21:00 Hr. | Maximum Temperature |  |  | 29.5 |  | °C
| Minimum Generation of the Day |  |  | 12236.68 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 967.84 |  | MMCFD
| Maximum Generation of the Day |  |  | 14992.2 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 5.9076 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 42.195 | 0 | 9.098 | 0 | 0 | 0.086132 | 0 | 0 | 51.3792 | Gas | 134.4166 | Gas | 454962712.48
| Chattogram Zone |  |  | 5.5025 | 40.1036 | 3.2181 | 0 | 5.0426 | 0.10714 | 0 | 0.0168 | 53.9907 | Coal | 106.9677 | Coal | 615640663.4929
| Cumilla Zone |  |  | 26.209 | 0 | 10.7613 | 0 | 0 | 0.32033 | 0.65376 | 0 | 37.9443 | HFO | 32.2758 | HFO | 593534223.608
| Mymensingh Zone |  |  | 0.82656 | 0 | 5.2687 | 0 | 0 | 0.20826 | 0 | 0 | 6.3035 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 29.2692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.2692 | Hydro | 5.0426 | Hydro | 504256.9
| Khulna Zone |  |  | 6.374 | 22.8145 | 0.19584 | 0 | 0 | 0.41184 | 22.6276 | 0 | 52.4239 | Solar | 2.6717 | Solar | 43385236.106
| Barishal Zone |  |  | 5.4261 | 39.0624 | 0 | 0 | 0 | 0.002023 | 0 | 0 | 44.4905 | Import | 48.5905 | Import | 241115136.45
| Rajshahi Zone |  |  | 18.6142 | 0 | 0.45303 | 0 | 0 | 0.63157 | 25.3091 | 0 | 45.0079 | Wind | 0.0168 | Wind | 245952
| Rangpur Zone |  |  | 0 | 4.9871 | 3.2808 | 0 | 0 | 0.90445 | 0 | 0 | 9.1723
| Total |  |  | 134.4166 | 106.9677 | 32.2758 | 0 | 5.0426 | 2.6717 | 48.5905 | 0.0168 | 329.9817
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 454962712.48 |  | Hydro | 504256.9
|  |  |  | Coal | 615640663.4929 |  | Solar | 43385236.106
|  |  |  | HFO | 593534223.608 |  | Import | 241115136.45
|  |  |  | HSD | 0 |  | Wind | 245952
[5 empty] | Total: | 194,93,88,181 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.7156 | Peak Hr Flow | 894.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 43671290.99 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 25.3091 | Peak Hr Flow | 1226.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 714 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.65376 | Peak Hr Flow | 28.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 936 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 47.6785 | Peak Hr Flow | 2148.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4983
|  |  |  | Chattogram |  | 0 |  | 1526
|  |  |  | Cumilla |  | 0 |  | 1357
|  |  |  | Mymensingh |  | 0 |  | 1147
|  |  |  | Sylhet |  | 0 |  | 646
|  |  |  | Khulna |  | 0 |  | 1781
|  |  |  | Barishal |  | 0 |  | 453
|  |  |  | Rajshahi |  | 0 |  | 1526
|  |  |  | Rangpur |  | 36 |  | 1048
|  |  |  | Total |  | 36 |  | 14467
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Bibiana-II 341 MW CCPP (Summit) GT |  |  | 222 | 3 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
|  | 4 | Bibiana-II 341 MW CCPP (Summit) ST |  |  | 119
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 641 |  |  |  | Total | 476
|  |  |  | Total Unavailable Capacity |  |  |  | 1117
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:23 | Dhamrai 132/33kV S/S Transformer-2 HT is restored.
|  | 08:24 | Dhamrai 132/33kV S/S Transformer-2 LT is restored.
| 09:17 | 18:02 | Bogura 400/230kV S/S ATR-02 HT Scheduled S/D Due to ATR-02 PAINTING
| 09:17 | 18:02 | Bogura 400/230kV S/S ATR-02 LT Scheduled S/D Due to ATR-02 PAINTING
|  | 09:30 | Borhanuddin 230/33kV S/S Tr-Load LT is restored.
|  | 09:32 | Borhanuddin 230/33kV S/S Tr-Load HT is restored.
| 09:59 | 10:35 | Bakulia 132/33kV S/S T-4 (432T) HT Forced S/D Due to Oil Leakage checking.
| 11:26 | 13:12 | Barishal 230/132kV S/S ATR-1 LT Scheduled S/D Due to oil leakage checking
| 11:27 | 13:14 | Barishal 230/132kV S/S ATR-1 HT Scheduled S/D
|  | 12:36 | Mahasthangar-Palashbari 132kV Ckt-2 is restored.
|  | 13:14 | Barishal 230/132kV S/S ATR-1 HT is restored.
| 13:27 | 18:20 | Mahasthangar-Palashbari 132kV Ckt-1 Project Work S/D from Mahasthangarh 132/33kV end Due
to Red hot maintenance work. and from Palashbari 132/33kV end Due to Project work
| 13:30 | 18:20 | Mahasthangar-Palashbari 132kV Ckt-1 Project Work S/D from Palashbari 132/33kV end Due to
Project work
| 14:52 | 18:04 | Mahasthangarh 132/33kV S/S 132KVMain bus 2 Project Work S/D Due to Red hot maintenance
work.
|  | 15:24 | Madunaghat 132/33kV S/S ATR-3(725T) HT is restored.
|  | 15:25 | Madunaghat 132/33kV S/S ATR-3(725T) LT is restored.
| 15:56 | 17:02 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 LT Forced S/D Due to To fix Red Hot in | [7 empty] | 35.0MW load
|  |  | 33kv Kanaighat feeder Isolator | [7 empty] | interrup.
| 15:57 | 16:59 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 HT Forced S/D Due to To fix Red Hot in | [7 empty] | 35.0MW load
|  |  | 33kv Kanaighat feeder Isolator | [7 empty] | interrup.
| 17:11 | 19:04 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 LT Scheduled S/D
| 17:28 | 18:15 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 LT Forced S/D Due to To fix Red Hot in | [7 empty] | 30.0MW load
|  |  | 33kv Alinagor feeder Isolator | [7 empty] | interrup.
| 17:29 | 18:14 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 HT Forced S/D Due to To fix Red Hot in | [7 empty] | 30.0MW load
|  |  | 33kv Alinagor feeder Isolator | [7 empty] | interrup.
| 17:42 | 19:18 | Hasnabad 132/33kV S/S 33kv Main Bus Scheduled S/D | [7 empty] | 6.0MW load
interrup.
| 21:00 |  | Evening peak Generation is 14992 MW
| 22:25 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- GT
| 02:10 | 03:37 | Sonargaon 132/33kV S/S Tr-2 LT Forced S/D Due to 33 kv langalband feeder underground loop | [7 empty] | 50.0MW load
|  |  | out | [7 empty] | interrup.
| 02:11 | 03:36 | Sonargaon 132/33kV S/S Tr-2 HT Forced S/D Due to 33 kv langalband underground feeder loop | [7 empty] | 50.0MW load
|  |  | out | [7 empty] | interrup.
| 03:19 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- ST
| 04:01 |  | Baghabari----Ruppur 230 KV ckt-1 S/D (Schedule S/D)
| 04:30 |  | Baghabari----Ruppur 230 KV ckt-2 S/D (Schedule S/D)
| 05:18 |  | Ishurdi---Dynamin Sun [Pabna Solar 100 MW] 132 KV ckt-1 S/D (Schedule S/D)
| 05:20 |  | Ishurdi---Dynamin Sun [Pabna Solar 100 MW] 132 KV ckt-2 S/D (Schedule S/D)
| 05:29 |  | Kamrangirchar-Keraniganj 132kV Ckt Scheduled S/D from Keranigonj 230/132/33kV end Due to
Red hot maintenance
| 06:19 |  | Halishahar 132/33kV S/S Halishahar-Khulshi-Ckt.-3 Project Work S/D Due to Due to
rectification work of 132 kV Khulsi ckt-03 Bus DS-01, Bus DS-02 and replacement of
faulty LA.
| 06:20 |  | Halishahar-Julda 132kV Ckt-1 Project Work S/D from Juldah 132/33kV end Due to Halishahar
Grid s/s project work.
| 06:42 |  | Meghnaghat 230/132kV S/S Meghnaghat-ST (MPL) Scheduled S/D Due to DS heating problem
| 06:50 |  | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-2 Scheduled S/D Due to Remove Redhot
| 06:56 |  | Mirpur-Uttara 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Red hot
maintenance work Line DS
| 07:00 |  | Minimum generation 12284 MW
| 07:30 |  | Bhulta-Narsingdi 132 kV Ckt-1 Scheduled S/D from Narshingdi 132/33kV end Due to 95 no
tower jumper reconnection
| 07:30 |  | Haripur-Narsingdi 132kV Ckt-1 Scheduled S/D from Narshingdi 132/33kV end Due to 95 no
tower jumper reconnection
| 07:39 |  | Aminbazar-Meghnaghat 400kV Ckt-2 Scheduled S/D from Meghnaghat 400/230kV end Due to For
Maintenence work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 17-07-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10108000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 314 | 7273018 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 198 | 4400000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 332 | 7943367 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 47 | 572760 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 80 | 495840 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 27 | 512610 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 34050 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23 | 501600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 461520 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 606720 | Engine Problem
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | -
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 846818 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 101 | 1414368 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1300800 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 265920 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 1139040 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 86132 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 688680 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 509 | 11507520 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 1220400 | Engine Problem
Dhaka Area Total |  |  |  |  | 5939.724 | 2350 | 51379163
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 12335.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 83295 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 40 | 480480 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 210 | 5042569 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5119913 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 31 | 153054 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 40 | 248928 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 679639 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 36 | 690240 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 22 | 382560 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 23844 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 95345 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 14 | 85309 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 772800 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1097 | 23187271 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 16800 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 793 | 16916363.64 | FGMO
Chattogram Area Total |  |  |  |  | 4895.72 | 2605 | 53990746.04
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 208 | 4866000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 350 | 8733000 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 8178000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 18 | 440712 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 50 | 1161600 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 602182 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 968544 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 50 | 508509 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 38 | 628976 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 35 | 835650 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 199 | 4464960 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 28 | 653760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 804677 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 423310 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 97 | 1991580 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 161280 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 2201280 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 320327 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1642.2 | 37944347
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 32 | 826560 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 132 | 2769600 | Engine Problem
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 102 | 1788000 | Engine Problem
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 200810 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 284160 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 426960 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 295 | 6303540
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1258200 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 156 | 3534055 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 719520 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1991040 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 171 | 4610770 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 432000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 183024 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under Maintenance
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 349 | 8876000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7664600 | -
Sylhet Area Total |  |  |  |  | 2325 | 1197 | 29269209
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 894 | 21715636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 247 | 6374016 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 51 | 195840 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 411840 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1099 | 22814540 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2329 | 52423872
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 437 | 11598840 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 0 | 0 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1110 | 22750545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5426120 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 280 | 4713000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2023 | -
Barishal Area Total |  |  |  |  | 2236 | 2047 | 44490528.45
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 29273 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 190 | 4961664 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 190 | 4665845 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8957454 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 123028 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 62 | 330000 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 18840 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1226 | 25309091 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 199496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 413230 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2112 | 45007921
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 49 | 1134109 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 158 | 3853000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 2274240 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 47451.6 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 1006536 | Schedule Maintenance
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 166519 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 690480 | -
Rangpur Area Total |  |  |  |  | 950 | 415 | 9172335.6
Eastern Grid Total |  |  |  |  | 16705.895 | 8089.2 | 178887005.04
Western Grid Total |  |  |  |  | 10378.16 | 6903 | 151094657.05
National Grid Total |  |  |  |  | 27084.055 | 14992.2 | 329981662.09
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 17-07-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9660.07 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4772.1 | MW
i) Dhaka area |  |  | 4983.38 |  | MW | i) Khulna area |  |  |  | 1781 | MW
ii) Chattogram area |  |  | 1526.3 |  | MW | ii) Barishal area |  |  |  | 452.9 | MW
iii) Cumilla area |  |  | 1357.39 |  | MW | iii) Rajshahi area |  |  |  | 1526.2 | MW
iv) Mymensingh area |  |  | 1147 |  | MW | iv) Rangpur area |  |  |  | 1012 | MW
v) Sylhet area |  |  | 646 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14432.17 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 85 | 00:00 | 133 | PHP | 7 | 13:00
2 | AKSML | 171.9 | 12:00 | 68 | Ishurdi | 83 | 19:30 | 134 | Pabna | 128 | 20:00
3 | Aftabnagar | 36 | 12:00 | 69 | Jaldhaka | 84 | 19:30 | 135 | Palashbari | 118 | 20:00
4 | Agargaon | 130 | 13:00 | 70 | Jamalpur | 131 | 20:00 | 136 | Panchagarh | 65 | 19:30
5 | Agrabad | 94 | 12:00 | 71 | Jashore | 141 | 21:00 | 137 | Patuakhali | 73 | 22:00
6 | Amnura | 38 | 22:00 | 72 | Jhenaidah | 126 | 23:00 | 138 | Payra | 38 | 23:00
7 | Ashuganj | 104 | 00:00 | 73 | Joydebpur | 145 | 12:00 | 139 | Postogola | 64 | 13:00
8 | BSRM | 206 | 23:00 | 74 | Joypurhat | 62 | 22:00 | 140 | Purbachal | 20 | 00:00
9 | Bagerhat | 86 | 21:00 | 75 | Juldah | 15 | 00:00 | 141 | Purbasadipur | 137 | 22:00
10 | Bajitpur | 69 | 21:00 | 76 | KSRM | 23 | 03:00 | 142 | Rahanpur | 33 | 23:00
11 | Bakulia | 95 | 20:00 | 77 | Kabirpur | 237 | 12:00 | 143 | Rahim | 30 | 11:00
12 | Banani | 35.6 | 13:00 | 78 | Kachua | 88 | 19:30 | 144 | Rajbari | 85 | 19:30
13 | Bangabhaban | 15 | 10:00 | 79 | Kallyanpur | 105 | 23:00 | 145 | Rajendrapur | 132 | 19:30
14 | Barapukuria | 66 | 19:30 | 80 | Kalurghat | 40 | 12:00 | 146 | Rajshahi | 125 | 13:00
15 | Barguna | 24 | 00:00 | 81 | Kamrangirchar | 77 | 13:00 | 147 | Rajshahi-230 | 87 | 21:00
16 | Barishal | 112 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Ramganj | 116 | 20:00
17 | Barishal-230 | 94 | 19:30 | 83 | Kasba | 36 | 00:00 | 149 | Rampur | 42 | 00:00
18 | Baroaulia | 70 | 13:00 | 84 | Kazla | 101 | 19:30 | 150 | Rangamati | 16 | 20:00
19 | Baroirhat | 61 | 00:00 | 85 | Keranigonj | 91 | 00:00 | 151 | Rangpur | 140 | 19:00
20 | Bashundhara | 186 | 13:00 | 86 | Khagrachori | 34 | 19:00 | 152 | Ruppur | 10.4 | 14:00
21 | BashundharaCement | 6 | 13:00 | 87 | Khulna | 88 | 13:00 | 153 | SSM | 10 | 21:00
22 | Beanibazar | 84 | 19:00 | 88 | Khulshi | 162 | 19:30 | 154 | Saidpur | 108 | 19:30
23 | Benapole | 66 | 22:00 | 89 | Kishoreganj | 141 | 20:00 | 155 | Satkhira | 137 | 22:00
24 | Bhaluka | 151 | 21:00 | 90 | Kodda | 315 | 08:00 | 156 | Satmasjid | 87 | 13:00
25 | Bhandaria | 56 | 01:00 | 91 | Kulaura | 57 | 20:00 | 157 | Savar | 236 | 12:00
26 | Bhangura | 38 | 19:30 | 92 | Kurigram | 64 | 19:30 | 158 | SevenRings | 9.33 | 17:00
27 | Bheramara(GK) | 68 | 21:00 | 93 | Kushtia | 157 | 19:30 | 159 | ShahCement | 20 | 01:00
28 | Bhulta | 256 | 15:00 | 94 | Laksam | 32 | 19:00 | 160 | Shahjadpur | 84 | 19:30
29 | Bog-Sherpur | 64 | 23:00 | 95 | Lakshmipur | 32 | 19:30 | 161 | Shahjibazar | 135 | 23:00
30 | Bogura | 173 | 20:00 | 96 | Lalbag | 58 | 13:00 | 162 | Shahmirpur | 65 | 02:00
31 | Borhanuddin | 93 | 21:00 | 97 | Lalmonirhat | 73 | 19:30 | 163 | Shariatpur | 85 | 21:00
32 | Brahmanbaria | 128 | 19:30 | 98 | MI_Cement | 10.1 | 02:00 | 164 | Sherpur | 150 | 00:00
33 | Cantonment | 153 | 13:00 | 99 | Madanganj | 40 | 23:00 | 165 | Shikalbaha | 17 | 18:30
34 | Chandina | 14.67 | 00:00 | 100 | Madaripur | 107 | 22:00 | 166 | Shitalakhya | 83.3 | 12:00
35 | Chandpur | 78 | 00:00 | 101 | Madartek | 84.51 | 23:00 | 167 | Sholosohor | 45 | 16:00
36 | Chandraghona | 37 | 19:00 | 102 | Madunaghat | 56 | 19:30 | 168 | Shyampur | 156 | 00:00
37 | Chapai | 69 | 21:00 | 103 | Magura | 65 | 19:30 | 169 | Siddhirganj | 118 | 12:00
38 | Charsaidpur | 41 | 21:00 | 104 | Mahasthangarh | 82 | 20:00 | 170 | Sirajganj | 108 | 21:00
39 | Chauddagram | 72 | 00:00 | 105 | Maijdee | 17 | 20:00 | 171 | Sonargaon | 123 | 11:00
40 | Chhatak | 42 | 23:00 | 106 | Manikganj | 125 | 20:00 | 172 | Sreemongol | 77 | 03:00
41 | Chowmuhani | 173 | 22:00 | 107 | Maniknagar | 78 | 15:00 | 173 | Sreepur | 97 | 19:00
42 | Chuadanga | 116 | 22:00 | 108 | Matarbari | 52 | 20:00 | 174 | Srinagar | 47.11 | 22:00
43 | Coxsbazar | 137 | 19:30 | 109 | Matuail | 62 | 10:00 | 175 | Sunamganj | 63 | 21:00
44 | Cumilla(N) | 143 | 00:00 | 110 | Millgate | 115 | 16:00 | 176 | Sylhet | 51 | 00:00
45 | Cumilla(S) | 146 | 00:00 | 111 | Mirpur | 119 | 14:00 | 177 | Sylhet-132 | 128 | 19:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 11 | 15:00 | 178 | TK | 42 | 00:00
47 | Daudkandi | 138 | 19:30 | 113 | Mirzapur | 44 | 21:00 | 179 | Tangail | 170 | 21:00
48 | Dhaka | 70 | 13:00 | 114 | Mithapukur | 73 | 20:00 | 180 | Taraganj | 22 | 20:00
49 | Dhamrai | 132 | 15:00 | 115 | Modern | N/A | N/A | 181 | Thakurgaon | 117 | 20:00
50 | Dhanmondi | 141.7 | 13:00 | 116 | Mogbazar | 146.4 | 13:00 | 182 | Tongi | 131 | 11:00
51 | Dohazari | 114 | 22:00 | 117 | Mongla | 38 | 00:00 | 183 | Ullahpara | 40 | 19:30
52 | Faridpur | 158 | 19:30 | 118 | Motijheel | 42 | 13:00 | 184 | Ullon | 38 | 19:30
53 | Fatullah | 102 | 12:00 | 119 | Muktagacha | 37 | 19:30 | 185 | Uttara | 78 | 13:00
54 | Fenchuganj | 49 | 22:00 | 120 | Munshiganj | 110 | 20:00 | 186 | UttaraNew | 73 | 01:00
55 | Feni | 116 | 00:00 | 121 | Muradnagar | 40 | 00:00 | 187 | Zigatola | 70 | 13:00
56 | GPH | 83 | 03:00 | 122 | Mymensingh | 193 | 19:30
57 | Ghatail | 80 | 19:30 | 123 | Naogaon | 130 | 20:00
58 | Ghorashal | 13 | 22:00 | 124 | Narail | 59 | 20:00
59 | Ghorashal-230 | 86 | 00:00 | 125 | Narinda | 78 | 13:00
60 | Goalpara | 33 | 00:00 | 126 | Narshingdi | 176 | 01:00
61 | Gollamari | 78 | 20:00 | 127 | Natore | 149 | 19:30
62 | Gopalganj | 103 | 21:00 | 128 | Nawabganj | 56 | 23:00
63 | Gulshan | 120 | 13:00 | 129 | Netrakona | 138 | 23:00
64 | Halishahar | 80 | 09:00 | 130 | New | 91.6 | 12:00
65 | HaripurSBU | 169 | 17:00 | 131 | Niamatpur | 75 | 22:00
66 | Hasnabad | 87 | 19:30 | 132 | Noapara | 43 | 23:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 17-07-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14611.25 | 32 |  | 14644.69
1:00 | 14111.44 | 32 |  | 14144.88
2:00 | 13693.33 | 31 |  | 13725.73
3:00 | 13409.83 | 30 |  | 13441.18
4:00 | 13092.92 | 0 |  | 13092.92
5:00 | 12775.86 | 0 |  | 12775.86
6:00 | 12331.27 | 0 |  | 12331.27
7:00 | 12236.68 | 0 |  | 12236.68
8:00 | 12272 | 0 |  | 12272
9:00 | 12548.04 | 0 |  | 12548.04
10:00 | 12843.84 | 0 |  | 12843.84
11:00 | 13213.8 | 0 |  | 13213.8
12:00 | 13712.55 | 0 |  | 13712.55
13:00 | 13889.95 | 0 |  | 13889.95
14:00 | 13717.17 | 0 |  | 13717.17
15:00 | 13859.92 | 0 |  | 13859.92
16:00 | 13735.34 | 0 |  | 13735.34
17:00 | 13316.42 | 0 |  | 13316.42
18:00 | 12750.94 | 0 |  | 12750.94
19:00 | 13868 | 0 |  | 13868
19:30 | 14827 | 0 |  | 14827
20:00 | 14961.2 | 42 |  | 15005.2
21:00 | 14992.2 | 36 |  | 15030.2
22:00 | 14867.6 | 32 |  | 14900.6
23:00 | 14812.77 | 46 |  | 14860.77
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 17-07-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8007.2 | 6604.05 | 14611.25 | DAILY GENERATION CURVE
00:30 | 7830.7 | 6530.645 | 14361.345
01:00 | 7654.2 | 6457.24 | 14111.44 | 17-07-2025
01:30 | 7517.2 | 6385.185 | 13902.385
02:00 | 7380.2 | 6313.13 | 13693.33
02:30 | 7316.95 | 6234.63 | 13551.58
03:00 | 7253.7 | 6156.13 | 13409.83
03:30 | 7155.2 | 6096.175 | 13251.375
04:00 | 7056.7 | 6036.22 | 13092.92
04:30 | 6973.7 | 5960.69 | 12934.39
05:00 | 6890.7 | 5885.16 | 12775.86
05:30 | 6823.32 | 5730.245 | 12553.565
06:00 | 6755.94 | 5575.33 | 12331.27
06:30 | 6680.6 | 5603.375 | 12283.975
07:00 | 6605.26 | 5631.42 | 12236.68
07:30 | 6607.475 | 5646.865 | 12254.34
08:00 | 6609.69 | 5662.31 | 12272
08:30 | 6681.32 | 5728.7 | 12410.02
09:00 | 6752.95 | 5795.09 | 12548.04
09:30 | 6776.51 | 5919.43 | 12695.94
10:00 | 6800.07 | 6043.77 | 12843.84
10:30 | 6953.345 | 6075.475 | 13028.82
11:00 | 7106.62 | 6107.18 | 13213.8
11:30 | 7223.655 | 6239.52 | 13463.175
12:00 | 7340.69 | 6371.86 | 13712.55
12:30 | 7445.01 | 6356.24 | 13801.25
13:00 | 7549.33 | 6340.62 | 13889.95
13:30 | 7540.88 | 6262.68 | 13803.56
14:00 | 7532.43 | 6184.74 | 13717.17
14:30 | 7555.07 | 6233.475 | 13788.545
15:00 | 7577.71 | 6282.21 | 13859.92
15:30 | 7550.215 | 6247.415 | 13797.63
16:00 | 7522.72 | 6212.62 | 13735.34
16:30 | 7450.615 | 6075.265 | 13525.88
17:00 | 7378.51 | 5937.91 | 13316.42
17:30 | 7210.94 | 5822.74 | 13033.68
18:00 | 7043.37 | 5707.57 | 12750.94
18:30 | 7466.185 | 5843.285 | 13309.47
19:00 | 7889 | 5979 | 13868
19:30 | 8227 | 6600 | 14827
20:00 | 8207.2 | 6754 | 14961.2
20:30 | 8148.2 | 6828.5 | 14976.7 |  | Executive Engineer
21:00 | 8089.2 | 6903 | 14992.2 |  | Network Operation Division
21:30 | 8034.2 | 6895.7 | 14929.9
22:00 | 7979.2 | 6888.4 | 14867.6
22:30 | 7942.7 | 6897.485 | 14840.185
23:00 | 7906.2 | 6906.57 | 14812.77

## En-Curve
QF-LDC-12
Date | 17-07-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3698 | 1907 | 892 | 38 | 34 | 1168.05 | 210 | 4864 | 0 | 352 | 1448.2 | 0 | 0 | 0 | 32 | DAILY ENERGY CURVE
00:30 | 3683.5 | 1882.5 | 892 | 38 | 33 | 1168.05 | 210 | 4790 | 0.095 | 321.5 | 1342.7 | 0 | 0 | 0 | 32 | 17-07-2025
01:00 | 3669 | 1858 | 892 | 38 | 32 | 1168.05 | 210 | 4716 | 0.19 | 291 | 1237.2 | 0 | 0 | 0 | 32
01:30 | 3625 | 1869.5 | 897 | 38 | 31 | 1158.09 | 210 | 4677 | 0.095 | 262.5 | 1134.2 | 0 | 0 | 0 | 31.5 | Energy Generated | 329.9817 |  | MKWHr
02:00 | 3581 | 1881 | 902 | 38 | 30 | 1148.13 | 210 | 4638 | 0 | 234 | 1031.2 | 0 | 0 | 0 | 31 | Energy not Served | 0.281 |  | MKWHr
02:30 | 3604.5 | 1858.25 | 902.5 | 38 | 29 | 1133.13 | 209.5 | 4556.5 | 0 | 234.5 | 985.7 | 0 | 0 | 0 | 30.5 | Total Energy Requirement | 330.2627 |  | MKWHr
03:00 | 3628 | 1835.5 | 903 | 38 | 28 | 1118.13 | 209 | 4475 | 0 | 235 | 940.2 | 0 | 0 | 0 | 30
03:30 | 3624.5 | 1837.5 | 902.5 | 38 | 28 | 1084.675 | 208.5 | 4417.5 | 0 | 213 | 897.2 | 0 | 0 | 0 | 15
04:00 | 3621 | 1839.5 | 902 | 38 | 28 | 1051.22 | 208 | 4360 | 0 | 191 | 854.2 | 0 | 0 | 0 | 0
04:30 | 3615.5 | 1840 | 902 | 38 | 28 | 979.19 | 208 | 4298.5 | 0 | 194 | 831.2 | 0 | 0 | 0 | 0
05:00 | 3610 | 1840.5 | 902 | 38 | 28 | 907.16 | 208 | 4237 | 0 | 197 | 808.2 | 0 | 0 | 0 | 0
05:30 | 3619 | 1818 | 902 | 38 | 27 | 885.92 | 208 | 4111 | 7.945 | 147 | 789.7 | 0 | 0 | 0 | 0
06:00 | 3628 | 1795.5 | 902 | 38 | 26 | 864.68 | 208 | 3985 | 15.89 | 97 | 771.2 | 0 | 0 | 0 | 0
06:30 | 3613 | 1737.75 | 902 | 38 | 25 | 871.365 | 207.5 | 4009 | 48.26 | 69.5 | 762.6 | 0 | 0 | 0 | 0
07:00 | 3598 | 1680 | 902 | 38 | 24 | 878.05 | 207 | 4033 | 80.63 | 42 | 754 | 0 | 0 | 0 | 0
07:30 | 3569 | 1666.5 | 902 | 38 | 24 | 874.525 | 207 | 4021.5 | 123.815 | 58.5 | 769.5 | 0 | 0 | 0 | 0
08:00 | 3540 | 1653 | 902 | 38 | 24 | 871 | 207 | 4010 | 167 | 75 | 785 | 0 | 0 | 0 | 0
08:30 | 3583 | 1664 | 896.5 | 38 | 24 | 873.5 | 208.5 | 4049.5 | 191.52 | 75 | 806.5 | 0 | 0 | 0 | 0
09:00 | 3626 | 1675 | 891 | 38 | 24 | 876 | 210 | 4089 | 216.04 | 75 | 828 | 0 | 0 | 0 | 0
09:30 | 3667 | 1688.5 | 891 | 38 | 24 | 876 | 210 | 4137.5 | 246.44 | 75 | 842.5 | 0 | 0 | 0 | 0
10:00 | 3708 | 1702 | 891 | 38 | 24 | 876 | 210 | 4186 | 276.84 | 75 | 857 | 0 | 0 | 0 | 0
10:30 | 3702 | 1781 | 891 | 38 | 25 | 875 | 210 | 4273 | 266.82 | 75 | 892 | 0 | 0 | 0 | 0
11:00 | 3696 | 1860 | 891 | 38 | 26 | 874 | 210 | 4360 | 256.8 | 75 | 927 | 0 | 0 | 0 | 0
11:30 | 3744 | 1920 | 891 | 38 | 26 | 930.5 | 210 | 4409.5 | 227.675 | 82.5 | 984 | 0 | 0 | 0 | 0
12:00 | 3792 | 1980 | 891 | 38 | 26 | 987 | 210 | 4459 | 198.55 | 90 | 1041 | 0 | 0 | 0 | 0
12:30 | 3730.5 | 1964 | 895.5 | 38 | 27 | 1061.5 | 210.5 | 4464.5 | 229.25 | 118.5 | 1059.5 | 0 | 0 | 2.5 | 0
13:00 | 3669 | 1948 | 900 | 38 | 28 | 1136 | 211 | 4470 | 259.95 | 147 | 1078 | 0 | 0 | 5 | 0
13:30 | 3663 | 1923 | 900.5 | 38 | 28 | 1124 | 211 | 4351.5 | 274.56 | 159 | 1127 | 0 | 0 | 4 | 0
14:00 | 3657 | 1898 | 901 | 38 | 28 | 1112 | 211 | 4233 | 289.17 | 171 | 1176 | 0 | 0 | 3 | 0
14:30 | 3683.5 | 1890 | 900.5 | 38 | 28 | 1124 | 211 | 4240.5 | 310.045 | 174 | 1184.5 | 0 | 0 | 4.5 | 0
15:00 | 3710 | 1882 | 900 | 38 | 28 | 1136 | 211 | 4248 | 330.92 | 177 | 1193 | 0 | 0 | 6 | 0
15:30 | 3699.5 | 1876 | 900 | 38 | 27 | 1125.5 | 211 | 4234 | 310.63 | 173.5 | 1198.5 | 0 | 0 | 4 | 0
16:00 | 3689 | 1870 | 900 | 38 | 26 | 1115 | 211 | 4220 | 290.34 | 170 | 1204 | 0 | 0 | 2 | 0
16:30 | 3678 | 1867.5 | 895 | 38 | 26 | 1068 | 211 | 4179.5 | 230.38 | 174 | 1157.5 | 0 | 0 | 1 | 0
17:00 | 3667 | 1865 | 890 | 38 | 26 | 1021 | 211 | 4139 | 170.42 | 178 | 1111 | 0 | 0 | 0 | 0
17:30 | 3547.5 | 1824 | 895 | 38 | 26 | 1025 | 211 | 4052 | 107.68 | 188.5 | 1119 | 0 | 0 | 0 | 0
18:00 | 3428 | 1783 | 900 | 38 | 26 | 1029 | 211 | 3965 | 44.94 | 199 | 1127 | 0 | 0 | 0 | 0
18:30 | 3540 | 1794.5 | 900 | 38 | 27 | 1066.5 | 211 | 4105.5 | 22.47 | 353 | 1251.5 | 0 | 0 | 0 | 0
19:00 | 3652 | 1806 | 900 | 38 | 28 | 1104 | 211 | 4246 | 0 | 507 | 1376 | 0 | 0 | 0 | 0
19:30 | 3747 | 1919 | 899 | 38 | 28 | 1203 | 211 | 4675 | 0 | 553 | 1554 | 0 | 0 | 0 | 0
20:00 | 3674 | 1915 | 900 | 38 | 28 | 1211 | 220 | 4834 | 0 | 550 | 1591.2 | 0 | 0 | 0 | 42
20:30 | 3696.5 | 1922.5 | 897 | 38 | 28 | 1218.5 | 215 | 4928.5 | 0 | 534 | 1498.7 | 0 | 0 | 0 | 39
21:00 | 3719 | 1930 | 894 | 38 | 28 | 1226 | 210 | 5023 | 0 | 518 | 1406.2 | 0 | 0 | 0 | 36
21:30 | 3723 | 1923 | 892.5 | 38 | 28 | 1220.2 | 210 | 5014 | 0 | 501.5 | 1379.7 | 0 | 0 | 0 | 34
22:00 | 3727 | 1916 | 891 | 38 | 28 | 1214.4 | 210 | 5005 | 0 | 485 | 1353.2 | 0 | 0 | 0 | 32
22:30 | 3721 | 1916 | 891 | 38 | 29 | 1214.985 | 210 | 5007 | 0 | 477.5 | 1335.7 | 0 | 0 | 0 | 39
23:00 | 3715 | 1916 | 891 | 38 | 30 | 1215.57 | 210 | 5009 | 0 | 470 | 1318.2 | 0 | 0 | 0 | 46
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 17-07-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 379 | 06:00 | 369 | 12:00 | Payra | 414 | 06:00 | 409 | 00:00
Ashuganj | 404 | 6:00 | 381 | 12:00 | Rahanpur | 398 | 10:00 | 372 | 23:00
Bhulta | 401 | 06:00 | 376 | 15:00 | Rampal | 405 | 08:00 | 391 | 00:00
Bibiana | 385 | 18:30 | 377 | 12:00
BIPTC | 403 | 04:00 | 393 | 20:00
Bogura | 386 | 06:00 | 361 | 21:00
Gopalganj | 396 | 08:00 | 384 | 23:00
Kaliakoir | 372 | 06:00 | 359 | 12:00
Madunaghat | 389 | 06:00 | 385 | 03:00
Meghnaghat | 380 | 06:00 | 370 | 23:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 222 | 06:00 | 214 | 11:00 | Keranigonj | 220 | 06:00 | 211 | 12:00
AKSML | 227 | 05:00 | 221 | 02:00 | Khulna(S) | 231 | 18:30 | 220 | 19:30
Aminbazar | 223 | 18:00 | 215 | 10:00 | Madunaghat | 230 | 18:30 | 226 | 00:00
Ashuganj | 232 | 06:00 | 222 | 00:00 | Madunaghat-400 | 229 | 05:00 | 226 | 15:00
Ashuganj-400 | 232 | 06:00 | 222 | 00:00 | Maniknagar | 216 | 04:00 | 209 | 12:00
Baghabari | 234 | 06:00 | 224 | 21:00 | Meghnaghat | 228 | 05:00 | 217 | 12:00
Barapukuria | 223 | 18:30 | 212 | 21:00 | Meghnaghat-400 | 221 | 05:00 | 214 | 12:00
Barapukuria-230 | 223 | 18:30 | 212 | 21:00 | Mirsorai | 225 | 18:30 | 217 | 01:00
Barishal | 228 | 07:00 | 219 | 00:00 | Rajshahi | 233 | 18:30 | 219 | 19:30
Bheramara | 232 | 06:00 | 222 | 23:00 | Rampal | 231 | 08:00 | 219 | 19:30
Bhulta | 231 | 05:00 | 211 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 228 | 06:00 | 220 | 22:00 | Rampura | 231 | 06:00 | 213 | 15:00
BIPTC | 235 | 06:00 | 223 | 19:30 | Shikalbaha | 229 | 04:00 | 222 | 15:00
Bogura | 234 | 06:00 | 219 | 21:00 | Shyampur | 220 | 06:00 | 211 | 12:00
Bogura-400 | 234 | 06:00 | 220 | 21:00 | Siddhirganj | 243 | 16:00 | 212 | 11:00
Borhanuddin | 233 | 08:00 | 224 | 00:00 | Sirajgonj | 239 | 07:00 | 231 | 22:00
BSRM | 225 | 18:30 | 217 | 23:00 | Sreepur | 230 | 06:00 | 218 | 21:00
Cumilla(N) | 221 | 06:00 | 214 | 00:00 | Tongi | 224 | 04:00 | 214 | 15:00
Faridpur | 226 | 18:30 | 217 | 00:00
Fenchuganj | 228 | 09:00 | 221 | 23:00
Ghorashal | 230 | 00:00 | 220 | 15:00
Ghorashal-230 | 228 | 06:00 | 214 | 12:00
Gopalganj | 226 | 07:00 | 218 | 23:00
GPH | 226 | 11:00 | 220 | 23:00
Haripur | 218 | 05:00 | 211 | 12:00
Hasnabad | 219 | 03:00 | 212 | 12:00
Hathazari | 227 | 20:00 | 220 | 00:00
Ishurdi | 235 | 18:30 | 224 | 23:00
Jhenaidah | 230 | 08:00 | 217 | 00:00
Kaliakoir | 229 | 06:00 | 219 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 05:00 | 128 | 12:00 | Lalmonirhat | 128 | 14:00 | 116 | 22:00
Agargaon | 130 | 06:00 | 123 | 12:00 | Madanganj | 127 | 18:30 | 122 | 11:00
Agrabad | 129 | 02:00 | 125 | 03:00 | Madaripur | 135 | 05:00 | 130 | 00:00
AKS | 127 | 18:30 | 124 | 11:00 | Madartek | 139 | 06:00 | 127 | 12:00
Aminbazar | 130 | 04:00 | 124 | 10:00 | Madunaghat | 130 | 05:00 | 127 | 15:00
Amnura | 135 | 10:00 | 123 | 22:00 | Magura | 134 | 06:00 | 122 | 19:30
Ashuganj | 140 | 06:00 | 135 | 00:00 | Mahasthangarh | 136 | 18:30 | 123 | 23:00
Bagerhat | 133 | 17:00 | 120 | 00:00 | Maijdee | 118 | 18:00 | 106 | 02:00
Bajitpur | 133 | 05:00 | 123 | 21:00 | Manikganj | 127 | 04:00 | 118 | 12:00
Bakulia | 129 | 03:00 | 127 | 00:00 | Maniknagar | 130 | 06:00 | 123 | 12:00
Banani | 139 | 06:00 | 126 | 16:00 | Matarbari | 114 | 10:00 | 107 | 19:00
Bangabhaban | 130 | 06:00 | 123 | 12:00 | Matuail | 128 | 06:00 | 122 | 12:00
Barapukuria | 137 | 18:30 | 124 | 23:00 | Millgate | 131 | 05:00 | 121 | 12:00
Barguna | 134 | 17:00 | 129 | 00:00 | Mirpur | 128 | 00:00 | 123 | 10:00
Barishal | 133 | 07:00 | 127 | 00:00 | Mirzapur | 130 | 06:00 | 122 | 12:00
Barishal-230 | 134 | 07:00 | 127 | 00:00 | Mithapukur | 134 | 18:30 | 121 | 21:00
Baroaulia | 130 | 18:30 | 126 | 15:00 | MI_Cement | 128 | 06:00 | 122 | 12:00
Baroirhat | 122 | 07:00 | 114 | 02:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 140 | 06:00 | 122 | 12:00 | Mogbazar | 140 | 06:00 | 128 | 12:00
BashundharaCement | 127 | 18:30 | 122 | 11:00 | Mongla | 134 | 18:30 | 123 | 23:00
Beanibazar | 128 | 07:00 | 122 | 23:00 | Motijheel | 130 | 06:00 | 123 | 12:00
Benapole | 133 | 18:00 | 121 | 23:00 | Muktagacha | 134 | 09:00 | 125 | 23:00
Bhaluka | 131 | 06:00 | 122 | 16:00 | Munshiganj | 127 | 05:00 | 122 | 10:00
Bhandaria | 130 | 09:00 | 119 | 00:00 | Muradnagar | 124 | 18:30 | 118 | 00:00
Bhangura | 133 | 03:00 | 127 | 18:30 | Mymensingh | 135 | 07:00 | 114 | 23:00
Bheramara | 137 | 06:00 | 132 | 22:00 | Naogaon | 134 | 18:30 | 121 | 23:00
Bheramara(GK) | 137 | 06:00 | 131 | 23:00 | Narail | 134 | 08:00 | 122 | 22:00
Bhulta | 122 | 06:00 | 116 | 11:00 | Narinda | 130 | 06:00 | 123 | 12:00
Bog-Sherpur | 135 | 06:00 | 125 | 23:00 | Narshingdi | 135 | 03:00 | 115 | 12:00
Bogura | 137 | 05:00 | 128 | 21:00 | Natore | 135 | 08:00 | 127 | 21:00
Bogura-230 | 138 | 06:00 | 128 | 21:00 | Nawabganj | 131 | 07:00 | 125 | 12:00
Brahmanbaria | 135 | 06:00 | 127 | 23:00 | Netrakona | 127 | 05:00 | 112 | 23:00
Cantonment | 130 | 07:00 | 123 | 12:00 | New | 134 | 07:00 | 123 | 12:00
Chandina | 126 | 06:00 | 121 | 00:00 | Niamatpur | 136 | 06:00 | 125 | 21:00
Chandpur | 127 | 11:00 | 118 | 00:00 | Noapara | 136 | 18:30 | 125 | 22:00
Chandraghona | 131 | 18:30 | 128 | 15:00 | Pabna | 134 | 05:00 | 128 | 19:30
Chapai | 135 | 06:00 | 125 | 22:00 | Palashbari | 132 | 18:30 | 118 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 128 | 18:30 | 122 | 12:00 | Panchagarh | 135 | 18:30 | 117 | 23:00
Chauddagram | 122 | 18:30 | 115 | 22:00 | Patuakhali | 134 | 07:00 | 130 | 22:00
Chhatak | 128 | 00:00 | 120 | 21:00 | Payra | 137 | 18:30 | 133 | 00:00
Chowmuhani | 118 | 11:00 | 110 | 00:00 | PHP | 121 | 08:00 | 114 | 02:00
Chuadanga | 133 | 08:00 | 120 | 22:00 | Postogola | 130 | 04:00 | 124 | 12:00
Coxsbazar | 114 | 09:00 | 107 | 19:00 | Purbachal | 139 | 05:00 | 122 | 12:00
Cumilla(N) | 126 | 06:00 | 121 | 00:00 | Purbasadipur | 130 | 01:00 | 117 | 20:00
Cumilla(S) | 133 | 05:00 | 119 | 00:00 | Rahanpur | 137 | 06:00 | 127 | 21:00
Daganbhuiyan | 119 | 11:00 | 110 | 02:00 | Rahanpur-400 | 137 | 08:00 | 128 | 21:00
Daudkandi | 123 | 18:30 | 116 | 01:00 | Rahim | 127 | 05:00 | 122 | 12:00
Dhaka | 140 | 06:00 | 127 | 12:00 | Rajbari | 133 | 08:00 | 126 | 00:00
Dhamrai | 134 | 18:30 | 122 | 12:00 | Rajendrapur | 136 | 18:30 | 121 | 16:00
Dhanmondi | 139 | 06:00 | 127 | 12:00 | Rajshahi | 133 | 06:00 | 126 | 22:00
Dohazari | 123 | 07:00 | 121 | 00:00 | Rajshahi-230 | 134 | 18:30 | 126 | 19:30
Faridpur | 134 | 18:30 | 128 | 22:00 | Ramganj | 121 | 11:00 | 110 | 03:00
Fatullah | 129 | 06:00 | 123 | 12:00 | Rampur | 128 | 05:00 | 125 | 15:00
Fenchuganj | 135 | 06:00 | 130 | 23:00 | Rampura | 140 | 06:00 | 127 | 15:00
Feni | 123 | 11:00 | 117 | 00:00 | Rangamati | 130 | 18:00 | 127 | 00:00
Ghatail | 130 | 07:00 | 122 | 22:00 | Rangpur | 133 | 18:30 | 118 | 23:00
Ghorashal | 137 | 06:00 | 130 | 15:00 | Ruppur | 164 | 14:00 | 131 | 23:00
Goalpara | 136 | 05:00 | 128 | 19:30 | Saidpur | 131 | 01:00 | 118 | 23:00
Gollamari | 138 | 18:30 | 129 | 21:00 | Satkhira | 134 | 18:00 | 121 | 22:00
Gopalganj | 136 | 18:30 | 128 | 19:30 | Satmasjid | 130 | 06:00 | 123 | 12:00
Gopalganj-400 | 137 | 18:30 | 131 | 00:00 | Savar | 130 | 18:00 | 123 | 09:00
Gulshan | 139 | 05:00 | 127 | 15:00 | SevenRings | 137 | 05:00 | 128 | 16:00
Halishahar | 130 | 18:30 | 125 | 15:00 | ShahCement | 128 | 18:30 | 122 | 12:00
Haripur | 127 | 07:00 | 122 | 12:00 | Shahjadpur | 136 | 08:00 | 132 | 21:00
HaripurSBU | 127 | 05:00 | 122 | 12:00 | Shahjibazar | 135 | 08:00 | 127 | 23:00
Hasnabad | 130 | 07:00 | 125 | 10:00 | Shahmirpur | 130 | 02:00 | 128 | 00:00
Hathazari | 132 | 09:00 | 128 | 15:00 | Shariatpur | 134 | 08:00 | 127 | 00:00
Ishurdi | 138 | 18:30 | 131 | 23:00 | Sherpur | 136 | 09:00 | 124 | 15:00
Jaldhaka | 130 | 18:30 | 115 | 23:00 | Shikalbaha | 121 | 04:00 | 116 | 02:00
Jamalpur | 139 | 07:00 | 127 | 16:00 | Shikalbaha-230 | 130 | 02:00 | 128 | 15:00
Jashore | 135 | 18:30 | 119 | 21:00 | Shitalakhya | 128 | 06:00 | 122 | 12:00
Jhenaidah | 135 | 06:00 | 120 | 23:00 | Sholosohor | 129 | 05:00 | 127 | 15:00
Jhenaidah-230 | 136 | 08:00 | 126 | 19:30 | Shyampur | 128 | 06:00 | 122 | 12:00
Joydebpur | 140 | 18:30 | 127 | 12:00 | Shyampur-230 | 128 | 05:00 | 122 | 12:00
Joypurhat | 133 | 18:30 | 119 | 22:00 | Siddhirganj | 128 | 05:00 | 122 | 12:00
Juldah | 129 | 01:00 | 127 | 14:00 | Sirajganj | 133 | 18:30 | 124 | 22:00
Kabirpur | 133 | 18:30 | 118 | 12:00 | Sonargaon | 126 | 05:00 | 120 | 12:00
Kachua | 125 | 18:00 | 116 | 00:00 | Sreemongol | 133 | 06:00 | 127 | 00:00
Kaliakoir | 134 | 06:00 | 126 | 12:00 | Sreepur | 134 | 05:00 | 126 | 23:00
Kallyanpur | 129 | 00:00 | 125 | 10:00 | Srinagar | 131 | 05:00 | 125 | 12:00
Kalurghat | 130 | 18:30 | 127 | 15:00 | SSM | 132 | 00:00 | 130 | 01:00
Kamrangirchar | 131 | 07:00 | 125 | 11:00 | Sunamganj | 127 | 08:00 | 118 | 21:00
Kaptai | 134 | 7:00 | 132 | 1:00 | Sylhet | 128 | 07:00 | 124 | 00:00
Kasba | 124 | 18:30 | 117 | 00:00 | Sylhet-132 | 129 | 09:00 | 126 | 15:00
Kazla | 129 | 05:00 | 123 | 12:00 | Tangail | 129 | 18:30 | 121 | 12:00
Keranigonj | 132 | 06:00 | 126 | 12:00 | Taraganj | 130 | 16:00 | 118 | 19:30
Khagrachori | 129 | 08:00 | 126 | 00:00 | Thakurgaon | 133 | 00:00 | 117 | 23:00
Khulna | 136 | 18:00 | 126 | 23:00 | TK | 130 | 18:30 | 127 | 15:00
Khulna(S) | 138 | 18:30 | 129 | 21:00 | Tongi | 133 | 04:00 | 126 | 15:00
Khulshi | 128 | 18:30 | 124 | 15:00 | Ullahpara | 134 | 05:00 | 126 | 23:00
Kishoreganj | 129 | 06:00 | 119 | 21:00 | Ullon | 139 | 06:00 | 127 | 12:00
Kodda | 132 | 05:00 | 121 | 12:00 | Uttara | 129 | 18:00 | 122 | 12:00
KSRM | 131 | 03:00 | 126 | 13:00 | UttaraNew | 129 | 18:30 | 122 | 12:00
Kulaura | 134 | 09:00 | 129 | 00:00 | Zigatola | 132 | 06:00 | 125 | 04:00
Kurigram | 130 | 14:00 | 116 | 19:30
Kushtia | 134 | 09:00 | 126 | 23:00
Laksam | 124 | 18:00 | 115 | 23:00
Lakshmipur | 119 | 18:00 | 107 | 02:00
Lalbag | 131 | 06:00 | 124 | 17:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division