## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 19-07-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-07-2025 | during | 19-07-2025 | during | 19-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 0 | 0 | 0 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 340 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 300 | 306 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 76 | 195 | 208.13 | 208.13 | 202 | 202 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 320 | 327 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 48 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 30 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 19.2 | 33 | 33 | 25 | 25 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 8 | 0 | 52.19 | 52.19 | 42 | 42 | Engine Problem
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 98 | 24 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 34 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 50 | 50 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 7 | 155 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 28 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 10 | 55 | 55 | 35 | 35 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 508 | 554 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 108 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 1890 | 2204.2 | 4725.65 | 4787.65 | 3275.83 | 3337.83
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 7 | 0 | 8 | 0 | 8 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 26 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 213 | 209 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 219 | 213 | 213 | 219 | 219 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 8 | 42 | 80 | 80 | 80 | 80 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 65 | 65 | 65 | 68 | 68 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 34 | 28 | 2 | 25 | 2 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.28 | 0 | 3.13 | 0 | 3.13 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 850 | 1155 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 1 | 0 | 1 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 701 | 737 | 790 | 790 | 790 | 790 | Machine Problem
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 2110.28 | 2505 | 3824.85 | 3835.72 | 3833.85 | 3844.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 204 | 206 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 334 | 340 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 320 | 340 | 340 | 340 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 17 | 17 | 46.7 | 46.7 | 18 | 18 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 20 | 48 | 55 | 55 | 51 | 51 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 45 | 195 | 195 | 111 | 111 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 38 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 158 | 185 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 28 | 28 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 25 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 17 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 70 | 97 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 9 | 113 | 113 | 18 | 37 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 74 | 115 | 115 | 115 | 115 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 80 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2891.241 | 1377 | 1538 | 2460.75 | 2400.75 | 2065.55 | 2024.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-07-2025 | during | 19-07-2025 | during | 19-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 47 | 99 | 157.5 | 157.5 | 100 | 100 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.4 | 0 | 1.4 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 105 | 180 | 200 | 200 | 186 | 186 | Engine Problem
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 84 | 92 | 115 | 115 | 105 | 105 | Engine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 14.23 | 0 | 49 | 0 | 49 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 35 | 35 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 263.23 | 400 | 599.4 | 549 | 488.4 | 438
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 60 | 60 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 141 | 148 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 20 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 85 | 85 | 85 | 85 | 85 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 172 | 170 | 172 | 172 | 172 | 172 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 6 | 8 | 25 | 25 | 8 | 8 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | Plant Shutdown as per schedule HGPI work
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 389 | 389 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1136 | 1228 | 1255 | 1255 | 1192 | 1192
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 884 | 887 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 205 | 241 | 410 | 410 | 280 | 280 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 60 | 60 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 104.94 | 0 | 50 | 0 | 50 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 745 | 898 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1976.94 | 2064 | 3602.2 | 3552.2 | 3427.2 | 3377.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 442 | 443 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 100 | 100 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 750 | 1112 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 174 | 223 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.19 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1646.19 | 2098 | 2162 | 2161 | 2112 | 2111
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 140 | 192 | 214 | 214 | 200 | 200 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 194 | 220 | 220 | 200 | 200 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 130 | 198 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 374 | 378 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 95 | 95 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.87 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 824.31 | 1228 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 63 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 95 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 1761.18 | 2190 | 3194.47 | 3027.87 | 3118.09 | 2951.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 48 | 50 | 50 | 50 | 50 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 185 | 190 | 150 | 150 | 155 | 155 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.1 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 50 | 115 | 115 | 115 | 95 | 95 | Engine Problem
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 15 | 0 | 18 | 0 | 18 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 152 | 0 | 142.4 | 0 | 142.4 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 489.1 | 466 | 629 | 462 | 614 | 447
System Total |  |  |  |  | 28565.2 | 27084.055 | 12649.92 | 14693.2 | 22453.32 | 22031.19 | 20126.92 | 19723.79
Forecast Scenario (19-07-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14410 |  | 0 |  | 14410
|  |  |  | 1:00 | 13981 |  | 0 |  | 13981
|  |  |  | 2:00 | 13606 |  | 0 |  | 13606
|  |  |  | 3:00 | 13247 |  | 0 |  | 13247
|  |  |  | 4:00 | 12968 |  | 0 |  | 12968
|  |  |  | 5:00 | 12708 |  | 0 |  | 12708
|  |  |  | 6:00 | 12200 |  | 0 |  | 12200
|  |  |  | 7:00 | 12160 |  | 0 |  | 12160
|  |  |  | 8:00 | 12126 |  | 0 |  | 12126
|  |  |  | 9:00 | 12359 |  | 0 |  | 12359
|  |  |  | 10:00 | 12450 |  | 0 |  | 12450
|  |  |  | 11:00 | 12809 |  | 0 |  | 12809
|  |  |  | 12:00 | 13062 |  | 0 |  | 13062
|  |  |  | 13:00 | 13420 |  | 0 |  | 13420
|  |  |  | 14:00 | 13651 |  | 0 |  | 13651
|  |  |  | 15:00 | 13928 |  | 0 |  | 13928
|  |  |  | 16:00 | 13828 |  | 0 |  | 13828
|  |  |  | 17:00 | 13526 |  | 0 |  | 13526
|  |  |  | 18:00 | 13201 |  | 0 |  | 13201
|  |  |  | 18:30 | 13700 |  | 0 |  | 13700
|  |  |  | 19:00 | 14331 |  | 0 |  | 14331
|  |  |  | 19:30 | 15361 |  | 0 |  | 15361
|  |  |  | 20:00 | 15770 |  | 0 |  | 15770
|  |  |  | 21:00 | 15970 |  | 0 |  | 15970
|  |  |  | 22:00 | 15821 |  | 0 |  | 15821
|  |  |  | 23:00 | 15186 |  | 0 |  | 15186
Probable Maximum Temperature: |  |  | 32.80°C
Probable Maximum Demand at Day Peak: |  |  | 13062.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15970.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15970.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 326.718 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:48 hrs on 19-07-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 18-07-2025 | [28 empty] | Date: | 18-07-2025 | [28 empty] | Date: | 18-07-2025 | [28 empty] | Date: | 18-07-2025 | [28 empty] | Date: | 18-07-2025 | [11 empty] | Date: | 18-07-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [11 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 506 | 48 | 0 | 70 | 48 | 0 | 0 | 17 | 32 | 0 | 450 | 312 | 0 | 0 | 0 | 335 | 199 | 0 | 0 | 108 | 27.5 | 19 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 65 | 46 | 0 | 25 | 25 | 0 | 211 | 15 | 32 | 765 | 0 | 0 | 19 | 0 | 30 | 221 | 0 | 0 | 0 | 1090 | 0 | 51 | 50 | 8 | 0 | 353 | 340 | 51 | 204 | 18 | 95 | 0 | 198 | 0 | 19 | 98 | 30 | 52.2 | 0 | 38 | 0 | 320 | 388 | 0 | 60 | 158 | 8 | 0 | 85 | 30 | 0 | 18 | 172 | 17 | 102 | 132 | 33 | 0 | 0 | 12 | 7956.7 | 891 | 239 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1153 | 34 | 1166.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 12 | 0 | 183 | 0 | 184 | 0 | 414 | 0 | 0 | 158 | 48 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 220 | 0 | 441 | 1120 | 0 | 6811.4 | 14768.1 | 98.85
01:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 47 | 0 | 70 | 48 | 0 | 0 | 0 | 32 | 0 | 450 | 303 | 0 | 0 | 0 | 335 | 200 | 0 | 0 | 70 | 20.8 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 39 | 0 | 25 | 25 | 0 | 211 | 15 | 32 | 760 | 0 | 0 | 19 | 0 | 31 | 221 | 0 | 0 | 0 | 1090 | 0 | 51 | 30 | 8 | 0 | 356 | 340 | 50 | 199 | 18 | 77 | 0 | 199 | 0 | 19 | 98 | 28 | 52.2 | 0 | 38 | 0 | 320 | 388 | 0 | 60 | 156 | 8 | 0 | 84 | 30 | 0 | 18 | 172 | 17 | 102 | 132 | 33 | 0 | 0 | 12 | 7817 | 891 | 213 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1096 | 17 | 1133.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 10 | 0 | 181 | 0 | 181 | 0 | 410 | 0 | 0 | 160 | 49 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 220 | 0 | 441 | 1111 | 0 | 6612.29 | 14429.29 | 98.85
02:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 48 | 0 | 70 | 48 | 0 | 0 | 0 | 17 | 0 | 450 | 311 | 0 | 0 | 0 | 332 | 200 | 0 | 0 | 70 | 20.8 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 39 | 0 | 25 | 25 | 0 | 211 | 16 | 32 | 780 | 0 | 0 | 19 | 0 | 32 | 221 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 8 | 0 | 351 | 340 | 50 | 209 | 18 | 74 | 0 | 198 | 0 | 19 | 98 | 26 | 52.2 | 0 | 38 | 0 | 320 | 389 | 0 | 60 | 158 | 8 | 0 | 84 | 30 | 0 | 18 | 172 | 17 | 93 | 132 | 33 | 0 | 0 | 12 | 7703 | 891 | 214 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1027 | 17 | 1037.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 181 | 0 | 182 | 0 | 414 | 0 | 0 | 158 | 49 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 220 | 0 | 441 | 1114 | 0 | 6434.21 | 14137.21 | 98.85
03:00 | 0 | 51 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 37 | 0 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 450 | 308 | 0 | 0 | 0 | 333 | 199 | 0 | 0 | 70 | 20.8 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 0 | 25 | 25 | 0 | 212 | 0 | 34 | 745 | 0 | 0 | 19 | 0 | 0 | 220 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 8 | 0 | 354 | 340 | 50 | 204 | 18 | 74 | 0 | 199 | 0 | 19 | 98 | 24 | 52.2 | 0 | 37 | 0 | 320 | 386 | 0 | 60 | 153 | 8 | 0 | 84 | 30 | 0 | 18 | 172 | 17 | 93 | 132 | 33 | 0 | 0 | 12 | 7521 | 890 | 216 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1008 | 0 | 1017.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 181 | 0 | 182 | 0 | 364 | 0 | 0 | 152 | 49 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 220 | 0 | 441 | 1050 | 0 | 6258.93 | 13779.93 | 98.84
04:00 | 0 | 51 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 16 | 0 | 68 | 16 | 0 | 0 | 0 | 0 | 0 | 450 | 303 | 0 | 0 | 0 | 333 | 200 | 0 | 0 | 52 | 20.8 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 25 | 25 | 0 | 212 | 0 | 34 | 750 | 0 | 0 | 19 | 0 | 0 | 221 | 0 | 0 | 0 | 920 | 0 | 51 | 0 | 8 | 0 | 353 | 340 | 50 | 204 | 18 | 77 | 0 | 199 | 0 | 20 | 98 | 24 | 52.2 | 0 | 38 | 0 | 320 | 388 | 0 | 60 | 142 | 8 | 0 | 84 | 30 | 0 | 18 | 172 | 17 | 93 | 132 | 33 | 0 | 0 | 12 | 7325 | 891 | 216 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 942 | 0 | 1022.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 181 | 0 | 182 | 0 | 376 | 0 | 0 | 157 | 49 | 70 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 220 | 0 | 441 | 1048 | 0 | 6129.3 | 13454.3 | 98.84
05:00 | 0 | 51 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 0 | 0 | 53 | 16 | 0 | 0 | 0 | 0 | 0 | 450 | 305 | 0 | 0 | 0 | 333 | 199 | 0 | 0 | 52 | 20.8 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 25 | 25 | 0 | 211 | 0 | 35 | 741 | 0 | 0 | 6 | 0 | 0 | 221 | 0 | 0 | 0 | 902 | 0 | 51 | 0 | 8 | 0 | 354 | 340 | 50 | 203 | 18 | 75 | 0 | 199 | 0 | 20 | 98 | 24 | 52.2 | 0 | 38 | 0 | 320 | 387 | 0 | 60 | 145 | 8 | 0 | 84 | 30 | 0 | 18 | 173 | 0 | 93 | 132 | 50 | 0 | 0 | 12 | 7256 | 891 | 213 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 910 | 0 | 1026.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 182 | 0 | 182 | 0 | 369 | 0 | 0 | 158 | 49 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 220 | 0 | 442 | 1047 | 0 | 6118.07 | 13374.07 | 98.83
06:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 0 | 0 | 53 | 16 | 0 | 0 | 0 | 0 | 0 | 125 | 294 | 0 | 0 | 0 | 335 | 134 | 0 | 1 | 52 | 20.8 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 25 | 25 | 0.11 | 170 | 0 | 38 | 696 | 0 | 0 | 11 | 0 | 0 | 221 | 0 | 0 | 0 | 885 | 1 | 51 | 0 | 8 | 0 | 300 | 340 | 50 | 194 | 18 | 74 | 0 | 199 | 0 | 20 | 98 | 22 | 52.2 | 2 | 37 | 0 | 320 | 299 | 0 | 60 | 134 | 8 | 0 | 84 | 30 | 0 | 18 | 173 | 0 | 93 | 132 | 48 | 0 | 1.64 | 12 | 6582.75 | 891 | 213 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1.49 | 874 | 0 | 1002.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 84 | 0 | 181 | 0 | 182 | 0 | 344 | 0 | 0.19 | 155 | 49 | 70 | 0 | 70 | 0 | 0 | 0.2 | 6 | 0.03 | 0 | 170 | 0 | 220 | 0 | 443 | 1000 | 0 | 5997.17 | 12579.92 | 98.83
07:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 509 | 0 | 0 | 75 | 48 | 0 | 0 | 32 | 0 | 0 | 125 | 298 | 0 | 0 | 0 | 280 | 135 | 0 | 2 | 52 | 20.8 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 33 | 0 | 0 | 25 | 25 | 0.24 | 169 | 0 | 25 | 669 | 0 | 0 | 25 | 0 | 0 | 221 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 8 | 0 | 300 | 305 | 50 | 195 | 18 | 84 | 0 | 198 | 3 | 20 | 98 | 22 | 52.2 | 23 | 37 | 0 | 320 | 313 | 0 | 60 | 131 | 8 | 0 | 51 | 20 | 0 | 18 | 173 | 9 | 92 | 110 | 48 | 0 | 7.26 | 12 | 6589.5 | 890 | 217 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 10.31 | 785 | 0 | 887.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.49 | 128 | 0 | 181 | 0 | 170 | 0 | 344 | 0 | 0.72 | 157 | 49 | 50 | 2 | 37 | 0 | 0 | 0.2 | 12 | 0.06 | 0 | 170 | 0 | 220 | 0 | 444 | 900 | 0 | 5698.7 | 12288.2 | 98.83
08:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 0 | 0 | 113 | 48 | 0 | 0 | 52 | 0 | 0 | 125 | 299 | 0 | 0 | 0 | 280 | 75 | 0 | 15 | 17 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 4 | 0 | 25 | 25 | 0.66 | 169 | 0 | 42 | 677 | 0 | 0 | 26 | 0 | 0 | 220 | 0 | 0 | 0 | 835 | 0 | 51 | 0 | 8 | 0 | 300 | 305 | 50 | 190 | 18 | 75 | 0 | 199 | 9 | 20 | 70 | 22 | 50 | 16 | 0 | 0 | 320 | 308 | 0 | 60 | 132 | 8 | 0 | 51 | 20 | 0 | 18 | 172 | 0 | 92 | 85 | 48 | 1 | 7.32 | 12 | 6472.98 | 894 | 214 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 32.76 | 784 | 0 | 856.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.23 | 171 | 0 | 130 | 0 | 130 | 0 | 350 | 0 | 1.55 | 156 | 49 | 50 | 9 | 34 | 0 | 0 | 1.1 | 28 | 0.4 | 0 | 171 | 0 | 220 | 0 | 444 | 880 | 0 | 5663.29 | 12136.27 | 98.83
09:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 0 | 0 | 113 | 48 | 0 | 0 | 55 | 0 | 0 | 125 | 308 | 0 | 0 | 0 | 280 | 77 | 0 | 23 | 17 | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 33 | 0 | 25 | 25 | 1.2 | 169 | 0 | 41 | 715 | 0 | 0 | 26 | 0 | 0 | 219 | 0 | 0 | 0 | 810 | 0 | 51 | 0 | 8 | 0 | 280 | 280 | 30 | 207 | 17 | 34 | 0 | 170 | 9 | 19 | 70 | 22 | 34 | 43 | 0 | 0 | 320 | 330 | 0 | 60 | 141 | 8 | 0 | 10 | 20 | 0 | 18 | 172 | 0 | 92 | 85 | 48 | 0 | 29.13 | 12 | 6386.33 | 895 | 204 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 69.34 | 789 | 0 | 827.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.76 | 140 | 0 | 130 | 0 | 130 | 0 | 384 | 0 | 1.95 | 153 | 49 | 50 | 19 | 34 | 0 | 0 | 5.6 | 41 | 0.26 | 0 | 178 | 0 | 220 | 0 | 443 | 750 | 0 | 5562.78 | 11949.11 | 98.82
10:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 0 | 0 | 113 | 32 | 0 | 0 | 0 | 0 | 0 | 125 | 306 | 0 | 0 | 0 | 280 | 75 | 0 | 28 | 17 | 19 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 36 | 0 | 25 | 25 | 2.48 | 169 | 0 | 32 | 726 | 0 | 0 | 26 | 0 | 0 | 220 | 0 | 0 | 0 | 811 | 0 | 51 | 0 | 8 | 0 | 280 | 280 | 20 | 210 | 18 | 34 | 0 | 164 | 8 | 19 | 70 | 24 | 25 | 66 | 0 | 0 | 320 | 338 | 0 | 60 | 139 | 8 | 0 | 10 | 20 | 0 | 18 | 172 | 0 | 75 | 75 | 48 | 1 | 36.07 | 12 | 6309.55 | 896 | 204 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 56.34 | 754 | 0 | 843.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 18.75 | 140 | 0 | 130 | 0 | 130 | 0 | 386 | 0 | 4.12 | 153 | 49 | 50 | 22 | 34 | 0 | 0 | 3.3 | 84 | 0.19 | 0 | 177 | 50 | 180 | 0 | 441 | 750 | 0 | 5666.28 | 11975.83 | 98.82
11:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 0 | 0 | 96 | 32 | 0 | 0 | 0 | 0 | 0 | 330 | 292 | 0 | 0 | 0 | 324 | 76 | 0 | 32 | 17 | 19.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 37 | 0 | 25 | 25 | 3.11 | 169 | 0 | 32 | 663 | 0 | 0 | 26 | 0 | 0 | 219 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 8 | 0 | 280 | 280 | 20 | 196 | 18 | 34 | 0 | 166 | 9 | 19 | 70 | 27 | 25 | 51 | 0 | 0 | 320 | 328 | 0 | 60 | 144 | 8 | 0 | 10 | 20 | 0 | 18 | 172 | 0 | 75 | 75 | 47 | 1 | 29.32 | 12 | 6461.93 | 896 | 206 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 29.95 | 770 | 0 | 822.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 34.69 | 140 | 0 | 130 | 0 | 130 | 0 | 354 | 0 | 2.63 | 156 | 49 | 50 | 20 | 34 | 0 | 0 | 7.8 | 134 | 0.13 | 0 | 171 | 100 | 180 | 0 | 441 | 750 | 0 | 5727.77 | 12189.7 | 98.82
12:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 0 | 0 | 98 | 48 | 0 | 0 | 0 | 7 | 0 | 340 | 300 | 0 | 0 | 0 | 320 | 76 | 0 | 28 | 52 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 25 | 25 | 2.28 | 213 | 0 | 34 | 701 | 0 | 0 | 26 | 0 | 0 | 219 | 0 | 0 | 0 | 850 | 7 | 51 | 0 | 8 | 0 | 334 | 320 | 20 | 204 | 17 | 34 | 0 | 158 | 9 | 19 | 70 | 28 | 25 | 80 | 0 | 0 | 320 | 389 | 0 | 60 | 141 | 6 | 0 | 10 | 20 | 0 | 18 | 172 | 0 | 84 | 105 | 47 | 1 | 14.23 | 12 | 6776.51 | 884 | 205 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 104.94 | 745 | 0 | 824.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 63 | 140 | 0 | 130 | 0 | 130 | 0 | 374 | 0 | 4.87 | 185 | 48 | 50 | 15 | 34 | 0 | 0 | 5.1 | 152 | 0.19 | 0 | 174 | 100 | 180 | 0 | 442 | 750 | 0 | 5873.41 | 12649.92 | 98.82
13:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 554 | 0 | 0 | 113 | 47 | 0 | 0 | 0 | 16 | 0 | 420 | 302 | 0 | 0 | 0 | 327 | 196 | 0 | 32 | 52 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 25 | 25 | 2.94 | 214 | 0 | 32 | 710 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 885 | 6 | 51 | 0 | 41 | 0 | 339 | 340 | 24 | 194 | 17 | 34 | 0 | 167 | 9 | 19 | 70 | 30 | 25 | 76 | 0 | 0 | 320 | 362 | 0 | 60 | 155 | 8 | 0 | 81 | 30 | 0 | 18 | 170 | 0 | 84 | 105 | 47 | 1 | 17.44 | 12 | 7211.38 | 884 | 215 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 95.31 | 788 | 0 | 867.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 55.28 | 170 | 0 | 180 | 0 | 130 | 0 | 396 | 0 | 5.3 | 190 | 49 | 50 | 35 | 34 | 0 | 0 | 5.1 | 128 | 0.2 | 0 | 219 | 100 | 220 | 0 | 442 | 780 | 0 | 6172.28 | 13383.66 | 98.81
14:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 482 | 0 | 0 | 113 | 47 | 0 | 0 | 0 | 14 | 0 | 350 | 305 | 0 | 0 | 0 | 250 | 74 | 0 | 29 | 52 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 8 | 0 | 25 | 25 | 3.26 | 214 | 0 | 32 | 750 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 905 | 12 | 51 | 0 | 45 | 0 | 280 | 285 | 44 | 208 | 17 | 34 | 0 | 157 | 9 | 20 | 70 | 28 | 25 | 26 | 0 | 0 | 320 | 346 | 0 | 60 | 144 | 8 | 0 | 82 | 30 | 0 | 18 | 170 | 12 | 83 | 105 | 47 | 1 | 20.99 | 12 | 6791.25 | 883 | 215 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 95.69 | 783 | 0 | 898.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 30.78 | 170 | 0 | 180 | 0 | 130 | 0 | 391 | 0 | 2.64 | 187 | 49 | 50 | 15 | 34 | 0 | 0 | 4.2 | 22 | 0.75 | 0 | 224 | 100 | 180 | 0 | 443 | 790 | 0 | 6013.99 | 12805.24 | 98.81
15:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 481 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 307 | 0 | 0 | 0 | 325 | 74 | 0 | 24 | 52 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 8 | 0 | 25 | 25 | 3.26 | 217 | 0 | 28 | 743 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 910 | 8 | 51 | 0 | 45 | 0 | 332 | 310 | 47 | 205 | 17 | 34 | 0 | 173 | 9 | 20 | 70 | 28 | 25 | 12 | 0 | 0 | 320 | 353 | 0 | 60 | 148 | 8 | 0 | 76 | 30 | 0 | 18 | 171 | 0 | 82 | 75 | 48 | 0 | 25.07 | 12 | 6874.33 | 883 | 214 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 21.44 | 828 | 0 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 22.76 | 170 | 0 | 180 | 0 | 130 | 0 | 387 | 0 | 2.58 | 190 | 48 | 50 | 27 | 34 | 0 | 0 | 6.2 | 103 | 0.75 | 0 | 222 | 100 | 180 | 0 | 442 | 790 | 0 | 5999.73 | 12874.06 | 98.8
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 481 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 295 | 0 | 0 | 0 | 319 | 133 | 0 | 8 | 52 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 8 | 0 | 25 | 25 | 0.88 | 217 | 0 | 26 | 710 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 890 | 10 | 51 | 0 | 45 | 0 | 338 | 340 | 47 | 196 | 17 | 34 | 0 | 164 | 8 | 17 | 70 | 26 | 25 | 11 | 0 | 0 | 320 | 330 | 0 | 60 | 141 | 8 | 0 | 76 | 30 | 0 | 18 | 170 | 0 | 82 | 75 | 53 | 1 | 18.97 | 12 | 6741.85 | 884 | 216 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 20.83 | 789 | 0 | 854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 18.05 | 170 | 0 | 180 | 0 | 130 | 0 | 350 | 0 | 1.66 | 189 | 48 | 35 | 20 | 34 | 0 | 0 | 4.3 | 86 | 0.24 | 0 | 218 | 100 | 180 | 0 | 443 | 800 | 0 | 5847.08 | 12588.93 | 98.8
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 481 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 16 | 0 | 340 | 294 | 0 | 0 | 0 | 320 | 132 | 0 | 5 | 35 | 19.4 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 8 | 0 | 25 | 25 | 1.62 | 212 | 0 | 21 | 691 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 840 | 2 | 51 | 0 | 45 | 0 | 300 | 340 | 46 | 191 | 17 | 34 | 0 | 154 | 9 | 17 | 70 | 26 | 25 | 17 | 0 | 0 | 320 | 305 | 0 | 60 | 132 | 7 | 0 | 79 | 30 | 0 | 18 | 171 | 0 | 82 | 65 | 90 | 0 | 7.55 | 7 | 6460.57 | 884 | 216 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 16.53 | 773 | 0 | 864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 9.29 | 170 | 0 | 180 | 0 | 130 | 0 | 342 | 0 | 0.78 | 185 | 48 | 35 | 6 | 34 | 0 | 0 | 2.3 | 51 | 0.2 | 0 | 167 | 100 | 180 | 0 | 443 | 720 | 0 | 5607.1 | 12067.67 | 98.8
18:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 15 | 0 | 340 | 298 | 0 | 0 | 0 | 280 | 74 | 0 | 2 | 35 | 19.4 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 12 | 25 | 0.48 | 211 | 0 | 20 | 635 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 850 | 1 | 51 | 0 | 8 | 0 | 300 | 280 | 47 | 198 | 17 | 16 | 0 | 136 | 8 | 17 | 70 | 26 | 25 | 3 | 0 | 0 | 320 | 336 | 0 | 60 | 132 | 8 | 0 | 41 | 20 | 0 | 18 | 171 | 2 | 65 | 65 | 100 | 0 | 2.1 | 11 | 6047.98 | 883 | 220 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9.25 | 770 | 0 | 872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.54 | 140 | 0 | 140 | 0 | 130 | 0 | 349 | 0 | 0.31 | 190 | 48 | 35 | 2 | 34 | 0 | 0 | 0.7 | 14 | 0.07 | 0 | 173 | 100 | 180 | 0 | 441 | 670 | 0 | 5442.87 | 11490.85 | 98.79
19:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17 | 0 | 0 | 0 | 6 | 27 | 0 | 420 | 305 | 0 | 0 | 0 | 320 | 195 | 0 | 0 | 70 | 18.4 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 8 | 0 | 20 | 25 | 0 | 211 | 0 | 20 | 701 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1019 | 0 | 51 | 0 | 22 | 0 | 324 | 300 | 47 | 210 | 17 | 26 | 0 | 144 | 9 | 17 | 97 | 28 | 25 | 0 | 26 | 0 | 320 | 381 | 0 | 60 | 146 | 8 | 0 | 71 | 30 | 0 | 18 | 170 | 17 | 92 | 68 | 99 | 0 | 0 | 12 | 6915.4 | 887 | 228 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 813 | 0 | 1039 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 18 | 0 | 140 | 0 | 142 | 0 | 130 | 0 | 398 | 0 | 0 | 195 | 48 | 108 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 100 | 220 | 0 | 443 | 720 | 0 | 6004 | 12919.4 | 98.79
19:30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 554 | 12 | 0 | 17 | 0 | 0 | 0 | 35 | 125 | 0 | 420 | 299 | 0 | 0 | 0 | 326 | 196 | 0 | 0 | 90 | 16.8 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 8 | 0 | 25 | 25 | 0 | 209 | 0 | 20 | 698 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1075 | 0 | 51 | 0 | 40 | 0 | 344 | 340 | 47 | 190 | 17 | 75 | 0 | 166 | 9 | 17 | 97 | 28 | 25 | 0 | 34 | 0 | 320 | 362 | 0 | 60 | 152 | 8 | 0 | 84 | 30 | 0 | 18 | 170 | 17 | 90 | 125 | 100 | 0 | 0 | 12 | 7493.8 | 887 | 238 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 913 | 0 | 1192 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 22 | 0 | 165 | 0 | 180 | 0 | 156 | 0 | 337 | 0 | 0 | 187 | 48 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 246 | 100 | 220 | 0 | 443 | 960 | 0 | 6595 | 14088.8
20:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 554 | 15 | 0 | 17 | 0 | 0 | 0 | 42 | 113 | 0 | 370 | 294 | 0 | 0 | 0 | 280 | 130 | 0 | 0 | 108 | 17.8 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 8 | 0 | 25 | 25 | 0 | 209 | 0 | 28 | 715 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 43 | 0 | 342 | 340 | 48 | 202 | 17 | 72 | 0 | 178 | 0 | 17 | 97 | 28 | 27 | 0 | 38 | 0 | 320 | 361 | 0 | 60 | 146 | 8 | 0 | 84 | 30 | 0 | 18 | 170 | 17 | 92 | 125 | 98 | 0 | 0 | 12 | 7423.8 | 887 | 237 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 928 | 0 | 1226 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 22 | 0 | 178 | 0 | 178 | 0 | 177 | 0 | 360 | 0 | 0 | 187 | 49 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 224 | 100 | 180 | 0 | 443 | 1019 | 0 | 6696 | 14119.8 | 98.79
21:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 554 | 0 | 10 | 24 | 0 | 0 | 0 | 30 | 155 | 0 | 420 | 306 | 0 | 0 | 0 | 327 | 195 | 0 | 0 | 108 | 19.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 42 | 0 | 25 | 25 | 0 | 209 | 0 | 28 | 737 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1155 | 0 | 51 | 0 | 45 | 0 | 340 | 340 | 48 | 206 | 17 | 74 | 0 | 185 | 9 | 17 | 97 | 28 | 43 | 0 | 38 | 0 | 320 | 389 | 0 | 60 | 148 | 8 | 0 | 85 | 30 | 0 | 18 | 170 | 17 | 92 | 180 | 99 | 0 | 0 | 12 | 7875.2 | 887 | 241 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 898 | 0 | 1228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 194 | 0 | 198 | 0 | 378 | 0 | 0 | 190 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 223 | 100 | 220 | 0 | 443 | 1112 | 0 | 6818 | 14693.2 | 98.78
22:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 554 | 9 | 17 | 34 | 0 | 0 | 0 | 17 | 153 | 0 | 420 | 302 | 0 | 0 | 0 | 328 | 195 | 0 | 0 | 108 | 19.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 48 | 0 | 25 | 25 | 0 | 209 | 0 | 36 | 731 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1155 | 0 | 51 | 0 | 45 | 0 | 346 | 340 | 49 | 203 | 17 | 74 | 0 | 181 | 18 | 17 | 97 | 30 | 43 | 0 | 38 | 0 | 320 | 389 | 0 | 60 | 144 | 8 | 0 | 85 | 30 | 0 | 18 | 171 | 13 | 92 | 182 | 100 | 0 | 0 | 12 | 7898.2 | 747 | 247 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 955 | 0 | 1225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 193 | 0 | 198 | 0 | 366 | 0 | 0 | 152 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 100 | 220 | 0 | 443 | 1202 | 0 | 6834 | 14732.2 | 98.78
23:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 17 | 17 | 34 | 0 | 0 | 0 | 17 | 157 | 0 | 420 | 303 | 0 | 0 | 0 | 327 | 196 | 0 | 0 | 108 | 19.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 48 | 0 | 25 | 25 | 0 | 210 | 0 | 38 | 717 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1180 | 0 | 51 | 0 | 45 | 0 | 347 | 340 | 49 | 206 | 17 | 74 | 0 | 187 | 18 | 18 | 97 | 32 | 43 | 0 | 38 | 0 | 320 | 390 | 0 | 60 | 148 | 8 | 0 | 85 | 30 | 0 | 18 | 171 | 17 | 92 | 182 | 100 | 0 | 0 | 12 | 7948.2 | 747 | 252 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1037 | 0 | 1234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 198 | 0 | 198 | 0 | 414 | 0 | 0 | 153 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 120 | 220 | 0 | 442 | 1187 | 0 | 6989 | 14937.2 | 98.77
Total KWH | 0 | 1271040 | 186240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12159762 | 206280 | 66600 | 1578384 | 541440 | 0 | 0 | 304115 | 959040 | 0 | 8194000 | 7297775 | 0 | 0 | 0 | 7511594 | 3692000 | 0 | 224954 | 1452000 | 474000 | 441000 | 0 | 0 | 0 | 10036 | 0 | 0 | 21120 | 838342 | 413544 | 0 | 574080 | 588480 | 20797 | 4814469 | 41800 | 790560 | 17338181.82 | 0 | 0 | 280320 | 0 | 94509 | 5271624 | 0 | 0 | 0 | 22876362 | 44820 | 1195571 | 60218 | 568727 | 0 | 8108700 | 7764000 | 1038240 | 4903000 | 430992 | 1392960 | 0 | 4299840 | 181440 | 443270 | 2061120 | 620160 | 914021 | 393300 | 478208 | 0 | 7658500 | 8868000 | 0 | 1401720 | 3471955 | 175176 | 0 | 1555200 | 644928 | 0 | 438000 | 4527060 | 239400 | 2078400 | 2803200 | 1382400 | 7500 | 216470 | 289920 | 171190864.82 | 21130181 | 5413536 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 564480 | 20938180 | 50880 | 23727273 | 0 | 0 | 0 | 0 | 0 | 93280 | 0 | 0 | 0 | 586820 | 59198 | 283504 | 3243000 | 0 | 4335173 | 0 | 4086809 | 0 | 9046109 | 0 | 27720 | 4143000 | 1103999 | 1807092 | 183864 | 1649280 | 0 | 0 | 47579.64 | 828000 | 2799 | 0 | 4996000 | 1439000 | 5262940 | 0 | 10624392 | 22731636.36 | 0 | 149317725 | 320508589.82

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 18-07-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12649.92 | MW | 12:00 Hr. | Energy Generated |  |  | 320.5086 |  | MKWHr.
| Day Peak Demand |  |  | 12649.92 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.468 |  | MKWHr.
| Evening Peak Generation |  |  | 14693.2 | MW | 21:00 Hr. | Energy Demand |  |  | 320.9766 |  | MKWHr.
| Evening Peak Demand |  |  | 14749.2 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35 |  | °C
| Minimum Generation of the Day |  |  | 11949.11 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 1013.39 |  | MMCFD
| Maximum Generation of the Day |  |  | 14937.2 | MW | 23:00 Hr. | Production Cost per KWHr |  |  | 5.7754 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.7701 | 0 | 6.5651 | 0 | 0 | 0.22495 | 0 | 0 | 46.5602 | Gas | 133.2343 | Gas | 446871875.1
| Chattogram Zone |  |  | 6.0622 | 40.2145 | 2.8411 | 0 | 4.8145 | 0.065617 | 0 | 0.02112 | 54.019 | Coal | 104.7518 | Coal | 605295344.7288
| Cumilla Zone |  |  | 24.4525 | 0 | 9.3878 | 0 | 0 | 0.3933 | 0.62016 | 0 | 34.8538 | HFO | 27.8647 | HFO | 514074467.6
| Mymensingh Zone |  |  | 1.3824 | 0 | 5.4109 | 0 | 0 | 0.22397 | 0 | 0 | 7.0173 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.7405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.7405 | Hydro | 4.8145 | Hydro | 481446.9
| Khulna Zone |  |  | 5.4135 | 20.9382 | 0.05088 | 0 | 0 | 0.56448 | 22.0422 | 0 | 49.0093 | Solar | 3.4326 | Solar | 55290053.7504
| Barishal Zone |  |  | 6.7019 | 38.352 | 0 | 0 | 0 | 0.002799 | 0 | 0 | 45.0568 | Import | 46.3896 | Import | 228727971.28
| Rajshahi Zone |  |  | 20.7111 | 0 | 0.15248 | 0 | 0 | 0.89804 | 23.7273 | 0 | 45.4889 | Wind | 0.02112 | Wind | 309196.8
| Rangpur Zone |  |  | 0 | 5.247 | 3.4564 | 0 | 0 | 1.0594 | 0 | 0 | 9.7628
| Total |  |  | 133.2343 | 104.7518 | 27.8647 | 0 | 4.8145 | 3.4326 | 46.3896 | 0.02112 | 320.5086
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 446871875.1 |  | Hydro | 481446.9
|  |  |  | Coal | 605295344.7288 |  | Solar | 55290053.7504
|  |  |  | HFO | 514074467.6 |  | Import | 228727971.28
|  |  |  | HSD | 0 |  | Wind | 309196.8
[5 empty] | Total: | 185,10,50,356 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.1302 | Peak Hr Flow | 887.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 40066181.88 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 23.7273 | Peak Hr Flow | 1228.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 786 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.62016 | Peak Hr Flow | 28.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 822 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 45.4776 | Peak Hr Flow | 2143.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4719
|  |  |  | Chattogram |  | 0 |  | 1401
|  |  |  | Cumilla |  | 5 |  | 1390
|  |  |  | Mymensingh |  | 0 |  | 1259
|  |  |  | Sylhet |  | 0 |  | 675
|  |  |  | Khulna |  | 0 |  | 1743
|  |  |  | Barishal |  | 0 |  | 455
|  |  |  | Rajshahi |  | 0 |  | 1490
|  |  |  | Rangpur |  | 49 |  | 1040
|  |  |  | Total |  | 54 |  | 14172
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Bibiana-II 341 MW CCPP (Summit) GT |  |  | 222 | 3 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
|  | 4 | Bibiana-II 341 MW CCPP (Summit) ST |  |  | 119
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 641 |  |  |  | Total | 476
|  |  |  | Total Unavailable Capacity |  |  |  | 1117
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:05 | 10:12 | Gollamari 132/33kV S/S Tr-2 HT Scheduled S/D Due to PBS Maintenance Work
| 08:05 | 10:14 | Gollamari 132/33kV S/S Tr-2 LT Scheduled S/D Due to PBS Maintenance Work
| 08:17 | 18:30 | Bogura 400/230kV S/S ATR-02 HT Project Work S/D Due to Painting
| 08:17 | 18:30 | Bogura 400/230kV S/S ATR-02 LT Project Work S/D Due to Painting
|  | 08:54 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-2 is restored.
|  | 09:21 | Aminbazar-Meghnaghat 400kV Ckt-2 is restored.
| 09:21 | 09:40 | Ghorasal-Narsingdi 132 kV Ckt-1 Tripped from Narshingdi 132/33kV end showing Dis. Relay | [7 empty] | 105.0MW load
|  |  | relays Due to Dis. Fault | [7 empty] | interrup.
Narshingdi 132/33kV
end
|  | 09:29 | Meghnaghat 230/132kV S/S Meghnaghat-ST (MPL) is restored.
| 09:38 |  | Ishurdi---Dynamin Sun [Pabna Solar 100 MW] 132 KV ckt-1 Syn
| 09:40 |  | Ishurdi---Dynamin Sun [Pabna Solar 100 MW] 132 KV ckt-2 Syn
| 10:12 | 11:54 | Meghnaghat 400/230kV S/S 400 kV Bus -02 Scheduled S/D Due to Maintenence purpose
| 10:15 |  | Mahasthangar-Palashbari 132kV Ckt-2 Project Work S/D from Palashbari 132/33kV end Due to
Tower rectification and from Mahasthangarh 132/33kV end Due to Project Work S/D
| 10:20 | 12:35 | Chapai 132/33kV S/S T-3 (425T) LT Forced S/D Due to Red hot Remove | [7 empty] | 15.0MW load
interrup.
| 10:22 | 12:30 | Chapai 132/33kV S/S T-3 (425T) HT Forced S/D Due to Red hot Remove | [7 empty] | 15.0MW load
interrup.
|  | 10:28 | Mirpur-Uttara 132kV Ckt-1 is restored.
|  | 10:45 | Haripur-Narsingdi 132kV Ckt-1 is restored.
|  | 10:56 | Halishahar-Julda 132kV Ckt-1 is restored.
| 11:21 | 22:50 | Kalurghat 132/33kV S/S TRFO-01(506T) LT Scheduled S/D Due to Upgrading work for BPDB
| 11:33 |  | Baghabari----Ruppur 230 KV ckt-1 Syn
| 11:58 |  | Baghabari----Ruppur 230 KV ckt-2 Syn
| 12:00 |  | Day Peak Generation 12629 MW.
|  | 12:25 | Halishahar 132/33kV S/S Halishahar-Khulshi-Ckt.-3 is restored.
| 12:53 | 13:13 | Cumilla(S) 132/33kV S/S TR-2 LT Tripped showing REF 615 relays Due to 33KV palpara feeder | [7 empty] | 28.0MW load
|  |  | fult | [7 empty] | interrup.
|  | 13:03 | Kamrangirchar-Keraniganj 132kV Ckt is restored.
| 17:48 | 17:57 | Cumilla(S) 132/33kV S/S TR-3 LT Tripped showing 1.RET670 2.REF615 relays. | [7 empty] | 24.0MW load
interrup.
| 23:58 | 02:36 | Agargaon 230/132kV S/S 132kV Transformer-1 (405T1) HT Tripped showing 86 relays Due to | [7 empty] | 40.0MW load
|  |  | Prd trip | [7 empty] | interrup.
| 06:07 |  | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T LT Scheduled S/D Due to Red hot
Maintenance
| 06:08 |  | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T HT Scheduled S/D Due to Red hot
Maintenance work
| 06:12 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) HT Scheduled S/D
| 06:13 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT Scheduled S/D
| 06:17 |  | Jashore 132/33kV S/S JH-2(L1) Scheduled S/D
| 06:17 |  | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-2 Project Work S/D Due to Project works
| 07:00 |  | Minimum Generation is 12721 MW
| 07:28 | 07:55 | Feni 132/33kV S/S T-1(405T) LT Tripped showing SIEMENS relays Due to Transformer T-1 33kV | [7 empty] | 34.0MW load
|  |  | side trip for Chowmuhani 33kV ckt-1 trip. Y phase bus loop out | [7 empty] | interrup.
| 07:56 |  | Bogura 132/33kV S/S Transformer-3 LT Scheduled S/D Due to Junction point temparature high
at 33 KV bus isolator (Y-phase upper point.)
| 07:57 |  | Bogura 132/33kV S/S Transformer-3 HT Scheduled S/D Due to Red hot.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 18-07-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8194000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 306 | 7297775 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 195 | 3692000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 327 | 7511594 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 206280 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 541440 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 30 | 304115 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19.2 | 474000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 441000 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 186240 | Engine Problem
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 24 | 1578384 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 1271040 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 155 | 959040 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 224954 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 10 | 66600 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 554 | 12159762 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 1452000 | Engine Problem
Dhaka Area Total |  |  |  |  | 5939.724 | 2204.2 | 46560224
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 44820 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 280320 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 209 | 4814469 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 219 | 5271624 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 94509 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 42 | 413544 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 838342 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 574080 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 28 | 790560 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20797 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 10036 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 41800 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 588480 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1155 | 22876362 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 21120 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 737 | 17338181.82 | FGMO
Chattogram Area Total |  |  |  |  | 4895.72 | 2505 | 54019044.82
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 206 | 4903000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 340 | 8108700 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 7764000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 17 | 430992 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 48 | 1038240 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 45 | 568727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1195571 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 60218 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 38 | 478208 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 185 | 4299840 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 28 | 620160 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 914021 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 443270 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 97 | 2061120 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 181440 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 74 | 1392960 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 393300 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1538 | 34853767
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 99 | 1382400 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7500 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 180 | 2803200 | Engine Problem
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 92 | 2078400 | Engine Problem
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 216470 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 289920 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 239400 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 400 | 7017290
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1401720 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 148 | 3471955 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 644928 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1555200 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 170 | 4527060 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 438000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 175176 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Plant Shutdown as per schedule HGPI work
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 389 | 8868000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7658500 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1228 | 28740539
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 887 | 21130181 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 241 | 5413536 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 50880 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 564480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 898 | 20938180 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2064 | 49009257
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 443 | 10624392 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 100 | 1439000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1112 | 22731636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5262940 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 223 | 4996000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2799 | -
Barishal Area Total |  |  |  |  | 2236 | 2098 | 45056767.36
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 192 | 3243000 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 194 | 4335173 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 198 | 4086809 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 378 | 9046109 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 59198 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 93280 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 27720 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1228 | 23727273 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 283504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 586820 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2190 | 45488886
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 48 | 1103999 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 190 | 4143000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1649280 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 47579.64 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1807092 | Engine Problem
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 183864 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 828000 | -
Rangpur Area Total |  |  |  |  | 950 | 466 | 9762814.64
Eastern Grid Total |  |  |  |  | 16705.895 | 7875.2 | 171190864.82
Western Grid Total |  |  |  |  | 10378.16 | 6818 | 149317725
National Grid Total |  |  |  |  | 27084.055 | 14693.2 | 320508589.82
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 18-07-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9438.29 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4679 | MW
i) Dhaka area |  |  | 4718.68 |  | MW | i) Khulna area |  |  |  | 1742.8 | MW
ii) Chattogram area |  |  | 1401 |  | MW | ii) Barishal area |  |  |  | 455 | MW
iii) Cumilla area |  |  | 1384.61 |  | MW | iii) Rajshahi area |  |  |  | 1490.2 | MW
iv) Mymensingh area |  |  | 1259 |  | MW | iv) Rangpur area |  |  |  | 991 | MW
v) Sylhet area |  |  | 675 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14117.29 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 81 | 22:00 | 133 | PHP | 9 | 13:00
2 | AKSML | 156 | 16:00 | 68 | Ishurdi | 79 | 21:00 | 134 | Pabna | 122 | 22:00
3 | Aftabnagar | 36 | 13:00 | 69 | Jaldhaka | 98 | 20:00 | 135 | Palashbari | 116 | 20:00
4 | Agargaon | 121 | 19:30 | 70 | Jamalpur | 134 | 22:00 | 136 | Panchagarh | 69 | 20:00
5 | Agrabad | 80 | 00:00 | 71 | Jashore | 138 | 23:00 | 137 | Patuakhali | 71.5 | 00:00
6 | Amnura | 39 | 22:00 | 72 | Jhenaidah | 127 | 22:00 | 138 | Payra | 38 | 03:00
7 | Ashuganj | 96 | 23:00 | 73 | Joydebpur | 114 | 00:00 | 139 | Postogola | 52 | 00:00
8 | BSRM | 199 | 19:00 | 74 | Joypurhat | 64 | 22:00 | 140 | Purbachal | 20 | 12:00
9 | Bagerhat | 83 | 00:00 | 75 | Juldah | 15.5 | 00:00 | 141 | Purbasadipur | 140 | 23:00
10 | Bajitpur | 72 | 13:00 | 76 | KSRM | 26 | 20:00 | 142 | Rahanpur | 31 | 01:00
11 | Bakulia | 83 | 21:00 | 77 | Kabirpur | 189 | 01:00 | 143 | Rahim | 22 | 02:00
12 | Banani | 26 | 15:00 | 78 | Kachua | 88 | 22:00 | 144 | Rajbari | 82 | 19:30
13 | Bangabhaban | 4 | 00:00 | 79 | Kallyanpur | 111 | 23:00 | 145 | Rajendrapur | 123 | 00:00
14 | Barapukuria | 68 | 23:00 | 80 | Kalurghat | 32 | 00:00 | 146 | Rajshahi | 112 | 00:00
15 | Barguna | 22 | 00:00 | 81 | Kamrangirchar | 66 | 01:00 | 147 | Rajshahi-230 | 86 | 12:00
16 | Barishal | 108 | 00:00 | 82 | Kaptai | N/A | N/A | 148 | Ramganj | 112 | 21:00
17 | Barishal-230 | 92 | 19:30 | 83 | Kasba | 36 | 21:00 | 149 | Rampur | 41 | 00:00
18 | Baroaulia | 60 | 01:00 | 84 | Kazla | 94 | 00:00 | 150 | Rangamati | 17 | 19:30
19 | Baroirhat | 59 | 19:00 | 85 | Keranigonj | 73 | 00:00 | 151 | Rangpur | 146 | 19:30
20 | Bashundhara | 176 | 13:00 | 86 | Khagrachori | 32 | 20:00 | 152 | Ruppur | 7.2 | 10:00
21 | BashundharaCement | 6 | 01:00 | 87 | Khulna | 74 | 13:00 | 153 | SSM | 16 | 05:00
22 | Beanibazar | 87 | 23:00 | 88 | Khulshi | 138 | 21:00 | 154 | Saidpur | 97 | 23:00
23 | Benapole | 64 | 00:00 | 89 | Kishoreganj | 145 | 21:00 | 155 | Satkhira | 132 | 21:00
24 | Bhaluka | 143 | 00:00 | 90 | Kodda | 269 | 00:00 | 156 | Satmasjid | 90 | 13:00
25 | Bhandaria | 55 | 23:00 | 91 | Kulaura | 55 | 01:00 | 157 | Savar | 171 | 20:00
26 | Bhangura | 38 | 23:00 | 92 | Kurigram | 67 | 19:30 | 158 | SevenRings | 15.31 | 23:00
27 | Bheramara(GK) | 68 | 21:00 | 93 | Kushtia | 152 | 00:00 | 159 | ShahCement | 18 | 18:00
28 | Bhulta | 223 | 23:00 | 94 | Laksam | 33 | 00:00 | 160 | Shahjadpur | 83 | 19:30
29 | Bog-Sherpur | 66 | 19:30 | 95 | Lakshmipur | 30 | 21:00 | 161 | Shahjibazar | 130 | 00:00
30 | Bogura | 164 | 00:00 | 96 | Lalbag | 51 | 00:00 | 162 | Shahmirpur | 53 | 00:00
31 | Borhanuddin | 92 | 22:00 | 97 | Lalmonirhat | 70 | 19:30 | 163 | Shariatpur | 89 | 23:00
32 | Brahmanbaria | 135 | 22:00 | 98 | MI_Cement | 11.8 | 23:00 | 164 | Sherpur | 160 | 21:00
33 | Cantonment | 144 | 19:00 | 99 | Madanganj | 44 | 14:00 | 165 | Shikalbaha | 19 | 22:00
34 | Chandina | 14.69 | 23:00 | 100 | Madaripur | 113 | 22:00 | 166 | Shitalakhya | 60.66 | 00:00
35 | Chandpur | 78 | 00:00 | 101 | Madartek | 91.06 | 23:00 | 167 | Sholosohor | 38 | 00:00
36 | Chandraghona | 35 | 19:30 | 102 | Madunaghat | 54 | 21:00 | 168 | Shyampur | 156 | 00:00
37 | Chapai | 68 | 23:00 | 103 | Magura | 65 | 20:00 | 169 | Siddhirganj | 102 | 21:00
38 | Charsaidpur | 43 | 23:00 | 104 | Mahasthangarh | 84 | 00:00 | 170 | Sirajganj | 103 | 19:30
39 | Chauddagram | 72 | 23:00 | 105 | Maijdee | 20 | 19:30 | 171 | Sonargaon | 118 | 01:00
40 | Chhatak | 42 | 21:00 | 106 | Manikganj | 127 | 21:00 | 172 | Sreemongol | 85 | 20:00
41 | Chowmuhani | 167 | 22:00 | 107 | Maniknagar | 70 | 00:00 | 173 | Sreepur | 83 | 00:00
42 | Chuadanga | 113 | 00:00 | 108 | Matarbari | 51 | 00:00 | 174 | Srinagar | 51.1 | 22:00
43 | Coxsbazar | 132 | 23:00 | 109 | Matuail | 60 | 00:00 | 175 | Sunamganj | 66 | 21:00
44 | Cumilla(N) | 149 | 20:00 | 110 | Millgate | 92 | 00:00 | 176 | Sylhet | 77 | 19:00
45 | Cumilla(S) | 134 | 00:00 | 111 | Mirpur | 119 | 19:00 | 177 | Sylhet-132 | 131 | 21:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 10 | 00:00 | 178 | TK | 34 | 00:00
47 | Daudkandi | 149 | 23:00 | 113 | Mirzapur | 43 | 19:30 | 179 | Tangail | 184 | 21:00
48 | Dhaka | 34 | 15:00 | 114 | Mithapukur | 66 | 00:00 | 180 | Taraganj | 23 | 20:00
49 | Dhamrai | 112 | 00:00 | 115 | Modern | N/A | N/A | 181 | Thakurgaon | 123 | 21:00
50 | Dhanmondi | 118.8 | 19:00 | 116 | Mogbazar | 122 | 16:00 | 182 | Tongi | 124 | 00:00
51 | Dohazari | 111 | 19:30 | 117 | Mongla | 39 | 00:00 | 183 | Ullahpara | 40 | 23:00
52 | Faridpur | 164 | 23:00 | 118 | Motijheel | 37 | 19:00 | 184 | Ullon | 41 | 23:00
53 | Fatullah | 83 | 00:00 | 119 | Muktagacha | 38 | 19:30 | 185 | Uttara | 77 | 19:00
54 | Fenchuganj | 47 | 00:00 | 120 | Munshiganj | 115 | 23:00 | 186 | UttaraNew | 58 | 13:00
55 | Feni | 112 | 00:00 | 121 | Muradnagar | 43 | 21:00 | 187 | Zigatola | 72 | 21:00
56 | GPH | 84 | 23:00 | 122 | Mymensingh | 196 | 22:00
57 | Ghatail | 84 | 19:30 | 123 | Naogaon | 135 | 23:00
58 | Ghorashal | 11 | 10:00 | 124 | Narail | 61 | 20:00
59 | Ghorashal-230 | 84 | 22:00 | 125 | Narinda | 55 | 00:00
60 | Goalpara | 39 | 23:00 | 126 | Narshingdi | 175 | 00:00
61 | Gollamari | 78 | 13:00 | 127 | Natore | 154 | 23:00
62 | Gopalganj | 106.8 | 21:00 | 128 | Nawabganj | 62.6 | 22:00
63 | Gulshan | 92 | 15:00 | 129 | Netrakona | 146 | 20:00
64 | Halishahar | 46.5 | 04:00 | 130 | New | 46.1 | 00:00
65 | HaripurSBU | 147 | 00:00 | 131 | Niamatpur | 77 | 01:00
66 | Hasnabad | 80 | 23:00 | 132 | Noapara | 44 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 18-07-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14768.1 | 52 |  | 14822.44
1:00 | 14429.29 | 45 |  | 14476.29
2:00 | 14137.21 | 42 |  | 14181.21
3:00 | 13779.93 | 40 |  | 13821.93
4:00 | 13454.3 | 35 |  | 13491.3
5:00 | 13374.07 | 26 |  | 13401.07
6:00 | 12579.92 | 0 |  | 12579.92
7:00 | 12288.2 | 0 |  | 12288.2
8:00 | 12136.27 | 0 |  | 12136.27
9:00 | 11949.11 | 0 |  | 11949.11
10:00 | 11975.83 | 0 |  | 11975.83
11:00 | 12189.7 | 0 |  | 12189.7
12:00 | 12649.92 | 0 |  | 12649.92
13:00 | 13383.66 | 0 |  | 13383.66
14:00 | 12805.24 | 0 |  | 12805.24
15:00 | 12874.06 | 0 |  | 12874.06
16:00 | 12588.93 | 0 |  | 12588.93
17:00 | 12067.67 | 0 |  | 12067.67
18:00 | 11490.85 | 0 |  | 11490.85
19:00 | 12919.4 | 0 |  | 12919.4
19:30 | 14088.8 | 0 |  | 14088.8
20:00 | 14119.8 | 49 |  | 14170.8
21:00 | 14693.2 | 54 |  | 14749.2
22:00 | 14732.2 | 65 |  | 14800.13
23:00 | 14937.2 | 60 |  | 14999.9
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 18-07-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7956.7 | 6811.4 | 14768.1 | DAILY GENERATION CURVE
00:30 | 7886.85 | 6711.845 | 14598.695
01:00 | 7817 | 6612.29 | 14429.29 | 18-07-2025
01:30 | 7760 | 6523.25 | 14283.25
02:00 | 7703 | 6434.21 | 14137.21
02:30 | 7612 | 6346.57 | 13958.57
03:00 | 7521 | 6258.93 | 13779.93
03:30 | 7423 | 6194.115 | 13617.115
04:00 | 7325 | 6129.3 | 13454.3
04:30 | 7290.5 | 6123.685 | 13414.185
05:00 | 7256 | 6118.07 | 13374.07
05:30 | 6919.375 | 6057.62 | 12976.995
06:00 | 6582.75 | 5997.17 | 12579.92
06:30 | 6586.125 | 5847.935 | 12434.06
07:00 | 6589.5 | 5698.7 | 12288.2
07:30 | 6531.24 | 5680.995 | 12212.235
08:00 | 6472.98 | 5663.29 | 12136.27
08:30 | 6429.655 | 5613.035 | 12042.69
09:00 | 6386.33 | 5562.78 | 11949.11
09:30 | 6347.94 | 5614.53 | 11962.47
10:00 | 6309.55 | 5666.28 | 11975.83
10:30 | 6385.74 | 5697.025 | 12082.765
11:00 | 6461.93 | 5727.77 | 12189.7
11:30 | 6619.22 | 5800.59 | 12419.81
12:00 | 6776.51 | 5873.41 | 12649.92
12:30 | 6993.945 | 6022.845 | 13016.79
13:00 | 7211.38 | 6172.28 | 13383.66
13:30 | 7001.315 | 6093.135 | 13094.45
14:00 | 6791.25 | 6013.99 | 12805.24
14:30 | 6832.79 | 6006.86 | 12839.65
15:00 | 6874.33 | 5999.73 | 12874.06
15:30 | 6808.09 | 5923.405 | 12731.495
16:00 | 6741.85 | 5847.08 | 12588.93
16:30 | 6601.21 | 5727.09 | 12328.3
17:00 | 6460.57 | 5607.1 | 12067.67
17:30 | 6254.275 | 5524.985 | 11779.26
18:00 | 6047.98 | 5442.87 | 11490.85
18:30 | 6481.69 | 5723.435 | 12205.125
19:00 | 6915.4 | 6004 | 12919.4
19:30 | 7493.8 | 6595 | 14088.8
20:00 | 7423.8 | 6696 | 14119.8
20:30 | 7649.5 | 6757 | 14406.5 |  | Executive Engineer
21:00 | 7875.2 | 6818 | 14693.2 |  | Network Operation Division
21:30 | 7886.7 | 6826 | 14712.7
22:00 | 7898.2 | 6834 | 14732.2
22:30 | 7923.2 | 6911.5 | 14834.7
23:00 | 7948.2 | 6989 | 14937.2

## En-Curve
QF-LDC-12
Date | 18-07-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3723 | 1946.5 | 891 | 38 | 30 | 1166.4 | 211 | 5055 | 0 | 413 | 1294.2 | 0 | 0 | 0 | 52 | DAILY ENERGY CURVE
00:30 | 3704 | 1937.65 | 891 | 38 | 29 | 1149.845 | 211 | 4996.5 | 0 | 390.5 | 1251.2 | 0 | 0 | 0 | 48.5 | 18-07-2025
01:00 | 3685 | 1928.8 | 891 | 38 | 28 | 1133.29 | 211 | 4938 | 0 | 368 | 1208.2 | 0 | 0 | 0 | 45
01:30 | 3689.5 | 1933.8 | 891 | 38 | 27 | 1085.25 | 211 | 4870 | 0 | 357 | 1180.7 | 0 | 0 | 0 | 43.5 | Energy Generated | 320.5086 |  | MKWHr
02:00 | 3694 | 1938.8 | 891 | 38 | 26 | 1037.21 | 211 | 4802 | 0 | 346 | 1153.2 | 0 | 0 | 0 | 42 | Energy not Served | 0.468 |  | MKWHr
02:30 | 3667 | 1935.8 | 890.5 | 38 | 25 | 1027.57 | 211.5 | 4739.5 | 0 | 316.5 | 1107.2 | 0 | 0 | 0 | 41 | Total Energy Requirement | 320.9766 |  | MKWHr
03:00 | 3640 | 1932.8 | 890 | 38 | 24 | 1017.93 | 212 | 4677 | 0 | 287 | 1061.2 | 0 | 0 | 0 | 40
03:30 | 3658 | 1925.3 | 890.5 | 38 | 24 | 1020.115 | 212 | 4579.5 | 0 | 242.5 | 1027.2 | 0 | 0 | 0 | 37.5
04:00 | 3676 | 1917.8 | 891 | 38 | 24 | 1022.3 | 212 | 4482 | 0 | 198 | 993.2 | 0 | 0 | 0 | 35
04:30 | 3702.5 | 1920.8 | 891 | 38 | 24 | 1024.185 | 211.5 | 4452.5 | 0 | 198 | 951.7 | 0 | 0 | 0 | 30.5
05:00 | 3729 | 1923.8 | 891 | 38 | 24 | 1026.07 | 211 | 4423 | 0 | 198 | 910.2 | 0 | 0 | 0 | 26
05:30 | 3611.5 | 1751.8 | 891 | 38 | 23 | 1014.515 | 190.5 | 4347.5 | 7.98 | 189 | 912.2 | 0 | 0 | 0 | 13
06:00 | 3494 | 1579.8 | 891 | 38 | 22 | 1002.96 | 170 | 4272 | 15.96 | 180 | 914.2 | 0 | 0 | 0 | 0
06:30 | 3470 | 1557.8 | 890.5 | 38 | 22 | 945.44 | 169.5 | 4148 | 39.62 | 231.5 | 920.7 | 0 | 0 | 1 | 0
07:00 | 3446 | 1535.8 | 890 | 38 | 22 | 887.92 | 169 | 4024 | 63.28 | 283 | 927.2 | 0 | 0 | 2 | 0
07:30 | 3387.5 | 1543.4 | 892 | 38 | 22 | 872.085 | 169 | 4010 | 97.65 | 257.5 | 922.1 | 0 | 0 | 1 | 0
08:00 | 3329 | 1551 | 894 | 38 | 22 | 856.25 | 169 | 3996 | 132.02 | 232 | 917 | 0 | 0 | 0 | 0
08:30 | 3322.5 | 1529 | 894.5 | 38 | 22 | 842.06 | 169 | 3941.5 | 188.13 | 220.5 | 875.5 | 0 | 0 | 0 | 0
09:00 | 3316 | 1507 | 895 | 38 | 22 | 827.87 | 169 | 3887 | 244.24 | 209 | 834 | 0 | 0 | 0 | 0
09:30 | 3347.5 | 1473 | 895.5 | 38 | 23 | 835.725 | 169 | 3874 | 319.245 | 202.5 | 785 | 0 | 0 | 0 | 0
10:00 | 3379 | 1439 | 896 | 38 | 24 | 843.58 | 169 | 3861 | 394.25 | 196 | 736 | 0 | 0 | 0 | 0
10:30 | 3398.5 | 1541.25 | 896 | 38 | 25.5 | 833.075 | 169 | 3855.5 | 410.44 | 186.5 | 729 | 0 | 0 | 0 | 0
11:00 | 3418 | 1643.5 | 896 | 38 | 27 | 822.57 | 169 | 3850 | 426.63 | 177 | 722 | 0 | 0 | 0 | 0
11:30 | 3506.5 | 1647.75 | 890 | 38 | 27.5 | 823.44 | 191 | 3872.5 | 499.62 | 181.5 | 742 | 0 | 0 | 0 | 0
12:00 | 3595 | 1652 | 884 | 38 | 28 | 824.31 | 213 | 3895 | 572.61 | 186 | 762 | 0 | 0 | 0 | 0
12:30 | 3712 | 1800.5 | 884 | 38 | 29 | 845.7 | 213.5 | 3979 | 564.09 | 185.5 | 765.5 | 0 | 0 | 0 | 0
13:00 | 3829 | 1949 | 884 | 38 | 30 | 867.09 | 214 | 4063 | 555.57 | 185 | 769 | 0 | 0 | 0 | 0
13:30 | 3668.5 | 1867 | 883.5 | 38 | 29 | 883.01 | 214 | 4097 | 457.94 | 185 | 768.5 | 0 | 0 | 3 | 0
14:00 | 3508 | 1785 | 883 | 38 | 28 | 898.93 | 214 | 4131 | 360.31 | 185 | 768 | 0 | 0 | 6 | 0
14:30 | 3583.5 | 1819 | 883 | 38 | 28 | 903.965 | 215.5 | 4152 | 318.685 | 143.5 | 748.5 | 0 | 0 | 6 | 0
15:00 | 3659 | 1853 | 883 | 38 | 28 | 909 | 217 | 4173 | 277.06 | 102 | 729 | 0 | 0 | 6 | 0
15:30 | 3672 | 1837 | 883.5 | 38 | 27 | 881.5 | 217 | 4130 | 257.995 | 93.5 | 687.5 | 0 | 0 | 6.5 | 0
16:00 | 3685 | 1821 | 884 | 38 | 26 | 854 | 217 | 4087 | 238.93 | 85 | 646 | 0 | 0 | 7 | 0
16:30 | 3668 | 1773.7 | 884 | 38 | 26 | 859 | 214.5 | 3977 | 185.1 | 76.5 | 622 | 0 | 0 | 4.5 | 0
17:00 | 3651 | 1726.4 | 884 | 38 | 26 | 864 | 212 | 3867 | 131.27 | 68 | 598 | 0 | 0 | 2 | 0
17:30 | 3561.5 | 1651.9 | 883.5 | 38 | 26 | 868 | 211.5 | 3822 | 84.86 | 64 | 567 | 0 | 0 | 1 | 0
18:00 | 3472 | 1577.4 | 883 | 38 | 26 | 872 | 211 | 3777 | 38.45 | 60 | 536 | 0 | 0 | 0 | 0
18:30 | 3635.5 | 1669.4 | 885 | 38 | 27 | 955.5 | 211 | 3958.5 | 19.225 | 144 | 662 | 0 | 0 | 0 | 0
19:00 | 3799 | 1761.4 | 887 | 38 | 28 | 1039 | 211 | 4140 | 0 | 228 | 788 | 0 | 0 | 0 | 0
19:30 | 3868 | 1942.8 | 887 | 38 | 28 | 1192 | 209 | 4570 | 0 | 277 | 1077 | 0 | 0 | 0 | 0
20:00 | 3817 | 1854.8 | 887 | 38 | 28 | 1226 | 209 | 4665 | 0 | 316 | 1079 | 0 | 0 | 0 | 49
20:30 | 3925 | 1913 | 887 | 38 | 28 | 1227 | 209 | 4735.5 | 0 | 301.5 | 1142.5 | 0 | 0 | 0 | 51.5
21:00 | 4033 | 1971.2 | 887 | 38 | 28 | 1228 | 209 | 4806 | 0 | 287 | 1206 | 0 | 0 | 0 | 54
21:30 | 4032.5 | 1971.7 | 817 | 38 | 29 | 1226.5 | 209 | 4886 | 0 | 290 | 1213 | 0 | 0 | 0 | 59.5
22:00 | 4032 | 1972.2 | 747 | 38 | 30 | 1225 | 209 | 4966 | 0 | 293 | 1220 | 0 | 0 | 0 | 65
22:30 | 4074 | 1976.7 | 747 | 38 | 31 | 1229.5 | 209.5 | 5005 | 0 | 293 | 1231 | 0 | 0 | 0 | 62.5
23:00 | 4116 | 1981.2 | 747 | 38 | 32 | 1234 | 210 | 5044 | 0 | 293 | 1242 | 0 | 0 | 0 | 60
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 18-07-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 383 | 08:00 | 370 | 00:00 | Payra | 415 | 10:00 | 408 | 00:00
Ashuganj | 404 | 6:00 | 381 | 12:00 | Rahanpur | 400 | 17:00 | 375 | 00:00
Bhulta | 399 | 07:00 | 380 | 00:00 | Rampal | 406 | 10:00 | 391 | 00:00
Bibiana | 387 | 07:00 | 377 | 00:00
BIPTC | 402 | 06:00 | 394 | 21:00
Bogura | 388 | 17:00 | 362 | 23:00
Gopalganj | 399 | 18:00 | 383 | 00:00
Kaliakoir | 376 | 08:00 | 363 | 22:00
Madunaghat | 393 | 08:00 | 385 | 23:00
Meghnaghat | 386 | 08:00 | 372 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 225 | 08:00 | 214 | 00:00 | Keranigonj | 223 | 08:00 | 212 | 00:00
AKSML | 231 | 07:00 | 126 | 16:00 | Khulna(S) | 233 | 10:00 | 217 | 23:00
Aminbazar | 226 | 07:00 | 215 | 00:00 | Madunaghat | 233 | 07:00 | 226 | 20:00
Ashuganj | 232 | 07:00 | 221 | 00:00 | Madunaghat-400 | 233 | 06:00 | 226 | 23:00
Ashuganj-400 | 232 | 18:00 | 222 | 12:00 | Maniknagar | 221 | 08:00 | 211 | 00:00
Baghabari | 235 | 17:00 | 225 | 20:00 | Meghnaghat | 227 | 09:00 | 218 | 00:00
Barapukuria | 224 | 19:00 | 212 | 00:00 | Meghnaghat-400 | 225 | 08:00 | 216 | 00:00
Barapukuria-230 | 224 | 19:00 | 211 | 21:00 | Mirsorai | 228 | 07:00 | 218 | 23:00
Barishal | 231 | 18:00 | 220 | 00:00 | Rajshahi | 233 | 06:00 | 218 | 21:00
Bheramara | 234 | 06:00 | 221 | 19:30 | Rampal | 232 | 10:00 | 219 | 00:00
Bhulta | 230 | 07:00 | 213 | 22:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 227 | 07:00 | 220 | 00:00 | Rampura | 229 | 07:00 | 216 | 00:00
BIPTC | 263 | 06:00 | 220 | 21:00 | Shikalbaha | 231 | 08:00 | 222 | 22:00
Bogura | 233 | 06:00 | 220 | 00:00 | Shyampur | 222 | 08:00 | 213 | 00:00
Bogura-400 | 233 | 17:00 | 220 | 00:00 | Siddhirganj | 223 | 08:00 | 214 | 00:00
Borhanuddin | 235 | 18:00 | 225 | 00:00 | Sirajgonj | 240 | 17:00 | 232 | 00:00
BSRM | 228 | 09:00 | 218 | 22:00 | Sreepur | 228 | 09:00 | 219 | 22:00
Cumilla(N) | 224 | 07:00 | 214 | 00:00 | Tongi | 226 | 17:00 | 215 | 00:00
Faridpur | 228 | 17:00 | 216 | 23:00
Fenchuganj | 228 | 09:00 | 222 | 00:00
Ghorashal | 230 | 00:00 | 230 | 00:00
Ghorashal-230 | 229 | 07:00 | 216 | 00:00
Gopalganj | 228 | 17:00 | 218 | 00:00
GPH | 228 | 10:00 | 221 | 00:00
Haripur | 222 | 08:00 | 212 | 00:00
Hasnabad | 222 | 08:00 | 213 | 00:00
Hathazari | 229 | 08:00 | 223 | 00:00
Ishurdi | 236 | 06:00 | 224 | 20:00
Jhenaidah | 232 | 17:00 | 215 | 23:00
Kaliakoir | 232 | 09:00 | 222 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 07:00 | 128 | 19:30 | Lalmonirhat | 128 | 16:00 | 12 | 18:30
Agargaon | 158 | 19:30 | 125 | 00:00 | Madanganj | 129 | 18:00 | 123 | 00:00
Agrabad | 131 | 07:00 | 126 | 19:30 | Madaripur | 137 | 18:00 | 129 | 22:00
AKS | 129 | 05:00 | 125 | 20:00 | Madartek | 137 | 07:00 | 129 | 00:00
Aminbazar | 133 | 05:00 | 124 | 00:00 | Madunaghat | 132 | 07:00 | 128 | 00:00
Amnura | 135 | 17:00 | 125 | 22:00 | Magura | 135 | 17:00 | 121 | 23:00
Ashuganj | 140 | 07:00 | 135 | 00:00 | Mahasthangarh | 134 | 06:00 | 123 | 23:00
Bagerhat | 135 | 10:00 | 119 | 23:00 | Maijdee | 118 | 08:00 | 106 | 22:00
Bajitpur | 132 | 17:00 | 123 | 00:00 | Manikganj | 128 | 18:00 | 119 | 00:00
Bakulia | 134 | 09:00 | 127 | 21:00 | Maniknagar | 131 | 08:00 | 126 | 00:00
Banani | 137 | 18:00 | 128 | 00:00 | Matarbari | 122 | 09:00 | 108 | 23:00
Bangabhaban | 132 | 08:00 | 125 | 00:00 | Matuail | 129.6 | 18:00 | 123 | 00:00
Barapukuria | 138 | 19:00 | 125 | 00:00 | Millgate | 133 | 07:00 | 124 | 00:00
Barguna | 135 | 17:00 | 130 | 00:00 | Mirpur | 131 | 07:00 | 124 | 00:00
Barishal | 136 | 18:00 | 127 | 01:00 | Mirzapur | 131 | 18:00 | 123 | 00:00
Barishal-230 | 135 | 17:00 | 128 | 01:00 | Mithapukur | 132 | 06:00 | 111 | 19:30
Baroaulia | 132 | 09:00 | 127 | 20:00 | MI_Cement | 130 | 18:00 | 123 | 00:00
Baroirhat | 125 | 07:00 | 115 | 22:00 | Modern | 0 | 00:00 | 0 | 00:00
Bashundhara | 137 | 07:00 | 124 | 00:00 | Mogbazar | 139 | 18:00 | 130 | 00:00
BashundharaCement | 129 | 18:00 | 123 | 00:00 | Mongla | 135 | 10:00 | 121 | 23:00
Beanibazar | 127 | 05:00 | 121 | 22:00 | Motijheel | 132 | 08:00 | 125 | 00:00
Benapole | 134 | 18:00 | 119 | 23:00 | Muktagacha | 133 | 06:00 | 126 | 00:00
Bhaluka | 131 | 07:00 | 123 | 00:00 | Munshiganj | 129 | 07:00 | 123 | 00:00
Bhandaria | 132 | 18:00 | 119 | 23:00 | Muradnagar | 127 | 08:00 | 118 | 22:00
Bhangura | 157 | 20:00 | 126 | 23:00 | Mymensingh | 134 | 06:00 | 114 | 19:30
Bheramara | 138 | 06:00 | 131 | 23:00 | Naogaon | 132 | 18:00 | 119 | 21:00
Bheramara(GK) | 137 | 10:00 | 131 | 00:00 | Narail | 135 | 17:00 | 122 | 00:00
Bhulta | 124 | 17:00 | 118 | 00:00 | Narinda | 131 | 08:00 | 126 | 00:00
Bog-Sherpur | 135 | 06:00 | 125 | 22:00 | Narshingdi | 138 | 07:00 | 115 | 00:00
Bogura | 137 | 06:00 | 127 | 23:00 | Natore | 135 | 06:00 | 125 | 23:00
Bogura-230 | 137 | 06:00 | 127 | 23:00 | Nawabganj | 134 | 08:00 | 125 | 00:00
Brahmanbaria | 135 | 18:00 | 126 | 22:00 | Netrakona | 126 | 07:00 | 110 | 22:00
Cantonment | 132 | 07:00 | 125 | 00:00 | New | 133 | 07:00 | 125 | 00:00
Chandina | 129 | 08:00 | 120 | 22:00 | Niamatpur | 136 | 05:00 | 125 | 22:00
Chandpur | 129 | 08:00 | 115 | 22:00 | Noapara | 137 | 18:00 | 122 | 23:00
Chandraghona | 133 | 08:00 | 128 | 23:00 | Pabna | 134 | 06:00 | 127 | 23:00
Chapai | 135 | 18:00 | 124 | 22:00 | Palashbari | 130 | 06:00 | 110 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 08:00 | 123 | 00:00 | Panchagarh | 136 | 19:00 | 118 | 00:00
Chauddagram | 125 | 07:00 | 114 | 22:00 | Patuakhali | 135 | 17:00 | 130 | 00:00
Chhatak | 126 | 07:00 | 119 | 23:00 | Payra | 137 | 18:00 | 134 | 00:00
Chowmuhani | 120 | 08:00 | 106 | 23:00 | PHP | 125 | 08:00 | 114 | 22:00
Chuadanga | 134 | 17:00 | 117 | 22:00 | Postogola | 132 | 18:00 | 125 | 00:00
Coxsbazar | 123 | 09:00 | 108 | 22:00 | Purbachal | 138 | 07:00 | 124 | 00:00
Cumilla(N) | 129 | 07:00 | 120 | 22:00 | Purbasadipur | 130 | 18:30 | 117 | 00:00
Cumilla(S) | 135 | 05:00 | 118 | 22:00 | Rahanpur | 137 | 11:00 | 128 | 00:00
Daganbhuiyan | 121 | 08:00 | 110 | 22:00 | Rahanpur-400 | 137 | 11:00 | 128 | 00:00
Daudkandi | 124 | 07:00 | 116 | 22:00 | Rahim | 129 | 08:00 | 123 | 00:00
Dhaka | 137 | 07:00 | 129 | 19:30 | Rajbari | 134 | 18:00 | 125 | 23:00
Dhamrai | 134 | 08:00 | 124 | 00:00 | Rajendrapur | 134 | 08:00 | 122 | 00:00
Dhanmondi | 138 | 07:00 | 129.5 | 19:30 | Rajshahi | 134 | 05:00 | 125 | 21:00
Dohazari | 130 | 09:00 | 121 | 22:00 | Rajshahi-230 | 134 | 06:00 | 125 | 21:00
Faridpur | 135 | 17:00 | 13 | 14:00 | Ramganj | 118 | 07:00 | 109 | 22:00
Fatullah | 131 | 07:00 | 125 | 00:00 | Rampur | 132 | 10:00 | 126 | 23:00
Fenchuganj | 134 | 06:00 | 131 | 00:00 | Rampura | 137 | 07:00 | 128 | 19:30
Feni | 125 | 08:00 | 114 | 19:30 | Rangamati | 132 | 07:00 | 127 | 23:00
Ghatail | 130 | 06:00 | 121 | 00:00 | Rangpur | 131 | 18:00 | 119 | 00:00
Ghorashal | 136 | 17:00 | 131 | 00:00 | Ruppur | 137 | 06:00 | 131 | 20:00
Goalpara | 139 | 18:30 | 126 | 23:00 | Saidpur | 131 | 15:00 | 118 | 00:00
Gollamari | 138 | 09:00 | 127 | 23:00 | Satkhira | 136 | 18:00 | 119 | 23:00
Gopalganj | 136 | 09:00 | 127 | 00:00 | Satmasjid | 132 | 08:00 | 125 | 00:00
Gopalganj-400 | 137 | 08:00 | 130 | 23:00 | Savar | 132 | 07:00 | 123 | 11:00
Gulshan | 137 | 07:00 | 129 | 00:00 | SevenRings | 139 | 07:00 | 129 | 23:00
Halishahar | 132 | 07:00 | 127 | 19:30 | ShahCement | 129 | 08:00 | 123 | 00:00
Haripur | 130 | 08:00 | 123 | 00:00 | Shahjadpur | 136 | 05:00 | 131 | 22:00
HaripurSBU | 130 | 08:00 | 124 | 00:00 | Shahjibazar | 133 | 06:00 | 127 | 01:00
Hasnabad | 131 | 07:00 | 125 | 00:00 | Shahmirpur | 134 | 07:00 | 128 | 19:30
Hathazari | 134 | 08:00 | 129 | 14:00 | Shariatpur | 136 | 18:00 | 127 | 22:00
Ishurdi | 138 | 06:00 | 131 | 21:00 | Sherpur | 135 | 05:00 | 125 | 18:30
Jaldhaka | 129 | 19:00 | 115 | 00:00 | Shikalbaha | 122 | 07:00 | 116 | 23:00
Jamalpur | 137 | 05:00 | 127 | 19:00 | Shikalbaha-230 | 134 | 08:00 | 126 | 00:00
Jashore | 136 | 17:00 | 118 | 23:00 | Shitalakhya | 130 | 18:00 | 123 | 00:00
Jhenaidah | 137 | 17:00 | 121 | 00:00 | Sholosohor | 132 | 10:00 | 128 | 00:00
Jhenaidah-230 | 136 | 08:00 | 125 | 21:00 | Shyampur | 132 | 18:30 | 125 | 00:00
Joydebpur | 140 | 06:00 | 123 | 23:00 | Shyampur-230 | 131 | 08:00 | 123 | 00:00
Joypurhat | 131 | 18:30 | 117 | 23:00 | Siddhirganj | 130 | 08:00 | 125 | 00:00
Juldah | 134 | 07:00 | 8 | 17:00 | Sirajganj | 134 | 11:00 | 126 | 19:30
Kabirpur | 134 | 07:00 | 122 | 00:00 | Sonargaon | 127 | 18:30 | 121 | 00:00
Kachua | 128 | 08:00 | 113 | 22:00 | Sreemongol | 132 | 07:00 | 126 | 22:00
Kaliakoir | 135 | 08:00 | 128 | 22:00 | Sreepur | 133 | 17:00 | 126 | 22:00
Kallyanpur | 131 | 07:00 | 125 | 13:00 | Srinagar | 135 | 07:00 | 126 | 00:00
Kalurghat | 132 | 07:00 | 127 | 21:00 | SSM | 136 | 10:00 | 128 | 00:00
Kamrangirchar | 134 | 08:00 | 127 | 01:00 | Sunamganj | 124 | 07:00 | 118 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 129 | 07:00 | 123 | 22:00
Kasba | 126 | 08:00 | 116 | 22:00 | Sylhet-132 | 129 | 07:00 | 125 | 00:00
Kazla | 139 | 20:00 | 125 | 00:00 | Tangail | 129 | 04:00 | 121 | 00:00
Keranigonj | 134 | 07:00 | 127 | 00:00 | Taraganj | 131 | 06:00 | 120 | 00:00
Khagrachori | 131 | 07:00 | 126 | 21:00 | Thakurgaon | 135 | 19:00 | 117 | 00:00
Khulna | 137 | 10:00 | 124 | 23:00 | TK | 132 | 09:00 | 127 | 00:00
Khulna(S) | 139 | 10:00 | 127 | 23:00 | Tongi | 134 | 08:00 | 128 | 00:00
Khulshi | 130 | 07:00 | 125 | 21:00 | Ullahpara | 135 | 10:00 | 126 | 00:00
Kishoreganj | 131 | 17:00 | 118 | 21:00 | Ullon | 137 | 18:00 | 129 | 00:00
Kodda | 134 | 08:00 | 123 | 22:00 | Uttara | 132 | 07:00 | 124 | 00:00
KSRM | 134 | 08:00 | 127 | 00:00 | UttaraNew | 131 | 08:00 | 124 | 00:00
Kulaura | 134 | 08:00 | 129 | 00:00 | Zigatola | 134 | 08:00 | 127 | 00:00
Kurigram | 129 | 16:00 | 116 | 19:30
Kushtia | 134 | 17:00 | 12 | 02:00
Laksam | 127 | 08:00 | 113 | 22:00
Lakshmipur | 120 | 08:00 | 107 | 22:00
Lalbag | 132 | 18:30 | 125 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division