## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 19-07-2025 | [28 empty] | Date: | 19-07-2025 | [28 empty] | Date: | 19-07-2025 | [28 empty] | Date: | 19-07-2025 | [28 empty] | Date: | 19-07-2025 | [11 empty] | Date: | 19-07-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [11 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553 | 16 | 17 | 34 | 0 | 0 | 0 | 17 | 155 | 0 | 420 | 307 | 0 | 0 | 0 | 328 | 197 | 0 | 0 | 108 | 19.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 65 | 46 | 0 | 25 | 25 | 0 | 210 | 0 | 38 | 708 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1155 | 0 | 51 | 0 | 63 | 0 | 348 | 340 | 50 | 200 | 17 | 74 | 0 | 183 | 15 | 20 | 97 | 34 | 52.2 | 0 | 38 | 0 | 320 | 388 | 0 | 60 | 158 | 8 | 0 | 85 | 30 | 0 | 18 | 172 | 17 | 92 | 181 | 101 | 0 | 0 | 11 | 7946.4 | 747 | 256 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1057 | 0 | 1217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 201 | 0 | 198 | 0 | 414 | 0 | 0 | 153 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 120 | 220 | 0 | 442 | 1157 | 0 | 6970 | 14916.4 | 98.77
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553 | 15 | 17 | 34 | 0 | 0 | 0 | 0 | 72 | 8 | 420 | 309 | 0 | 0 | 0 | 327 | 133 | 0 | 0 | 108 | 19.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 46 | 0 | 25 | 25 | 0 | 205 | 0 | 38 | 742 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 71 | 0 | 347 | 340 | 49 | 204 | 17 | 74 | 0 | 175 | 10 | 20 | 97 | 28 | 52.2 | 0 | 38 | 0 | 320 | 390 | 0 | 60 | 154 | 8 | 0 | 85 | 30 | 0 | 18 | 171 | 17 | 92 | 181 | 101 | 0 | 0 | 12 | 7715.7 | 870 | 256 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1047 | 0 | 1029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 201 | 0 | 198 | 0 | 414 | 0 | 0 | 153 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 120 | 220 | 0 | 401 | 1100 | 0 | 6723 | 14438.7 | 98.76
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 16 | 420 | 310 | 0 | 0 | 0 | 327 | 134 | 0 | 0 | 90 | 19.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 65 | 0 | 0 | 25 | 25 | 0 | 205 | 0 | 38 | 746 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1050 | 0 | 51 | 0 | 71 | 0 | 346 | 340 | 50 | 205 | 17 | 75 | 0 | 180 | 0 | 20 | 97 | 28 | 52.2 | 0 | 38 | 0 | 320 | 390 | 0 | 60 | 157 | 8 | 0 | 85 | 30 | 0 | 18 | 171 | 17 | 92 | 181 | 100 | 0 | 0 | 10 | 7527.7 | 870 | 261 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1032 | 0 | 1015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 201 | 0 | 198 | 0 | 414 | 0 | 0 | 150 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 120 | 220 | 0 | 395 | 996 | 0 | 6585 | 14112.7 | 98.76
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 350 | 308 | 0 | 0 | 0 | 327 | 134 | 0 | 0 | 90 | 19.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 25 | 25 | 0 | 206 | 0 | 31 | 670 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 71 | 0 | 345 | 340 | 50 | 203 | 16 | 73 | 0 | 183 | 0 | 20 | 97 | 26 | 52.2 | 0 | 36 | 0 | 320 | 391 | 0 | 60 | 157 | 8 | 0 | 85 | 30 | 0 | 18 | 172 | 17 | 92 | 172 | 100 | 0 | 0 | 0 | 7266.7 | 870 | 263 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 975 | 0 | 1011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 201 | 0 | 198 | 0 | 414 | 0 | 0 | 150 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 120 | 220 | 0 | 397 | 997 | 0 | 6530 | 13796.7 | 98.75
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 300 | 309 | 0 | 0 | 0 | 328 | 134 | 0 | 0 | 70 | 19.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 25 | 25 | 0 | 206 | 0 | 31 | 696 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 990 | 0 | 51 | 0 | 71 | 0 | 346 | 335 | 50 | 204 | 16 | 74 | 0 | 180 | 0 | 20 | 97 | 26 | 52.2 | 0 | 15 | 0 | 320 | 394 | 0 | 60 | 155 | 8 | 0 | 85 | 30 | 0 | 18 | 172 | 17 | 93 | 84 | 101 | 0 | 0 | 0 | 7091.7 | 870 | 269 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 892 | 0 | 993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 204 | 0 | 202 | 0 | 414 | 0 | 0 | 153 | 48 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 120 | 220 | 0 | 398 | 980 | 0 | 6409 | 13500.7 | 98.75
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 554 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 300 | 305 | 0 | 0 | 0 | 328 | 134 | 0 | 0 | 70 | 19.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 65 | 0 | 0 | 25 | 25 | 0 | 206 | 0 | 38 | 665 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 950 | 0 | 51 | 0 | 71 | 0 | 352 | 335 | 50 | 199 | 16 | 74 | 0 | 183 | 0 | 20 | 97 | 26 | 52.2 | 0 | 16 | 0 | 320 | 385 | 0 | 60 | 157 | 8 | 0 | 85 | 30 | 0 | 18 | 172 | 17 | 93 | 84 | 101 | 0 | 0 | 4 | 7040.7 | 870 | 281 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 861 | 0 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 206 | 0 | 208 | 0 | 414 | 0 | 0 | 154 | 49 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 120 | 220 | 0 | 398 | 950 | 0 | 6280 | 13320.7 | 98.74
06:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 130 | 300 | 0 | 0 | 0 | 331 | 134 | 0 | 1 | 70 | 19.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 25 | 25 | 0.09 | 206 | 0 | 38 | 637 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 71 | 0 | 354 | 300 | 50 | 191 | 16 | 74 | 0 | 175 | 0 | 20 | 97 | 24 | 52.2 | 1 | 16 | 0 | 320 | 360 | 0 | 60 | 154 | 8 | 0 | 85 | 30 | 0 | 18 | 172 | 0 | 93 | 84 | 101 | 0 | 2 | 0 | 6707.79 | 870 | 282 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 839 | 0 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.13 | 202 | 0 | 170 | 0 | 170 | 0 | 343 | 0 | 0 | 156 | 48 | 115 | 2 | 92 | 0 | 0 | 0.2 | 14 | 0.04 | 0 | 196 | 120 | 190 | 0 | 398 | 950 | 0 | 6099.37 | 12807.16 | 98.74
07:00 | 0 | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 554 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 302 | 0 | 0 | 0 | 332 | 135 | 0 | 5 | 70 | 19.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 25 | 25 | 0.58 | 204 | 0 | 20 | 650 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 842 | 1 | 51 | 0 | 71 | 0 | 350 | 300 | 50 | 197 | 16 | 74 | 0 | 166 | 5 | 20 | 97 | 24 | 52.2 | 10 | 16 | 0 | 320 | 380 | 0 | 60 | 150 | 8 | 0 | 85 | 30 | 0 | 18 | 172 | 0 | 93 | 84 | 100 | 0 | 9.18 | 0 | 6685.46 | 871 | 296 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 23 | 836 | 0 | 847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.13 | 203 | 0 | 170 | 0 | 170 | 0 | 353 | 0 | 0.86 | 156 | 48 | 115 | 7 | 104 | 0 | 0 | 0.3 | 32 | 0.13 | 0 | 202 | 120 | 190 | 0 | 396 | 850 | 0 | 6038.42 | 12723.88 | 98.73
08:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 305 | 0 | 0 | 0 | 327 | 135 | 0 | 14 | 70 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 25 | 25 | 0.88 | 210 | 0 | 2 | 642 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 842 | 3 | 51 | 0 | 71 | 0 | 349 | 300 | 50 | 194 | 16 | 74 | 0 | 165 | 9 | 20 | 96 | 24 | 52.2 | 17 | 16 | 0 | 320 | 360 | 0 | 60 | 149 | 7 | 0 | 79 | 30 | 0 | 18 | 172 | 16 | 92 | 100 | 101 | 1 | 8.76 | 0 | 6718.84 | 870 | 298 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 35 | 826 | 0 | 854.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.82 | 173 | 0 | 167 | 0 | 168 | 0 | 346 | 0 | 0.93 | 153 | 48 | 115 | 10 | 113 | 0 | 0 | 1.5 | 82 | 0.31 | 0 | 198 | 120 | 190 | 0 | 396 | 830 | 0 | 6041.96 | 12760.8 | 98.73
09:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 0 | 17 | 23 | 0 | 0 | 0 | 8 | 0 | 0 | 130 | 308 | 0 | 0 | 0 | 326 | 133 | 0 | 12 | 70 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 25 | 25 | 1.09 | 209 | 0 | 2 | 656 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 847 | 9 | 51 | 0 | 71 | 0 | 345 | 300 | 48 | 197 | 13 | 74 | 0 | 173 | 9 | 20 | 96 | 24 | 52.2 | 14 | 15 | 0 | 320 | 376 | 0 | 60 | 154 | 7 | 0 | 79 | 30 | 0 | 18 | 172 | 17 | 92 | 100 | 99 | 1 | 22.82 | 0 | 6801.11 | 870 | 310 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 54 | 878 | 0 | 857.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.29 | 158 | 0 | 171 | 0 | 173 | 0 | 355 | 0 | 2.21 | 153 | 48 | 115 | 18 | 113 | 0 | 0 | 1.6 | 100 | 0.56 | 0 | 203 | 120 | 190 | 0 | 394 | 800 | 0 | 6131.57 | 12932.68 | 98.73
10:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 40 | 19 | 38 | 0 | 0 | 0 | 35 | 7 | 26 | 130 | 292 | 0 | 0 | 0 | 326 | 132 | 0 | 17 | 52 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 25 | 13 | 1.7 | 208 | 0 | 2 | 650 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 822 | 2 | 51 | 0 | 71 | 0 | 345 | 340 | 45 | 193 | 13 | 73 | 0 | 173 | 8 | 17 | 96 | 26 | 52.2 | 42 | 15 | 0 | 320 | 364 | 0 | 60 | 156 | 7 | 0 | 79 | 30 | 0 | 18 | 172 | 28 | 92 | 100 | 98 | 1 | 19.09 | 0 | 6870.99 | 870 | 320 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 88 | 584 | 0 | 855.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 10.4 | 156 | 0 | 176 | 0 | 171 | 0 | 398 | 0 | 0.99 | 160 | 48 | 115 | 24 | 113 | 0 | 0 | 3.3 | 86 | 0.43 | 0 | 198 | 120 | 220 | 0 | 395 | 810 | 0 | 6026.22 | 12897.21 | 98.73
11:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 452 | 54 | 17 | 70 | 0 | 0 | 0 | 35 | 16 | 32 | 350 | 302 | 0 | 0 | 0 | 322 | 132 | 0 | 32 | 52 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 25 | 25 | 3.01 | 208 | 0 | 2 | 673 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 857 | 7 | 51 | 0 | 71 | 0 | 210 | 340 | 45 | 204 | 20 | 75 | 0 | 173 | 9 | 17 | 52 | 26 | 34 | 65 | 15 | 0 | 320 | 337 | 0 | 60 | 146 | 7 | 0 | 79 | 30 | 0 | 18 | 172 | 35 | 82 | 85 | 98 | 2 | 36.28 | 0 | 6938.29 | 870 | 318 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 55 | 595 | 0 | 872.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 24.45 | 159 | 0 | 183 | 0 | 173 | 0 | 370 | 0 | 2.66 | 158 | 48 | 70 | 26 | 70 | 0 | 0 | 3.1 | 199 | 0.84 | 0 | 174 | 120 | 220 | 0 | 347 | 850 | 0 | 6011.45 | 12949.74 | 98.73
12:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556 | 54 | 17 | 70 | 0 | 0 | 0 | 36 | 53 | 16 | 420 | 305 | 0 | 0 | 0 | 321 | 192 | 0 | 35 | 52 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 25 | 25 | 3.29 | 209 | 0 | 2 | 714 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1031 | 12 | 51 | 0 | 122 | 0 | 10 | 340 | 46 | 197 | 23 | 73 | 0 | 185 | 9 | 19 | 52 | 28 | 34 | 48 | 29 | 0 | 320 | 385 | 0 | 60 | 154 | 7 | 0 | 82 | 30 | 0 | 18 | 171 | 35 | 82 | 95 | 93 | 3 | 50.13 | 0 | 7359.42 | 870 | 318 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 93 | 594 | 0 | 1003.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 22.09 | 158 | 0 | 179 | 0 | 200 | 0 | 351 | 0 | 2.59 | 159 | 48 | 70 | 18 | 70 | 0 | 0 | 6.1 | 162 | 0.35 | 0 | 225 | 120 | 220 | 0 | 347 | 895 | 0 | 6285.03 | 13644.45 | 98.73
13:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556 | 54 | 17 | 70 | 0 | 0 | 0 | 55 | 104 | 16 | 420 | 306 | 0 | 0 | 0 | 321 | 190 | 0 | 30 | 52 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 25 | 25 | 1.57 | 210 | 0 | 4 | 724 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1051 | 16 | 51 | 0 | 168 | 0 | 0 | 340 | 45 | 202 | 26 | 74 | 0 | 180 | 9 | 19 | 70 | 30 | 34 | 35 | 34 | 0 | 320 | 388 | 0 | 60 | 157 | 8 | 0 | 82 | 30 | 0 | 18 | 172 | 35 | 72 | 120 | 82 | 2 | 29.34 | 0 | 7499.91 | 870 | 315 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 72 | 601 | 0 | 1029.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 43.34 | 167 | 0 | 179 | 0 | 200 | 0 | 405 | 0 | 2.57 | 156 | 48 | 70 | 21 | 68 | 0 | 0 | 1 | 152 | 0.32 | 0 | 251 | 120 | 220 | 0 | 346 | 1044 | 0 | 6495.79 | 13995.7 | 98.73
14:00 | 0 | 37 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556 | 54 | 17 | 70 | 0 | 0 | 0 | 55 | 101 | 16 | 450 | 300 | 0 | 0 | 0 | 320 | 189 | 0 | 28 | 52 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 33 | 0 | 0 | 25 | 25 | 2.17 | 211 | 0 | 2 | 707 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1125 | 12 | 51 | 0 | 177 | 0 | 0 | 335 | 45 | 195 | 23 | 74 | 0 | 184 | 9 | 17 | 97 | 30 | 34 | 44 | 35 | 0 | 320 | 376 | 0 | 60 | 155 | 8 | 0 | 78 | 30 | 0 | 18 | 173 | 35 | 82 | 140 | 69 | 2 | 36.81 | 0 | 7593.98 | 871 | 306 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 1070.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 34.91 | 177 | 0 | 187 | 0 | 195 | 0 | 380 | 0 | 1.71 | 156 | 48 | 70 | 19 | 68 | 0 | 0 | 1.3 | 156 | 0.08 | 0 | 252 | 120 | 220 | 0 | 406 | 1110 | 0 | 6035.66 | 13629.64 | 98.73
15:00 | 0 | 52 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 54 | 17 | 70 | 16 | 80 | 4 | 55 | 132 | 16 | 450 | 300 | 0 | 0 | 20 | 319 | 190 | 0 | 25 | 108 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 33 | 0 | 0 | 12 | 25 | 2.7 | 211 | 0 | 2 | 717 | 10 | 0 | 0 | 0 | 10 | 218 | 0 | 0 | 0 | 1156 | 14 | 51 | 6 | 177 | 0 | 0 | 335 | 45 | 196 | 20 | 73 | 0 | 183 | 8 | 19 | 97 | 30 | 39 | 53 | 33 | 0 | 320 | 388 | 0 | 60 | 155 | 8 | 0 | 78 | 20 | 0 | 18 | 169 | 35 | 82 | 124 | 71 | 1 | 37.12 | 0 | 7882.82 | 870 | 308 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 21 | 20 | 0 | 0 | 1155.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 40.59 | 186 | 0 | 185 | 0 | 188 | 0 | 390 | 0 | 3.81 | 156 | 47 | 95 | 24 | 90 | 0 | 0 | 4.9 | 122 | 0.18 | 0 | 307 | 117 | 220 | 0 | 501 | 1170 | 0 | 6331.85 | 14214.67 | 98.73
16:00 | 12 | 65 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556 | 35 | 17 | 101 | 0 | 145 | 25 | 55 | 150 | 0 | 450 | 297 | 0 | 0 | 35 | 318 | 190 | 0 | 18 | 108 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 33 | 0 | 0 | 25 | 25 | 2.47 | 212 | 8 | 2 | 693 | 17 | 0 | 11 | 0 | 32 | 217 | 0 | 0 | 0 | 1145 | 10 | 51 | 75 | 177 | 0 | 0 | 340 | 44 | 194 | 18 | 73 | 0 | 179 | 9 | 17 | 97 | 30 | 52.2 | 36 | 20 | 0 | 320 | 365 | 0 | 60 | 135 | 8 | 0 | 80 | 20 | 0 | 18 | 170 | 35 | 90 | 144 | 69 | 1 | 26.68 | 0 | 8042.35 | 870 | 304 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 85 | 33 | 0 | 0 | 1159.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 30.11 | 178 | 0 | 177 | 0 | 167 | 0 | 347 | 0 | 2.14 | 156 | 48 | 70 | 16 | 70 | 0 | 0 | 5.3 | 100 | 0.08 | 8 | 278 | 117 | 220 | 0 | 559 | 1140 | 27 | 6258.12 | 14300.47 | 98.73
17:00 | 15 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 35 | 17 | 114 | 0 | 95 | 30 | 55 | 108 | 0 | 450 | 303 | 0 | 0 | 17 | 321 | 133 | 0 | 7 | 70 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 25 | 25 | 0.57 | 212 | 31 | 11 | 697 | 17 | 0 | 17 | 0 | 32 | 217 | 0 | 0 | 0 | 1144 | 4 | 51 | 80 | 184 | 0 | 0 | 280 | 44 | 195 | 26 | 74 | 0 | 175 | 8 | 19 | 97 | 28 | 52.2 | 11 | 24 | 0 | 320 | 381 | 0 | 60 | 148 | 8 | 0 | 83 | 30 | 0 | 18 | 170 | 35 | 90 | 110 | 69 | 0 | 12.81 | 4 | 7776.58 | 871 | 301 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 85 | 37 | 0 | 0 | 1155.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 12.49 | 167 | 0 | 185 | 0 | 168 | 0 | 393 | 0 | 1.27 | 157 | 48 | 70 | 3 | 70 | 0 | 0 | 0.5 | 59 | 0.15 | 16 | 229 | 117 | 220 | 0 | 559 | 1120 | 27 | 6138.68 | 13915.26 | 98.73
18:00 | 15 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 35 | 17 | 113 | 0 | 95 | 30 | 55 | 96 | 0 | 380 | 305 | 0 | 0 | 17 | 325 | 133 | 0 | 2 | 70 | 25.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 12 | 25 | 0 | 212 | 30 | 11 | 711 | 17 | 0 | 19 | 0 | 31 | 217 | 0 | 0 | 0 | 1095 | 0 | 51 | 80 | 185 | 0 | 0 | 280 | 45 | 195 | 26 | 73 | 0 | 175 | 11 | 19 | 97 | 28 | 52.2 | 5 | 28 | 0 | 320 | 325 | 0 | 60 | 151 | 8 | 0 | 83 | 30 | 0 | 18 | 171 | 35 | 89 | 110 | 69 | 0 | 1.99 | 12 | 7591.69 | 870 | 299 | 0 | 0 | 3 | 38 | 0 | 0 | 0 | 0 | 85 | 10 | 0 | 0 | 1164.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 3.06 | 160 | 0 | 192 | 0 | 163 | 0 | 394 | 0 | 0.27 | 158 | 47 | 70 | 1 | 70 | 0 | 0 | 0 | 8 | 0.04 | 16 | 229 | 120 | 220 | 0 | 558 | 1080 | 35 | 5997.59 | 13589.28 | 98.73
19:00 | 16 | 105 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 35 | 17 | 114 | 80 | 145 | 34 | 55 | 108 | 0 | 450 | 303 | 0 | 0 | 45 | 322 | 190 | 0 | 0 | 125 | 26 | 22 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 65 | 21 | 0 | 25 | 25 | 0 | 212 | 32 | 12 | 744 | 35 | 0 | 22 | 1 | 34 | 216 | 0 | 0 | 0 | 1182 | 0 | 51 | 102 | 185 | 0 | 0 | 325 | 45 | 208 | 27 | 73 | 0 | 185 | 17 | 19 | 97 | 32 | 52.2 | 0 | 34 | 0 | 320 | 386 | 0 | 60 | 154 | 8 | 0 | 84 | 30 | 0 | 18 | 171 | 35 | 88 | 156 | 69 | 0 | 0 | 12 | 8478.2 | 871 | 296 | 0 | 7 | 14 | 38 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 17 | 1238.67 | 0 | 13 | 0 | 11 | 4 | 70 | 50 | 12 | 0 | 0 | 26 | 0 | 175 | 0 | 199 | 0 | 178 | 0 | 402 | 0 | 0 | 158 | 47 | 90 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 32 | 285 | 120 | 220 | 0 | 560 | 1060 | 54 | 6420.67 | 14898.87 | 98.73
19:30 | 56 | 105 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 35 | 17 | 134 | 132 | 245 | 55 | 55 | 161 | 0 | 450 | 307 | 0 | 0 | 55 | 323 | 191 | 0 | 0 | 125 | 26 | 22 | 0 | 0 | 16 | 32 | 0 | 0 | 0 | 64 | 23 | 0 | 25 | 25 | 0 | 212 | 40 | 18 | 725 | 160 | 0 | 40 | 8 | 73 | 217 | 0 | 0 | 0 | 1190 | 0 | 51 | 129 | 185 | 0 | 0 | 340 | 45 | 202 | 28 | 73 | 0 | 200 | 17 | 20 | 97 | 32 | 52.2 | 0 | 36 | 0 | 320 | 388 | 0 | 60 | 156 | 8 | 0 | 85 | 30 | 0 | 18 | 172 | 35 | 79 | 157 | 69 | 0 | 0 | 12 | 9045.2 | 870 | 294 | 0 | 32 | 22 | 38 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 34 | 1277.84 | 0 | 25 | 0 | 90 | 5 | 95 | 90 | 19 | 0 | 0 | 30 | 0 | 192 | 0 | 202 | 0 | 203 | 0 | 407 | 0 | 0 | 157 | 47 | 90 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 48 | 291 | 120 | 220 | 0 | 559 | 1110 | 72 | 6837.84 | 15883.04
20:00 | 64 | 105 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505 | 35 | 17 | 133 | 142 | 260 | 55 | 55 | 155 | 0 | 450 | 276 | 0 | 0 | 55 | 327 | 132 | 0 | 0 | 125 | 26 | 22 | 0 | 0 | 17 | 32 | 0 | 0 | 0 | 64 | 31 | 0 | 25 | 25 | 0 | 211 | 44 | 20 | 770 | 160 | 0 | 43 | 17 | 83 | 217 | 0 | 0 | 0 | 1224 | 0 | 51 | 128 | 185 | 0 | 0 | 335 | 45 | 187 | 28 | 73 | 0 | 196 | 18 | 20 | 97 | 32 | 52.2 | 0 | 36 | 0 | 320 | 358 | 0 | 60 | 150 | 8 | 0 | 84 | 30 | 0 | 18 | 170 | 35 | 80 | 156 | 69 | 0 | 0 | 12 | 8987.2 | 870 | 290 | 0 | 35 | 24 | 38 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 34 | 1255.86 | 0 | 32 | 0 | 95 | 5 | 95 | 108 | 31 | 0 | 0 | 28 | 0 | 186 | 0 | 197 | 0 | 200 | 0 | 336 | 0 | 0 | 157 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 64 | 309 | 120 | 220 | 0 | 560 | 1160 | 81 | 6890.86 | 15878.06 | 98.73
21:00 | 64 | 105 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 35 | 17 | 120 | 111 | 160 | 30 | 55 | 144 | 0 | 450 | 300 | 0 | 0 | 55 | 327 | 195 | 0 | 0 | 125 | 26 | 22 | 0 | 0 | 77 | 32 | 1 | 0 | 0 | 64 | 56 | 0 | 25 | 25 | 0 | 210 | 51 | 20 | 740 | 35 | 0 | 40 | 22 | 94 | 218 | 0 | 0 | 0 | 1224 | 0 | 51 | 80 | 185 | 0 | 0 | 340 | 46 | 192 | 31 | 73 | 0 | 200 | 18 | 20 | 97 | 32 | 52.2 | 0 | 36 | 0 | 320 | 360 | 0 | 60 | 146 | 8 | 0 | 84 | 28 | 0 | 18 | 170 | 35 | 90 | 158 | 69 | 0 | 0 | 12 | 8873.2 | 870 | 281 | 0 | 30 | 25 | 38 | 0 | 0 | 0 | 0 | 85 | 0 | 125 | 34 | 1257 | 0 | 38 | 0 | 70 | 6 | 95 | 70 | 37 | 25 | 0 | 28 | 0 | 177 | 0 | 182 | 0 | 178 | 0 | 395 | 0 | 0 | 158 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 96 | 309 | 120 | 220 | 0 | 560 | 1232 | 117 | 7133 | 16006.2 | 98.73
22:00 | 8 | 105 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 35 | 0 | 105 | 111 | 95 | 15 | 55 | 145 | 8 | 450 | 303 | 0 | 0 | 55 | 326 | 196 | 0 | 0 | 125 | 26 | 22 | 0 | 0 | 15 | 65 | 22 | 0 | 0 | 64 | 39 | 0 | 25 | 25 | 0 | 210 | 68 | 20 | 754 | 17 | 0 | 40 | 25.5 | 97 | 217 | 0 | 0 | 0 | 1145 | 0 | 51 | 80 | 185 | 0 | 0 | 335 | 46 | 196 | 31 | 73 | 0 | 196 | 18 | 20 | 96 | 32 | 52.2 | 0 | 36 | 0 | 320 | 380 | 0 | 60 | 153 | 8 | 0 | 84 | 28 | 0 | 18 | 171 | 35 | 90 | 158 | 69 | 0 | 0 | 12 | 8653.7 | 870 | 279 | 0 | 30 | 20 | 38 | 0 | 0 | 0 | 0 | 85 | 0 | 270 | 34 | 1344 | 0 | 38 | 0 | 70 | 15 | 95 | 70 | 37 | 52.2 | 0 | 28 | 0 | 181 | 0 | 190 | 0 | 191 | 0 | 414 | 0 | 0 | 160 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 64 | 278 | 120 | 220 | 0 | 561 | 1145 | 124 | 7298.2 | 15951.9 | 98.73
23:00 | 7 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 35 | 0 | 104 | 111 | 95 | 15 | 55 | 146 | 16 | 450 | 300 | 0 | 0 | 55 | 327 | 196 | 0 | 0 | 125 | 20.4 | 22 | 0 | 0 | 15 | 65 | 24 | 0 | 0 | 65 | 39 | 0 | 25 | 25 | 0 | 210 | 61 | 22 | 753 | 17 | 0 | 40 | 25.5 | 92 | 219 | 0 | 0 | 0 | 1134 | 0 | 51 | 80 | 185 | 0 | 0 | 340 | 47 | 192 | 31 | 86 | 0 | 200 | 17 | 20 | 96 | 34 | 52.2 | 0 | 36 | 0 | 320 | 362 | 0 | 60 | 153 | 8 | 0 | 84 | 28 | 0 | 18 | 170 | 35 | 90 | 158 | 69 | 0 | 0 | 12 | 8638.1 | 869 | 274 | 0 | 30 | 20 | 38 | 0 | 0 | 0 | 0 | 85 | 0 | 331 | 49 | 1307 | 0 | 43 | 0 | 70 | 15 | 95 | 70 | 37 | 52.2 | 0 | 28 | 0 | 182 | 0 | 191 | 0 | 190 | 0 | 397 | 0 | 0 | 161 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 64 | 275 | 120 | 220 | 0 | 559 | 1120 | 133 | 7300.2 | 15938.3 | 98.73
Total KWH | 238608 | 1140480 | 553440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13048480 | 664200 | 381240 | 1570752 | 608160 | 1161960 | 269028 | 790401 | 1789920 | 242880 | 8199000 | 7271011 | 0 | 0 | 376358 | 7814985 | 4008000 | 0 | 211944 | 2074800 | 483000 | 519840 | 0 | 0 | 176891 | 258436 | 73920 | 0 | 21600 | 1302997 | 257568 | 0 | 582720 | 598080 | 18785 | 5034762 | 398100 | 410400 | 17032727.27 | 296073 | 0 | 279360 | 119710.8 | 601345 | 5220043 | 0 | 0 | 0 | 25047270 | 88695 | 1179520 | 863127 | 3044364 | 0 | 4150400 | 7866000 | 1126560 | 4848000 | 514584 | 1822080 | 0 | 4377600 | 223440 | 435500 | 2217300 | 674880 | 1176485 | 390373 | 652848 | 0 | 7671400 | 9353000 | 0 | 1392240 | 3663900 | 182952 | 0 | 1967040 | 685536 | 0 | 432000 | 3523150 | 665640 | 2078400 | 3038400 | 1981440 | 12500 | 271840 | 115200 | 183835669.07 | 20988363 | 7114176 | 0 | 132960 | 114768 | 912000 | 0 | 0 | 0 | 0 | 767376 | 596160 | 12610909 | 207360 | 25626573 | 0 | 178854 | 0 | 423168 | 43723 | 483424 | 385920 | 151618 | 133118 | 490430 | 134000 | 243752 | 4409727 | 0 | 4726164 | 0 | 4712482 | 0 | 9281963 | 0 | 24480 | 3821000 | 1083927 | 2443922 | 189101 | 2368905 | 0 | 0 | 31027.2 | 1266480 | 3486 | 424320 | 5694000 | 2870000 | 5303100 | 0 | 10916364 | 25271272.73 | 685200 | 157265572.93 | 341101242

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 20-07-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-07-2025 | during | 20-07-2025 | during | 20-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 0 | 0 | 0 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 305 | 300 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 192 | 195 | 208.13 | 208.13 | 202 | 202 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 321 | 327 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 64 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 54 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 111 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 36 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 26 | 33 | 33 | 26 | 26 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 33 | 32 | 52.19 | 52.19 | 42 | 42 | Engine Problem
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 160 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 70 | 120 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 16 | 0 | 104 | 104 | 50 | 50 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 53 | 144 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 35 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 35 | 35 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 556 | 555 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 125 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2236 | 2928 | 4721.65 | 4787.65 | 3272.83 | 3338.83
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 22 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 12 | 0 | 5 | 0 | 5 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 40 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 209 | 210 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 218 | 218 | 213 | 213 | 213 | 213 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 94 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 56 | 80 | 80 | 80 | 80 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 33 | 64 | 65 | 65 | 68 | 68 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 20 | 2 | 25 | 2 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 1 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.29 | 0 | 2.48 | 0 | 2.48 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 32 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 51 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 77 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 35 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1031 | 1224 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 4 | 0 | 4 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 714 | 740 | 790 | 790 | 790 | 790 | FGMO
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 2272.29 | 2934 | 3820.2 | 3839.72 | 3793.2 | 3812.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 197 | 192 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 10 | 0 | 353.35 | 353.35 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 340 | 340 | 340 | 340 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 23 | 31 | 46.7 | 46.7 | 31 | 31 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 46 | 46 | 55 | 55 | 51 | 51 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 122 | 185 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 80 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 29 | 36 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 185 | 200 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 28 | 32 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 97 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 18 | 113 | 113 | 9 | 37 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 73 | 73 | 115 | 115 | 115 | 115 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 48 | 0 | 40 | 0 | 40 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.491 | 1266 | 1453.2 | 2440.75 | 2400.75 | 1780.2 | 1768.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-07-2025 | during | 20-07-2025 | during | 20-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 93 | 69 | 157.5 | 157.5 | 101 | 101 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 3 | 0 | 1.8 | 0 | 1.8 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 95 | 158 | 200 | 200 | 186 | 186 | Engine Problem
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 82 | 90 | 115 | 115 | 105 | 105 | Engine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 50.13 | 0 | 33 | 0 | 33 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 35 | 35 | 54.5 | 54.5 | 35 | 35 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 358.13 | 364 | 583.8 | 549 | 473.8 | 439
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 60 | 60 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 154 | 146 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 28 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 84 | 85 | 85 | 85 | 85 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 171 | 170 | 172 | 172 | 172 | 172 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 7 | 8 | 25 | 25 | 8 | 8 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | Plant Shutdown as per schedule HGPI work
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 385 | 360 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1227 | 1194 | 1258 | 1258 | 1197 | 1197
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 870 | 870 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 30 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 25 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 318 | 281 | 410 | 410 | 320 | 320 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 34 | 105 | 105 | 60 | 60 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 85 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 93 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 594 | 125 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1913 | 1488 | 3642.2 | 3552.2 | 3507 | 3417
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 347 | 560 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 96 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 895 | 1232 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 117 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 225 | 309 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.35 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1807.35 | 2654 | 2162 | 2161 | 2102 | 2101
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 38 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 6 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 158 | 177 | 214 | 214 | 190 | 190 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 179 | 182 | 220 | 220 | 198 | 198 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 200 | 178 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 351 | 395 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 32 | 32 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 95 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.59 | 0 | 4.2 | 0 | 4.2 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1003.9 | 1257 | 1435.88 | 1435.88 | 1355 | 1355 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 22.09 | 0 | 25 | 0 | 25 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 115 | 0 | 75 | 0 | 75 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 2031.58 | 2558 | 3133.07 | 3028.87 | 2962.4 | 2858.2
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 47 | 50 | 50 | 50 | 50 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 159 | 158 | 150 | 150 | 155 | 155 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 70 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.1 | 0 | 4.2 | 0 | 4.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 70 | 115 | 115 | 115 | 95 | 95 | Engine Problem
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 18 | 0 | 18 | 0 | 18 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 162 | 0 | 107.47 | 0 | 107.47 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 533.1 | 433 | 591.67 | 462 | 576.67 | 447
System Total |  |  |  |  | 28565.2 | 27046.305 | 13644.45 | 16006.2 | 22353.34 | 22039.19 | 19665.1 | 19378.95
Forecast Scenario (20-07-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15850 |  | 0 |  | 15850
|  |  |  | 1:00 | 15600 |  | 0 |  | 15600
|  |  |  | 2:00 | 15450 |  | 0 |  | 15450
|  |  |  | 3:00 | 15050 |  | 0 |  | 15050
|  |  |  | 4:00 | 14850 |  | 0 |  | 14850
|  |  |  | 5:00 | 14500 |  | 0 |  | 14500
|  |  |  | 6:00 | 14050 |  | 0 |  | 14050
|  |  |  | 7:00 | 14200 |  | 0 |  | 14200
|  |  |  | 8:00 | 14220 |  | 0 |  | 14220
|  |  |  | 9:00 | 14500 |  | 0 |  | 14500
|  |  |  | 10:00 | 14660 |  | 0 |  | 14660
|  |  |  | 11:00 | 15030 |  | 0 |  | 14030
|  |  |  | 12:00 | 15110 |  | 0 |  | 14110
|  |  |  | 13:00 | 15310 |  | 0 |  | 14310
|  |  |  | 14:00 | 14890 |  | 0 |  | 13890
|  |  |  | 15:00 | 14660 |  | 0 |  | 13660
|  |  |  | 16:00 | 14030 |  | 0 |  | 13030
|  |  |  | 17:00 | 13540 |  | 0 |  | 12540
|  |  |  | 18:00 | 13370 |  | 0 |  | 12370
|  |  |  | 18:30 | 14100 |  | 0 |  | 13100
|  |  |  | 19:00 | 14880 |  | 0 |  | 13880
|  |  |  | 19:30 | 15760 |  | 0 |  | 14760
|  |  |  | 20:00 | 15800 |  | 0 |  | 14800
|  |  |  | 21:00 | 16080 |  | 0 |  | 15080
|  |  |  | 22:00 | 16150 |  | 0 |  | 15150
|  |  |  | 23:00 | 15900 |  | 0 |  | 14900
Probable Maximum Temperature: |  |  | 32.10°C
Probable Maximum Demand at Day Peak: |  |  | 14660.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 15080.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16080.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 357.68 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:44 hrs on 20-07-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 19-07-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13644.45 | MW | 12:00 Hr. | Energy Generated |  |  | 341.1012 |  | MKWHr.
| Day Peak Demand |  |  | 13644.45 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.96 |  | MKWHr.
| Evening Peak Generation |  |  | 16006.2 | MW | 21:00 Hr. | Energy Demand |  |  | 342.0612 |  | MKWHr.
| Evening Peak Demand |  |  | 16129.51 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.3 |  | °C
| Minimum Generation of the Day |  |  | 12723.88 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 1034.84 |  | MMCFD
| Maximum Generation of the Day |  |  | 16006.2 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.2976 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 41.3443 | 0 | 11.8622 | 0 | 0 | 0.21194 | 0 | 0 | 53.4185 | Gas | 139.41 | Gas | 469352536.59
| Chattogram Zone |  |  | 5.6304 | 42.08 | 4.9452 | 0 | 5.0348 | 0.10748 | 0 | 0.0216 | 57.8195 | Coal | 101.4775 | Coal | 573264780.0365
| Cumilla Zone |  |  | 23.1649 | 0 | 11.3329 | 0 | 0 | 0.39037 | 0.67488 | 0 | 35.5631 | HFO | 43.1166 | HFO | 799842460.006
| Mymensingh Zone |  |  | 1.9814 | 0 | 5.8976 | 0 | 0 | 0.28434 | 0 | 0 | 8.1634 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.8712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.8712 | Hydro | 5.0348 | Hydro | 503476.2
| Khulna Zone |  |  | 7.1142 | 12.6109 | 1.2225 | 0 | 0 | 0.59616 | 21.9004 | 0 | 43.4441 | Solar | 3.8391 | Solar | 63467306.982
| Barishal Zone |  |  | 8.1731 | 41.8816 | 1.1095 | 0 | 0 | 0.003486 | 0 | 0 | 51.1677 | Import | 48.2018 | Import | 241363500.9
| Rajshahi Zone |  |  | 23.1303 | 0 | 1.9338 | 0 | 0 | 0.75866 | 25.6266 | 0 | 51.4494 | Wind | 0.0216 | Wind | 316224
| Rangpur Zone |  |  | 0 | 4.9049 | 4.8128 | 0 | 0 | 1.4866 | 0 | 0 | 11.2044
| Total |  |  | 139.41 | 101.4775 | 43.1166 | 0 | 5.0348 | 3.8391 | 48.2018 | 0.0216 | 341.1012
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 469352536.59 |  | Hydro | 503476.2
|  |  |  | Coal | 573264780.0365 |  | Solar | 63467306.982
|  |  |  | HFO | 799842460.006 |  | Import | 241363500.9
|  |  |  | HSD | 0 |  | Wind | 316224
[5 empty] | Total: | 214,81,10,284 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.9884 | Peak Hr Flow | 870.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 40408545.54 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 25.6266 | Peak Hr Flow | 1257.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 894 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.67488 | Peak Hr Flow | 32.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 1008 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 47.2898 | Peak Hr Flow | 2159.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5499
|  |  |  | Chattogram |  | 0 |  | 1452
|  |  |  | Cumilla |  | 20 |  | 1451
|  |  |  | Mymensingh |  | 20 |  | 1286
|  |  |  | Sylhet |  | 0 |  | 702
|  |  |  | Khulna |  | 0 |  | 1878
|  |  |  | Barishal |  | 0 |  | 496
|  |  |  | Rajshahi |  | 0 |  | 1700
|  |  |  | Rangpur |  | 78 |  | 1121
|  |  |  | Total |  | 118 |  | 15585
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Bibiana-II 341 MW CCPP (Summit) GT |  |  | 222 | 3 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
|  | 4 | Bibiana-II 341 MW CCPP (Summit) ST |  |  | 119
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 641 |  |  |  | Total | 476
|  |  |  | Total Unavailable Capacity |  |  |  | 1117
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:21 | 11:12 | Mahasthangarh 132/33kV S/S 406T MTR1 LT Scheduled S/D Due to MTR-01 LT side bushing Red
hot.
| 08:22 | 11:12 | Mahasthangarh 132/33kV S/S 406T MTR1 HT Scheduled S/D
| 08:27 | 09:40 | Meghnaghat 230/132kV S/S Meghnaghat-ST (MPL) Scheduled S/D Due to DS heating problem | [7 empty] | 120.0MW load
interrup.
|  | 08:29 | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T HT is restored.
|  | 08:31 | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T LT is restored.
| 08:35 | 15:35 | Bogura 400/230kV S/S ATR-02 HT Scheduled S/D Due to ATR-02 Painting.
| 08:35 | 15:35 | Bogura 400/230kV S/S ATR-02 LT Scheduled S/D Due to ATR-02 Painting.
| 08:37 |  | Maijdee 132/33kV S/S Chowmuhoni-Maijdee ckt -01 Scheduled S/D Due to Chowmuhani 230/132
KV GIS S/S interlocking test,testing activities related to Tr-1 and Maijdee line bay-2.
| 08:40 | 09:41 | Barapukuria 230/132/33kV S/S 230/132 KV T-02, 713T HT Scheduled S/D Due to Red hot
maintenance work
| 08:40 | 09:42 | Barapukuria 230/132/33kV S/S 230/132 KV T-02, 713T LT Scheduled S/D Due to Red hot
maintenance work.
| 09:00 |  | Lakshmipur 132/33kV S/S Lakshmipur-Chowmuhani Circuit 1 Project Work S/D | [7 empty] | 25.0MW load
interrup.
| 09:15 |  | Ashuganj-Brahmanbaria 132kV Ckt-2 Scheduled S/D from Brahmanbaria 132/33kV end Due to
Project work and from Ashuganj 230/132/33kV end Due to 132KV GIS project work
| 09:22 | 13:02 | Sherpur 132/33kV S/S Transformer- 01 LT Scheduled S/D Due to Red Hot 33 KV Bus Side | [7 empty] | 15.0MW load
interrup.
| 09:22 | 13:02 | Sherpur 132/33kV S/S Transformer- 01 HT Scheduled S/D Due to Red hot 33 KV Remove Bus | [7 empty] | 15.0MW load
|  |  | Side | [7 empty] | interrup.
| 09:24 |  | Rampal 1320 MW (BIFPCL) Shutdown with remarks:- U2
| 09:24 |  | Rampal 1320 MW (BIFPCL) unit-2 was shutdown due to Generator DAVR system checking.
| 09:25 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- unit-2 ( False )
| 09:25 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- unit-1 ( False )
| 09:32 | 10:52 | Bog-Sherpur 132/33kV S/S Main Bus-1 Scheduled S/D Due to For installation work of
transformer 3
| 09:42 | 12:46 | Haripur-Sonargaon 132kV Ckt-2 Scheduled S/D from Sonargaon 132/33kV end Due to
Conductor Repairing work at Sonargaon - Haripur ckt 2 ( B phase). and from Haripur
230/132kV end Due to ordered by NLDC
| 09:46 |  | Ashuganj-Ghorasal 132kV Ckt-1 Project Work S/D from Ashuganj 230/132/33kV end Due to
132KV GIS project work
| 09:50 | 16:14 | Shahjibazar 132/33kV S/S TR-02 LT Scheduled S/D Due to Shutdown taken by PDB for changing
Isolator.
| 09:50 |  | Ishurdi - Pabna 100mw solar 132kv Ckt 1&2 Syn.
| 09:51 | 16:10 | Shahjibazar 132/33kV S/S TR-02 HT Scheduled S/D Due to Shutdown taken by PDB for changing
Isolator.
| 10:01 | 14:03 | Mithapukur-Palashbari 132kV Ckt-2 Forced S/D from Mithapukur 132/33kV end Due to
According to order of ALDC Bogura. and from Palashbari 132/33kV end Due to Red hot
Maintenance
| 10:18 |  | Meghnaghat 450MW CCPP ST was sync.
| 10:24 | 12:45 | Jaldhaka 132/33kV S/S 406T-1 LT Forced S/D Due to Red-hot at B phase in jaldhaka 33 kv | [7 empty] | 32.0MW load
|  |  | feeder | [7 empty] | interrup.
| 10:24 | 12:44 | Jaldhaka 132/33kV S/S 406T-1 HT Forced S/D Due to Red hot at B phase in jaldhaka 33kv | [7 empty] | 32.0MW load
|  |  | feeder | [7 empty] | interrup.
| 10:40 |  | Rampal 400/230kV S/S Generator Transformer-2 (GT-2) LT Project Work S/D Due to Electrical
Protection Checking
| 10:43 | 10:49 | Barishal 132/33kV S/S T-2 (415T) LT Tripped showing O/C, E/F relays Due to Kashipur 33 kV | [7 empty] | 42.0MW load
|  |  | feeder fault. | [7 empty] | interrup.
| 11:09 | 13:10 | Bog-Sherpur 132/33kV S/S Main Bus-2 Scheduled S/D Due to For installation work of
transformer 3
| 11:11 | 12:49 | Chapai 132/33kV S/S T-1 (405T) LT Forced S/D Due to Forced shut down # T1 33 kV CB R
phase hot spot maintenance
| 11:11 | 12:48 | Chapai 132/33kV S/S T-1 (405T) HT Forced S/D Due to Forced Shut down
| 11:18 | 17:36 | Mahasthangarh 132/33kV S/S 416T MTR 2 LT Scheduled S/D | [7 empty] | 15.0MW load
interrup.
| 11:21 | 17:35 | Mahasthangarh 132/33kV S/S 416T MTR 2 HT Scheduled S/D | [7 empty] | 15.0MW load
interrup.
| 11:40 |  | BB230 - Ruppoor 230kv Ckt 01 Syn.
| 12:00 |  | Day Peak Generation: 13642 MW.
| 12:01 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- GT
| 12:01 |  | Ashuganj North CCPP was shutdown due to compressor offline water wash.
| 12:08 |  | BB230 - Ruppoor 230kv Ckt 02 Syn.
|  | 12:39 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) HT is restored.
|  | 12:40 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT is restored.
| 13:52 |  | Rampal 1320 MW (BIFPCL) Tripped with remarks:- U1
| 14:18 | 16:05 | Ishwardi-Natore 132kV Ckt-2 Scheduled S/D from Natore 132/33kV end. and from Ishurdi
132/33kVend.
|  | 14:31 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-2 is restored.
|  | 14:32 | Jashore 132/33kV S/S JH-2(L1) is restored.
| 18:36 |  | Raozan 25 MW PP Synchronized
| 20:08 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U1
| 20:08 |  | Rampal 1320 MW (BIFPCL) unit-1 sync.
| 20:08 |  | Rampal 1320 MW (BIFPCL) U-1 Synchronized with remarks:- None
|  | 20:14 | Bogura 132/33kV S/S Transformer-3 HT is restored.
|  | 20:15 | Bogura 132/33kV S/S Transformer-3 LT is restored.
| 21:00 |  | Evening Peak Generation 16006 MW.
| 21:56 | 23:09 | Sirajganj 132/33kV S/S T3-(435) LT Forced S/D Due to Sirajgonj PBS-2 has been taken shut | [7 empty] | 22.0MW load
|  |  | down for emergency Redhot maintenance at Kazipur 33kv CT R-Phase | [7 empty] | interrup.
| 21:57 | 23:09 | Sirajganj 132/33kV S/S T3-(435) HT Forced S/D Due to Sirajgonj PBS-2 has been taken shut
down for emergency Redhot maintenance at Kazipur 33kv CT R-Phase
| 23:04 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- gt
| 01:27 |  | Raozan 25 MW PP Shutdown
| 01:43 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U2
| 01:43 |  | Rampal 1320 MW (BIFPCL) U-2 Synchronized with remarks:- None
| 03:20 |  | BB230 - Ruppoor 230kv Ckt 01 S/D.
| 03:21 |  | BB230 - Ruppoor 230kv Ckt 02 S/D.
| 04:03 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- st
| 04:33 |  | Ishurdi - Pabna 100mw solar 132kv Ckt 1 S/D.
| 04:34 |  | Ishurdi - Pabna 100mw solar 132kv Ckt 2 S/D.
| 06:29 |  | Borhanuddin 230/33kV S/S Tr-Load HT Scheduled S/D Due to Red Hot Maintenance. | [7 empty] | 45.0MW load
interrup.
| 06:30 |  | Barishal 132/33kV S/S T-1 (405T) LT Scheduled S/D Due to Red hot maintenance and loop | [7 empty] | 42.0MW load
|  |  | changing work at 33kV incoming ( 33kV CB to DS ) | [7 empty] | interrup.
| 06:30 |  | Barishal 132/33kV S/S T-1 (405T) HT Scheduled S/D Due to Red hot maintenance and loop | [7 empty] | 42.0MW load
|  |  | changing work at 33kV incoming ( 33kV CB to DS ) | [7 empty] | interrup.
| 07:03 | 07:16 | Cumilla(S) 132/33kV S/S TR-3 LT Tripped showing RET 650 REF 615 relays Due to 33 KV | [7 empty] | 26.0MW load
|  |  | Kaliyajuri feeder Fault | [7 empty] | interrup.
| 07:05 |  | Feni 132/33kV S/S Bus-1 Scheduled S/D Due to Chaumuhani 33kv feeder loop repair | [7 empty] | 27.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 19-07-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8199000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 300 | 7271011 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 30 | 269028 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 195 | 4008000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 327 | 7814985 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 64 | 238608 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 664200 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 111 | 608160 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 790401 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 376358 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 26 | 483000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 519840 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 32 | 553440 | Engine Problem
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 160 | 1161960 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 120 | 1570752 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1140480 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 242880 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1789920 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 211944 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 381240 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 555 | 13048480 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 125 | 2074800 | Engine Problem
Dhaka Area Total |  |  |  |  | 5939.724 | 2928 | 53418487
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 22 | 119710.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 88695 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 40 | 279360 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 210 | 5034762 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 5220043 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 94 | 601345 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 56 | 257568 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 64 | 1302997 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 582720 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 20 | 410400 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 1 | 73920 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 18785 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 32 | 258436 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 51 | 398100 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 598080 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 77 | 176891 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 35 | 296073 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 25047270 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 21600 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 740 | 17032727.27 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.72 | 2934 | 57819483.07
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 192 | 4848000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 4150400 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 340 | 7866000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 31 | 514584 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 46 | 1126560 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 185 | 3044364 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1179520 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 80 | 863127 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 652848 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 4377600 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 32 | 674880 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 1176485 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 435500 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 97 | 2217300 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 18 | 223440 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 73 | 1822080 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 390373 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1453.2 | 35563061
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 69 | 1981440 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12500 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 158 | 3038400 | Engine Problem
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 90 | 2078400 | Engine Problem
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 271840 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 115200 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 665640 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 364 | 8163420
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1392240 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 146 | 3663900 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 28 | 685536 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1967040 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 170 | 3523150 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 432000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 182952 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Plant Shutdown as per schedule HGPI work
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 360 | 9353000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7671400 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1194 | 28871218
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 870 | 20988363 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 30 | 132960 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 25 | 114768 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 281 | 7114176 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 34 | 207360 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 85 | 767376 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 596160 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 125 | 12610909 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1488 | 43444072
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 560 | 10916364 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 96 | 424320 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2870000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1232 | 25271272.73 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5303100 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 117 | 685200 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 309 | 5694000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3486 | -
Barishal Area Total |  |  |  |  | 2236 | 2654 | 51167742.73
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 38 | 178854 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 6 | 43723 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 151618 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 177 | 4409727 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 182 | 4726164 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 178 | 4712482 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 395 | 9281963 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 134000 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 25 | 133118 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 483424 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 423168 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 70 | 385920 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 24480 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1257 | 25626573 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 243752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 490430 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2558 | 51449396
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 47 | 1083927 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 158 | 3821000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 2368905 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 31027.2 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2443922 | Engine Problem
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 189101 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1266480 | -
Rangpur Area Total |  |  |  |  | 950 | 433 | 11204362.2
Eastern Grid Total |  |  |  |  | 16667.715 | 8873.2 | 183835669.07
Western Grid Total |  |  |  |  | 10378.16 | 7133 | 157265572.93
National Grid Total |  |  |  |  | 27045.875 | 16006.2 | 341101242
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 19-07-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10350.51 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5116.6 | MW
i) Dhaka area |  |  | 5498.95 |  | MW | i) Khulna area |  |  |  | 1878 | MW
ii) Chattogram area |  |  | 1452.3 |  | MW | ii) Barishal area |  |  |  | 496 | MW
iii) Cumilla area |  |  | 1431.26 |  | MW | iii) Rajshahi area |  |  |  | 1699.6 | MW
iv) Mymensingh area |  |  | 1266 |  | MW | iv) Rangpur area |  |  |  | 1043 | MW
v) Sylhet area |  |  | 702 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15467.11 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 83 | 19:30 | 133 | PHP | 8 | 10:00
2 | AKSML | 145 | 13:00 | 68 | Ishurdi | 90 | 19:30 | 134 | Pabna | 137 | 20:00
3 | Aftabnagar | 40 | 20:00 | 69 | Jaldhaka | 94 | 19:30 | 135 | Palashbari | 110 | 23:00
4 | Agargaon | 134 | 21:00 | 70 | Jamalpur | 146 | 23:00 | 136 | Panchagarh | 69 | 00:00
5 | Agrabad | 90 | 18:30 | 71 | Jashore | 146 | 21:00 | 137 | Patuakhali | 77.6 | 23:00
6 | Amnura | 42 | 21:00 | 72 | Jhenaidah | 130 | 23:00 | 138 | Payra | 38 | 22:00
7 | Ashuganj | 108 | 23:00 | 73 | Joydebpur | 140 | 19:00 | 139 | Postogola | 63 | 19:00
8 | BSRM | 189 | 00:00 | 74 | Joypurhat | 72 | 22:00 | 140 | Purbachal | 22 | 19:00
9 | Bagerhat | 86 | 22:00 | 75 | Juldah | 13.5 | 00:00 | 141 | Purbasadipur | 151 | 22:00
10 | Bajitpur | 74 | 21:00 | 76 | KSRM | 25 | 09:00 | 142 | Rahanpur | 34 | 22:00
11 | Bakulia | 93 | 19:00 | 77 | Kabirpur | 230 | 19:00 | 143 | Rahim | 23 | 22:00
12 | Banani | 32.8 | 15:00 | 78 | Kachua | 98 | 22:00 | 144 | Rajbari | 89 | 19:30
13 | Bangabhaban | 7 | 11:00 | 79 | Kallyanpur | 114 | 00:00 | 145 | Rajendrapur | 142 | 19:30
14 | Barapukuria | 78 | 21:00 | 80 | Kalurghat | 38 | 11:00 | 146 | Rajshahi | 134 | 21:00
15 | Barguna | 24 | 22:00 | 81 | Kamrangirchar | 78 | 19:00 | 147 | Rajshahi-230 | 88 | 22:00
16 | Barishal | 119 | 21:00 | 82 | Kaptai | N/A | N/A | 148 | Ramganj | 122 | 19:00
17 | Barishal-230 | 104 | 21:00 | 83 | Kasba | 39 | 22:00 | 149 | Rampur | 42 | 23:00
18 | Baroaulia | 70 | 10:00 | 84 | Kazla | 98 | 13:00 | 150 | Rangamati | 17 | 19:00
19 | Baroirhat | 62 | 19:00 | 85 | Keranigonj | 85 | 19:30 | 151 | Rangpur | 144 | 15:00
20 | Bashundhara | 195 | 19:00 | 86 | Khagrachori | 32 | 19:00 | 152 | Ruppur | 14 | 01:00
21 | BashundharaCement | 1 | 00:00 | 87 | Khulna | 83 | 21:00 | 153 | SSM | 0 | 00:00
22 | Beanibazar | 88 | 22:00 | 88 | Khulshi | 149 | 20:00 | 154 | Saidpur | 115 | 20:00
23 | Benapole | 74 | 21:00 | 89 | Kishoreganj | 152 | 22:00 | 155 | Satkhira | 131 | 00:00
24 | Bhaluka | 162 | 19:00 | 90 | Kodda | 311 | 10:00 | 156 | Satmasjid | 120 | 15:00
25 | Bhandaria | 58 | 23:00 | 91 | Kulaura | 57 | 19:00 | 157 | Savar | 243 | 15:00
26 | Bhangura | 42 | 19:30 | 92 | Kurigram | 66 | 03:00 | 158 | SevenRings | 20.19 | 16:00
27 | Bheramara(GK) | 74 | 23:00 | 93 | Kushtia | 162 | 20:00 | 159 | ShahCement | 35 | 18:00
28 | Bhulta | 243 | 10:00 | 94 | Laksam | 35 | 23:00 | 160 | Shahjadpur | 91 | 20:00
29 | Bog-Sherpur | 72 | 20:00 | 95 | Lakshmipur | 27 | 05:00 | 161 | Shahjibazar | 138 | 21:00
30 | Bogura | 197 | 21:00 | 96 | Lalbag | 55 | 18:30 | 162 | Shahmirpur | 56 | 15:00
31 | Borhanuddin | 93 | 23:00 | 97 | Lalmonirhat | 71 | 19:00 | 163 | Shariatpur | 97 | 22:00
32 | Brahmanbaria | 142 | 22:00 | 98 | MI_Cement | 16.3 | 07:00 | 164 | Sherpur | 166 | 23:00
33 | Cantonment | 156 | 15:00 | 99 | Madanganj | 44 | 23:00 | 165 | Shikalbaha | 22 | 21:00
34 | Chandina | 16.34 | 20:00 | 100 | Madaripur | 117 | 22:00 | 166 | Shitalakhya | 86.9 | 16:00
35 | Chandpur | 84 | 23:00 | 101 | Madartek | 95 | 23:00 | 167 | Sholosohor | 45 | 15:00
36 | Chandraghona | 37 | 20:00 | 102 | Madunaghat | 55 | 23:00 | 168 | Shyampur | 166 | 12:00
37 | Chapai | 77 | 22:00 | 103 | Magura | 76 | 19:30 | 169 | Siddhirganj | 124 | 12:00
38 | Charsaidpur | 42 | 00:00 | 104 | Mahasthangarh | 104 | 00:00 | 170 | Sirajganj | 120 | 21:00
39 | Chauddagram | 72 | 00:00 | 105 | Maijdee | 11 | 02:00 | 171 | Sonargaon | 124 | 23:00
40 | Chhatak | 45 | 00:00 | 106 | Manikganj | 136 | 21:00 | 172 | Sreemongol | 90 | 22:00
41 | Chowmuhani | 192 | 19:30 | 107 | Maniknagar | 74 | 13:00 | 173 | Sreepur | 108 | 19:00
42 | Chuadanga | 116 | 22:00 | 108 | Matarbari | 51 | 22:00 | 174 | Srinagar | 52.38 | 22:00
43 | Coxsbazar | 131 | 01:00 | 109 | Matuail | 64 | 12:00 | 175 | Sunamganj | 65 | 23:00
44 | Cumilla(N) | 142 | 20:00 | 110 | Millgate | 133 | 15:00 | 176 | Sylhet | 52 | 00:00
45 | Cumilla(S) | 148 | 19:00 | 111 | Mirpur | 130 | 19:00 | 177 | Sylhet-132 | 131 | 20:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 11 | 15:00 | 178 | TK | 36 | 19:30
47 | Daudkandi | 150 | 21:00 | 113 | Mirzapur | 45 | 19:30 | 179 | Tangail | 194 | 19:30
48 | Dhaka | 64 | 13:00 | 114 | Mithapukur | 77 | 19:30 | 180 | Taraganj | 25 | 19:00
49 | Dhamrai | 132 | 19:00 | 115 | Modern | N/A | N/A | 181 | Thakurgaon | 119 | 00:00
50 | Dhanmondi | 136 | 13:00 | 116 | Mogbazar | 147.8 | 15:00 | 182 | Tongi | 128 | 00:00
51 | Dohazari | 106 | 00:00 | 117 | Mongla | 44 | 12:00 | 183 | Ullahpara | 40 | 19:30
52 | Faridpur | 178 | 19:30 | 118 | Motijheel | 43 | 13:00 | 184 | Ullon | 42 | 20:00
53 | Fatullah | 100 | 12:00 | 119 | Muktagacha | 41 | 21:00 | 185 | Uttara | 83 | 18:30
54 | Fenchuganj | 47 | 23:00 | 120 | Munshiganj | 117 | 00:00 | 186 | UttaraNew | 65 | 23:00
55 | Feni | 129 | 20:00 | 121 | Muradnagar | 48 | 22:00 | 187 | Zigatola | 78 | 19:00
56 | GPH | 84 | 16:00 | 122 | Mymensingh | 222 | 20:00
57 | Ghatail | 90 | 23:00 | 123 | Naogaon | 147 | 22:00
58 | Ghorashal | 14 | 08:00 | 124 | Narail | 63 | 19:30
59 | Ghorashal-230 | 93 | 21:00 | 125 | Narinda | 76 | 13:00
60 | Goalpara | 42 | 23:00 | 126 | Narshingdi | 186 | 23:00
61 | Gollamari | 86 | 23:00 | 127 | Natore | 163 | 23:00
62 | Gopalganj | 110.8 | 22:00 | 128 | Nawabganj | 64 | 22:00
63 | Gulshan | 112 | 13:00 | 129 | Netrakona | 141 | 00:00
64 | Halishahar | 83 | 16:00 | 130 | New | 57.4 | 15:00
65 | HaripurSBU | 134 | 20:00 | 131 | Niamatpur | 82 | 22:00
66 | Hasnabad | 92 | 19:00 | 132 | Noapara | 50 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 19-07-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14916.4 | 82 |  | 15002.09
1:00 | 14438.7 | 88 |  | 14530.7
2:00 | 14112.7 | 74 |  | 14189.7
3:00 | 13796.7 | 61 |  | 13860.7
4:00 | 13500.7 | 48 |  | 13550.7
5:00 | 13320.7 | 47 |  | 13369.82
6:00 | 12807.16 | 47 |  | 12856.28
7:00 | 12723.88 | 37 |  | 12762.55
8:00 | 12760.8 | 0 |  | 12760.8
9:00 | 12932.68 | 0 |  | 12932.68
10:00 | 12897.21 | 0 |  | 12897.21
11:00 | 12949.74 | 0 |  | 12949.74
12:00 | 13644.45 | 0 |  | 13644.45
13:00 | 13995.7 | 0 |  | 13995.7
14:00 | 13629.64 | 0 |  | 13629.64
15:00 | 14214.67 | 0 |  | 14214.67
16:00 | 14300.47 | 0 |  | 14300.47
17:00 | 13915.26 | 0 |  | 13915.26
18:00 | 13589.28 | 0 |  | 13589.28
19:00 | 14898.87 | 0 |  | 14898.87
19:30 | 15883.04 | 46 |  | 15931.11
20:00 | 15878.06 | 127 |  | 16010.78
21:00 | 16006.2 | 118 |  | 16129.51
22:00 | 15951.9 | 123 |  | 16080.9
23:00 | 15938.3 | 108 |  | 16051.3
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 19-07-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7946.4 | 6970 | 14916.4 | DAILY GENERATION CURVE
00:30 | 7831.05 | 6846.5 | 14677.55
01:00 | 7715.7 | 6723 | 14438.7 | 19-07-2025
01:30 | 7621.7 | 6654 | 14275.7
02:00 | 7527.7 | 6585 | 14112.7
02:30 | 7397.2 | 6557.5 | 13954.7
03:00 | 7266.7 | 6530 | 13796.7
03:30 | 7179.2 | 6469.5 | 13648.7
04:00 | 7091.7 | 6409 | 13500.7
04:30 | 7066.2 | 6344.5 | 13410.7
05:00 | 7040.7 | 6280 | 13320.7
05:30 | 6874.245 | 6189.685 | 13063.93
06:00 | 6707.79 | 6099.37 | 12807.16
06:30 | 6696.625 | 6068.895 | 12765.52
07:00 | 6685.46 | 6038.42 | 12723.88
07:30 | 6702.15 | 6040.19 | 12742.34
08:00 | 6718.84 | 6041.96 | 12760.8
08:30 | 6759.975 | 6086.765 | 12846.74
09:00 | 6801.11 | 6131.57 | 12932.68
09:30 | 6836.05 | 6078.895 | 12914.945
10:00 | 6870.99 | 6026.22 | 12897.21
10:30 | 6904.64 | 6018.835 | 12923.475
11:00 | 6938.29 | 6011.45 | 12949.74
11:30 | 7148.855 | 6148.24 | 13297.095
12:00 | 7359.42 | 6285.03 | 13644.45
12:30 | 7429.665 | 6390.41 | 13820.075
13:00 | 7499.91 | 6495.79 | 13995.7
13:30 | 7546.945 | 6265.725 | 13812.67
14:00 | 7593.98 | 6035.66 | 13629.64
14:30 | 7738.4 | 6183.755 | 13922.155
15:00 | 7882.82 | 6331.85 | 14214.67
15:30 | 7962.585 | 6294.985 | 14257.57
16:00 | 8042.35 | 6258.12 | 14300.47
16:30 | 7909.465 | 6198.4 | 14107.865
17:00 | 7776.58 | 6138.68 | 13915.26
17:30 | 7684.135 | 6068.135 | 13752.27
18:00 | 7591.69 | 5997.59 | 13589.28
18:30 | 8034.945 | 6209.13 | 14244.075
19:00 | 8478.2 | 6420.67 | 14898.87
19:30 | 9045.2 | 6837.84 | 15883.04
20:00 | 8987.2 | 6890.86 | 15878.06
20:30 | 8930.2 | 7011.93 | 15942.13 |  | Executive Engineer
21:00 | 8873.2 | 7133 | 16006.2 |  | Network Operation Division
21:30 | 8763.45 | 7215.6 | 15979.05
22:00 | 8653.7 | 7298.2 | 15951.9
22:30 | 8645.9 | 7299.2 | 15945.1
23:00 | 8638.1 | 7300.2 | 15938.3

## En-Curve
QF-LDC-12
Date | 19-07-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4122 | 2014.2 | 747 | 38 | 34 | 1217 | 210 | 5000 | 0 | 291 | 1239.2 | 0 | 0 | 4 | 82 | DAILY ENERGY CURVE
00:30 | 4093 | 2016.85 | 808.5 | 38 | 31 | 1123 | 207.5 | 4897 | 0 | 274 | 1186.7 | 0 | 0 | 2 | 85 | 19-07-2025
01:00 | 4064 | 2019.5 | 870 | 38 | 28 | 1029 | 205 | 4794 | 0 | 257 | 1134.2 | 0 | 0 | 0 | 88
01:30 | 4066 | 2022 | 870 | 38 | 28 | 1022 | 205 | 4707 | 0 | 225 | 1091.7 | 0 | 0 | 1 | 81 | Energy Generated | 341.1012 |  | MKWHr
02:00 | 4068 | 2024.5 | 870 | 38 | 28 | 1015 | 205 | 4620 | 0 | 193 | 1049.2 | 0 | 0 | 2 | 74 | Energy not Served | 0.96 |  | MKWHr
02:30 | 4069 | 1986 | 870 | 38 | 27 | 1013 | 205.5 | 4530 | 0 | 192 | 1023.2 | 0 | 0 | 1 | 67.5 | Total Energy Requirement | 342.0612 |  | MKWHr
03:00 | 4070 | 1947.5 | 870 | 38 | 26 | 1011 | 206 | 4440 | 0 | 191 | 997.2 | 0 | 0 | 0 | 61
03:30 | 4080 | 1922 | 870 | 38 | 26 | 1002 | 206 | 4399.5 | 0 | 170.5 | 934.7 | 0 | 0 | 0 | 54.5
04:00 | 4090 | 1896.5 | 870 | 38 | 26 | 993 | 206 | 4359 | 0 | 150 | 872.2 | 0 | 0 | 0 | 48
04:30 | 4095 | 1898.5 | 870 | 38 | 26 | 948.5 | 206 | 4294 | 0 | 150.5 | 882.2 | 0 | 0 | 2 | 47.5
05:00 | 4100 | 1900.5 | 870 | 38 | 26 | 904 | 206 | 4229 | 0 | 151 | 892.2 | 0 | 0 | 4 | 47
05:30 | 3997.5 | 1797 | 870 | 38 | 25 | 902 | 206 | 4176.5 | 12.23 | 159 | 878.7 | 0 | 0 | 2 | 47
06:00 | 3895 | 1693.5 | 870 | 38 | 24 | 900 | 206 | 4124 | 24.46 | 167 | 865.2 | 0 | 0 | 0 | 47
06:30 | 3920 | 1683 | 870.5 | 38 | 24 | 873.5 | 205 | 4052 | 61.82 | 168 | 869.7 | 0 | 0 | 0 | 42
07:00 | 3945 | 1672.5 | 871 | 38 | 24 | 847 | 204 | 3980 | 99.18 | 169 | 874.2 | 0 | 0 | 0 | 37
07:30 | 3911 | 1662.25 | 870.5 | 38 | 24 | 850.7 | 207 | 3957.5 | 141.19 | 185 | 895.2 | 0 | 0 | 0 | 18.5
08:00 | 3877 | 1652 | 870 | 38 | 24 | 854.4 | 210 | 3935 | 183.2 | 201 | 916.2 | 0 | 0 | 0 | 0
08:30 | 3887 | 1654.5 | 870 | 38 | 24 | 856.155 | 209.5 | 3957 | 213.885 | 209 | 927.7 | 0 | 0 | 0 | 0
09:00 | 3897 | 1657 | 870 | 38 | 24 | 857.91 | 209 | 3979 | 244.57 | 217 | 939.2 | 0 | 0 | 0 | 0
09:30 | 3934.5 | 1652 | 870 | 38 | 25 | 856.505 | 208.5 | 3823 | 303.24 | 208 | 996.2 | 0 | 0 | 0 | 0
10:00 | 3972 | 1647 | 870 | 38 | 26 | 855.1 | 208 | 3667 | 361.91 | 199 | 1053.2 | 0 | 0 | 0 | 0
10:30 | 3887 | 1715.5 | 870 | 38 | 26 | 863.75 | 208 | 3684.5 | 441.625 | 183 | 1006.1 | 0 | 0 | 0 | 0
11:00 | 3802 | 1784 | 870 | 38 | 26 | 872.4 | 208 | 3702 | 521.34 | 167 | 959 | 0 | 0 | 0 | 0
11:30 | 3753 | 1905 | 870 | 38 | 27 | 938.15 | 208.5 | 3857.5 | 545.945 | 174 | 980 | 0 | 0 | 0 | 0
12:00 | 3704 | 2026 | 870 | 38 | 28 | 1003.9 | 209 | 4013 | 570.55 | 181 | 1001 | 0 | 0 | 0 | 0
12:30 | 3728.5 | 2052 | 870 | 38 | 29 | 1016.73 | 209.5 | 4117 | 526.345 | 183.5 | 1049.5 | 0 | 0 | 0 | 0
13:00 | 3753 | 2078 | 870 | 38 | 30 | 1029.56 | 210 | 4221 | 482.14 | 186 | 1098 | 0 | 0 | 0 | 0
13:30 | 3722 | 2079.5 | 870.5 | 38 | 30 | 1050.11 | 210.5 | 4012.5 | 484.06 | 187.5 | 1127 | 0 | 0 | 1 | 0
14:00 | 3691 | 2081 | 871 | 38 | 30 | 1070.66 | 211 | 3804 | 485.98 | 189 | 1156 | 0 | 0 | 2 | 0
14:30 | 3694.5 | 2091.5 | 870.5 | 38 | 30 | 1113.015 | 211 | 3929 | 453.14 | 242 | 1246.5 | 0 | 0 | 3 | 0
15:00 | 3698 | 2102 | 870 | 38 | 30 | 1155.37 | 211 | 4054 | 420.3 | 295 | 1337 | 0 | 0 | 4 | 0
15:30 | 3643.5 | 2092 | 870 | 38 | 30 | 1157.43 | 211.5 | 4036.5 | 377.04 | 319 | 1479.6 | 0 | 0 | 3 | 0
16:00 | 3589 | 2082 | 870 | 38 | 30 | 1159.49 | 212 | 4019 | 333.78 | 343 | 1622.2 | 0 | 0 | 2 | 0
16:30 | 3570 | 2077.5 | 870.5 | 38 | 29 | 1157.38 | 212 | 3986.5 | 255.785 | 328.5 | 1581.7 | 0 | 0 | 1 | 0
17:00 | 3551 | 2073 | 871 | 38 | 28 | 1155.27 | 212 | 3954 | 177.79 | 314 | 1541.2 | 0 | 0 | 0 | 0
17:30 | 3524 | 2043.25 | 870.5 | 38 | 28 | 1159.745 | 212 | 3916 | 106.575 | 317.5 | 1536.7 | 0 | 0 | 0 | 0
18:00 | 3497 | 2013.5 | 870 | 38 | 28 | 1164.22 | 212 | 3878 | 35.36 | 321 | 1532.2 | 0 | 0 | 0 | 0
18:30 | 3604.5 | 2073.75 | 870.5 | 38 | 30 | 1201.445 | 212 | 3957 | 17.68 | 507 | 1732.2 | 0 | 0 | 0 | 0
19:00 | 3712 | 2134 | 871 | 38 | 32 | 1238.67 | 212 | 4036 | 0 | 693 | 1932.2 | 0 | 0 | 0 | 0
19:30 | 3776 | 2148 | 870 | 38 | 32 | 1277.84 | 212 | 4079 | 0 | 830 | 2620.2 | 0 | 0 | 0 | 46
20:00 | 3580 | 2062 | 870 | 38 | 32 | 1255.86 | 211 | 4227 | 0 | 870 | 2732.2 | 0 | 0 | 0 | 127
20:30 | 3620.5 | 2097.5 | 870 | 38 | 32 | 1256.43 | 210.5 | 4311 | 0 | 871.5 | 2634.7 | 0 | 0 | 0 | 122.5
21:00 | 3661 | 2133 | 870 | 38 | 32 | 1257 | 210 | 4395 | 0 | 873 | 2537.2 | 0 | 0 | 0 | 118
21:30 | 3691.5 | 2138 | 870 | 38 | 32 | 1300.5 | 210 | 4377.5 | 0 | 866.5 | 2455.05 | 0 | 0 | 0 | 120.5
22:00 | 3722 | 2143 | 870 | 38 | 32 | 1344 | 210 | 4360 | 0 | 860 | 2372.9 | 0 | 0 | 0 | 123
22:30 | 3704 | 2140.2 | 869.5 | 38 | 33 | 1325.5 | 210 | 4370 | 0 | 863.5 | 2391.4 | 0 | 0 | 0 | 115.5
23:00 | 3686 | 2137.4 | 869 | 38 | 34 | 1307 | 210 | 4380 | 0 | 867 | 2409.9 | 0 | 0 | 0 | 108
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 19-07-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 382 | 06:00 | 366 | 15:00 | Payra | 415 | 09:00 | 405 | 15:00
Ashuganj | 405 | 6:00 | 364 | 13:00 | Rahanpur | 400 | 09:00 | 371 | 22:00
Bhulta | 403 | 06:00 | 360 | 12:00 | Rampal | 404 | 08:00 | 369 | 19:30
Bibiana | 385 | 07:00 | 377 | 12:00
BIPTC | 403 | 06:00 | 391 | 23:00
Bogura | 388 | 09:00 | 361 | 22:00
Gopalganj | 397 | 07:00 | 289 | 02:00
Kaliakoir | 373 | 06:00 | 357 | 14:00
Madunaghat | 393 | 08:00 | 384 | 16:00
Meghnaghat | 385 | 07:00 | 372 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 223 | 06:00 | 212 | 15:00 | Keranigonj | 221 | 06:00 | 210 | 14:00
AKSML | 230 | 07:00 | 222 | 00:00 | Khulna(S) | 231 | 08:00 | 211 | 19:30
Aminbazar | 228 | 01:00 | 213 | 14:00 | Madunaghat | 232 | 07:00 | 227 | 00:00
Ashuganj | 233 | 06:00 | 218 | 13:00 | Madunaghat-400 | 233 | 08:00 | 226 | 00:00
Ashuganj-400 | 233 | 06:00 | 218 | 13:00 | Maniknagar | 219 | 03:00 | 210 | 13:00
Baghabari | 234 | 06:00 | 225 | 19:30 | Meghnaghat | 226 | 06:00 | 218 | 15:00
Barapukuria | 226 | 06:00 | 212 | 21:00 | Meghnaghat-400 | 223 | 07:00 | 215 | 13:00
Barapukuria-230 | 226 | 06:00 | 212 | 21:00 | Mirsorai | 228 | 08:00 | 218 | 00:00
Barishal | 228 | 07:00 | 219 | 19:30 | Rajshahi | 233 | 08:00 | 220 | 15:00
Bheramara | 234 | 06:00 | 222 | 19:30 | Rampal | 230 | 06:00 | 208 | 19:30
Bhulta | 233 | 06:00 | 208 | 15:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 226 | 07:00 | 219 | 23:00 | Rampura | 231 | 06:00 | 205 | 15:00
BIPTC | 237 | 06:00 | 222 | 19:30 | Shikalbaha | 229 | 05:00 | 223 | 13:00
Bogura | 234 | 06:00 | 220 | 00:00 | Shyampur | 220 | 06:00 | 211 | 15:00
Bogura-400 | 234 | 06:00 | 221 | 00:00 | Siddhirganj | 219 | 06:00 | 212 | 13:00
Borhanuddin | 233 | 09:00 | 226 | 22:00 | Sirajgonj | 238 | 07:00 | 232 | 06:00
BSRM | 228 | 08:00 | 218 | 00:00 | Sreepur | 231 | 06:00 | 218 | 12:00
Cumilla(N) | 223 | 07:00 | 213 | 15:00 | Tongi | 225 | 09:00 | 210 | 13:00
Faridpur | 225 | 06:00 | 212 | 22:00
Fenchuganj | 229 | 07:00 | 222 | 21:00
Ghorashal | 230 | 00:00 | 220 | 14:00
Ghorashal-230 | 229 | 06:00 | 210 | 13:00
Gopalganj | 226 | 05:00 | 214 | 21:00
GPH | 230 | 08:00 | 221 | 01:00
Haripur | 220 | 06:00 | 211 | 21:00
Hasnabad | 221 | 07:00 | 211 | 15:00
Hathazari | 229 | 05:00 | 221 | 12:00
Ishurdi | 235 | 06:00 | 225 | 19:30
Jhenaidah | 230 | 06:00 | 212 | 19:30
Kaliakoir | 230 | 06:00 | 216 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 141 | 07:00 | 122 | 14:00 | Lalmonirhat | 128 | 02:00 | 119 | 21:00
Agargaon | 131 | 06:00 | 122 | 13:00 | Madanganj | 127 | 05:00 | 122 | 15:00
Agrabad | 131 | 07:00 | 126 | 00:00 | Madaripur | 135 | 07:00 | 127 | 20:00
AKS | 129 | 10:00 | 125 | 00:00 | Madartek | 139 | 06:00 | 121 | 15:00
Aminbazar | 131 | 04:00 | 125 | 11:00 | Madunaghat | 132 | 07:00 | 128 | 00:00
Amnura | 134 | 06:00 | 122 | 22:00 | Magura | 134 | 09:00 | 119 | 19:30
Ashuganj | 140 | 06:00 | 133 | 21:00 | Mahasthangarh | 135 | 10:00 | 123 | 01:00
Bagerhat | 132 | 07:00 | 115 | 19:30 | Maijdee | 119 | 08:00 | 106 | 00:00
Bajitpur | 132 | 05:00 | 121 | 21:00 | Manikganj | 128 | 05:00 | 115 | 15:00
Bakulia | 132 | 07:00 | 128 | 00:00 | Maniknagar | 131 | 06:00 | 124 | 13:00
Banani | 140 | 07:00 | 123 | 13:00 | Matarbari | 125 | 09:00 | 108 | 00:00
Bangabhaban | 130 | 03:00 | 124 | 13:00 | Matuail | 128 | 04:00 | 123 | 12:00
Barapukuria | 137 | 10:00 | 124 | 21:00 | Millgate | 133 | 05:00 | 118 | 14:00
Barguna | 136 | 22:00 | 130 | 00:00 | Mirpur | 130 | 07:00 | 123 | 11:00
Barishal | 134 | 09:00 | 127 | 15:00 | Mirzapur | 130 | 08:00 | 122 | 19:30
Barishal-230 | 134 | 07:00 | 128 | 00:00 | Mithapukur | 132 | 10:00 | 111 | 00:00
Baroaulia | 132 | 06:00 | 126 | 12:00 | MI_Cement | 128.4 | 06:00 | 123 | 14:00
Baroirhat | 126 | 08:00 | 116 | 23:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 140 | 06:00 | 119 | 15:00 | Mogbazar | 140 | 06:00 | 123 | 13:00
BashundharaCement | 127 | 05:00 | 122 | 15:00 | Mongla | 133 | 05:00 | 116 | 19:30
Beanibazar | 128 | 07:00 | 120 | 23:00 | Motijheel | 130 | 03:00 | 123 | 16:00
Benapole | 132 | 09:00 | 116 | 15:00 | Muktagacha | 135 | 09:00 | 124 | 19:30
Bhaluka | 132 | 07:00 | 119 | 23:00 | Munshiganj | 127 | 05:00 | 122 | 13:00
Bhandaria | 130 | 09:00 | 119 | 00:00 | Muradnagar | 126 | 08:00 | 117 | 12:00
Bhangura | 133 | 01:00 | 126 | 00:00 | Mymensingh | 137 | 08:00 | 110 | 23:00
Bheramara | 137 | 06:00 | 132 | 00:00 | Naogaon | 132 | 08:00 | 120 | 00:00
Bheramara(GK) | 137 | 06:00 | 131 | 00:00 | Narail | 134 | 09:00 | 118 | 19:30
Bhulta | 122 | 04:00 | 114 | 23:00 | Narinda | 131 | 06:00 | 124 | 13:00
Bog-Sherpur | 135 | 08:00 | 126 | 00:00 | Narshingdi | 135 | 09:00 | 115 | 23:00
Bogura | 138 | 09:00 | 127 | 00:00 | Natore | 135 | 06:00 | 126 | 00:00
Bogura-230 | 138 | 08:00 | 128 | 00:00 | Nawabganj | 133 | 06:00 | 123 | 15:00
Brahmanbaria | 135 | 06:00 | 125 | 21:00 | Netrakona | 124 | 07:00 | 107 | 23:00
Cantonment | 130 | 03:00 | 123 | 13:00 | New | 132 | 04:00 | 120 | 14:00
Chandina | 129 | 08:00 | 120 | 19:30 | Niamatpur | 136 | 07:00 | 123 | 22:00
Chandpur | 128 | 08:00 | 116 | 00:00 | Noapara | 134 | 08:00 | 119 | 19:30
Chandraghona | 132 | 06:00 | 129 | 00:00 | Pabna | 135 | 06:00 | 128 | 00:00
Chapai | 135 | 09:00 | 122 | 22:00 | Palashbari | 130 | 10:00 | 110 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 128 | 05:00 | 123 | 13:00 | Panchagarh | 137 | 18:30 | 122 | 13:00
Chauddagram | 124 | 07:00 | 115 | 00:00 | Patuakhali | 137 | 22:00 | 131 | 00:00
Chhatak | 127 | 07:00 | 118 | 21:00 | Payra | 136 | 06:00 | 133 | 00:00
Chowmuhani | 119 | 10:00 | 107 | 01:00 | PHP | 125 | 08:00 | 115 | 00:00
Chuadanga | 132 | 09:00 | 116 | 19:30 | Postogola | 130 | 05:00 | 124 | 15:00
Coxsbazar | 125 | 09:00 | 108 | 00:00 | Purbachal | 140 | 05:00 | 120 | 14:00
Cumilla(N) | 128 | 07:00 | 120 | 21:00 | Purbasadipur | 131 | 09:00 | 120 | 13:00
Cumilla(S) | 133 | 04:00 | 118 | 19:30 | Rahanpur | 137 | 09:00 | 126 | 22:00
Daganbhuiyan | 122 | 08:00 | 110 | 19:30 | Rahanpur-400 | 137 | 09:00 | 126 | 22:00
Daudkandi | 123 | 06:00 | 114 | 12:00 | Rahim | 128 | 06:00 | 123 | 13:00
Dhaka | 139 | 07:00 | 122 | 15:00 | Rajbari | 132 | 07:00 | 122 | 23:00
Dhamrai | 131 | 05:00 | 120 | 14:00 | Rajendrapur | 131 | 07:00 | 120 | 23:00
Dhanmondi | 141 | 06:00 | 123.5 | 15:00 | Rajshahi | 133 | 06:00 | 125 | 00:00
Dohazari | 131 | 08:00 | 121 | 00:00 | Rajshahi-230 | 134 | 08:00 | 126 | 00:00
Faridpur | 134 | 09:00 | 126 | 15:00 | Ramganj | 121 | 07:00 | 109 | 19:30
Fatullah | 130 | 06:00 | 123 | 15:00 | Rampur | 132 | 07:00 | 125 | 13:00
Fenchuganj | 135 | 06:00 | 129 | 23:00 | Rampura | 140 | 06:00 | 123 | 13:00
Feni | 125 | 08:00 | 113 | 23:00 | Rangamati | 132 | 06:00 | 128 | 00:00
Ghatail | 130 | 08:00 | 120 | 22:00 | Rangpur | 131 | 05:00 | 119 | 21:00
Ghorashal | 137 | 06:00 | 127 | 13:00 | Ruppur | 137 | 06:00 | 131 | 21:00
Goalpara | 137 | 07:00 | 124 | 15:00 | Saidpur | 131 | 06:00 | 120 | 21:00
Gollamari | 137 | 09:00 | 125 | 19:30 | Satkhira | 134 | 09:00 | 119 | 21:00
Gopalganj | 135 | 09:00 | 126 | 15:00 | Satmasjid | 132 | 07:00 | 122 | 15:00
Gopalganj-400 | 136 | 05:00 | 129 | 19:30 | Savar | 129 | 00:00 | 122 | 11:00
Gulshan | 140 | 07:00 | 122 | 15:00 | SevenRings | 136 | 07:00 | 127 | 13:00
Halishahar | 133 | 08:00 | 125 | 16:00 | ShahCement | 128 | 05:00 | 123 | 13:00
Haripur | 128 | 05:00 | 123 | 13:00 | Shahjadpur | 136 | 07:00 | 131 | 00:00
HaripurSBU | 128 | 07:00 | 123 | 13:00 | Shahjibazar | 135 | 07:00 | 125 | 22:00
Hasnabad | 130 | 04:00 | 124 | 15:00 | Shahmirpur | 133 | 05:00 | 128 | 00:00
Hathazari | 134 | 10:00 | 130 | 00:00 | Shariatpur | 135 | 09:00 | 125 | 20:00
Ishurdi | 138 | 06:00 | 132 | 00:00 | Sherpur | 138 | 11:00 | 122 | 19:30
Jaldhaka | 129 | 10:00 | 116 | 21:00 | Shikalbaha | 123 | 07:00 | 116 | 00:00
Jamalpur | 139 | 08:00 | 126 | 19:30 | Shikalbaha-230 | 134 | 08:00 | 129 | 00:00
Jashore | 131 | 09:00 | 115 | 19:30 | Shitalakhya | 128.4 | 06:00 | 123 | 13:00
Jhenaidah | 134 | 05:00 | 121 | 00:00 | Sholosohor | 132 | 08:00 | 127 | 13:00
Jhenaidah-230 | 136 | 09:00 | 122 | 20:00 | Shyampur | 129 | 08:00 | 125 | 13:00
Joydebpur | 132 | 04:00 | 123 | 12:00 | Shyampur-230 | 129 | 05:00 | 123 | 15:00
Joypurhat | 130 | 06:00 | 117 | 00:00 | Siddhirganj | 129 | 06:00 | 123 | 15:00
Juldah | 132 | 08:00 | 128 | 00:00 | Sirajganj | 133 | 06:00 | 126 | 00:00
Kabirpur | 132 | 20:00 | 117 | 15:00 | Sonargaon | 126 | 07:00 | 121 | 15:00
Kachua | 125 | 07:00 | 115 | 00:00 | Sreemongol | 133 | 07:00 | 124 | 21:00
Kaliakoir | 137 | 17:00 | 125 | 13:00 | Sreepur | 134 | 07:00 | 125 | 12:00
Kallyanpur | 131 | 07:00 | 126 | 10:00 | Srinagar | 133 | 06:00 | 125 | 12:00
Kalurghat | 131 | 02:00 | 128 | 12:00 | SSM | 136 | 07:00 | 130 | 00:00
Kamrangirchar | 132 | 08:00 | 124 | 13:00 | Sunamganj | 125 | 06:00 | 116 | 23:00
Kaptai | 135 | 8:00 | 131 | 23:00 | Sylhet | 128 | 07:00 | 123 | 00:00
Kasba | 125 | 08:00 | 116 | 12:00 | Sylhet-132 | 129 | 07:00 | 125 | 00:00
Kazla | 131 | 06:00 | 124 | 13:00 | Tangail | 128 | 08:00 | 120 | 19:30
Keranigonj | 133 | 06:00 | 125 | 13:00 | Taraganj | 131 | 10:00 | 120 | 21:00
Khagrachori | 131 | 07:00 | 127 | 00:00 | Thakurgaon | 135 | 18:30 | 121 | 13:00
Khulna | 135 | 08:00 | 120 | 19:30 | TK | 131 | 06:00 | 127 | 00:00
Khulna(S) | 137 | 08:00 | 124 | 15:00 | Tongi | 132 | 04:00 | 124 | 13:00
Khulshi | 131 | 05:00 | 124 | 16:00 | Ullahpara | 134 | 06:00 | 127 | 21:00
Kishoreganj | 128 | 09:00 | 115 | 23:00 | Ullon | 140 | 06:00 | 122 | 15:00
Kodda | 132 | 20:00 | 118 | 12:00 | Uttara | 130 | 07:00 | 122 | 11:00
KSRM | 133 | 18:00 | 127 | 13:00 | UttaraNew | 129 | 06:00 | 123 | 11:00
Kulaura | 134 | 07:00 | 128 | 21:00 | Zigatola | 133 | 06:00 | 125 | 13:00
Kurigram | 130 | 10:00 | 116 | 21:00
Kushtia | 133 | 04:00 | 126 | 00:00
Laksam | 125 | 08:00 | 114 | 00:00
Lakshmipur | 120 | 08:00 | 109 | 00:00
Lalbag | 133 | 05:00 | 124 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division