## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 21-07-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-07-2025 | during | 21-07-2025 | during | 21-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 0 | 0 | 0 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 307 | 305 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 194 | 196 | 208.13 | 208.13 | 198 | 198 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 325 | 327 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 92 | 73 | 7 | 102 | 80 | 80 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 48 | 47 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 146 | 110 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 0 | 0 | 33 | 33 | 26 | 26 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 33 | 33 | 52.19 | 52.19 | 42 | 42 | Engine Problem
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 175 | 262 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 122 | 133 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 16 | 104 | 104 | 50 | 50 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 153 | 162 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 12 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 502 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 125 | 125 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2413 | 3013 | 4705.45 | 4772.45 | 3374.33 | 3346.33
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 7 | 0 | 15 | 0 | 15 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 33 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 216 | 220 | 0 | 0 | 0 | 0 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 218 | 213 | 213 | 213 | 213 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 16 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 42 | 76 | 64 | 80 | 80 | 80 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 33 | 65 | 65 | 65 | 68 | 68 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 3 | 20 | 2 | 20 | 2 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 62 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0 | 0 | 2.28 | 0 | 2.28 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 14 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 108 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1067 | 1140 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 707 | 713 | 775 | 775 | 775 | 775 | -
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 2434 | 2705 | 3589 | 3605.72 | 3608 | 3608.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 42 | 198 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 344 | 346 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 345 | 340 | 318.81 | 318.81 | 318.81 | 318.81 | machine problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 27 | 32 | 46.7 | 46.7 | 31 | 31 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 36 | 48 | 55 | 55 | 50 | 50 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 76 | 53 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 130 | 132 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 29 | 36 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 104 | 193 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 28 | 26 | 0 | 0 | 0 | 0 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 20 | 20.83 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 96 | 96 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 10 | 18 | 113 | 113 | 18 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 95 | 95 | 115 | 115 | 115 | 115 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 39 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1503 | 1736.2 | 2270.89 | 2219.56 | 1975.36 | 1940.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-07-2025 | during | 21-07-2025 | during | 21-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 62 | 66 | 157.5 | 157.5 | 101 | 101 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 100 | 172 | 200 | 200 | 186 | 186 | Engine Problem
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 85 | 111 | 115 | 115 | 105 | 105 | Engine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 24.05 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 35 | 35 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 301.05 | 378 | 599.1 | 549 | 489.1 | 439
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 0 | 60 | 60 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 157 | 137 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 88 | 85 | 85 | 85 | 85 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 172 | 0 | 0 | 0 | 172 | 172 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 0 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 8 | 8 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | Plant Shutdown as per schedule HGPI work
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 346 | 347 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | machine problem
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1196 | 930 | 1086 | 1086 | 1213 | 1213
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 865 | 868 | 0 | 0 | 0 | 0 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 227 | 215 | 410 | 410 | 320 | 320 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 60 | 60 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 48 | 0 | 97 | 0 | 97 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 794 | 1104 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1972 | 2242 | 2609.2 | 2512.2 | 2474.2 | 2377.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 351 | 301 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 850 | 740 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 175 | 173 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.16 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1676.16 | 1554 | 2162 | 2161 | 2102 | 2101
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 30 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 11 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 189 | 176 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 190 | 202 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 160 | 199 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 379 | 356 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 89 | 95 | 95 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 111 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0.2 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1120.7 | 1308.3 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 11.55 | 0 | 35 | 0 | 35 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 32 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 2082.45 | 2711.5 | 3166.47 | 3025.87 | 3126.09 | 2985.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 52 | 49 | 50 | 50 | 50 | 50 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 158 | 157 | 150 | 150 | 150 | 150 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 0.8 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 114 | 115 | 115 | 95 | 95 | Engine Problem
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 11 | 0 | 24 | 0 | 24 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 145 | 0 | 89.2 | 0 | 89.2 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 366.8 | 433 | 581.8 | 462 | 561.8 | 442
System Total |  |  |  |  | 28565.2 | 27045.875 | 13944.46 | 15702.7 | 20769.91 | 20393.8 | 18923.88 | 18453.1
Forecast Scenario (21-07-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 16030 |  | 0 |  | 16030
|  |  |  | 1:00 | 15560 |  | 0 |  | 15560
|  |  |  | 2:00 | 15050 |  | 0 |  | 15050
|  |  |  | 3:00 | 14630 |  | 0 |  | 14630
|  |  |  | 4:00 | 14230 |  | 0 |  | 14230
|  |  |  | 5:00 | 13980 |  | 0 |  | 13980
|  |  |  | 6:00 | 13600 |  | 0 |  | 13600
|  |  |  | 7:00 | 13260 |  | 0 |  | 13260
|  |  |  | 8:00 | 12780 |  | 0 |  | 12780
|  |  |  | 9:00 | 13440 |  | 0 |  | 13440
|  |  |  | 10:00 | 13310 |  | 0 |  | 13310
|  |  |  | 11:00 | 13710 |  | 0 |  | 13710
|  |  |  | 12:00 | 13940 |  | 0 |  | 13940
|  |  |  | 13:00 | 14290 |  | 0 |  | 14290
|  |  |  | 14:00 | 14200 |  | 0 |  | 14200
|  |  |  | 15:00 | 14540 |  | 0 |  | 14540
|  |  |  | 16:00 | 14300 |  | 0 |  | 14300
|  |  |  | 17:00 | 13930 |  | 0 |  | 13930
|  |  |  | 18:00 | 13360 |  | 0 |  | 13360
|  |  |  | 18:30 | 14000 |  | 0 |  | 14000
|  |  |  | 19:00 | 14930 |  | 0 |  | 14930
|  |  |  | 19:30 | 15860 |  | 0 |  | 15860
|  |  |  | 20:00 | 15700 |  | 0 |  | 15700
|  |  |  | 21:00 | 15810 |  | 0 |  | 15810
|  |  |  | 22:00 | 15750 |  | 0 |  | 15750
|  |  |  | 23:00 | 15700 |  | 0 |  | 15700
Probable Maximum Temperature: |  |  | 32.70°C
Probable Maximum Demand at Day Peak: |  |  | 13940.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15860.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15860.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 341.61089 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:07 hrs on 21-07-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 20-07-2025 | [28 empty] | Date: | 20-07-2025 | [28 empty] | Date: | 20-07-2025 | [28 empty] | Date: | 20-07-2025 | [28 empty] | Date: | 20-07-2025 | [11 empty] | Date: | 20-07-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [11 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 7 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 35 | 0 | 104 | 111 | 95 | 15 | 55 | 142 | 16 | 450 | 297 | 0 | 0 | 55 | 328 | 198 | 0 | 0 | 125 | 26.2 | 22 | 0 | 0 | 12 | 65 | 25 | 0 | 0 | 65 | 39 | 0 | 25 | 25 | 0 | 210 | 64 | 23 | 754 | 0 | 0 | 40 | 25 | 91 | 219 | 0 | 0 | 0 | 1120 | 0 | 51 | 80 | 185 | 0 | 60 | 335 | 48 | 191 | 27 | 95 | 0 | 200 | 13 | 20 | 96 | 34 | 52.2 | 0 | 36 | 0 | 320 | 375 | 0 | 60 | 150 | 8 | 0 | 85 | 28 | 0 | 18 | 172 | 35 | 92 | 158 | 69 | 0 | 0 | 12 | 8681.4 | 870 | 270 | 0 | 30 | 0 | 38 | 0 | 0 | 0 | 0 | 85 | 0 | 543 | 49 | 1303 | 0 | 43 | 0 | 70 | 0 | 95 | 35 | 37 | 16 | 0 | 28 | 0 | 178 | 0 | 187 | 0 | 186 | 0 | 343 | 0 | 0 | 161 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 32 | 275 | 120 | 190 | 0 | 560 | 1120 | 132 | 7271 | 15952.4 | 98.73
01:00 | 7 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 35 | 0 | 104 | 95 | 95 | 15 | 55 | 139 | 16 | 450 | 298 | 0 | 0 | 55 | 327 | 198 | 0 | 0 | 125 | 26.2 | 22 | 0 | 0 | 0 | 30 | 24 | 0 | 0 | 65 | 39 | 0 | 25 | 25 | 0 | 211 | 63 | 23 | 755 | 0 | 0 | 40 | 25.5 | 90 | 219 | 0 | 0 | 0 | 1128 | 0 | 51 | 80 | 185 | 0 | 17 | 340 | 48 | 188 | 27 | 78 | 0 | 180 | 15 | 20 | 96 | 32 | 45 | 0 | 36 | 0 | 320 | 354 | 0 | 60 | 149 | 8 | 0 | 85 | 30 | 0 | 18 | 171 | 35 | 92 | 158 | 69 | 0 | 0 | 12 | 8516.7 | 868 | 270 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 6 | 0 | 615 | 50 | 1219 | 0 | 43 | 0 | 35 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 10.15 | 175 | 0 | 184 | 0 | 182 | 0 | 337 | 0 | 0 | 157 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 120 | 190 | 0 | 563 | 1102 | 129 | 6935.15 | 15451.85 | 98.73
02:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 35 | 0 | 89 | 80 | 95 | 0 | 55 | 142 | 16 | 450 | 302 | 0 | 0 | 55 | 328 | 135 | 0 | 0 | 125 | 26.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 39 | 0 | 25 | 25 | 0 | 211 | 51 | 23 | 752 | 0 | 0 | 40 | 0 | 92 | 221 | 0 | 0 | 0 | 1135 | 0 | 51 | 80 | 185 | 0 | 18 | 340 | 48 | 190 | 27 | 73 | 0 | 112 | 9 | 20 | 96 | 30 | 52.2 | 0 | 37 | 0 | 320 | 353 | 0 | 60 | 150 | 8 | 0 | 85 | 30 | 0 | 18 | 171 | 35 | 92 | 149 | 69 | 0 | 0 | 12 | 8212.4 | 868 | 270 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 671 | 50 | 1217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 186 | 0 | 185 | 0 | 342 | 0 | 0 | 158 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 252 | 120 | 190 | 0 | 563 | 1052 | 124 | 6738 | 14950.4 | 98.73
03:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 554 | 35 | 0 | 82 | 80 | 0 | 0 | 0 | 90 | 0 | 400 | 274 | 0 | 0 | 0 | 328 | 133 | 0 | 0 | 125 | 26.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 45 | 30 | 0 | 25 | 25 | 0 | 212 | 34 | 24 | 752 | 0 | 0 | 40 | 0 | 91 | 221 | 0 | 0 | 0 | 1136 | 0 | 51 | 80 | 185 | 0 | 35 | 290 | 47 | 189 | 27 | 73 | 0 | 110 | 9 | 20 | 96 | 28 | 52.2 | 0 | 37 | 0 | 320 | 353 | 0 | 60 | 131 | 8 | 0 | 85 | 30 | 0 | 18 | 171 | 35 | 92 | 149 | 69 | 0 | 0 | 12 | 7753.4 | 868 | 270 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 970 | 34 | 1215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 186 | 0 | 185 | 0 | 343 | 0 | 0 | 159 | 47 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 115 | 190 | 0 | 514 | 1048 | 31 | 6793 | 14546.4 | 98.73
04:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 35 | 0 | 70 | 80 | 0 | 0 | 0 | 32 | 0 | 400 | 279 | 0 | 0 | 0 | 327 | 134 | 0 | 0 | 108 | 26.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 25 | 25 | 0 | 212 | 0 | 24 | 756 | 0 | 0 | 19 | 0 | 51 | 221 | 0 | 0 | 0 | 1160 | 0 | 51 | 0 | 185 | 0 | 40 | 285 | 47 | 200 | 27 | 73 | 0 | 108 | 9 | 20 | 96 | 28 | 52.2 | 0 | 37 | 0 | 320 | 385 | 0 | 60 | 131 | 8 | 0 | 85 | 30 | 0 | 18 | 172 | 17 | 92 | 159 | 85 | 0 | 0 | 12 | 7504.4 | 868 | 271 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1046 | 0 | 1142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 187 | 0 | 186 | 0 | 355 | 0 | 0 | 160 | 47 | 35 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 115 | 190 | 0 | 499 | 1045 | 0 | 6644 | 14148.4 | 98.73
05:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556 | 0 | 0 | 70 | 63 | 0 | 0 | 0 | 0 | 0 | 400 | 278 | 0 | 0 | 0 | 327 | 134 | 0 | 0 | 108 | 26.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 25 | 25 | 0 | 212 | 0 | 27 | 751 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1049 | 0 | 51 | 0 | 185 | 0 | 127 | 285 | 48 | 194 | 27 | 83 | 0 | 103 | 9 | 20 | 96 | 28 | 52.2 | 0 | 37 | 0 | 320 | 370 | 0 | 60 | 141 | 8 | 0 | 85 | 30 | 0 | 18 | 171 | 17 | 92 | 159 | 86 | 0 | 0 | 12 | 7319.4 | 868 | 271 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1055 | 0 | 1102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 180 | 0 | 183 | 0 | 352 | 0 | 0 | 160 | 47 | 35 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 115 | 190 | 0 | 499 | 1046 | 0 | 6594 | 13913.4 | 98.73
06:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 501 | 0 | 0 | 58 | 31 | 0 | 0 | 0 | 0 | 0 | 400 | 267 | 0 | 0 | 0 | 329 | 133 | 0 | 1 | 108 | 27.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 25 | 25 | 0.05 | 212 | 0 | 28 | 750 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 951 | 1 | 51 | 0 | 185 | 0 | 213 | 285 | 47 | 182 | 27 | 95 | 0 | 103 | 9 | 20 | 96 | 26 | 52.2 | 0 | 37 | 0 | 320 | 370 | 0 | 60 | 130 | 8 | 0 | 85 | 30 | 0 | 18 | 171 | 17 | 92 | 148 | 86 | 0 | 0.88 | 12 | 7177.33 | 868 | 272 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 1045 | 0 | 1105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.19 | 156 | 0 | 163 | 0 | 165 | 0 | 332 | 0 | 0.1 | 160 | 47 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 115 | 190 | 0 | 499 | 981 | 0 | 6370.29 | 13547.62 | 98.73
07:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 502 | 0 | 0 | 51 | 32 | 0 | 0 | 0 | 0 | 0 | 400 | 281 | 0 | 0 | 0 | 328 | 133 | 0 | 6 | 108 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 25 | 25 | 0 | 212 | 0 | 24 | 695 | 0 | 0 | 2 | 0 | 0 | 221 | 0 | 0 | 0 | 957 | 3 | 51 | 0 | 125 | 0 | 325 | 280 | 48 | 202 | 27 | 95 | 0 | 103 | 9 | 20 | 96 | 26 | 25 | 5 | 37 | 0 | 320 | 383 | 0 | 60 | 133 | 8 | 0 | 85 | 30 | 0 | 18 | 171 | 17 | 92 | 150 | 86 | 0 | 4.63 | 12 | 7234.63 | 868 | 276 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12 | 902 | 0 | 963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.35 | 160 | 0 | 168 | 0 | 168 | 0 | 370 | 0 | 0.38 | 161 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06 | 0 | 173 | 115 | 190 | 0 | 500 | 900 | 0 | 6014.79 | 13249.42 | 98.73
08:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 32 | 0 | 0 | 2 | 0 | 0 | 400 | 292 | 0 | 0 | 0 | 326 | 133 | 0 | 5 | 70 | 25.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 25 | 25 | 0 | 210 | 0 | 2 | 708 | 0 | 0 | 18 | 0 | 0 | 221 | 0 | 0 | 0 | 970 | 9 | 51 | 0 | 123 | 0 | 342 | 280 | 47 | 207 | 28 | 96 | 0 | 103 | 9 | 20 | 96 | 5 | 25 | 18 | 36 | 0 | 320 | 387 | 0 | 60 | 132 | 8 | 0 | 85 | 30 | 0 | 18 | 171 | 17 | 92 | 110 | 65 | 0 | 2.54 | 12 | 6678.04 | 869 | 275 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 47 | 871 | 0 | 997.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8 | 161 | 0 | 170 | 0 | 170 | 0 | 382 | 0 | 0.72 | 160 | 46 | 0 | 0 | 0 | 0 | 0 | 0.7 | 3 | 0.19 | 0 | 177 | 115 | 190 | 0 | 498 | 900 | 0 | 6080.13 | 12758.17 | 98.73
09:00 | 0 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 53 | 73 | 40 | 0 | 42 | 116 | 0 | 450 | 309 | 0 | 0 | 17 | 328 | 196 | 0 | 4 | 100 | 23.2 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 25 | 25 | 0 | 209 | 0 | 2 | 695 | 0 | 0 | 19 | 0 | 0 | 219 | 0 | 0 | 0 | 1000 | 14 | 51 | 1 | 177 | 0 | 344 | 340 | 48 | 215 | 23 | 95 | 0 | 103 | 9 | 19 | 96 | 24 | 25 | 21 | 29 | 0 | 320 | 390 | 0 | 60 | 157 | 8 | 0 | 83 | 30 | 0 | 18 | 171 | 17 | 92 | 130 | 62 | 0 | 3.53 | 12 | 7274.73 | 868 | 270 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 62 | 872 | 0 | 1067.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.16 | 181 | 0 | 190 | 0 | 198 | 0 | 414 | 0 | 0.62 | 157 | 50 | 0 | 1 | 0 | 0 | 0 | 0 | 27 | 0.62 | 0 | 174 | 120 | 220 | 0 | 450 | 800 | 0 | 6170.27 | 13445 | 98.74
10:00 | 8 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 81 | 123 | 105 | 22 | 54 | 150 | 0 | 450 | 294 | 0 | 0 | 45 | 329 | 197 | 0 | 6 | 125 | 22.5 | 14 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 33 | 0 | 0 | 25 | 25 | 0 | 208 | 0 | 2 | 665 | 0 | 0 | 19 | 0 | 0 | 219 | 0 | 0 | 0 | 1040 | 18 | 51 | 38 | 78 | 0 | 252 | 270 | 37 | 74 | 24 | 95 | 0 | 103 | 9 | 19 | 96 | 22 | 36 | 18 | 29 | 0 | 320 | 360 | 0 | 60 | 156 | 8 | 0 | 82 | 30 | 0 | 18 | 171 | 17 | 92 | 130 | 62 | 0 | 5.44 | 12 | 7186.94 | 868 | 262 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 55 | 807 | 0 | 1100.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 8.42 | 170 | 0 | 204 | 0 | 193 | 0 | 397 | 0 | 0.71 | 156 | 49 | 0 | 3 | 0 | 0 | 0 | 1.1 | 58 | 0.3 | 0 | 172 | 120 | 220 | 0 | 400 | 822 | 0 | 6131.31 | 13318.25 | 98.74
11:00 | 64 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 107 | 146 | 175 | 55 | 54 | 152 | 0 | 450 | 300 | 0 | 0 | 55 | 329 | 195 | 0 | 5 | 125 | 22 | 14 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 33 | 0 | 0 | 25 | 25 | 0 | 208 | 14 | 2 | 698 | 0 | 0 | 25 | 0 | 15 | 218 | 0 | 0 | 0 | 1070 | 19 | 51 | 77 | 76 | 0 | 349 | 340 | 15 | 31 | 24 | 95 | 0 | 103 | 9 | 19 | 96 | 24 | 34 | 16 | 29 | 0 | 320 | 346 | 0 | 60 | 156 | 8 | 0 | 85 | 30 | 0 | 18 | 172 | 17 | 93 | 100 | 62 | 0 | 7.83 | 12 | 7615.83 | 865 | 258 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 91 | 798 | 0 | 1124.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 10.15 | 190 | 0 | 190 | 0 | 160 | 0 | 356 | 0 | 0.68 | 157 | 48 | 0 | 10 | 0 | 0 | 0 | 1 | 108 | 0.25 | 0 | 174 | 120 | 180 | 0 | 351 | 850 | 0 | 6094.33 | 13710.16 | 98.74
12:00 | 92 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 122 | 146 | 175 | 55 | 55 | 153 | 0 | 450 | 307 | 0 | 0 | 55 | 325 | 194 | 0 | 12 | 125 | 0 | 14 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 33 | 42 | 0 | 25 | 25 | 0 | 216 | 14 | 3 | 707 | 0 | 0 | 50 | 0 | 16 | 214 | 0 | 0 | 0 | 1067 | 7 | 51 | 130 | 76 | 0 | 344 | 345 | 36 | 42 | 27 | 95 | 0 | 104 | 10 | 17 | 96 | 28 | 34 | 39 | 29 | 0 | 320 | 346 | 0 | 60 | 157 | 8 | 0 | 85 | 30 | 0 | 18 | 172 | 17 | 85 | 100 | 62 | 1 | 24.05 | 12 | 7847.05 | 865 | 227 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 48 | 794 | 0 | 1120.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 11.55 | 189 | 0 | 190 | 0 | 160 | 0 | 379 | 0 | 0.2 | 158 | 52 | 0 | 11 | 0 | 0 | 0 | 0.8 | 145 | 0.16 | 0 | 175 | 120 | 180 | 0 | 351 | 850 | 0 | 6097.41 | 13944.46 | 98.75
13:00 | 96 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 51 | 0 | 132 | 145 | 195 | 55 | 55 | 160 | 13 | 450 | 296 | 0 | 0 | 55 | 326 | 193 | 0 | 19 | 125 | 22.5 | 14 | 0 | 0 | 0 | 15 | 0 | 0 | 2 | 33 | 62 | 0 | 25 | 25 | 4.39 | 218 | 15 | 12 | 666 | 0 | 0 | 50 | 0 | 17 | 214 | 0 | 0 | 0 | 1054 | 14 | 51 | 140 | 123 | 0 | 348 | 340 | 40 | 61 | 27 | 95 | 0 | 105 | 9 | 17 | 96 | 28 | 34 | 79 | 33 | 0 | 320 | 386 | 0 | 60 | 160 | 6 | 0 | 85 | 30 | 0 | 18 | 172 | 17 | 94 | 100 | 35 | 1 | 17.15 | 12 | 8112.04 | 865 | 235 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 40 | 822 | 0 | 1131.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 10.34 | 189 | 0 | 190 | 0 | 160 | 0 | 357 | 0 | 0.96 | 158 | 50 | 0 | 12 | 0 | 0 | 0 | 3 | 148 | 0.31 | 0 | 174 | 120 | 180 | 0 | 351 | 850 | 0 | 6128.98 | 14241.02 | 98.75
14:00 | 88 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 49 | 0 | 132 | 145 | 220 | 55 | 55 | 155 | 16 | 450 | 305 | 0 | 0 | 55 | 326 | 194 | 0 | 10 | 125 | 22.5 | 22 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 50 | 62 | 0 | 25 | 25 | 3.52 | 218 | 15 | 4 | 715 | 0 | 0 | 50 | 0 | 15 | 214 | 0 | 0 | 0 | 1095 | 18 | 51 | 138 | 143 | 0 | 347 | 340 | 43 | 103 | 28 | 95 | 0 | 103 | 9 | 17 | 96 | 28 | 43 | 36 | 36 | 0 | 320 | 390 | 0 | 60 | 157 | 0 | 0 | 85 | 30 | 0 | 0 | 0 | 17 | 85 | 100 | 36 | 2 | 18.16 | 3 | 8082.18 | 866 | 223 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 57 | 787 | 0 | 1126.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 19.74 | 187 | 0 | 190 | 0 | 160 | 0 | 363 | 0 | 2.29 | 153 | 51 | 0 | 14 | 0 | 0 | 0 | 3.5 | 119 | 0.13 | 0 | 173 | 117 | 180 | 0 | 351 | 848 | 0 | 6078.7 | 14160.88 | 98.75
15:00 | 78 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 50 | 0 | 133 | 127 | 235 | 55 | 55 | 157 | 16 | 450 | 305 | 0 | 0 | 55 | 325 | 192 | 0 | 14 | 125 | 22.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 44 | 62 | 0 | 25 | 30 | 2.86 | 219 | 0 | 2 | 683 | 0 | 0 | 50 | 1 | 0 | 213 | 0 | 0 | 0 | 1051 | 13 | 51 | 133 | 147 | 0 | 346 | 340 | 41 | 209 | 28 | 94 | 0 | 104 | 9 | 20 | 96 | 28 | 43 | 28 | 35 | 0 | 320 | 376 | 0 | 60 | 157 | 6 | 0 | 84 | 30 | 0 | 0 | 0 | 17 | 85 | 127 | 36 | 2 | 17.63 | 6 | 8283.99 | 866 | 223 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 42 | 803 | 0 | 1121.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 29.14 | 185 | 0 | 196 | 0 | 180 | 0 | 408 | 0 | 2.91 | 154 | 49 | 0 | 10 | 0 | 0 | 0 | 3 | 142 | 0.25 | 0 | 172 | 117 | 220 | 0 | 352 | 855 | 0 | 6198.06 | 14482.05 | 98.75
16:00 | 93 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 50 | 0 | 132 | 111 | 245 | 55 | 55 | 162 | 28 | 450 | 300 | 0 | 0 | 35 | 327 | 192 | 0 | 14 | 125 | 22.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 60 | 0 | 25 | 27 | 1.22 | 219 | 0 | 2 | 672 | 108 | 0 | 50 | 8 | 0 | 213 | 0 | 0 | 0 | 874 | 12 | 51 | 130 | 120 | 0 | 345 | 340 | 44 | 188 | 29 | 94 | 0 | 103 | 9 | 20 | 96 | 28 | 45 | 22 | 35 | 0 | 320 | 382 | 0 | 60 | 154 | 6 | 0 | 84 | 30 | 0 | 0 | 0 | 17 | 85 | 142 | 36 | 1 | 23.34 | 12 | 8222.76 | 866 | 223 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 29 | 777 | 0 | 1218.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 16.56 | 180 | 0 | 197 | 0 | 195 | 0 | 363 | 0 | 1.43 | 154 | 50 | 0 | 16 | 0 | 0 | 0 | 2.7 | 63 | 0.35 | 0 | 171 | 117 | 220 | 0 | 353 | 751 | 0 | 6009.25 | 14232.01 | 98.75
17:00 | 88 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 47 | 0 | 133 | 126 | 248 | 55 | 55 | 162 | 30 | 380 | 300 | 0 | 0 | 17 | 325 | 139 | 0 | 6 | 125 | 22.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 66 | 0 | 25 | 29 | 1.1 | 220 | 0 | 8 | 670 | 108 | 0 | 50 | 3 | 0 | 215 | 0 | 0 | 0 | 852 | 5 | 51 | 128 | 107 | 0 | 345 | 340 | 24 | 190 | 26 | 95 | 0 | 103 | 9 | 18 | 96 | 26 | 52.2 | 16 | 35 | 0 | 320 | 324 | 0 | 60 | 152 | 6 | 0 | 87 | 30 | 0 | 0 | 0 | 17 | 98 | 162 | 58 | 1 | 8.01 | 12 | 8061.51 | 867 | 218 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 15 | 762 | 0 | 1219.65 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 17 | 0 | 11.31 | 177 | 0 | 205 | 0 | 195 | 0 | 341 | 0 | 1.07 | 155 | 50 | 0 | 6 | 0 | 0 | 0 | 1.1 | 54 | 0.25 | 0 | 169 | 117 | 180 | 0 | 353 | 651 | 0 | 5811.38 | 13872.89 | 98.76
18:00 | 94 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 457 | 47 | 0 | 132 | 126 | 262 | 55 | 55 | 162 | 31 | 340 | 306 | 0 | 0 | 17 | 280 | 131 | 0 | 0 | 125 | 22.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 67 | 0 | 25 | 30 | 0.17 | 220 | 0 | 12 | 704 | 53 | 0 | 50 | 8 | 0 | 213 | 0 | 0 | 0 | 842 | 0 | 51 | 133 | 53 | 0 | 300 | 280 | 10 | 151 | 28 | 94 | 0 | 161 | 12 | 20 | 96 | 26 | 52.2 | 3 | 35 | 0 | 320 | 332 | 0 | 0 | 138 | 6 | 0 | 88 | 30 | 0 | 0 | 0 | 17 | 111 | 161 | 59 | 0 | 2.69 | 11 | 7837.26 | 868 | 215 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5 | 776 | 0 | 1126.1 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 7 | 0 | 3.81 | 140 | 0 | 140 | 0 | 140 | 0 | 381 | 0 | 0.34 | 156 | 49 | 0 | 1 | 0 | 0 | 0 | 0.5 | 23 | 0.05 | 0 | 174 | 100 | 180 | 0 | 301 | 641 | 0 | 5473.8 | 13311.06 | 98.76
19:00 | 80 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 47 | 0 | 133 | 143 | 262 | 55 | 55 | 162 | 16 | 450 | 305 | 0 | 0 | 17 | 310 | 157 | 0 | 0 | 125 | 22.2 | 22 | 0 | 0 | 4 | 15 | 6 | 0 | 1 | 65 | 73 | 0 | 25 | 25 | 0 | 220 | 3 | 12 | 746 | 160 | 0 | 50 | 0 | 7 | 215 | 0 | 0 | 0 | 1020 | 0 | 51 | 130 | 53 | 0 | 331 | 310 | 10 | 209 | 28 | 95 | 0 | 189 | 18 | 17 | 96 | 30 | 52.2 | 0 | 36 | 0 | 320 | 356 | 0 | 0 | 136 | 6 | 0 | 88 | 30 | 0 | 0 | 0 | 17 | 111 | 171 | 60 | 0 | 0 | 12 | 8608.4 | 868 | 215 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 922 | 21 | 1313.85 | 0 | 8 | 0 | 5 | 4 | 80 | 0 | 11 | 52.2 | 0 | 20 | 0 | 147 | 0 | 170 | 0 | 170 | 0 | 398 | 0 | 0 | 154 | 49 | 95 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 120 | 220 | 0 | 301 | 645 | 0 | 6236.05 | 14844.45 | 98.77
19:30 | 74 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 47 | 0 | 133 | 143 | 262 | 55 | 55 | 162 | 16 | 450 | 305 | 0 | 0 | 17 | 327 | 196 | 0 | 0 | 125 | 22.2 | 22 | 0 | 0 | 14 | 15 | 41 | 0 | 2 | 65 | 76 | 0 | 25 | 25 | 0 | 220 | 10 | 13 | 698 | 160 | 0 | 50 | 0 | 17 | 216 | 0 | 0 | 0 | 1060 | 0 | 51 | 129 | 53 | 0 | 346 | 340 | 40 | 195 | 28 | 95 | 0 | 193 | 18 | 20 | 96 | 28 | 52.2 | 0 | 36 | 0 | 320 | 364 | 0 | 0 | 139 | 8 | 0 | 88 | 30 | 0 | 0 | 0 | 17 | 111 | 172 | 60 | 0 | 0 | 12 | 8852.4 | 868 | 216 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1101 | 34 | 1307.56 | 0 | 27 | 0 | 110 | 5 | 89 | 35 | 11 | 52.2 | 0 | 28 | 0 | 177 | 0 | 195 | 0 | 194 | 0 | 349 | 0 | 0 | 155 | 47 | 109 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 120 | 220 | 0 | 301 | 680 | 0 | 6747.76 | 15600.16 | 98.77
20:00 | 72 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 47 | 0 | 133 | 143 | 262 | 55 | 55 | 162 | 16 | 450 | 300 | 0 | 0 | 17 | 327 | 196 | 0 | 0 | 125 | 23.2 | 22 | 0 | 0 | 0 | 0 | 39 | 0 | 1 | 65 | 76 | 0 | 25 | 25 | 0 | 220 | 15 | 14 | 688 | 160 | 0 | 49 | 0 | 15 | 217 | 0 | 0 | 0 | 1042 | 0 | 51 | 128 | 53 | 0 | 350 | 340 | 32 | 184 | 32 | 94 | 0 | 193 | 19 | 17 | 96 | 28 | 52.2 | 0 | 36 | 0 | 320 | 328 | 0 | 0 | 136 | 8 | 0 | 88 | 30 | 0 | 0 | 0 | 17 | 111 | 171 | 64 | 0 | 0 | 12 | 8739.4 | 868 | 215 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1094 | 32 | 1301.58 | 0 | 30 | 0 | 105 | 6 | 89 | 95 | 31 | 52.2 | 0 | 28 | 0 | 176 | 0 | 194 | 0 | 192 | 0 | 331 | 0 | 0 | 157 | 49 | 109 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 120 | 220 | 0 | 300 | 695 | 0 | 6798.78 | 15538.18 | 98.78
21:00 | 73 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 502 | 47 | 0 | 133 | 110 | 262 | 55 | 55 | 162 | 16 | 450 | 305 | 0 | 0 | 35 | 327 | 196 | 0 | 0 | 125 | 0 | 22 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 65 | 76 | 0 | 25 | 25 | 0 | 220 | 0 | 20 | 713 | 108 | 0 | 33 | 0 | 0 | 218 | 0 | 0 | 0 | 1140 | 0 | 51 | 132 | 53 | 0 | 346 | 340 | 48 | 198 | 32 | 95 | 0 | 193 | 18 | 20 | 96 | 26 | 52.2 | 0 | 36 | 0 | 320 | 347 | 0 | 0 | 137 | 8 | 0 | 88 | 30 | 0 | 0 | 0 | 17 | 111 | 172 | 66 | 0 | 0 | 12 | 8762.2 | 868 | 215 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1104 | 17 | 1308.3 | 0 | 30 | 0 | 111 | 11 | 89 | 113 | 36 | 52.2 | 0 | 28 | 0 | 176 | 0 | 202 | 0 | 199 | 0 | 356 | 0 | 0 | 157 | 49 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 120 | 220 | 0 | 301 | 740 | 0 | 6940.5 | 15702.7 | 98.79
22:00 | 83 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 502 | 46 | 0 | 132 | 110 | 262 | 55 | 55 | 162 | 16 | 450 | 304 | 0 | 0 | 35 | 329 | 196 | 0 | 0 | 125 | 0 | 22 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 65 | 68 | 0 | 25 | 25 | 0 | 217 | 0 | 22 | 710 | 108 | 0 | 33 | 15.5 | 0 | 218 | 0 | 0 | 0 | 1146 | 0 | 51 | 133 | 53 | 0 | 348 | 340 | 48 | 197 | 32 | 95 | 0 | 182 | 18 | 20 | 96 | 30 | 52.2 | 0 | 36 | 0 | 320 | 354 | 0 | 0 | 135 | 8 | 0 | 88 | 30 | 0 | 0 | 0 | 17 | 111 | 172 | 67 | 0 | 0 | 12 | 8787.7 | 868 | 206 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1058 | 17 | 1307.07 | 0 | 30 | 0 | 113 | 25 | 89 | 113 | 36 | 52.2 | 0 | 28 | 0 | 173 | 0 | 205 | 0 | 210 | 0 | 354 | 0 | 0 | 158 | 49 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 120 | 220 | 0 | 301 | 700 | 0 | 6870.27 | 15657.97 | 98.8
23:00 | 90 | 90 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 502 | 48 | 0 | 132 | 79 | 262 | 55 | 55 | 162 | 16 | 450 | 297 | 0 | 0 | 55 | 327 | 196 | 0 | 0 | 125 | 0 | 22 | 0 | 0 | 0 | 0 | 72 | 0 | 5 | 65 | 68 | 0 | 25 | 25 | 0 | 217 | 0 | 30 | 696 | 108 | 0 | 33 | 25.5 | 0 | 219 | 0 | 0 | 0 | 1135 | 0 | 51 | 138 | 73 | 0 | 348 | 340 | 48 | 191 | 32 | 94 | 0 | 181 | 18 | 20 | 96 | 30 | 52.2 | 0 | 36 | 0 | 320 | 366 | 0 | 0 | 139 | 8 | 0 | 88 | 30 | 0 | 0 | 0 | 17 | 110 | 130 | 67 | 0 | 0 | 12 | 8754.7 | 868 | 203 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 17 | 1307.85 | 0 | 31 | 0 | 113 | 25 | 89 | 113 | 36 | 8 | 0 | 28 | 0 | 170 | 0 | 208 | 0 | 210 | 0 | 400 | 0 | 0 | 159 | 49 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 120 | 220 | 0 | 302 | 698 | 0 | 6857.85 | 15612.55 | 98.81
Total KWH | 1219360 | 1810560 | 726720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8606080 | 870120 | 0 | 2550960 | 2414880 | 3607320 | 824197 | 1007360 | 2904480 | 262080 | 9969500 | 7166633 | 0 | 0 | 775604 | 7800140 | 4410000 | 0 | 97174 | 2889600 | 444000 | 478440 | 0 | 0 | 33873 | 143018 | 349440 | 0 | 13920 | 1175108 | 925392 | 0 | 598080 | 625920 | 15281 | 5170298 | 285200 | 338880 | 17236363.64 | 869818 | 0 | 841920 | 134870.4 | 493454 | 5093614 | 0 | 0 | 0 | 25107270 | 125685 | 1182828 | 2149454 | 2893818 | 0 | 6614200 | 7750000 | 951360 | 4013000 | 680040 | 2184960 | 0 | 3118560 | 275520 | 420790 | 2318760 | 634560 | 1063555 | 320955 | 842656 | 0 | 7665100 | 9086000 | 0 | 1060560 | 3483245 | 168240 | 0 | 2056320 | 711936 | 0 | 234000 | 2442950 | 495720 | 2282400 | 3393600 | 1432320 | 5850 | 140340 | 274800 | 192761010.04 | 21006545 | 5974560 | 0 | 17760 | 7552 | 912000 | 0 | 0 | 0 | 0 | 40176 | 524160 | 21229090 | 283200 | 28104097 | 0 | 218677 | 0 | 643008 | 74375 | 611792 | 511584 | 158132 | 229008 | 226130 | 144320 | 156000 | 4278000 | 0 | 4725327 | 0 | 4613536 | 0 | 8892218 | 0 | 12060 | 3876000 | 1124072 | 1073474 | 87819 | 1262457 | 0 | 0 | 19946.28 | 840960 | 2644 | 21504 | 4451000 | 2803000 | 5122330 | 0 | 9687272.72 | 21397818.18 | 290400 | 155654004.18 | 348415014.22

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 20-07-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13944.46 | MW | 12:00 Hr. | Energy Generated |  |  | 348.415 |  | MKWHr.
| Day Peak Demand |  |  | 13944.46 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.51 |  | MKWHr.
| Evening Peak Generation |  |  | 15702.7 | MW | 21:00 Hr. | Energy Demand |  |  | 349.925 |  | MKWHr.
| Evening Peak Demand |  |  | 15860.16 | MW | 19:30 Hr. | Maximum Temperature |  |  | 32 |  | °C
| Minimum Generation of the Day |  |  | 12758.17 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 983.09 |  | MMCFD
| Maximum Generation of the Day |  |  | 15952.4 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.7524 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 38.8748 | 0 | 21.8632 | 0 | 0 | 0.097174 | 0 | 0 | 60.8352 | Gas | 133.563 | Gas | 463755106.07
| Chattogram Zone |  |  | 5.4325 | 42.3436 | 6.4761 | 0 | 5.1703 | 0.14097 | 0 | 0.01392 | 59.5774 | Coal | 104.1089 | Coal | 609025395.0682
| Cumilla Zone |  |  | 24.506 | 0 | 11.9535 | 0 | 0 | 0.32095 | 0.63456 | 0 | 37.415 | HFO | 52.3267 | HFO | 979617675.318
| Mymensingh Zone |  |  | 1.4323 | 0 | 6.4465 | 0 | 0 | 0.14619 | 0 | 0 | 8.025 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.9084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.9084 | Hydro | 5.1703 | Hydro | 517029.8
| Khulna Zone |  |  | 5.9746 | 21.2291 | 0.34869 | 0 | 0 | 0.52416 | 21.9185 | 0 | 49.995 | Solar | 2.575 | Solar | 42169124.3708
| Barishal Zone |  |  | 7.9253 | 35.5361 | 0.3119 | 0 | 0 | 0.002644 | 0 | 0 | 43.776 | Import | 50.6572 | Import | 257360048.28
| Rajshahi Zone |  |  | 22.5091 | 0 | 2.5909 | 0 | 0 | 0.39419 | 28.1041 | 0 | 53.5983 | Wind | 0.01392 | Wind | 203788.8
| Rangpur Zone |  |  | 0 | 5.0001 | 2.3359 | 0 | 0 | 0.94873 | 0 | 0 | 8.2847
| Total |  |  | 133.563 | 104.1089 | 52.3267 | 0 | 5.1703 | 2.575 | 50.6572 | 0.01392 | 348.415
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 463755106.07 |  | Hydro | 517029.8
|  |  |  | Coal | 609025395.0682 |  | Solar | 42169124.3708
|  |  |  | HFO | 979617675.318 |  | Import | 257360048.28
|  |  |  | HSD | 0 |  | Wind | 203788.8
[5 empty] | Total: | 235,26,48,167 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.0065 | Peak Hr Flow | 868.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 40447163.73 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 28.1041 | Peak Hr Flow | 1308.30 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 992 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.63456 | Peak Hr Flow | 26.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 1060 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 49.7452 | Peak Hr Flow | 2202.30 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 47 |  | 5435
|  |  |  | Chattogram |  | 0 |  | 1452
|  |  |  | Cumilla |  | 0 |  | 1458
|  |  |  | Mymensingh |  | 0 |  | 1273
|  |  |  | Sylhet |  | 38 |  | 631
|  |  |  | Khulna |  | 0 |  | 1876
|  |  |  | Barishal |  | 0 |  | 472
|  |  |  | Rajshahi |  | 0 |  | 1605
|  |  |  | Rangpur |  | 18 |  | 1025
|  |  |  | Total |  | 103 |  | 15227
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Bibiana-II 341 MW CCPP (Summit) GT |  |  | 222 | 3 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
|  | 4 | Bibiana-II 341 MW CCPP (Summit) ST |  |  | 119 | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 641 |  |  |  | Total | 707
|  |  |  | Total Unavailable Capacity |  |  |  | 1348
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:26 | Feni 132/33kV S/S Bus-1 is restored.
|  | 08:31 | Borhanuddin 230/33kV S/S Tr-Load HT is restored.
| 09:00 | 18:28 | Bogura 400/230kV S/S ATR-03 HT Project Work S/D Due to Painting work
| 09:00 | 18:28 | Bogura 400/230kV S/S ATR-03 LT Project Work S/D Due to Painting work
| 09:10 |  | Ishurdi - Pabna 100mw solar 132kv Ckt 1 SYN.
| 09:11 |  | Ishurdi - Pabna 100mw solar 132kv Ckt 2 SYN.
|  | 09:26 | Barishal 132/33kV S/S T-1 (405T) HT is restored.
|  | 09:27 | Barishal 132/33kV S/S T-1 (405T) LT is restored.
| 09:38 |  | Ashuganj CCPP 225 MW Tripped with remarks:- ST
| 09:46 | 10:08 | Barishal 230/132kV S/S T-4 LT Tripped showing Micom p142 relays Due to 33kv nabagram | [7 empty] | 45.0MW load
|  |  | feeder | [7 empty] | interrup.
| 09:46 | 10:08 | Barishal 230/132kV S/S T-5 LT Tripped showing Micom p142 relays Due to Nabagram 33kv | [7 empty] | 45.0MW load
|  |  | feeder | [7 empty] | interrup.
| 10:00 |  | Ashuganj CCPP 225 MW Synchronized
| 10:23 | 12:40 | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-2 Scheduled S/D from Bog-Sherpur 132/33kV end Due
to Maintenance work and from Bogura 230/132kVend.
| 10:27 | 16:32 | Sonargaon 132/33kV S/S OPML(IEL-1) Scheduled S/D Due to Line Distance Relay change
purpose
| 11:19 |  | BB230 - Ruppoor 230kv Ckt 01 SYN.
| 11:30 |  | BB230 - Ruppoor 230kv Ckt 02 SYN.
| 11:40 | 11:51 | Cumilla(S) 132/33kV S/S TR-3 LT Tripped showing REF 615 RET 650 relays. | [7 empty] | 24.0MW load
interrup.
| 12:10 |  | Hathazari 230/132/33kV S/S MT-02 LT Forced S/D Due to Oil Acidity high.
| 12:10 |  | Hathazari 230/132/33kV S/S MT-02 HT Forced S/D Due to Oil Acidity high.
| 13:45 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- ST
| 14:24 |  | JERA Meghnaghat Power Limited 718 MW CCPP ST was sync.
| 14:35 | 18:29 | Ashuganj-Brahmanbaria 132kV Ckt-1 Scheduled S/D from Brahmanbaria 132/33kV end Due to
Project work and from Ashuganj 230/132/33kV end Due to 132KV GIS project work
| 14:41 |  | Raozan 25 MW PP Synchronized
| 15:50 |  | JERA Meghnaghat Power Limited 718 MW CCPP GT-11 was sync.
| 16:02 |  | JERA Meghnaghat Power Limited 718 MW CCPP GT-11 tripped.
| 16:38 |  | JERA Meghnaghat Power Limited 718 MW CCPP GT-11 was sync.
| 17:14 | 18:41 | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to Nobogram 33 kV feeder Bus DS | [7 empty] | 38.0MW load
|  |  | maintenance (Y-phase) | [7 empty] | interrup.
| 17:15 | 18:37 | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to Nobogram 33 kV feeder Bus DS | [7 empty] | 38.0MW load
|  |  | maintenance (Y-phase) | [7 empty] | interrup.
| 17:22 | 18:04 | Barguna 132/33kV S/S Transformer-2 LT Scheduled S/D Due to WZPDCL-1 , B-Phase Hi | [7 empty] | 8.0MW load
|  |  | Temperature Maintenance. | [7 empty] | interrup.
| 17:23 | 18:03 | Barguna 132/33kV S/S Transformer-2 HT Scheduled S/D Due to WZPDCL-1 , B-Phase Hi | [7 empty] | 8.0MW load
|  |  | Temperature Maintenance. | [7 empty] | interrup.
| 18:11 | 18:30 | Ishurdi 132/33kV S/S 132/33 kV T-2 LT Scheduled S/D Due to station auxiliary fuse | [7 empty] | 30.0MW load
|  |  | changing work. | [7 empty] | interrup.
| 18:11 | 18:29 | Ishurdi 132/33kV S/S 132/33 kV T-2 HT Scheduled S/D Due to station auxiliary fuse | [7 empty] | 30.0MW load
|  |  | changing work. | [7 empty] | interrup.
| 18:57 |  | Raozan 25 MW PP Tripped
|  | 20:02 | Maijdee 132/33kV S/S Chowmuhoni-Maijdee ckt -01 is restored.
|  | 20:03 | Lakshmipur 132/33kV S/S Lakshmipur-Chowmuhani Circuit 1 is restored.
| 21:00 |  | Evening Peak Generation: 15702 MW.
| 21:02 | 00:18 | Kushtia 132/33kV S/S T2 LT Forced S/D Due to T2A 33kV side CT load side Y phase Red Hot | [7 empty] | 10.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 21:03 | 00:17 | Kushtia 132/33kV S/S T2 HT Forced S/D Due to T2A 33kV side CT load side Y phase Red Hot | [7 empty] | 10.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 21:06 |  | Raozan 25 MW PP Synchronized
| 02:21 |  | Raozan 25 MW PP Shutdown
| 05:20 |  | Baropukuria unit-3 tripped.
| 06:05 | 07:46 | Barishal 132/33kV S/S T-2 (415T) LT Scheduled S/D
| 06:06 | 07:45 | Barishal 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to T-2 HT bushing high temperature
Remedy work
| 06:21 |  | Kabirpur 132/33kV S/S XFR, T-2 LT Scheduled S/D Due to 33 kv bus section ds maintenance. | [7 empty] | 82.0MW load
interrup.
| 06:22 |  | Kabirpur 132/33kV S/S XFR, T-2 HT Scheduled S/D Due to 33 kv bus section ds maintenance. | [7 empty] | 82.0MW load
interrup.
| 06:26 |  | Kabirpur 132/33kV S/S XFR, T-I LT Scheduled S/D Due to 33 kv bus section ds maintenance. | [7 empty] | 64.0MW load
interrup.
| 06:27 |  | Kabirpur 132/33kV S/S XFR, T-I HT Scheduled S/D Due to 33 kv bus section ds maintenance. | [7 empty] | 64.0MW load
interrup.
| 07:00 |  | Min. Gen. 12989 MW
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 20-07-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9969500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 305 | 7166633 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 824197 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 196 | 4410000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 327 | 7800140 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 73 | 1219360 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 47 | 870120 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 110 | 2414880 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 1007360 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 775604 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 0 | 444000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 478440 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 33 | 726720 | Engine Problem
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 262 | 3607320 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 133 | 2550960 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1810560 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 262080 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2904480 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 97174 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 502 | 8606080 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 125 | 2889600 | Engine Problem
Dhaka Area Total |  |  |  |  | 5939.724 | 3013 | 60835208
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 134870.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 125685 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 841920 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5170298 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 5093614 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 493454 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 76 | 925392 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 1175108 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 598080 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 20 | 338880 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 62 | 349440 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 15281 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 143018 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 285200 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 625920 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 33873 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 108 | 869818 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1140 | 25107270 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 13920 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 713 | 17236363.64 | FGMO
Chattogram Area Total |  |  |  |  | 4895.72 | 2705 | 59577405.04
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 198 | 4013000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 346 | 6614200 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 340 | 7750000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 32 | 680040 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 48 | 951360 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 53 | 2893818 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1182828 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 132 | 2149454 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 842656 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 193 | 3118560 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 26 | 634560 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 1063555 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 420790 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 96 | 2318760 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 18 | 275520 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 95 | 2184960 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 320955 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1736.2 | 37415016
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 66 | 1432320 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 5850 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 172 | 3393600 | Engine Problem
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 111 | 2282400 | Engine Problem
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 140340 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 274800 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 495720 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 378 | 8025030
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 1060560 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 137 | 3483245 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 711936 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 88 | 2056320 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 2442950 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 234000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 168240 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Plant Shutdown as per schedule HGPI work
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 347 | 9086000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7665100 | -
Sylhet Area Total |  |  |  |  | 2325 | 930 | 26908351
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 868 | 21006545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 17760 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 7552 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 215 | 5974560 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 283200 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 40176 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 524160 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1104 | 21229090 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2242 | 49995043
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 301 | 9687272.72 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 21504 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2803000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 740 | 21397818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5122330 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 290400 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 173 | 4451000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2644 | -
Barishal Area Total |  |  |  |  | 2236 | 1554 | 43775968.9
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 30 | 218677 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 11 | 74375 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 158132 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 176 | 4278000 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 202 | 4725327 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 199 | 4613536 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 356 | 8892218 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 144320 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 229008 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 89 | 611792 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 111 | 643008 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 511584 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 12060 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1308.3 | 28104097 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 156000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 226130 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2711.5 | 53598264
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 49 | 1124072 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 157 | 3876000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1262457 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 19946.28 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 114 | 1073474 | Engine Problem
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 87819 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 840960 | -
Rangpur Area Total |  |  |  |  | 950 | 433 | 8284728.28
Eastern Grid Total |  |  |  |  | 16667.715 | 8762.2 | 192761010.04
Western Grid Total |  |  |  |  | 10378.16 | 6940.5 | 155654004.18
National Grid Total |  |  |  |  | 27045.875 | 15702.7 | 348415014.22
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 20-07-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10164.22 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4960.3 | MW
i) Dhaka area |  |  | 5388.38 |  | MW | i) Khulna area |  |  |  | 1876.5 | MW
ii) Chattogram area |  |  | 1451.5 |  | MW | ii) Barishal area |  |  |  | 472 | MW
iii) Cumilla area |  |  | 1458.34 |  | MW | iii) Rajshahi area |  |  |  | 1604.8 | MW
iv) Mymensingh area |  |  | 1273 |  | MW | iv) Rangpur area |  |  |  | 1007 | MW
v) Sylhet area |  |  | 593 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15124.52 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 80 | 19:00 | 133 | PHP | 8 | 14:00
2 | AKSML | 144 | 01:00 | 68 | Ishurdi | 86 | 19:30 | 134 | Pabna | 134 | 21:00
3 | Aftabnagar | 40 | 14:00 | 69 | Jaldhaka | 80 | 22:00 | 135 | Palashbari | 116 | 00:00
4 | Agargaon | 142 | 13:00 | 70 | Jamalpur | 147 | 00:00 | 136 | Panchagarh | 58 | 19:30
5 | Agrabad | 94 | 16:00 | 71 | Jashore | 149 | 19:30 | 137 | Patuakhali | 75.3 | 00:00
6 | Amnura | 40 | 00:00 | 72 | Jhenaidah | 136 | 22:00 | 138 | Payra | 36 | 00:00
7 | Ashuganj | 109 | 02:00 | 73 | Joydebpur | 162 | 16:00 | 139 | Postogola | 61 | 13:00
8 | BSRM | 200 | 02:00 | 74 | Joypurhat | 72 | 00:00 | 140 | Purbachal | 23 | 21:00
9 | Bagerhat | 86 | 19:30 | 75 | Juldah | 14 | 00:00 | 141 | Purbasadipur | 150 | 00:00
10 | Bajitpur | 72 | 22:00 | 76 | KSRM | 28 | 14:00 | 142 | Rahanpur | 34 | 00:00
11 | Bakulia | 95 | 20:00 | 77 | Kabirpur | 234 | 11:00 | 143 | Rahim | 29 | 12:00
12 | Banani | 38 | 11:00 | 78 | Kachua | 102 | 23:00 | 144 | Rajbari | 88 | 20:00
13 | Bangabhaban | 18 | 10:00 | 79 | Kallyanpur | 93 | 00:00 | 145 | Rajendrapur | 137 | 22:00
14 | Barapukuria | 73 | 00:00 | 80 | Kalurghat | 40 | 16:00 | 146 | Rajshahi | 131 | 00:00
15 | Barguna | 24 | 00:00 | 81 | Kamrangirchar | 83.5 | 13:00 | 147 | Rajshahi-230 | 83 | 22:00
16 | Barishal | 128 | 11:00 | 82 | Kaptai | N/A | N/A | 148 | Ramganj | 118 | 19:00
17 | Barishal-230 | 98 | 00:00 | 83 | Kasba | 38 | 22:00 | 149 | Rampur | 42 | 00:00
18 | Baroaulia | 66 | 12:00 | 84 | Kazla | 95 | 00:00 | 150 | Rangamati | 18 | 19:00
19 | Baroirhat | 66 | 19:00 | 85 | Keranigonj | 81 | 21:00 | 151 | Rangpur | 148 | 21:00
20 | Bashundhara | 199 | 13:00 | 86 | Khagrachori | 38 | 19:30 | 152 | Ruppur | 6.8 | 09:00
21 | BashundharaCement | 16 | 14:00 | 87 | Khulna | 82 | 13:00 | 153 | SSM | 9 | 01:00
22 | Beanibazar | 87 | 00:00 | 88 | Khulshi | 148 | 10:00 | 154 | Saidpur | 112 | 19:30
23 | Benapole | 70 | 00:00 | 89 | Kishoreganj | 147 | 00:00 | 155 | Satkhira | 142 | 22:00
24 | Bhaluka | 154 | 21:00 | 90 | Kodda | 327 | 09:00 | 156 | Satmasjid | 118 | 19:00
25 | Bhandaria | 66 | 20:00 | 91 | Kulaura | 56 | 00:00 | 157 | Savar | 237 | 16:00
26 | Bhangura | 40 | 19:30 | 92 | Kurigram | 66 | 21:00 | 158 | SevenRings | 21.57 | 08:00
27 | Bheramara(GK) | 70 | 22:00 | 93 | Kushtia | 166 | 19:30 | 159 | ShahCement | 33 | 00:00
28 | Bhulta | 226 | 08:00 | 94 | Laksam | 36 | 23:00 | 160 | Shahjadpur | 88 | 19:30
29 | Bog-Sherpur | 72 | 00:00 | 95 | Lakshmipur | 23 | 22:00 | 161 | Shahjibazar | 135 | 00:00
30 | Bogura | 183 | 00:00 | 96 | Lalbag | 57 | 20:00 | 162 | Shahmirpur | 57 | 08:00
31 | Borhanuddin | 93 | 01:00 | 97 | Lalmonirhat | 67 | 23:00 | 163 | Shariatpur | 97 | 22:00
32 | Brahmanbaria | 142 | 01:00 | 98 | MI_Cement | 15.9 | 02:00 | 164 | Sherpur | 166 | 00:00
33 | Cantonment | 154 | 14:00 | 99 | Madanganj | 42 | 00:00 | 165 | Shikalbaha | 23 | 12:00
34 | Chandina | 19.1 | 00:00 | 100 | Madaripur | 118 | 01:00 | 166 | Shitalakhya | 86.6 | 13:00
35 | Chandpur | 86 | 20:00 | 101 | Madartek | 96 | 00:00 | 167 | Sholosohor | 44 | 15:00
36 | Chandraghona | 39 | 19:30 | 102 | Madunaghat | 59 | 22:00 | 168 | Shyampur | 158 | 01:00
37 | Chapai | 68 | 06:00 | 103 | Magura | 71 | 19:30 | 169 | Siddhirganj | 125 | 12:00
38 | Charsaidpur | 41 | 02:00 | 104 | Mahasthangarh | 104 | 00:00 | 170 | Sirajganj | 120 | 21:00
39 | Chauddagram | 77 | 23:00 | 105 | Maijdee | 16 | 22:00 | 171 | Sonargaon | 121 | 00:00
40 | Chhatak | 42 | 00:00 | 106 | Manikganj | 134 | 00:00 | 172 | Sreemongol | 88 | 00:00
41 | Chowmuhani | 215 | 19:00 | 107 | Maniknagar | 84 | 13:00 | 173 | Sreepur | 100 | 19:30
42 | Chuadanga | 123 | 23:00 | 108 | Matarbari | 51 | 00:00 | 174 | Srinagar | 50.46 | 22:00
43 | Coxsbazar | 139 | 19:00 | 109 | Matuail | 62 | 16:00 | 175 | Sunamganj | 64 | 00:00
44 | Cumilla(N) | 154 | 23:00 | 110 | Millgate | 126 | 15:00 | 176 | Sylhet | 53 | 19:00
45 | Cumilla(S) | 151 | 19:00 | 111 | Mirpur | 124 | 15:00 | 177 | Sylhet-132 | 125 | 00:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 11 | 16:00 | 178 | TK | 34.5 | 00:00
47 | Daudkandi | 151 | 20:00 | 113 | Mirzapur | 49 | 21:00 | 179 | Tangail | 184 | 22:00
48 | Dhaka | 80 | 13:00 | 114 | Mithapukur | 78 | 03:00 | 180 | Taraganj | 25 | 00:00
49 | Dhamrai | 128 | 15:00 | 115 | Modern | N/A | N/A | 181 | Thakurgaon | 109 | 00:00
50 | Dhanmondi | 154 | 13:00 | 116 | Mogbazar | 159 | 15:00 | 182 | Tongi | 139 | 11:00
51 | Dohazari | 107 | 23:00 | 117 | Mongla | 44 | 12:00 | 183 | Ullahpara | 40 | 19:30
52 | Faridpur | 172 | 00:00 | 118 | Motijheel | 46 | 13:00 | 184 | Ullon | 42 | 00:00
53 | Fatullah | 104 | 12:00 | 119 | Muktagacha | 41 | 00:00 | 185 | Uttara | 90 | 13:00
54 | Fenchuganj | 45 | 00:00 | 120 | Munshiganj | 119 | 00:00 | 186 | UttaraNew | 65 | 00:00
55 | Feni | 124 | 19:30 | 121 | Muradnagar | 46 | 22:00 | 187 | Zigatola | 76 | 20:00
56 | GPH | 78 | 02:00 | 122 | Mymensingh | 210 | 20:00
57 | Ghatail | 90 | 19:00 | 123 | Naogaon | 142 | 00:00
58 | Ghorashal | 14 | 00:00 | 124 | Narail | 62 | 19:30
59 | Ghorashal-230 | 92 | 02:00 | 125 | Narinda | 80 | 13:00
60 | Goalpara | 42 | 23:00 | 126 | Narshingdi | 187 | 01:00
61 | Gollamari | 88 | 00:00 | 127 | Natore | 167 | 19:30
62 | Gopalganj | 110.6 | 22:00 | 128 | Nawabganj | 62.4 | 22:00
63 | Gulshan | 126 | 11:00 | 129 | Netrakona | 149 | 20:00
64 | Halishahar | 75 | 15:00 | 130 | New | 64 | 12:00
65 | HaripurSBU | 159 | 13:00 | 131 | Niamatpur | 78 | 22:00
66 | Hasnabad | 89 | 19:30 | 132 | Noapara | 47 | 23:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 20-07-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15952.4 | 74 |  | 16029.73
1:00 | 15451.85 | 104 |  | 15560.53
2:00 | 14950.4 | 96 |  | 15050.4
3:00 | 14546.4 | 80 |  | 14630.4
4:00 | 14148.4 | 78 |  | 14230.4
5:00 | 13913.4 | 64 |  | 13980.4
6:00 | 13547.62 | 52 |  | 13601.96
7:00 | 13249.42 | 16 |  | 13266.42
8:00 | 12758.17 | 25 |  | 12784.3
9:00 | 13445 | 0 |  | 13445
10:00 | 13318.25 | 0 |  | 13318.25
11:00 | 13710.16 | 0 |  | 13710.16
12:00 | 13944.46 | 0 |  | 13944.46
13:00 | 14241.02 | 50 |  | 14293.02
14:00 | 14160.88 | 45 |  | 14207.88
15:00 | 14482.05 | 64 |  | 14549.05
16:00 | 14232.01 | 73 |  | 14308.01
17:00 | 13872.89 | 56 |  | 13931.41
18:00 | 13311.06 | 50 |  | 13363.31
19:00 | 14844.45 | 83 |  | 14931.45
19:30 | 15600.16 | 249 |  | 15860.16
20:00 | 15538.18 | 156 |  | 15701.18
21:00 | 15702.7 | 103 |  | 15810.7
22:00 | 15657.97 | 127 |  | 15790.97
23:00 | 15612.55 | 114 |  | 15731.55
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 20-07-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8681.4 | 7271 | 15952.4 | DAILY GENERATION CURVE
00:30 | 8599.05 | 7103.075 | 15702.125
01:00 | 8516.7 | 6935.15 | 15451.85 | 20-07-2025
01:30 | 8364.55 | 6836.575 | 15201.125
02:00 | 8212.4 | 6738 | 14950.4
02:30 | 7982.9 | 6765.5 | 14748.4
03:00 | 7753.4 | 6793 | 14546.4
03:30 | 7628.9 | 6718.5 | 14347.4
04:00 | 7504.4 | 6644 | 14148.4
04:30 | 7411.9 | 6619 | 14030.9
05:00 | 7319.4 | 6594 | 13913.4
05:30 | 7248.365 | 6482.145 | 13730.51
06:00 | 7177.33 | 6370.29 | 13547.62
06:30 | 7205.98 | 6192.54 | 13398.52
07:00 | 7234.63 | 6014.79 | 13249.42
07:30 | 6956.335 | 6047.46 | 13003.795
08:00 | 6678.04 | 6080.13 | 12758.17
08:30 | 6976.385 | 6125.2 | 13101.585
09:00 | 7274.73 | 6170.27 | 13445
09:30 | 7230.835 | 6150.79 | 13381.625
10:00 | 7186.94 | 6131.31 | 13318.25
10:30 | 7401.385 | 6112.82 | 13514.205
11:00 | 7615.83 | 6094.33 | 13710.16
11:30 | 7731.44 | 6095.87 | 13827.31
12:00 | 7847.05 | 6097.41 | 13944.46
12:30 | 7979.545 | 6113.195 | 14092.74
13:00 | 8112.04 | 6128.98 | 14241.02
13:30 | 8097.11 | 6103.84 | 14200.95
14:00 | 8082.18 | 6078.7 | 14160.88
14:30 | 8183.085 | 6138.38 | 14321.465
15:00 | 8283.99 | 6198.06 | 14482.05
15:30 | 8253.375 | 6103.655 | 14357.03
16:00 | 8222.76 | 6009.25 | 14232.01
16:30 | 8142.135 | 5910.315 | 14052.45
17:00 | 8061.51 | 5811.38 | 13872.89
17:30 | 7949.385 | 5642.59 | 13591.975
18:00 | 7837.26 | 5473.8 | 13311.06
18:30 | 8222.83 | 5854.925 | 14077.755
19:00 | 8608.4 | 6236.05 | 14844.45
19:30 | 8852.4 | 6747.76 | 15600.16
20:00 | 8739.4 | 6798.78 | 15538.18
20:30 | 8750.8 | 6869.64 | 15620.44 |  | Executive Engineer
21:00 | 8762.2 | 6940.5 | 15702.7 |  | Network Operation Division
21:30 | 8774.95 | 6905.385 | 15680.335
22:00 | 8787.7 | 6870.27 | 15657.97
22:30 | 8771.2 | 6864.06 | 15635.26
23:00 | 8754.7 | 6857.85 | 15612.55

## En-Curve
QF-LDC-12
Date | 20-07-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3684 | 2110.2 | 870 | 38 | 34 | 1303 | 210 | 4580 | 0 | 832 | 2291.2 | 0 | 0 | 0 | 74 | DAILY ENERGY CURVE
00:30 | 3645 | 2110.2 | 869 | 38 | 33 | 1261 | 210.5 | 4609.5 | 5.075 | 737 | 2183.85 | 0 | 0 | 0 | 89 | 20-07-2025
01:00 | 3606 | 2110.2 | 868 | 38 | 32 | 1219 | 211 | 4639 | 10.15 | 642 | 2076.5 | 0 | 0 | 0 | 104
01:30 | 3583 | 2112.7 | 868 | 38 | 31 | 1218 | 211 | 4634.5 | 5.075 | 545.5 | 1954.35 | 0 | 0 | 0 | 100 | Energy Generated | 348.415 |  | MKWHr
02:00 | 3560 | 2115.2 | 868 | 38 | 30 | 1217 | 211 | 4630 | 0 | 449 | 1832.2 | 0 | 0 | 0 | 96 | Energy not Served | 1.51 |  | MKWHr
02:30 | 3540.5 | 2066.2 | 868 | 38 | 29 | 1216 | 211.5 | 4737.5 | 0 | 434.5 | 1605.2 | 0 | 0 | 2 | 88 | Total Energy Requirement | 349.925 |  | MKWHr
03:00 | 3521 | 2017.2 | 868 | 38 | 28 | 1215 | 212 | 4845 | 0 | 420 | 1378.2 | 0 | 0 | 4 | 80
03:30 | 3558.5 | 2020.2 | 868 | 38 | 28 | 1178.5 | 212 | 4865.5 | 0 | 378 | 1198.7 | 0 | 0 | 2 | 79
04:00 | 3596 | 2023.2 | 868 | 38 | 28 | 1142 | 212 | 4886 | 0 | 336 | 1019.2 | 0 | 0 | 0 | 78
04:30 | 3620 | 2030.2 | 868 | 38 | 28 | 1122 | 212 | 4830.5 | 0 | 327.5 | 954.7 | 0 | 0 | 0 | 71
05:00 | 3644 | 2037.2 | 868 | 38 | 28 | 1102 | 212 | 4775 | 0 | 319 | 890.2 | 0 | 0 | 0 | 64
05:30 | 3646 | 1999.2 | 868 | 38 | 27 | 1103.5 | 212 | 4685 | 3.11 | 303 | 845.7 | 0 | 0 | 0 | 58
06:00 | 3648 | 1961.2 | 868 | 38 | 26 | 1105 | 212 | 4595 | 6.22 | 287 | 801.2 | 0 | 0 | 0 | 52
06:30 | 3744.5 | 1938.6 | 868 | 38 | 26 | 1034 | 212 | 4464.5 | 20.82 | 300.5 | 751.6 | 0 | 0 | 0 | 34
07:00 | 3841 | 1916 | 868 | 38 | 26 | 963 | 212 | 4334 | 35.42 | 314 | 702 | 0 | 0 | 0 | 16
07:30 | 3851 | 1656.75 | 868.5 | 38 | 15.5 | 980.36 | 211 | 4332 | 65.185 | 294 | 691.5 | 0 | 0 | 0 | 20.5
08:00 | 3861 | 1397.5 | 869 | 38 | 5 | 997.72 | 210 | 4330 | 94.95 | 274 | 681 | 0 | 0 | 0 | 25
08:30 | 3975 | 1479.35 | 868.5 | 38 | 14.5 | 1032.795 | 209.5 | 4264 | 118.94 | 297 | 804 | 0 | 0 | 0 | 12.5
09:00 | 4089 | 1561.2 | 868 | 38 | 24 | 1067.87 | 209 | 4198 | 142.93 | 320 | 927 | 0 | 0 | 0 | 0
09:30 | 3910.5 | 1497.35 | 868 | 38 | 23 | 1084.325 | 208.5 | 4154.5 | 171.45 | 357.5 | 1068.5 | 0 | 0 | 0 | 0
10:00 | 3732 | 1433.5 | 868 | 38 | 22 | 1100.78 | 208 | 4111 | 199.97 | 395 | 1210 | 0 | 0 | 0 | 0
10:30 | 3750 | 1405.75 | 866.5 | 38 | 23 | 1112.515 | 208 | 4128.5 | 241.44 | 406.5 | 1334 | 0 | 0 | 0 | 0
11:00 | 3768 | 1378 | 865 | 38 | 24 | 1124.25 | 208 | 4146 | 282.91 | 418 | 1458 | 0 | 0 | 0 | 0
11:30 | 3766 | 1381 | 865 | 38 | 26 | 1122.475 | 212 | 4150 | 307.335 | 439 | 1520.5 | 0 | 0 | 0 | 0
12:00 | 3764 | 1384 | 865 | 38 | 28 | 1120.7 | 216 | 4154 | 331.76 | 460 | 1583 | 0 | 0 | 0 | 0
12:30 | 3772.5 | 1440.75 | 865 | 38 | 28 | 1126.035 | 217 | 4139.5 | 362.455 | 480.5 | 1622 | 0 | 0 | 1 | 25
13:00 | 3781 | 1497.5 | 865 | 38 | 28 | 1131.37 | 218 | 4125 | 393.15 | 501 | 1661 | 0 | 0 | 2 | 50
13:30 | 3704.5 | 1524 | 865.5 | 38 | 28 | 1128.705 | 218 | 4149 | 373.245 | 511 | 1660 | 0 | 0 | 1 | 47.5
14:00 | 3628 | 1550.5 | 866 | 38 | 28 | 1126.04 | 218 | 4173 | 353.34 | 521 | 1659 | 0 | 0 | 0 | 45
14:30 | 3706 | 1684 | 866 | 38 | 28 | 1123.9 | 218.5 | 4146 | 344.565 | 508.5 | 1656.5 | 0 | 0 | 1.5 | 54.5
15:00 | 3784 | 1817.5 | 866 | 38 | 28 | 1121.76 | 219 | 4119 | 335.79 | 496 | 1654 | 0 | 0 | 3 | 64
15:30 | 3760.5 | 1813.35 | 866 | 38 | 28 | 1169.985 | 219 | 3960.5 | 272.695 | 497.5 | 1730 | 0 | 0 | 1.5 | 68.5
16:00 | 3737 | 1809.2 | 866 | 38 | 28 | 1218.21 | 219 | 3802 | 209.6 | 499 | 1806 | 0 | 0 | 0 | 73
16:30 | 3681 | 1765.7 | 866.5 | 38 | 27 | 1218.93 | 219.5 | 3732 | 176.22 | 513.5 | 1814.1 | 0 | 0 | 0 | 64.5
17:00 | 3625 | 1722.2 | 867 | 38 | 26 | 1219.65 | 220 | 3662 | 142.84 | 528 | 1822.2 | 0 | 0 | 0 | 56
17:30 | 3432.5 | 1713.7 | 867.5 | 38 | 26 | 1172.875 | 220 | 3652.5 | 94.7 | 528.5 | 1845.7 | 0 | 0 | 0 | 53
18:00 | 3240 | 1705.2 | 868 | 38 | 26 | 1126.1 | 220 | 3643 | 46.56 | 529 | 1869.2 | 0 | 0 | 0 | 50
18:30 | 3393 | 1798.7 | 868 | 38 | 28 | 1219.975 | 220 | 3829.5 | 23.28 | 616 | 2042.8 | 0 | 0 | 0.5 | 66.5
19:00 | 3546 | 1892.2 | 868 | 38 | 30 | 1313.85 | 220 | 4016 | 0 | 703 | 2216.4 | 0 | 0 | 1 | 83
19:30 | 3673 | 1986.2 | 868 | 38 | 28 | 1307.56 | 220 | 4213 | 0 | 743 | 2521.4 | 0 | 0 | 2 | 249
20:00 | 3616 | 1969.2 | 868 | 38 | 28 | 1301.58 | 220 | 4188 | 0 | 767 | 2541.4 | 0 | 0 | 1 | 156
20:30 | 3652 | 1946.6 | 868 | 38 | 27 | 1304.94 | 220 | 4282.5 | 0 | 755.5 | 2525.4 | 0 | 0 | 0.5 | 129.5
21:00 | 3688 | 1924 | 868 | 38 | 26 | 1308.3 | 220 | 4377 | 0 | 744 | 2509.4 | 0 | 0 | 0 | 103
21:30 | 3693.5 | 1923.5 | 868 | 38 | 28 | 1307.685 | 218.5 | 4336 | 0 | 747 | 2520.15 | 0 | 0 | 0 | 115
22:00 | 3699 | 1923 | 868 | 38 | 30 | 1307.07 | 217 | 4295 | 0 | 750 | 2530.9 | 0 | 0 | 0 | 127
22:30 | 3723 | 1935.5 | 868 | 38 | 30 | 1307.46 | 217 | 4276 | 0 | 727.5 | 2510.3 | 0 | 0 | 2.5 | 120.5
23:00 | 3747 | 1948 | 868 | 38 | 30 | 1307.85 | 217 | 4257 | 0 | 705 | 2489.7 | 0 | 0 | 5 | 114
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 20-07-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 388 | 18:30 | 368 | 00:00 | Payra | 417 | 18:00 | 407 | 01:00
Ashuganj | 399 | 18:00 | 366 | 23:00 | Rahanpur | 395 | 08:00 | 371 | 00:00
Bhulta | 395 | 18:00 | 373 | 00:00 | Rampal | 407 | 18:30 | 382 | 01:00
Bibiana | 384 | 07:00 | 375 | 08:00
BIPTC | 404 | 06:00 | 284 | 01:00
Bogura | 380 | 08:00 | 359 | 00:00
Gopalganj | 401 | 18:00 | 379 | 01:00
Kaliakoir | 371 | 18:00 | 351 | 08:00
Madunaghat | 393 | 18:00 | 385 | 04:00
Meghnaghat | 387 | 18:00 | 372 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 225 | 18:30 | 214 | 00:00 | Keranigonj | 222 | 18:00 | 210 | 19:00
AKSML | 231 | 18:00 | 223 | 00:00 | Khulna(S) | 233 | 18:30 | 215 | 00:00
Aminbazar | 225 | 18:00 | 215 | 02:00 | Madunaghat | 232 | 17:00 | 227 | 13:00
Ashuganj | 231 | 18:30 | 218 | 00:00 | Madunaghat-400 | 233 | 19:00 | 227 | 04:00
Ashuganj-400 | 231 | 18:30 | 218 | 00:00 | Maniknagar | 218 | 18:30 | 210 | 00:00
Baghabari | 233 | 18:00 | 224 | 00:00 | Meghnaghat | 227 | 18:00 | 220 | 00:00
Barapukuria | 222 | 06:00 | 212 | 00:00 | Meghnaghat-400 | 223 | 18:00 | 215 | 00:00
Barapukuria-230 | 222 | 06:00 | 212 | 00:00 | Mirsorai | 230 | 19:30 | 219 | 00:00
Barishal | 228 | 18:00 | 217 | 01:00 | Rajshahi | 233 | 18:30 | 220 | 02:00
Bheramara | 234 | 18:00 | 222 | 00:00 | Rampal | 233 | 18:30 | 216 | 01:00
Bhulta | 227 | 07:00 | 211 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 227 | 18:30 | 218 | 19:00 | Rampura | 226 | 07:00 | 214 | 00:00
BIPTC | 236 | 18:30 | 222 | 01:00 | Shikalbaha | 230 | 17:00 | 225 | 05:00
Bogura | 231 | 08:00 | 220 | 00:00 | Shyampur | 221 | 18:00 | 212 | 00:00
Bogura-400 | 231 | 08:00 | 220 | 00:00 | Siddhirganj | 220 | 18:00 | 213 | 00:00
Borhanuddin | 233 | 18:00 | 225 | 01:00 | Sirajgonj | 239 | 18:00 | 232 | 00:00
BSRM | 229 | 17:00 | 217 | 02:00 | Sreepur | 230 | 18:00 | 218 | 00:00
Cumilla(N) | 223 | 18:00 | 213 | 00:00 | Tongi | 224 | 17:00 | 212 | 07:00
Faridpur | 225 | 18:00 | 212 | 00:00
Fenchuganj | 228 | 13:00 | 218 | 19:00
Ghorashal | 232 | 07:00 | 225 | 09:00
Ghorashal-230 | 228 | 18:30 | 216 | 00:00
Gopalganj | 225 | 18:00 | 213 | 01:00
GPH | 230 | 18:00 | 222 | 02:00
Haripur | 220 | 18:00 | 211 | 00:00
Hasnabad | 223 | 18:00 | 213 | 00:00
Hathazari | 229 | 00:00 | 223 | 15:00
Ishurdi | 236 | 18:00 | 225 | 00:00
Jhenaidah | 231 | 18:00 | 214 | 00:00
Kaliakoir | 230 | 18:00 | 217 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 06:00 | 128 | 00:00 | Lalmonirhat | 131 | 06:00 | 118 | 00:00
Agargaon | 130 | 18:30 | 124 | 00:00 | Madanganj | 129 | 18:00 | 122 | 00:00
Agrabad | 130 | 07:00 | 126 | 14:00 | Madaripur | 136 | 18:00 | 127 | 01:00
AKS | 130 | 18:00 | 126 | 00:00 | Madartek | 135 | 07:00 | 126 | 17:00
Aminbazar | 133 | 18:00 | 127 | 05:00 | Madunaghat | 132 | 18:00 | 128 | 06:00
Amnura | 135 | 18:30 | 123 | 00:00 | Magura | 134 | 18:30 | 119 | 00:00
Ashuganj | 140 | 14:00 | 133 | 00:00 | Mahasthangarh | 133 | 08:00 | 124 | 01:00
Bagerhat | 134 | 18:30 | 119 | 01:00 | Maijdee | 107 | 22:00 | 106 | 21:00
Bajitpur | 132 | 18:00 | 122 | 00:00 | Manikganj | 127 | 18:00 | 118 | 00:00
Bakulia | 131 | 01:00 | 128 | 15:00 | Maniknagar | 129 | 18:00 | 124 | 00:00
Banani | 137 | 07:00 | 128 | 00:00 | Matarbari | 122 | 18:00 | 109 | 21:00
Bangabhaban | 128 | 18:00 | 124 | 00:00 | Matuail | 128 | 18:00 | 123 | 00:00
Barapukuria | 136 | 06:00 | 124 | 00:00 | Millgate | 131 | 18:00 | 122 | 09:00
Barguna | 136 | 00:00 | 131 | 22:00 | Mirpur | 131 | 18:00 | 123 | 08:00
Barishal | 134 | 18:00 | 125 | 01:00 | Mirzapur | 131 | 18:30 | 123 | 08:00
Barishal-230 | 135 | 18:00 | 126 | 01:00 | Mithapukur | 131 | 06:00 | 120 | 00:00
Baroaulia | 132 | 18:00 | 128 | 04:00 | MI_Cement | 130 | 18:00 | 124 | 00:00
Baroirhat | 124 | 18:00 | 115 | 00:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 136 | 07:00 | 122 | 09:00 | Mogbazar | 135 | 06:00 | 129 | 11:00
BashundharaCement | 132 | 18:00 | 122 | 00:00 | Mongla | 134 | 18:30 | 121 | 00:00
Beanibazar | 127 | 06:00 | 117 | 19:00 | Motijheel | 128 | 18:00 | 124 | 00:00
Benapole | 134 | 18:30 | 118 | 00:00 | Muktagacha | 136 | 18:00 | 122 | 04:00
Bhaluka | 132 | 10:00 | 119 | 00:00 | Munshiganj | 129 | 18:00 | 122 | 00:00
Bhandaria | 128 | 18:00 | 120 | 19:30 | Muradnagar | 125 | 18:00 | 117 | 00:00
Bhangura | 133 | 18:00 | 127 | 02:00 | Mymensingh | 137 | 10:00 | 110 | 00:00
Bheramara | 137 | 10:00 | 132 | 00:00 | Naogaon | 131 | 10:00 | 120 | 01:00
Bheramara(GK) | 137 | 18:00 | 131 | 23:00 | Narail | 135 | 18:30 | 119 | 00:00
Bhulta | 123 | 18:30 | 115 | 00:00 | Narinda | 0 | 00:00 | N/A | N/A
Bog-Sherpur | 133 | 08:00 | 125 | 02:00 | Narshingdi | ` | 18:00 | 124 | 00:00
Bogura | 135 | 07:00 | 128 | 01:00 | Natore | 135 | 18:30 | 126 | 01:00
Bogura-230 | 136 | 08:00 | 128 | 01:00 | Nawabganj | 132 | 18:30 | 125 | 00:00
Brahmanbaria | 135 | 18:30 | 126 | 00:00 | Netrakona | 126 | 12:00 | 107 | 00:00
Cantonment | 130 | 18:30 | 125 | 00:00 | New | 132 | 18:00 | 123 | 08:00
Chandina | 128 | 18:30 | 119 | 12:00 | Niamatpur | 132 | 08:00 | 124 | 01:00
Chandpur | 129 | 18:00 | 115 | 15:00 | Noapara | 136 | 18:00 | 123 | 00:00
Chandraghona | 133 | 18:00 | 129 | 12:00 | Pabna | 134 | 18:00 | 128 | 00:00
Chapai | 132 | 11:00 | 123 | 00:00 | Palashbari | 128 | 07:00 | 116 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 18:30 | 123 | 00:00 | Panchagarh | 136 | 05:00 | 120 | 12:00
Chauddagram | 123 | 18:00 | 114 | 19:00 | Patuakhali | 136 | 00:00 | 131 | 05:00
Chhatak | 126 | 06:00 | 112 | 23:00 | Payra | 137 | 18:00 | 134 | 03:00
Chowmuhani | 117 | 18:00 | 107 | 05:00 | PHP | 123 | 18:30 | 114 | 21:00
Chuadanga | 132 | 18:00 | 117 | 00:00 | Postogola | 131 | 18:00 | 126 | 01:00
Coxsbazar | 120 | 18:00 | 110 | 00:00 | Purbachal | 135 | 06:00 | 122 | 09:00
Cumilla(N) | 128 | 18:00 | 120 | 00:00 | Purbasadipur | 131 | 05:00 | 119 | 15:00
Cumilla(S) | 134 | 04:00 | 118 | 00:00 | Rahanpur | 134 | 08:00 | 126 | 00:00
Daganbhuiyan | 120 | 18:00 | 108 | 19:00 | Rahanpur-400 | 135 | 08:00 | 127 | 00:00
Daudkandi | 123 | 18:00 | 115 | 00:00 | Rahim | 127 | 22:00 | 123 | 03:00
Dhaka | 135 | 18:00 | 129 | 00:00 | Rajbari | 132 | 18:00 | 122 | 00:00
Dhamrai | 129 | 18:00 | 122 | 08:00 | Rajendrapur | 137 | 18:00 | 120 | 00:00
Dhanmondi | 136.5 | 07:00 | 128 | 11:00 | Rajshahi | 134 | 18:30 | 127 | 00:00
Dohazari | 130 | 18:00 | 123 | 21:00 | Rajshahi-230 | 134 | 18:30 | 127 | 00:00
Faridpur | 134 | 18:00 | 126 | 00:00 | Ramganj | 120 | 18:30 | 108 | 02:00
Fatullah | 131 | 18:30 | 124 | 00:00 | Rampur | 131 | 18:00 | 127 | 08:00
Fenchuganj | 134 | 09:00 | 126 | 19:00 | Rampura | 136 | 06:00 | 128 | 11:00
Feni | 123 | 18:00 | 113 | 00:00 | Rangamati | 131 | 18:00 | 128 | 03:00
Ghatail | 132 | 17:00 | 122 | 00:00 | Rangpur | 130 | 06:00 | 120 | 00:00
Ghorashal | 137 | 18:00 | 130 | 00:00 | Ruppur | 136 | 07:00 | 130 | 00:00
Goalpara | 139 | 18:30 | 125 | 01:00 | Saidpur | 132 | 06:00 | 120 | 00:00
Gollamari | 138 | 18:00 | 125 | 01:00 | Satkhira | 135 | 18:30 | 120 | 00:00
Gopalganj | 136 | 18:30 | 125 | 01:00 | Satmasjid | 130 | 18:30 | 124 | 00:00
Gopalganj-400 | 138 | 18:00 | 129 | 01:00 | Savar | 134 | 21:00 | 124 | 08:00
Gulshan | 136 | 06:00 | 128 | 10:00 | SevenRings | 137 | 18:00 | 128 | 09:00
Halishahar | 132 | 18:00 | 127 | 10:00 | ShahCement | 130 | 18:30 | 123 | 00:00
Haripur | 129 | 18:30 | 123 | 00:00 | Shahjadpur | 136 | 18:00 | 132 | 00:00
HaripurSBU | 129 | 18:30 | 123 | 00:00 | Shahjibazar | 134 | 10:00 | 125 | 00:00
Hasnabad | 130 | 23:00 | 125 | 00:00 | Shahmirpur | 133 | 18:00 | 128 | 14:00
Hathazari | 133 | 17:00 | 129 | 01:00 | Shariatpur | 135 | 18:00 | 125 | 01:00
Ishurdi | 138 | 18:00 | 131 | 01:00 | Sherpur | 138 | 18:00 | 126 | 00:00
Jaldhaka | 131 | 06:00 | 116 | 00:00 | Shikalbaha | 122 | 18:00 | 118 | 00:00
Jamalpur | 140 | 11:00 | 130 | 00:00 | Shikalbaha-230 | 133 | 17:00 | 129 | 05:00
Jashore | 132 | 09:00 | 117 | 00:00 | Shitalakhya | 130 | 18:00 | 124 | 00:00
Jhenaidah | 136 | 18:30 | 121 | 00:00 | Sholosohor | 132 | 18:00 | 128 | 02:00
Jhenaidah-230 | 136 | 18:00 | 124 | 00:00 | Shyampur | 130 | 18:00 | 125 | 00:00
Joydebpur | 136 | 18:00 | 121 | 08:00 | Shyampur-230 | 132 | 18:00 | 124 | 00:00
Joypurhat | 130 | 10:00 | 116 | 01:00 | Siddhirganj | 129 | 18:00 | 123 | 00:00
Juldah | 132 | 17:00 | 129 | 09:00 | Sirajganj | 132 | 05:00 | 126 | 00:00
Kabirpur | 134 | 18:00 | 119 | 09:00 | Sonargaon | 128 | 20:00 | 121 | 00:00
Kachua | 126 | 18:30 | 115 | 02:00 | Sreemongol | 133 | 08:00 | 124 | 23:00
Kaliakoir | 135 | 18:00 | 124 | 08:00 | Sreepur | 134 | 18:00 | 125 | 21:00
Kallyanpur | 132 | 18:00 | 127 | 00:00 | Srinagar | 133 | 18:00 | 126 | 00:00
Kalurghat | 132 | 18:00 | 128 | 04:00 | SSM | 132 | 00:00 | 132 | 00:00
Kamrangirchar | 132 | 18:00 | 125 | 00:00 | Sunamganj | 124 | 07:00 | 110 | 19:00
Kaptai | 134 | 18:00 | 125 | 12:00 | Sylhet | 129 | 08:00 | 117 | 23:00
Kasba | 124 | 18:00 | 116 | 00:00 | Sylhet-132 | 128 | 06:00 | 119 | 19:00
Kazla | 128 | 18:30 | 124 | 00:00 | Tangail | 129 | 16:00 | 121 | 00:00
Keranigonj | 133 | 18:30 | 126 | 00:00 | Taraganj | 131 | 06:00 | 120 | 00:00
Khagrachori | 131 | 18:00 | 127 | 12:00 | Thakurgaon | 134 | 05:00 | 118 | 12:00
Khulna | 136 | 18:00 | 123 | 01:00 | TK | 132 | 17:00 | 128 | 10:00
Khulna(S) | 139 | 18:30 | 126 | 00:00 | Tongi | 132 | 06:00 | 125 | 00:00
Khulshi | 132 | 11:00 | 126 | 03:00 | Ullahpara | 133 | 07:00 | 127 | 00:00
Kishoreganj | 130 | 18:00 | 115 | 00:00 | Ullon | 136 | 07:00 | 128 | 00:00
Kodda | 136 | 18:00 | 120 | 08:00 | Uttara | 132 | 18:30 | 124 | 08:00
KSRM | 133 | 18:00 | 127 | 14:00 | UttaraNew | 132 | 18:00 | 124 | 04:00
Kulaura | 133 | 06:00 | 125 | 19:00 | Zigatola | 131 | 19:00 | 126 | 00:00
Kurigram | 129 | 08:00 | 117 | 02:00
Kushtia | 133 | 18:00 | 126 | 00:00
Laksam | 125 | 18:30 | 112 | 04:00
Lakshmipur | 117 | 20:00 | 109 | 21:00
Lalbag | 132 | 18:30 | 125 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division