## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 22-07-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 21-07-2025 | during | 22-07-2025 | during | 22-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 0 | 0 | 0 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 301 | 296 | 335 | 335 | 331.5 | 331.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 196 | 194 | 208.13 | 208.13 | 198 | 198 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 324 | 335 | 335 | 330 | 330 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 90 | 7 | 102 | 80 | 80 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 49.3 | 47.5 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 110 | 133 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 17.5 | 22.5 | 33 | 33 | 26 | 26 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 33 | 33 | 52.19 | 52.19 | 42 | 42 | Engine Problem
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 245 | 261 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 108 | 132 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 16 | 16 | 104 | 104 | 50 | 50 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 155 | 150 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 35 | 0 | 35 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 35 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 455 | 451 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 125 | 125 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2847.8 | 3052 | 4727.65 | 4787.65 | 3955.83 | 3920.83
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 3 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 17 | 0 | 17 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 217 | 220 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 217 | 213 | 213 | 213 | 213 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 3 | 48 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 14 | 59 | 56 | 80 | 80 | 80 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 65 | 65 | 65 | 68 | 68 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 11 | 36 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 24 | 2 | 25 | 2 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 57 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.53 | 0 | 3.84 | 0 | 3.84 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 30 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 2 | 33 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 90 | 160 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1156 | 1125 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 0 | 3 | 0 | 3 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 700 | 682 | 790 | 790 | 790 | 790 | Machine Problem
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 2513.53 | 2856.5 | 3812.56 | 3835.72 | 3839.56 | 3838.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 201 | 188 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 337 | 343 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 340 | 340 | 318.81 | 318.81 | 318.81 | 318.81 | machine problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 28 | 35 | 46.7 | 46.7 | 32 | 32 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 46 | 46 | 55 | 55 | 48 | 48 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 98 | 45 | 195 | 195 | 185 | 185 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 123 | 143 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 30 | 36 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 104 | 195 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 26 | 26 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 47 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 16 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 96 | 95 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 28 | 113 | 113 | 18 | 37 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 95 | 95 | 115 | 115 | 115 | 115 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 46 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1693 | 1734.2 | 2434.56 | 2379.56 | 2124.36 | 2088.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 21-07-2025 | during | 22-07-2025 | during | 22-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 58 | 63 | 157.5 | 157.5 | 86 | 86 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 122 | 153 | 200 | 200 | 186 | 186 | Engine Problem
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 100 | 112 | 115 | 115 | 105 | 105 | Engine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 47.51 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 11 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 35 | 35 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 346.51 | 356 | 600.9 | 549 | 475.9 | 424
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 59 | 60 | 60 | 60 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 135 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 84 | 85 | 85 | 85 | 85 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 20 | 20 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 7 | 8 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | Plant Shutdown as per schedule HGPI work
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 306 | 355 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | machine problem
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 958 | 1010 | 1088 | 1088 | 1025 | 1025
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 882 | 856 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 197 | 181 | 410 | 410 | 270 | 270 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 60 | 60 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 72.83 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 857 | 1040 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2046.83 | 2132 | 3627.2 | 3552.2 | 3442 | 3367
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 300 | 302 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 117 | 117 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 655 | 750 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 171 | 167 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.19 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1463.19 | 1516 | 2162 | 2161 | 2152 | 2151
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 47 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 6 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 40 | 40 | 40 | 40 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 169 | 140 | 214 | 214 | 198 | 198 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 220 | 150 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 130 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 364 | 333 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 98 | 95 | 95 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.4 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1163 | 1404.18 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 61.54 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 99 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 2231.94 | 2495.38 | 3192.47 | 3025.87 | 3136.09 | 2969.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 0 | 48 | 48 | 48 | 48 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 70 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.1 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 70 | 0 | 115 | 115 | 95 | 95 | Engine Problem
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 20 | 0 | 20 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 205 | 0 | 151.54 | 0 | 151.54 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 435.1 | 0 | 488.14 | 310 | 468.14 | 290
System Total |  |  |  |  | 28565.2 | 27045.875 | 14535.9 | 15152.08 | 22133.48 | 21689 | 20618.88 | 20074.4
Forecast Scenario (22-07-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15000 |  | 0 |  | 15000
|  |  |  | 1:00 | 14760 |  | 0 |  | 14760
|  |  |  | 2:00 | 14600 |  | 0 |  | 14600
|  |  |  | 3:00 | 14250 |  | 0 |  | 14250
|  |  |  | 4:00 | 13900 |  | 0 |  | 13900
|  |  |  | 5:00 | 13750 |  | 0 |  | 13750
|  |  |  | 6:00 | 13200 |  | 573 |  | 13800
|  |  |  | 7:00 | 13070 |  | 477.5 |  | 13570
|  |  |  | 8:00 | 13000 |  | 477.5 |  | 13500
|  |  |  | 9:00 | 13300 |  | 477.5 |  | 13800
|  |  |  | 10:00 | 13950 |  | 286.5 |  | 14250
|  |  |  | 11:00 | 14200 |  | 191 |  | 14400
|  |  |  | 12:00 | 14580 |  | 191 |  | 14780
|  |  |  | 13:00 | 14790 |  | 95.5 |  | 14890
|  |  |  | 14:00 | 14500 |  | 95.5 |  | 14600
|  |  |  | 15:00 | 14700 |  | 0 |  | 14700
|  |  |  | 16:00 | 14900 |  | 0 |  | 14900
|  |  |  | 17:00 | 14600 |  | 0 |  | 14600
|  |  |  | 18:00 | 13800 |  | 0 |  | 13800
|  |  |  | 18:30 | 14400 |  | 0 |  | 14400
|  |  |  | 19:00 | 15200 |  | 0 |  | 15200
|  |  |  | 19:30 | 15900 |  | 0 |  | 15900
|  |  |  | 20:00 | 16000 |  | 0 |  | 16000
|  |  |  | 21:00 | 16200 |  | 0 |  | 16200
|  |  |  | 22:00 | 16100 |  | 0 |  | 16100
|  |  |  | 23:00 | 16000 |  | 0 |  | 16000
Probable Maximum Temperature: |  |  | 33.40°C
Probable Maximum Demand at Day Peak: |  |  | 14780.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16200.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16200.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 348.35 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:06 hrs on 22-07-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 21-07-2025 | [28 empty] | Date: | 21-07-2025 | [28 empty] | Date: | 21-07-2025 | [28 empty] | Date: | 21-07-2025 | [28 empty] | Date: | 21-07-2025 | [11 empty] | Date: | 21-07-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [11 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 87 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 502 | 50 | 0 | 133 | 79 | 262 | 55 | 55 | 162 | 16 | 450 | 307 | 0 | 0 | 55 | 323 | 196 | 0 | 0 | 125 | 23 | 22 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 65 | 68 | 0 | 25 | 25 | 0 | 218 | 0 | 31 | 737 | 53 | 0 | 33 | 25 | 0 | 219 | 0 | 0 | 0 | 1150 | 0 | 51 | 138 | 81 | 0 | 341 | 340 | 48 | 210 | 32 | 95 | 0 | 147 | 0 | 20 | 96 | 28 | 52.2 | 0 | 36 | 0 | 320 | 366 | 0 | 0 | 146 | 8 | 0 | 85 | 30 | 0 | 0 | 0 | 17 | 111 | 130 | 67 | 0 | 0 | 6 | 8759.2 | 868 | 202 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1055 | 17 | 1239.33 | 0 | 31 | 0 | 113 | 0 | 89 | 113 | 36 | 8 | 0 | 28 | 0 | 194 | 0 | 206 | 0 | 209 | 0 | 414 | 0 | 0 | 159 | 48 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 120 | 220 | 0 | 302 | 699 | 0 | 6815.33 | 15574.53 | 98.82
01:00 | 77 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 502 | 51 | 0 | 111 | 79 | 262 | 55 | 55 | 162 | 16 | 450 | 309 | 0 | 0 | 55 | 326 | 195 | 0 | 0 | 125 | 24 | 14 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 65 | 68 | 0 | 25 | 25 | 0 | 219 | 0 | 31 | 741 | 17 | 0 | 19 | 25.5 | 0 | 218 | 0 | 0 | 0 | 1097 | 0 | 51 | 132 | 81 | 0 | 343 | 340 | 48 | 209 | 32 | 79 | 0 | 51 | 0 | 20 | 96 | 28 | 52.2 | 0 | 36 | 0 | 320 | 392 | 0 | 0 | 145 | 8 | 0 | 85 | 30 | 0 | 0 | 0 | 17 | 110 | 130 | 67 | 0 | 0 | 8 | 8438.7 | 868 | 187 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1013 | 17 | 1249.13 | 0 | 31 | 0 | 113 | 0 | 89 | 50 | 36 | 8 | 0 | 28 | 0 | 198 | 0 | 204 | 0 | 150 | 0 | 388 | 0 | 0 | 158 | 48 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 120 | 220 | 0 | 302 | 699 | 0 | 6616.13 | 15054.83 | 98.86
02:00 | 8 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 502 | 50 | 0 | 96 | 62 | 195 | 30 | 55 | 162 | 16 | 450 | 306 | 0 | 0 | 55 | 324 | 195 | 0 | 0 | 125 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 69 | 0 | 25 | 25 | 0 | 219 | 0 | 31 | 726 | 17 | 0 | 19 | 8 | 0 | 220 | 0 | 0 | 0 | 1095 | 0 | 51 | 137 | 81 | 0 | 348 | 340 | 48 | 200 | 32 | 73 | 0 | 51 | 0 | 20 | 96 | 28 | 52.2 | 0 | 36 | 0 | 320 | 388 | 0 | 0 | 148 | 8 | 0 | 85 | 30 | 0 | 0 | 0 | 17 | 110 | 130 | 67 | 0 | 0 | 12 | 8155.2 | 868 | 185 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 990 | 0 | 1229.48 | 0 | 31 | 0 | 50 | 0 | 89 | 50 | 36 | 8 | 0 | 28 | 0 | 198 | 0 | 203 | 0 | 150 | 0 | 367 | 0 | 0 | 156 | 48 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 120 | 220 | 0 | 302 | 699 | 0 | 6462.48 | 14617.68 | 98.9
03:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 502 | 49 | 0 | 81 | 31 | 45 | 15 | 55 | 162 | 16 | 450 | 307 | 0 | 0 | 35 | 326 | 194 | 0 | 0 | 125 | 24 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 69 | 0 | 25 | 25 | 0 | 220 | 0 | 21 | 737 | 0 | 0 | 12 | 0 | 0 | 221 | 0 | 0 | 0 | 1109 | 0 | 51 | 138 | 43 | 0 | 345 | 340 | 48 | 205 | 32 | 69 | 0 | 51 | 0 | 20 | 96 | 26 | 52.2 | 0 | 35 | 0 | 320 | 392 | 0 | 40 | 158 | 8 | 0 | 85 | 30 | 0 | 0 | 0 | 17 | 110 | 130 | 67 | 0 | 0 | 12 | 7897.2 | 868 | 188 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 986 | 0 | 1219.32 | 0 | 31 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 198 | 0 | 203 | 0 | 150 | 0 | 388 | 0 | 0 | 155 | 46 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 120 | 220 | 0 | 302 | 698 | 0 | 6246.32 | 14143.52 | 98.94
04:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 502 | 50 | 0 | 51 | 31 | 15 | 15 | 55 | 162 | 0 | 450 | 303 | 0 | 0 | 17 | 327 | 196 | 0 | 0 | 108 | 22 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 69 | 0 | 25 | 25 | 0 | 220 | 0 | 23 | 710 | 0 | 0 | 19 | 0 | 0 | 220 | 0 | 0 | 0 | 1005 | 0 | 51 | 80 | 45 | 0 | 349 | 340 | 49 | 209 | 32 | 74 | 0 | 51 | 0 | 20 | 96 | 24 | 52.2 | 0 | 35 | 0 | 320 | 388 | 0 | 40 | 158 | 7 | 0 | 85 | 30 | 0 | 0 | 0 | 17 | 110 | 130 | 67 | 0 | 0 | 12 | 7612.2 | 868 | 188 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 992 | 0 | 1258.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 198 | 0 | 206 | 0 | 150 | 0 | 361 | 0 | 0 | 156 | 48 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 120 | 220 | 0 | 302 | 699 | 0 | 6187.24 | 13799.44 | 98.98
05:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 502 | 47 | 0 | 51 | 31 | 15 | 0 | 55 | 162 | 0 | 450 | 298 | 0 | 0 | 17 | 328 | 196 | 0 | 0 | 108 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 65 | 62 | 0 | 25 | 25 | 0 | 220 | 0 | 18 | 703 | 0 | 0 | 19 | 0 | 0 | 220 | 0 | 0 | 0 | 990 | 0 | 51 | 80 | 45 | 0 | 349 | 340 | 48 | 195 | 29 | 74 | 0 | 51 | 0 | 20 | 96 | 24 | 34 | 0 | 35 | 0 | 320 | 366 | 0 | 40 | 156 | 7 | 0 | 85 | 30 | 0 | 0 | 0 | 17 | 111 | 130 | 67 | 0 | 0 | 12 | 7497 | 868 | 198 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 965 | 0 | 1254.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 209 | 0 | 150 | 0 | 350 | 0 | 0 | 160 | 47 | 70 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 120 | 220 | 0 | 301 | 698 | 0 | 6128.67 | 13625.67 | 99.02
06:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 502 | 45 | 0 | 51 | 31 | 15 | 0 | 52 | 162 | 0 | 450 | 296 | 0 | 0 | 17 | 332 | 197 | 0 | 1 | 108 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 0.35 | 220 | 0 | 23 | 713 | 0 | 0 | 19 | 0 | 0 | 220 | 0 | 0 | 0 | 986 | 1 | 51 | 10 | 45 | 0 | 353 | 340 | 47 | 205 | 29 | 78 | 0 | 51 | 0 | 20 | 70 | 24 | 25 | 0 | 35 | 0 | 320 | 386 | 0 | 40 | 150 | 7 | 0 | 85 | 30 | 0 | 0 | 0 | 17 | 103 | 130 | 67 | 0 | 1.26 | 6 | 7292.61 | 868 | 197 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 946 | 0 | 1215.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 2.13 | 197 | 0 | 211 | 0 | 150 | 0 | 341 | 0 | 0 | 0 | 47 | 70 | 1 | 60 | 0 | 0 | 0 | 11 | 0 | 0 | 165 | 120 | 220 | 0 | 301 | 685 | 0 | 5851.89 | 13144.5 | 99.06
07:00 | 0 | 52 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 502 | 21 | 0 | 51 | 31 | 15 | 0 | 35 | 108 | 0 | 420 | 298 | 0 | 0 | 0 | 333 | 196 | 0 | 5 | 90 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 0.85 | 220 | 0 | 20 | 699 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1000 | 3 | 51 | 10 | 45 | 0 | 353 | 340 | 48 | 202 | 29 | 73 | 0 | 51 | 0 | 20 | 70 | 22 | 8 | 11 | 36 | 0 | 320 | 382 | 0 | 40 | 156 | 7 | 0 | 85 | 30 | 0 | 0 | 0 | 17 | 103 | 85 | 67 | 0 | 8.53 | 0 | 7066.38 | 867 | 202 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 10 | 942 | 0 | 1215.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 9.09 | 195 | 0 | 220 | 0 | 150 | 0 | 348 | 0 | 0.84 | 0 | 47 | 70 | 4 | 55 | 0 | 0 | 2.1 | 27 | 0.02 | 0 | 169 | 120 | 220 | 0 | 302 | 690 | 0 | 5922.75 | 12989.13 | 99.1
08:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455 | 15 | 0 | 51 | 16 | 15 | 0 | 31 | 108 | 16 | 420 | 298 | 0 | 0 | 0 | 290 | 196 | 0 | 12 | 90 | 19 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 1.63 | 220 | 0 | 2 | 724 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1002 | 7 | 51 | 10 | 8 | 0 | 300 | 340 | 47 | 203 | 29 | 73 | 0 | 54 | 0 | 20 | 70 | 22 | 8 | 23 | 36 | 0 | 320 | 386 | 0 | 40 | 147 | 7 | 0 | 85 | 30 | 0 | 0 | 0 | 17 | 103 | 85 | 58 | 1 | 17.52 | 0 | 6937.15 | 869 | 204 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 15 | 929 | 0 | 1214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 25.24 | 195 | 0 | 220 | 0 | 150 | 0 | 361 | 0 | 2.21 | 0 | 47 | 70 | 9 | 70 | 0 | 0 | 1.3 | 52 | 0.08 | 0 | 172 | 120 | 180 | 0 | 301 | 703 | 0 | 5993.83 | 12930.98 | 99.14
09:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455 | 23 | 0 | 51 | 16 | 52 | 4 | 28 | 151 | 16 | 450 | 307 | 0 | 0 | 0 | 331 | 194 | 0 | 9 | 90 | 18 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 2.24 | 219 | 0 | 2 | 732 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1004 | 7 | 51 | 18 | 8 | 0 | 343 | 340 | 48 | 204 | 32 | 74 | 0 | 58 | 0 | 20 | 70 | 22 | 9 | 21 | 36 | 0 | 320 | 386 | 0 | 40 | 145 | 7 | 0 | 85 | 30 | 0 | 0 | 0 | 17 | 103 | 85 | 58 | 1 | 16.13 | 0 | 7172.37 | 868 | 202 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 21 | 910 | 0 | 1208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 41.36 | 168 | 0 | 220 | 0 | 150 | 0 | 373 | 0 | 3.58 | 0 | 48 | 70 | 14 | 70 | 0 | 0 | 5.3 | 101 | 0.29 | 0 | 172 | 120 | 180 | 0 | 301 | 702 | 0 | 6046.53 | 13218.9 | 99.17
10:00 | 7 | 52 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455 | 48.9 | 0 | 56 | 90 | 245 | 45 | 43 | 153 | 16 | 450 | 308 | 0 | 0 | 35 | 328 | 194 | 0 | 18 | 125 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 25 | 0 | 219 | 0 | 2 | 735 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1074 | 15 | 51 | 67 | 48 | 0 | 342 | 340 | 48 | 205 | 29 | 72 | 0 | 100 | 0 | 17 | 70 | 20 | 37 | 34 | 30 | 0 | 320 | 388 | 0 | 40 | 156 | 7 | 0 | 85 | 30 | 0 | 0 | 0 | 17 | 110 | 95 | 58 | 2 | 37.6 | 0 | 7894.5 | 876 | 201 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 49 | 794 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 30.32 | 169 | 0 | 220 | 0 | 150 | 0 | 381 | 0 | 4.35 | 0 | 48 | 70 | 23 | 70 | 0 | 0 | 3.6 | 137 | 0.23 | 0 | 173 | 120 | 180 | 0 | 303 | 662 | 0 | 5967.5 | 13862 | 99.2
11:00 | 7 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455 | 49.6 | 0 | 94 | 110 | 245 | 55 | 55 | 155 | 16 | 450 | 297 | 0 | 0 | 35 | 328 | 196 | 0 | 35 | 125 | 17.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 25 | 3.05 | 217 | 0 | 2 | 690 | 0 | 0 | 4 | 0 | 0 | 218 | 0 | 0 | 0 | 1160 | 12 | 51 | 113 | 85 | 0 | 344 | 340 | 47 | 195 | 28 | 85 | 0 | 108 | 4 | 17 | 88 | 24 | 44 | 47 | 30 | 0 | 320 | 323 | 0 | 60 | 156 | 7 | 0 | 84 | 30 | 0 | 0 | 0 | 17 | 110 | 103 | 58 | 2 | 28.7 | 0 | 8122.85 | 877 | 203 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 69.09 | 778 | 0 | 1165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112 | 0 | 53.27 | 169 | 0 | 220 | 0 | 150 | 0 | 350 | 0 | 4.9 | 0 | 48 | 70 | 36 | 70 | 0 | 0 | 4 | 201 | 0.97 | 0 | 168 | 120 | 180 | 0 | 300 | 651 | 0 | 6038.23 | 14161.08 | 99.23
12:00 | 7 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455 | 49.3 | 0 | 108 | 110 | 245 | 55 | 55 | 155 | 16 | 450 | 301 | 0 | 0 | 35 | 330 | 196 | 0 | 31 | 125 | 17.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 14 | 0 | 11 | 25 | 4.53 | 217 | 2 | 2 | 700 | 90 | 0 | 50 | 3 | 3 | 216 | 0 | 0 | 0 | 1156 | 19 | 51 | 123 | 98 | 0 | 337 | 340 | 46 | 201 | 28 | 95 | 0 | 104 | 8 | 17 | 96 | 26 | 47 | 46 | 30 | 0 | 320 | 306 | 0 | 59 | 155 | 7 | 0 | 81 | 30 | 0 | 0 | 0 | 17 | 100 | 122 | 58 | 2 | 47.51 | 0 | 8358.84 | 882 | 197 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 72.83 | 857 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 61.54 | 169 | 0 | 220 | 0 | 150 | 0 | 364 | 0 | 5.4 | 0 | 48 | 70 | 35 | 70 | 0 | 0 | 7.1 | 205 | 0.19 | 0 | 171 | 117 | 220 | 0 | 300 | 655 | 0 | 6177.06 | 14535.9 | 99.26
13:00 | 7 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455 | 47.8 | 0 | 113 | 118 | 260 | 55 | 55 | 152 | 16 | 450 | 297 | 0 | 0 | 35 | 325 | 193 | 0 | 21 | 125 | 17.5 | 22 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 34 | 35 | 0 | 11 | 25 | 4.35 | 216 | 15 | 2 | 703 | 145 | 0 | 50 | 24 | 16 | 214 | 0 | 0 | 0 | 1145 | 15 | 51 | 128 | 93 | 0 | 339 | 340 | 43 | 162 | 34 | 95 | 0 | 104 | 9 | 17 | 96 | 28 | 52.2 | 35 | 30 | 0 | 320 | 295 | 0 | 59 | 153 | 8 | 0 | 84 | 30 | 0 | 0 | 0 | 17 | 110 | 122 | 58 | 2 | 29.17 | 0 | 8471.02 | 882 | 196 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 99.46 | 877 | 0 | 1299 | 0 | 0 | 0 | 0 | 0 | 8.8 | 0 | 0 | 0 | 51 | 0 | 57.37 | 160 | 0 | 220 | 0 | 130 | 0 | 350 | 0 | 5.1 | 0 | 48 | 70 | 34 | 61 | 0 | 0 | 6.8 | 185 | 0.59 | 0 | 169 | 117 | 220 | 0 | 299 | 604 | 0 | 6188.12 | 14659.14 | 99.29
14:00 | 7 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455 | 47.5 | 0 | 113 | 110 | 260 | 55 | 55 | 152 | 16 | 450 | 303 | 0 | 0 | 35 | 320 | 190 | 0 | 26 | 125 | 18 | 22 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 34 | 55 | 0 | 11 | 25 | 2.56 | 218 | 15 | 2 | 714 | 145 | 0 | 50 | 25.5 | 15 | 213 | 0 | 0 | 0 | 1161 | 9 | 51 | 127 | 53 | 0 | 334 | 340 | 42 | 182 | 31 | 95 | 0 | 114 | 8 | 19 | 96 | 28 | 52.2 | 57 | 35 | 0 | 320 | 320 | 0 | 59 | 153 | 8 | 0 | 84 | 30 | 0 | 0 | 0 | 17 | 110 | 122 | 54 | 1 | 46.62 | 0 | 8592.38 | 860 | 194 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 81.76 | 848 | 0 | 1274.59 | 0 | 0 | 0 | 0 | 0 | 8.8 | 0 | 0 | 0 | 24 | 0 | 34.99 | 157 | 0 | 220 | 0 | 130 | 0 | 377 | 0 | 1.83 | 0 | 48 | 115 | 30 | 98 | 0 | 0 | 3.9 | 134 | 0.68 | 0 | 172 | 117 | 220 | 0 | 298 | 601 | 0 | 6087.55 | 14679.93 | 99.32
15:00 | 7 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 50.4 | 0 | 117 | 118 | 261 | 55 | 55 | 157 | 16 | 450 | 300 | 0 | 0 | 17 | 318 | 190 | 0 | 12 | 125 | 17.5 | 22 | 0 | 0 | 0 | 0 | 68 | 0 | 14 | 34 | 52 | 0 | 11 | 25 | 2.07 | 218 | 16 | 2 | 700 | 160 | 0 | 50 | 25.5 | 16 | 213 | 0 | 0 | 0 | 1153 | 6 | 51 | 130 | 53 | 0 | 336 | 340 | 42 | 195 | 30 | 95 | 0 | 112 | 9 | 19 | 96 | 28 | 52.2 | 21 | 34 | 0 | 320 | 302 | 0 | 60 | 152 | 8 | 0 | 84 | 30 | 0 | 0 | 0 | 17 | 107 | 122 | 55 | 1 | 35.9 | 0 | 8585.57 | 860 | 186 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 73 | 884 | 0 | 1261.05 | 0 | 0 | 0 | 10 | 0 | 32 | 0 | 0 | 0 | 90 | 0 | 45.43 | 161 | 0 | 199 | 0 | 200 | 0 | 362 | 0 | 4.39 | 0 | 47 | 114 | 25 | 105 | 0 | 0 | 2.4 | 144 | 0.55 | 0 | 171 | 117 | 220 | 0 | 301 | 610 | 0 | 6262.82 | 14848.39 | 99.36
16:00 | 30 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 48.9 | 0 | 132 | 118 | 261 | 55 | 55 | 153 | 32 | 450 | 300 | 0 | 0 | 35 | 318 | 190 | 0 | 18 | 125 | 17.5 | 22 | 0 | 0 | 0 | 0 | 74 | 0 | 4 | 63 | 53 | 0 | 36 | 25 | 1.51 | 218 | 16 | 2 | 690 | 160 | 0 | 50 | 25.5 | 15 | 214 | 0 | 0 | 0 | 1161 | 13 | 51 | 125 | 53 | 0 | 336 | 340 | 41 | 193 | 27 | 93 | 0 | 101 | 18 | 19 | 95 | 28 | 52.2 | 37 | 34 | 0 | 320 | 375 | 0 | 60 | 152 | 8 | 0 | 84 | 30 | 0 | 0 | 0 | 17 | 107 | 120 | 56 | 1 | 23.6 | 0 | 8764.21 | 859 | 186 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 57 | 844 | 0 | 1362.11 | 0 | 0 | 0 | 35 | 0 | 34 | 35 | 0 | 0 | 1 | 0 | 21.56 | 182 | 0 | 194 | 0 | 194 | 0 | 355 | 0 | 1.7 | 0 | 47 | 114 | 17 | 105 | 0 | 0 | 3.1 | 89 | 0.39 | 0 | 171 | 117 | 220 | 0 | 301 | 590 | 0 | 6173.86 | 14938.07 | 99.4
17:00 | 40 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 45.7 | 25 | 132 | 129 | 261 | 55 | 55 | 143 | 32 | 450 | 300 | 0 | 0 | 35 | 319 | 192 | 0 | 7 | 125 | 17.5 | 22 | 0 | 0 | 0 | 0 | 69 | 0 | 2 | 50 | 54 | 0 | 36 | 25 | 0.89 | 218 | 15 | 3 | 674 | 160 | 0 | 50 | 25.5 | 15 | 216 | 0 | 0 | 0 | 1157 | 4 | 51 | 127 | 53 | 0 | 338 | 340 | 42 | 190 | 25 | 94 | 0 | 101 | 17 | 19 | 95 | 26 | 43 | 21 | 34 | 0 | 320 | 362 | 0 | 60 | 151 | 8 | 0 | 84 | 30 | 0 | 0 | 0 | 17 | 100 | 121 | 58 | 0 | 7.38 | 0 | 8619.97 | 860 | 184 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 32 | 812 | 0 | 1358.11 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 18 | 0 | 14.68 | 189 | 0 | 194 | 0 | 194 | 0 | 345 | 0 | 1.35 | 0 | 47 | 114 | 8 | 111 | 0 | 0 | 1.6 | 54 | 0.22 | 0 | 168 | 117 | 180 | 0 | 301 | 580 | 0 | 5955.96 | 14575.93 | 99.44
18:00 | 76 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 44.6 | 33 | 132 | 110 | 225 | 55 | 55 | 142 | 21 | 380 | 295 | 0 | 0 | 35 | 322 | 131 | 0 | 2 | 108 | 17.5 | 22 | 0 | 0 | 0 | 15 | 82 | 0 | 0 | 65 | 66 | 0 | 36 | 25 | 0.25 | 218 | 15 | 12 | 676 | 124 | 0 | 50 | 25.5 | 15 | 216 | 0 | 0 | 0 | 1040 | 1 | 51 | 130 | 8 | 0 | 300 | 300 | 43 | 192 | 25 | 95 | 0 | 122 | 18 | 19 | 95 | 22 | 43 | 3 | 35 | 0 | 320 | 365 | 0 | 60 | 133 | 8 | 0 | 84 | 30 | 0 | 0 | 0 | 17 | 109 | 121 | 59 | 0 | 2.55 | 0 | 8223.4 | 856 | 182 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9.73 | 773 | 0 | 1259.85 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 8 | 7 | 0 | 3.55 | 160 | 0 | 160 | 0 | 160 | 0 | 346 | 0 | 0.33 | 0 | 47 | 114 | 2 | 112 | 0 | 0 | 0.7 | 27 | 0.05 | 0 | 170 | 117 | 180 | 0 | 301 | 580 | 0 | 5648.21 | 13871.61 | 99.48
19:00 | 88 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 45.3 | 35 | 132 | 122 | 245 | 55 | 55 | 143 | 16 | 450 | 306 | 0 | 0 | 45 | 322 | 191 | 0 | 0 | 125 | 17.5 | 22 | 0 | 0 | 0 | 20 | 87 | 0 | 3 | 65 | 67 | 0 | 36 | 25 | 0 | 220 | 15 | 12 | 733 | 124 | 0 | 50 | 25.5 | 17 | 216 | 0 | 0 | 0 | 1135 | 0 | 51 | 137 | 31 | 0 | 336 | 340 | 45 | 208 | 32 | 95 | 0 | 195 | 27 | 17 | 95 | 30 | 52.2 | 0 | 35 | 0 | 320 | 314 | 0 | 60 | 133 | 8 | 0 | 84 | 30 | 0 | 0 | 0 | 17 | 109 | 153 | 60 | 0 | 0 | 5 | 8937.5 | 856 | 182 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 875 | 18 | 1407 | 0 | 0 | 0 | 13 | 6 | 90 | 35 | 6 | 43 | 0 | 28 | 0 | 169 | 0 | 184 | 0 | 160 | 0 | 390 | 0 | 0 | 0 | 47 | 114 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 117 | 180 | 0 | 301 | 650 | 0 | 6195 | 15132.5 | 99.52
19:30 | 88 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 48.3 | 35 | 132 | 123 | 261 | 55 | 55 | 143 | 16 | 450 | 300 | 0 | 0 | 55 | 322 | 193 | 0 | 0 | 125 | 17.5 | 22 | 0 | 0 | 0 | 30 | 80 | 0 | 4 | 65 | 64 | 0 | 36 | 25 | 0 | 220 | 17 | 13 | 690 | 160 | 0 | 50 | 25.5 | 44 | 217 | 0 | 0 | 0 | 1150 | 0 | 51 | 147 | 43 | 0 | 340 | 340 | 45 | 195 | 32 | 94 | 0 | 195 | 28 | 19 | 95 | 28 | 52.2 | 0 | 36 | 0 | 320 | 308 | 0 | 60 | 133 | 8 | 0 | 84 | 30 | 0 | 0 | 0 | 17 | 113 | 153 | 61 | 0 | 0 | 11 | 9007.5 | 855 | 176 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 34 | 1371.57 | 0 | 0 | 0 | 0 | 6 | 98 | 70 | 10 | 52.2 | 0 | 28 | 0 | 140 | 0 | 150 | 0 | 130 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 117 | 180 | 0 | 301 | 780 | 0 | 6011.77 | 15019.27
20:00 | 88 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 47.8 | 35 | 132 | 123 | 261 | 55 | 55 | 151 | 16 | 450 | 303 | 0 | 0 | 55 | 326 | 193 | 0 | 0 | 125 | 22.5 | 22 | 0 | 0 | 0 | 30 | 67 | 0 | 0 | 65 | 59 | 0 | 36 | 25 | 0 | 220 | 21 | 16 | 698 | 160 | 0 | 50 | 25.5 | 48 | 217 | 0 | 0 | 0 | 1156 | 0 | 51 | 145 | 45 | 0 | 341 | 340 | 44 | 196 | 32 | 93 | 0 | 195 | 28 | 16 | 95 | 30 | 52.2 | 0 | 36 | 0 | 320 | 334 | 0 | 60 | 137 | 8 | 0 | 84 | 30 | 0 | 0 | 0 | 17 | 112 | 153 | 63 | 0 | 0 | 11 | 9060 | 855 | 178 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1036 | 34 | 1380.22 | 0 | 17 | 0 | 0 | 6 | 98 | 70 | 15 | 52.2 | 0 | 28 | 0 | 140 | 0 | 150 | 0 | 130 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 117 | 180 | 0 | 301 | 750 | 0 | 6071.42 | 15131.42 | 99.56
21:00 | 90 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451 | 47.5 | 35 | 132 | 133 | 261 | 55 | 55 | 150 | 16 | 450 | 296 | 0 | 0 | 55 | 324 | 194 | 0 | 0 | 125 | 22.5 | 22 | 0 | 0 | 0 | 30 | 57 | 0 | 0 | 65 | 59 | 0 | 36 | 25 | 0 | 220 | 33 | 24 | 682 | 160 | 0 | 50 | 25.5 | 48 | 217 | 0 | 0 | 0 | 1125 | 0 | 51 | 143 | 45 | 0 | 343 | 340 | 46 | 188 | 35 | 95 | 0 | 195 | 28 | 16 | 95 | 26 | 52.2 | 0 | 36 | 0 | 320 | 355 | 0 | 60 | 135 | 8 | 0 | 84 | 30 | 0 | 18 | 0 | 17 | 112 | 153 | 63 | 0 | 0 | 11 | 9008.7 | 856 | 181 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1040 | 17 | 1404.18 | 0 | 47 | 0 | 35 | 6 | 98 | 35 | 37 | 52.2 | 0 | 28 | 0 | 140 | 0 | 150 | 0 | 130 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 117 | 180 | 0 | 302 | 750 | 0 | 6143.38 | 15152.08 | 99.6
22:00 | 83 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451 | 44 | 35 | 132 | 135 | 261 | 55 | 55 | 141 | 16 | 450 | 299 | 0 | 0 | 55 | 326 | 195 | 0 | 0 | 125 | 21 | 22 | 0 | 0 | 0 | 30 | 75 | 0 | 0 | 65 | 60 | 0 | 36 | 25 | 0 | 220 | 33 | 25 | 683 | 160 | 0 | 50 | 25.5 | 45 | 218 | 0 | 0 | 0 | 1130 | 0 | 51 | 148 | 45 | 0 | 345 | 340 | 47 | 191 | 32 | 95 | 0 | 194 | 26 | 16 | 95 | 26 | 52.2 | 0 | 36 | 0 | 320 | 362 | 0 | 60 | 130 | 8 | 0 | 84 | 30 | 0 | 18 | 0 | 17 | 112 | 173 | 63 | 0 | 0 | 11 | 9046.7 | 855 | 184 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1018 | 17 | 1454.35 | 0 | 47 | 0 | 70 | 6 | 98 | 35 | 36 | 52.2 | 0 | 28 | 0 | 140 | 0 | 150 | 0 | 130 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 117 | 180 | 0 | 301 | 720 | 0 | 6203.55 | 15250.25 | 99.64
23:00 | 24 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 502 | 47 | 35 | 132 | 141 | 261 | 55 | 55 | 151 | 16 | 450 | 303 | 0 | 0 | 55 | 325 | 195 | 0 | 0 | 125 | 21 | 22 | 0 | 0 | 0 | 30 | 72 | 0 | 0 | 65 | 60 | 0 | 36 | 25 | 0 | 220 | 34 | 28 | 685 | 160 | 0 | 50 | 25.5 | 49 | 218 | 0 | 0 | 0 | 1155 | 0 | 51 | 148 | 45 | 0 | 341 | 335 | 46 | 202 | 29 | 93 | 0 | 193 | 27 | 16 | 95 | 30 | 52.2 | 0 | 36 | 0 | 320 | 372 | 0 | 60 | 145 | 8 | 0 | 85 | 30 | 0 | 18 | 0 | 17 | 111 | 163 | 63 | 0 | 0 | 11 | 9107.7 | 856 | 183 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1056 | 17 | 1455.8 | 0 | 47 | 0 | 70 | 6 | 98 | 35 | 36 | 52.2 | 0 | 28 | 0 | 153 | 0 | 183 | 0 | 181 | 0 | 381 | 0 | 0 | 0 | 35 | 0 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 117 | 220 | 0 | 302 | 700 | 0 | 6534 | 15641.7 | 99.68
Total KWH | 713232 | 1417920 | 637440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11522140 | 1071720 | 262440 | 2403936 | 2079360 | 4495789 | 971460 | 1247081 | 3600000 | 366720 | 10179000 | 7252945 | 0 | 0 | 814878 | 7818958 | 4818000 | 0 | 195557 | 2812800 | 435000 | 466560 | 0 | 0 | 0 | 190691 | 877440 | 0 | 23520 | 1015385 | 1041696 | 0 | 576960 | 589440 | 27359 | 5264800 | 271800 | 312960 | 11680000 | 1881818 | 0 | 787680 | 357782.4 | 359636 | 5210624 | 0 | 0 | 0 | 26274543 | 111780 | 1181426 | 2671345 | 1237818 | 0 | 8487900 | 8164000 | 1098240 | 4822000 | 717768 | 2061120 | 0 | 2592000 | 262080 | 413830 | 2160300 | 607680 | 1036862 | 346882 | 828656 | 0 | 7661100 | 9038000 | 0 | 1037520 | 3564164 | 180432 | 0 | 2021760 | 713952 | 0 | 70000 | 0 | 425880 | 2564400 | 3064800 | 1417920 | 13550 | 309130 | 127920 | 193339285.4 | 20965091 | 4712544 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 619920 | 22196360 | 146400 | 30804459 | 0 | 278337 | 0 | 666528 | 29802 | 834736 | 473664 | 210100 | 297566 | 618630 | 281860 | 430496 | 4296818 | 0 | 4908509 | 0 | 3978636 | 0 | 8808581 | 0 | 38340 | 843046 | 933381 | 1815295 | 235949 | 2081337 | 0 | 0 | 44727.6 | 1450800 | 3807 | 0 | 4146000 | 2842000 | 5179380 | 0 | 7250184 | 16669090.91 | 0 | 150004374.51 | 343343659.91

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 21-07-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14535.9 | MW | 12:00 Hr. | Energy Generated |  |  | 343.3437 |  | MKWHr.
| Day Peak Demand |  |  | 14583.97 | MW | 12:00 Hr. | Energy Unserverd |  |  | 4.203 |  | MKWHr.
| Evening Peak Generation |  |  | 15152.08 | MW | 21:00 Hr. | Energy Demand |  |  | 347.5467 |  | MKWHr.
| Evening Peak Demand |  |  | 16001.08 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.3 |  | °C
| Minimum Generation of the Day |  |  | 12930.98 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 983.86 |  | MMCFD
| Maximum Generation of the Day |  |  | 15641.7 | MW | 23:00 Hr. | Production Cost per KWHr |  |  | 6.9727 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 42.4926 | 0 | 22.8948 | 0 | 0 | 0.19556 | 0 | 0 | 65.5829 | Gas | 134.5705 | Gas | 456427166.19
| Chattogram Zone |  |  | 5.5236 | 37.9545 | 7.9503 | 0 | 5.2648 | 0.13914 | 0 | 0.02352 | 56.8559 | Coal | 89.9926 | Coal | 545157470.1451
| Cumilla Zone |  |  | 26.123 | 0 | 11.6124 | 0 | 0 | 0.34688 | 0.60768 | 0 | 38.6899 | HFO | 55.7561 | HFO | 1043423427.078
| Mymensingh Zone |  |  | 1.4179 | 0 | 6.183 | 0 | 0 | 0.32268 | 0 | 0 | 7.9236 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 24.2869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.2869 | Hydro | 5.2648 | Hydro | 526480
| Khulna Zone |  |  | 4.7125 | 22.1964 | 0.1464 | 0 | 0 | 0.61992 | 21.8771 | 0 | 49.5523 | Solar | 4.4469 | Solar | 73385524.736
| Barishal Zone |  |  | 8.0214 | 28.0653 | 0 | 0 | 0 | 0.003807 | 0 | 0 | 36.0905 | Import | 53.2892 | Import | 274784663.32
| Rajshahi Zone |  |  | 21.9925 | 0 | 3.0726 | 0 | 0 | 1.0875 | 30.8045 | 0 | 56.9571 | Wind | 0.02352 | Wind | 344332.8
| Rangpur Zone |  |  | 0 | 1.7764 | 3.8966 | 0 | 0 | 1.7315 | 0 | 0 | 7.4045
| Total |  |  | 134.5705 | 89.9926 | 55.7561 | 0 | 5.2648 | 4.4469 | 53.2892 | 0.02352 | 343.3437
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 456427166.19 |  | Hydro | 526480
|  |  |  | Coal | 545157470.1451 |  | Solar | 73385524.736
|  |  |  | HFO | 1043423427.078 |  | Import | 274784663.32
|  |  |  | HSD | 0 |  | Wind | 344332.8
[5 empty] | Total: | 239,40,49,064 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.9651 | Peak Hr Flow | 856.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 35000745.55 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 30.8045 | Peak Hr Flow | 1404.18 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 908 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.60768 | Peak Hr Flow | 26.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 1054 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 52.3772 | Peak Hr Flow | 2286.18 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5565
|  |  |  | Chattogram |  | 0 |  | 1493
|  |  |  | Cumilla |  | 40 |  | 1520
|  |  |  | Mymensingh |  | 30 |  | 1298
|  |  |  | Sylhet |  | 55 |  | 658
|  |  |  | Khulna |  | 0 |  | 1924
|  |  |  | Barishal |  | 0 |  | 502
|  |  |  | Rajshahi |  | 0 |  | 1684
|  |  |  | Rangpur |  | 687 |  | 694
|  |  |  | Total |  | 812 |  | 15338
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Bibiana-II 341 MW CCPP (Summit) GT |  |  | 222 | 3 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
|  | 4 | Bibiana-II 341 MW CCPP (Summit) ST |  |  | 119 | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 641 |  |  |  | Total | 707
|  |  |  | Total Unavailable Capacity |  |  |  | 1348
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:20 | 08:36 | Bagerhat-Bhandaria 132 kV Ckt-1 Tripped from Bagerhat 132/33kV end showing
Distance(Zone-2),R phase relays Due to None
| 08:24 | 10:52 | Barishal-Bhandaria 132 kV Ckt-1 Scheduled S/D from Barishal 132/33kV end Due to CT High
temperature removal works. and from Bhandaria 132/33kV end Due to Red hot Maintenance at
Barishal Sub-Station End.
| 08:25 |  | Bhandaria 132/33kV S/S Transformer-2 HT Tripped showing Protection relay 81 U/F Under | [7 empty] | 34.0MW load
|  |  | voltage blocking relays Due to Trip for Bagerhat line trip | [7 empty] | interrup.
|  | 08:34 | Kabirpur 132/33kV S/S XFR, T-2 LT is restored.
|  | 08:34 | Kabirpur 132/33kV S/S XFR, T-2 HT is restored.
| 08:47 | 14:50 | Bagerhat-Bhandaria 132 kV Ckt-1 Tripped from Bagerhat 132/33kV end showing Distance
(Zone-2),R phase relays.
| 08:47 | 18:10 | Bogura 400/230kV S/S ATR-03 HT Project Work S/D Due to Painting work of ATR-03
| 09:13 | 14:32 | Purbasadipur 132/33kV S/S T-4 Transformer LT Scheduled S/D Due to Re-routing work of 33kV | [7 empty] | 5.0MW load
|  |  | Sadar feeder | [7 empty] | interrup.
| 09:15 | 14:30 | Purbasadipur 132/33kV S/S T-4 Transformer HT Scheduled S/D Due to Re-routing work of 33kV | [7 empty] | 5.0MW load
|  |  | Sadar feeder | [7 empty] | interrup.
|  | 09:18 | Kabirpur 132/33kV S/S XFR, T-I LT is restored.
|  | 09:18 | Kabirpur 132/33kV S/S XFR, T-I HT is restored.
| 09:55 | 10:26 | Sreemongol 132/33kV S/S 132/33kv T-3 LT Scheduled S/D Due to For 33kV GCB gas refiling
work.
| 09:55 | 10:25 | Sreemongol 132/33kV S/S 132/33kv T-3 HT Scheduled S/D Due to For 33kV GCB gas refiling
work.
| 10:15 | 13:55 | Ishurdi 132/33kV S/S 132 kV Bus-2 Scheduled S/D Due to Bus DS-649S redhot maintenance
work.
| 10:17 | 12:13 | Mithapukur 132/33kV S/S TR-1(404T) HT Forced S/D Due to Red hot work. | [7 empty] | 25.0MW load
interrup.
| 11:39 |  | Raozan 25 MW PP Synchronized
| 11:58 | 12:11 | Bheramara(GK) 132/33kV S/S TR-2 LT Tripped showing OC/EF relays Due to Taragunia 33kV PBS | [7 empty] | 17.0MW load
|  |  | Feeder & Pragpur 33kV PBS Feeder Fault | [7 empty] | interrup.
| 11:58 | 12:11 | Bheramara(GK) 132/33kV S/S TR-1 LT Tripped showing OC/EF relays Due to Taragunia 33kV PBS | [7 empty] | 17.0MW load
|  |  | Feeder & Pragpur 33kV PBS Feeder Fault | [7 empty] | interrup.
| 12:00 |  | Day peak Generation is 14532 MW
| 13:16 | 14:21 | Bhaluka 132/33kV S/S Transformer- 01 LT Scheduled S/D Due to Oil level LO/HI signal not | [7 empty] | 40.0MW load
|  |  | reset. | [7 empty] | interrup.
| 13:18 | 14:19 | Bhaluka 132/33kV S/S Transformer- 01 HT Scheduled S/D Due to Oil level LO/HI signal not | [7 empty] | 40.0MW load
|  |  | reset. | [7 empty] | interrup.
|  | 14:48 | Rahanpur 400/132kV S/S Rahanpur-Monakasha 400KV Line ckt-02 is restored.
| 16:40 | 18:21 | Kabirpur 132/33kV S/S XFR, T-I LT Scheduled S/D Due to DS maintanence work of Auxiliary | [7 empty] | 75.0MW load
|  |  | Transformer -1 | [7 empty] | interrup.
| 16:40 | 18:20 | Kabirpur 132/33kV S/S XFR, T-I HT Scheduled S/D Due to DS maintanence work of Auxiliary | [7 empty] | 75.0MW load
|  |  | Transformer-1 | [7 empty] | interrup.
| 19:05 | 20:08 | Barapukuria S/S-P/S 230 kV Ckt-2 Tripped from Barapukuria 230/132/33kV end showing | [7 empty] | 30.0MW load
|  |  | Siemens relays. | [7 empty] | interrup.
Barapukuria
230/132/33kV end
| 19:05 | 20:47 | Barapukuria-Bogura 230 kV Ckt-1 Tripped from Barapukuria 230/132/33kV end showing | [7 empty] | 30.0MW load
|  |  | Directional over current relay relays Due to Directional over current | [7 empty] | interrup.
Barapukuria
230/132/33kV end
| 19:06 | 19:22 | Mithapukur-Palashbari 132kV Ckt-1 Tripped from Palashbari 132/33kV end showing SPS Relay | [7 empty] | 42.0MW load
|  |  | relays Due to SPS Relay operate | [7 empty] | interrup.
Palashbari 132/33kV
end
| 19:06 | 19:20 | Mahasthangar-Palashbari 132kV Ckt-1 Tripped from Palashbari 132/33kV end showing SPS | [7 empty] | 85.0MW load
|  |  | Relay operate relays Due to SPS Relay pick up and from Mahasthangarh 132/33kV end showing | [7 empty] | interrup.
|  |  | Micom P132 relays Due to Over Current | [7 empty] | Palashbari 132/33kV
end and 204.0MW
load interrup.
Mahasthangarh
132/33kV end
| 19:06 | 19:18 | Bogura 230/132kV S/S Confidance UN-2 Tripped showing Over Voltage trip relays.
| 19:06 | 19:31 | Mithapukur-Palashbari 132kV Ckt-2 Tripped from Palashbari 132/33kV end showing SPS Relay | [7 empty] | 42.0MW load
|  |  | relays Due to SPS Relay operate | [7 empty] | interrup.
Palashbari 132/33kV
end
|  | 19:41 | Mahasthangar-Palashbari 132kV Ckt-2 is restored.
| 20:33 |  | Bogura 400/230kV S/S Bogura - Rooppur 400 KV Line-1 Tripped showing Bay Controal Unit-1 &
2 Bus Bar Protection-2 relays Due to 1.Lockout Relay Operated 2.START BFP 3
Phase 3.Lockout Relay (KT86.1) Operated. 4.Lockout Relay (KT86.2)
Operated. 5.Lockout-1(K86.1) Operated. 6.Lockout-2(K86.2) Operated. 7.3P
INITIATION 8.Lockout Optd.
| 20:45 | 20:54 | Mahasthangar-Palashbari 132kV Ckt-2 Tripped from Palashbari 132/33kV end showing | [7 empty] | 100.0MW load
|  |  | Distance relay, Backup over current protection relay relays Due to Distance relay, Backup | [7 empty] | interrup.
|  |  | over current protection | [7 empty] | Palashbari 132/33kV
end
| 20:48 | 21:49 | Barapukuria-Bogura 230 kV Ckt-2 Tripped from Barapukuria 230/132/33kV end showing 51N | [7 empty] | 32.0MW load
|  |  | relays. | [7 empty] | interrup.
Barapukuria
230/132/33kV end
| 20:48 | 21:38 | Barapukuria-Bogura 230 kV Ckt-1 Tripped from Barapukuria 230/132/33kV end showing 50,51N | [7 empty] | 32.0MW load
|  |  | relays. | [7 empty] | interrup.
Barapukuria
230/132/33kV end
| 20:50 | 20:59 | Mahasthangar-Palashbari 132kV Ckt-1 Tripped from Mahasthangarh 132/33kV end showing | [7 empty] | 54.0MW load
|  |  | Micom P443 relays Due to Distance Trip | [7 empty] | interrup.
Mahasthangarh
132/33kV end
| 21:38 |  | Barapukuria S/S-P/S 230 kV Ckt-1 Forced S/D from Barapukuria 230/132/33kV end Due to | [7 empty] | 32.0MW load
|  |  | 230KV circuit breaker Pole discrepancy problem at BPDB power station end. | [7 empty] | interrup.
Barapukuria
230/132/33kV end
| 21:38 | 21:38 | Barapukuria-Bogura 230 kV Ckt-1 Forced S/D from Barapukuria 230/132/33kV end Due to 230 | [7 empty] | 31.0MW load
|  |  | KV circuit breaker Pole discrepancy problem at BPDB power station end. | [7 empty] | interrup.
Barapukuria
230/132/33kV end
| 21:58 | 23:55 | Maijdee 132/33kV S/S Tr-02 HT Forced S/D Due to 33 Kv sudharam feeder red hot maintenance
| 21:58 | 23:56 | Maijdee 132/33kV S/S Tr-02 LT Forced S/D Due to 33kv sudharam feeder red Hot maintenance
| 22:35 | 02:24 | Barapukuria-Saidpur 132 kV Ckt-2 Forced S/D from Saidpur 132/33kV end Due to Baropukuria
ckt-02 Breaker (R- phase) pole not opened.
| 22:51 | 02:27 | Barapukuria-Saidpur 132 kV Ckt-2 Forced S/D from Barapukuria 230/132/33kV end Due to 132
KV circuit breaker R phase pole don't operate nat saidpur Sub station .so need shut down
for bypass with bus coupler breaker at saidpur Sub station.
| 22:51 |  | Barapukuria PS Unit-1 was sync.
| 23:05 | 01:16 | Kaliakoir 400/230/132kV S/S 400/230kV TR2 LT Forced S/D Due to red hot ds maintenance
| 23:05 | 01:16 | Kaliakoir 400/230/132kV S/S 400/230kV TR2 HT Forced S/D Due to red hot ds maintenance
| 02:30 |  | Raozan 25 MW PP Shutdown
| 06:00 |  | Minimum Generation: 13571 MW.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 21-07-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10179000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 296 | 7252945 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 971460 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 194 | 4818000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 324 | 7818958 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 90 | 713232 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 47.5 | 1071720 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 133 | 2079360 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 1247081 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 814878 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22.5 | 435000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 466560 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 33 | 637440 | Engine Problem
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 261 | 4495789 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 2403936 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1417920 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 366720 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 150 | 3600000 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 195557 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 262440 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 451 | 11522140 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 125 | 2812800 | Engine Problem
Dhaka Area Total |  |  |  |  | 5939.724 | 3052 | 65582936
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 357782.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 111780 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 787680 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5264800 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5210624 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 48 | 359636 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 59 | 1041696 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 1015385 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 36 | 576960 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 24 | 312960 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 57 | 877440 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 27359 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 30 | 190691 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 33 | 271800 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 589440 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 160 | 1881818 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1125 | 26274543 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 23520 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 682 | 11680000 | -
Chattogram Area Total |  |  |  |  | 4895.72 | 2856.5 | 56855914.4
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 188 | 4822000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 343 | 8487900 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 340 | 8164000 | machine problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 35 | 717768 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 46 | 1098240 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 45 | 1237818 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1181426 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 143 | 2671345 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 828656 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 195 | 2592000 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 26 | 607680 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 1036862 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 16 | 413830 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 95 | 2160300 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 262080 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 95 | 2061120 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 346882 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1734.2 | 38689907
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 63 | 1417920 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13550 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 153 | 3064800 | Engine Problem
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 112 | 2564400 | Engine Problem
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 309130 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 11 | 127920 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 425880 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 356 | 7923600
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1037520 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 135 | 3564164 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 713952 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 2021760 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 70000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 180432 | machine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Plant Shutdown as per schedule HGPI work
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 355 | 9038000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7661100 | machine problem
Sylhet Area Total |  |  |  |  | 2325 | 1010 | 24286928
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 856 | 20965091 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 181 | 4712544 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 146400 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 619920 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1040 | 22196360 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2132 | 49552315
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 302 | 7250184 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 117 | 2842000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 750 | 16669090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 180 | 5179380 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 167 | 4146000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3807 | -
Barishal Area Total |  |  |  |  | 2236 | 1516 | 36090461.91
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 47 | 278337 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 6 | 29802 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 210100 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 140 | 4296818 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 150 | 4908509 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 130 | 3978636 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 333 | 8808581 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 281860 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 297566 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 98 | 834736 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 666528 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 473664 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 38340 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1404.18 | 30804459 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 430496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 618630 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2495.38 | 56957062
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 933381 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 843046 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 2081337 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 44727.6 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 1815295 | Engine Problem
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 235949 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1450800 | -
Rangpur Area Total |  |  |  |  | 950 | 0 | 7404535.6
Eastern Grid Total |  |  |  |  | 16667.715 | 9008.7 | 193339285.4
Western Grid Total |  |  |  |  | 10378.16 | 6143.38 | 150004374.51
National Grid Total |  |  |  |  | 27045.875 | 15152.08 | 343343659.91
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 21-07-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10409.28 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4117.5 | MW
i) Dhaka area |  |  | 5565.29 |  | MW | i) Khulna area |  |  |  | 1924 | MW
ii) Chattogram area |  |  | 1492.8 |  | MW | ii) Barishal area |  |  |  | 502 | MW
iii) Cumilla area |  |  | 1480.19 |  | MW | iii) Rajshahi area |  |  |  | 1684.5 | MW
iv) Mymensingh area |  |  | 1268 |  | MW | iv) Rangpur area |  |  |  | 7 | MW
v) Sylhet area |  |  | 603 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14526.78 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 87 | 20:00 | 133 | PHP | 8 | 01:00
2 | AKSML | 165.2 | 18:00 | 68 | Ishurdi | 90 | 19:30 | 134 | Pabna | 134 | 22:00
3 | Aftabnagar | 42 | 23:00 | 69 | Jaldhaka | 80 | 19:00 | 135 | Palashbari | 110 | 00:00
4 | Agargaon | 144 | 15:00 | 70 | Jamalpur | 141 | 21:00 | 136 | Panchagarh | 54 | 19:00
5 | Agrabad | 94 | 15:00 | 71 | Jashore | 154 | 19:30 | 137 | Patuakhali | 75 | 22:00
6 | Amnura | 43 | 21:00 | 72 | Jhenaidah | 138 | 19:30 | 138 | Payra | 38 | 23:00
7 | Ashuganj | 97 | 22:00 | 73 | Joydebpur | 147 | 19:30 | 139 | Postogola | 63 | 13:00
8 | BSRM | 200 | 04:00 | 74 | Joypurhat | 70 | 22:00 | 140 | Purbachal | 24 | 23:00
9 | Bagerhat | 86 | 00:00 | 75 | Juldah | 15.5 | 23:00 | 141 | Purbasadipur | 136 | 00:00
10 | Bajitpur | 77 | 21:00 | 76 | KSRM | 25 | 09:00 | 142 | Rahanpur | 34 | 22:00
11 | Bakulia | 104 | 17:00 | 77 | Kabirpur | 264 | 11:00 | 143 | Rahim | 30 | 11:00
12 | Banani | 40.6 | 15:00 | 78 | Kachua | 102 | 22:00 | 144 | Rajbari | 93 | 19:30
13 | Bangabhaban | 19 | 10:00 | 79 | Kallyanpur | 96 | 23:00 | 145 | Rajendrapur | 136 | 21:00
14 | Barapukuria | 64 | 00:00 | 80 | Kalurghat | 42 | 15:00 | 146 | Rajshahi | 148 | 21:00
15 | Barguna | 24 | 00:00 | 81 | Kamrangirchar | 80 | 13:00 | 147 | Rajshahi-230 | 84 | 23:00
16 | Barishal | 119 | 22:00 | 82 | Kaptai | N/A | N/A | 148 | Ramganj | 100 | 19:00
17 | Barishal-230 | 108 | 22:00 | 83 | Kasba | 39 | 22:00 | 149 | Rampur | 43 | 23:00
18 | Baroaulia | 70 | 11:00 | 84 | Kazla | 98 | 12:00 | 150 | Rangamati | 17 | 19:00
19 | Baroirhat | 60 | 00:00 | 85 | Keranigonj | 83 | 19:30 | 151 | Rangpur | 141 | 12:00
20 | Bashundhara | 207 | 16:00 | 86 | Khagrachori | 38 | 20:00 | 152 | Ruppur | 6.8 | 09:00
21 | BashundharaCement | 17 | 10:00 | 87 | Khulna | 85 | 19:30 | 153 | SSM | 0 | 00:00
22 | Beanibazar | 74 | 02:00 | 88 | Khulshi | 171 | 14:00 | 154 | Saidpur | 116 | 14:00
23 | Benapole | 70 | 23:00 | 89 | Kishoreganj | 157 | 22:00 | 155 | Satkhira | 144 | 22:00
24 | Bhaluka | 155 | 15:00 | 90 | Kodda | 306 | 19:00 | 156 | Satmasjid | 120 | 16:00
25 | Bhandaria | 64 | 02:00 | 91 | Kulaura | 54 | 15:00 | 157 | Savar | 231 | 12:00
26 | Bhangura | 42 | 19:30 | 92 | Kurigram | 62 | 00:00 | 158 | SevenRings | 20.05 | 17:00
27 | Bheramara(GK) | 72 | 23:00 | 93 | Kushtia | 160 | 21:00 | 159 | ShahCement | 34 | 12:00
28 | Bhulta | 259 | 20:00 | 94 | Laksam | 38 | 06:00 | 160 | Shahjadpur | 95 | 20:00
29 | Bog-Sherpur | 72 | 19:30 | 95 | Lakshmipur | 29 | 23:00 | 161 | Shahjibazar | 131 | 22:00
30 | Bogura | 179 | 22:00 | 96 | Lalbag | 56 | 11:00 | 162 | Shahmirpur | 59 | 00:00
31 | Borhanuddin | 92 | 01:00 | 97 | Lalmonirhat | 67 | 19:00 | 163 | Shariatpur | 100 | 23:00
32 | Brahmanbaria | 140 | 21:00 | 98 | MI_Cement | 12.2 | 13:00 | 164 | Sherpur | 162 | 00:00
33 | Cantonment | 166 | 13:00 | 99 | Madanganj | 40 | 00:00 | 165 | Shikalbaha | 23 | 13:00
34 | Chandina | 18.03 | 22:00 | 100 | Madaripur | 124 | 23:00 | 166 | Shitalakhya | 86 | 11:00
35 | Chandpur | 84 | 22:00 | 101 | Madartek | 96 | 00:00 | 167 | Sholosohor | 45 | 15:00
36 | Chandraghona | 38 | 21:00 | 102 | Madunaghat | 57 | 14:00 | 168 | Shyampur | 150 | 00:00
37 | Chapai | 75 | 21:00 | 103 | Magura | 74 | 19:30 | 169 | Siddhirganj | 122 | 11:00
38 | Charsaidpur | 45 | 02:00 | 104 | Mahasthangarh | 102 | 23:00 | 170 | Sirajganj | 126 | 21:00
39 | Chauddagram | 79 | 23:00 | 105 | Maijdee | 17 | 00:00 | 171 | Sonargaon | 125 | 23:00
40 | Chhatak | 38 | 19:00 | 106 | Manikganj | 139 | 21:00 | 172 | Sreemongol | 79 | 19:00
41 | Chowmuhani | 172 | 22:00 | 107 | Maniknagar | 88 | 13:00 | 173 | Sreepur | 105 | 20:00
42 | Chuadanga | 126 | 22:00 | 108 | Matarbari | 55 | 23:00 | 174 | Srinagar | 49.63 | 21:00
43 | Coxsbazar | 137 | 00:00 | 109 | Matuail | 66 | 23:00 | 175 | Sunamganj | 56 | 03:00
44 | Cumilla(N) | 158 | 19:30 | 110 | Millgate | 133 | 15:00 | 176 | Sylhet | 56 | 20:00
45 | Cumilla(S) | 160 | 19:00 | 111 | Mirpur | 130 | 16:00 | 177 | Sylhet-132 | 130 | 18:30
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 11 | 19:00 | 178 | TK | 40 | 00:00
47 | Daudkandi | 161 | 20:00 | 113 | Mirzapur | 48 | 20:00 | 179 | Tangail | 191 | 22:00
48 | Dhaka | 78 | 12:00 | 114 | Mithapukur | 71 | 00:00 | 180 | Taraganj | 26 | 23:00
49 | Dhamrai | 128 | 11:00 | 115 | Modern | N/A | N/A | 181 | Thakurgaon | 104 | 15:00
50 | Dhanmondi | 155 | 13:00 | 116 | Mogbazar | 165.6 | 15:00 | 182 | Tongi | 143 | 11:00
51 | Dohazari | 107 | 19:00 | 117 | Mongla | 43 | 14:00 | 183 | Ullahpara | 43 | 19:30
52 | Faridpur | 187 | 22:00 | 118 | Motijheel | 46 | 13:00 | 184 | Ullon | 46 | 00:00
53 | Fatullah | 106 | 15:00 | 119 | Muktagacha | 40 | 20:00 | 185 | Uttara | 96 | 13:00
54 | Fenchuganj | 47 | 20:00 | 120 | Munshiganj | 118 | 22:00 | 186 | UttaraNew | 68 | 23:00
55 | Feni | 126 | 19:00 | 121 | Muradnagar | 46 | 22:00 | 187 | Zigatola | 76 | 00:00
56 | GPH | 88 | 02:00 | 122 | Mymensingh | 210 | 19:30
57 | Ghatail | 88 | 19:00 | 123 | Naogaon | 146 | 22:00
58 | Ghorashal | 14 | 15:00 | 124 | Narail | 64 | 20:00
59 | Ghorashal-230 | 93 | 21:00 | 125 | Narinda | 82 | 13:00
60 | Goalpara | 42 | 19:30 | 126 | Narshingdi | 188 | 23:00
61 | Gollamari | 90 | 20:00 | 127 | Natore | 161 | 19:30
62 | Gopalganj | 116.8 | 20:00 | 128 | Nawabganj | 65 | 23:00
63 | Gulshan | 138 | 15:00 | 129 | Netrakona | 146 | 00:00
64 | Halishahar | 78 | 09:00 | 130 | New | 62.6 | 16:00
65 | HaripurSBU | 159 | 17:00 | 131 | Niamatpur | 84 | 22:00
66 | Hasnabad | 94 | 23:00 | 132 | Noapara | 47 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 21-07-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15574.53 | 152 |  | 15733.37
1:00 | 15054.83 | 144 |  | 15204.83
2:00 | 14617.68 | 103 |  | 14725.68
3:00 | 14143.52 | 102 |  | 14250.52
4:00 | 13799.44 | 96 |  | 13899.44
5:00 | 13625.67 | 91 |  | 13720.67
6:00 | 13144.5 | 54 |  | 13200.5
7:00 | 12989.13 | 71 |  | 13063.13
8:00 | 12930.98 | 68 |  | 13002.04
9:00 | 13218.9 | 60 |  | 13281.6
10:00 | 13862 | 39 |  | 13902.76
11:00 | 14161.08 | 32 |  | 14194.52
12:00 | 14535.9 | 46 |  | 14583.97
13:00 | 14659.14 | 130 |  | 14795.14
14:00 | 14679.93 | 146 |  | 14832.5
15:00 | 14848.39 | 111 |  | 14964.39
16:00 | 14938.07 | 112 |  | 15055.11
17:00 | 14575.93 | 37 |  | 14614.6
18:00 | 13871.61 | 0 |  | 13871.61
19:00 | 15132.5 | 95 |  | 15231.5
19:30 | 15019.27 | 557 |  | 15601.27
20:00 | 15131.42 | 641 |  | 15801.42
21:00 | 15152.08 | 812 |  | 16001.08
22:00 | 15250.25 | 717 |  | 15999.25
23:00 | 15641.7 | 344 |  | 16001.18
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 21-07-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8759.2 | 6815.33 | 15574.53 | DAILY GENERATION CURVE
00:30 | 8598.95 | 6715.73 | 15314.68
01:00 | 8438.7 | 6616.13 | 15054.83 | 21-07-2025
01:30 | 8296.95 | 6539.305 | 14836.255
02:00 | 8155.2 | 6462.48 | 14617.68
02:30 | 8026.2 | 6354.4 | 14380.6
03:00 | 7897.2 | 6246.32 | 14143.52
03:30 | 7754.7 | 6216.78 | 13971.48
04:00 | 7612.2 | 6187.24 | 13799.44
04:30 | 7554.6 | 6157.955 | 13712.555
05:00 | 7497 | 6128.67 | 13625.67
05:30 | 7394.805 | 5990.28 | 13385.085
06:00 | 7292.61 | 5851.89 | 13144.5
06:30 | 7179.495 | 5887.32 | 13066.815
07:00 | 7066.38 | 5922.75 | 12989.13
07:30 | 7001.765 | 5958.29 | 12960.055
08:00 | 6937.15 | 5993.83 | 12930.98
08:30 | 7054.76 | 6020.18 | 13074.94
09:00 | 7172.37 | 6046.53 | 13218.9
09:30 | 7533.435 | 6007.015 | 13540.45
10:00 | 7894.5 | 5967.5 | 13862
10:30 | 8008.675 | 6002.865 | 14011.54
11:00 | 8122.85 | 6038.23 | 14161.08
11:30 | 8240.845 | 6107.645 | 14348.49
12:00 | 8358.84 | 6177.06 | 14535.9
12:30 | 8414.93 | 6182.59 | 14597.52
13:00 | 8471.02 | 6188.12 | 14659.14
13:30 | 8531.7 | 6137.835 | 14669.535
14:00 | 8592.38 | 6087.55 | 14679.93
14:30 | 8588.975 | 6175.185 | 14764.16
15:00 | 8585.57 | 6262.82 | 14848.39
15:30 | 8674.89 | 6218.34 | 14893.23
16:00 | 8764.21 | 6173.86 | 14938.07
16:30 | 8692.09 | 6064.91 | 14757
17:00 | 8619.97 | 5955.96 | 14575.93
17:30 | 8421.685 | 5802.085 | 14223.77
18:00 | 8223.4 | 5648.21 | 13871.61
18:30 | 8580.45 | 5921.605 | 14502.055
19:00 | 8937.5 | 6195 | 15132.5
19:30 | 9007.5 | 6011.77 | 15019.27
20:00 | 9060 | 6071.42 | 15131.42
20:30 | 9034.35 | 6107.4 | 15141.75 |  | Executive Engineer
21:00 | 9008.7 | 6143.38 | 15152.08 |  | Network Operation Division
21:30 | 9027.7 | 6173.465 | 15201.165
22:00 | 9046.7 | 6203.55 | 15250.25
22:30 | 9077.2 | 6368.775 | 15445.975
23:00 | 9107.7 | 6534 | 15641.7

## En-Curve
QF-LDC-12
Date | 21-07-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3789 | 1994 | 868 | 38 | 28 | 1239.33 | 218 | 4330 | 0 | 695 | 2375.2 | 0 | 0 | 0 | 152 | DAILY ENERGY CURVE
00:30 | 3754 | 1991 | 868 | 38 | 28 | 1244.23 | 218.5 | 4281.5 | 0 | 656 | 2235.45 | 0 | 0 | 0 | 148 | 21-07-2025
01:00 | 3719 | 1988 | 868 | 38 | 28 | 1249.13 | 219 | 4233 | 0 | 617 | 2095.7 | 0 | 0 | 0 | 144
01:30 | 3703 | 1988 | 868 | 38 | 28 | 1239.305 | 219 | 4209.5 | 0 | 608.5 | 1934.95 | 0 | 0 | 0 | 123.5 | Energy Generated | 343.3437 |  | MKWHr
02:00 | 3687 | 1988 | 868 | 38 | 28 | 1229.48 | 219 | 4186 | 0 | 600 | 1774.2 | 0 | 0 | 0 | 103 | Energy not Served | 4.203 |  | MKWHr
02:30 | 3723 | 1969.5 | 868 | 38 | 27 | 1224.4 | 219.5 | 4197 | 0 | 513 | 1601.2 | 0 | 0 | 0 | 102.5 | Total Energy Requirement | 347.5467 |  | MKWHr
03:00 | 3759 | 1951 | 868 | 38 | 26 | 1219.32 | 220 | 4208 | 0 | 426 | 1428.2 | 0 | 0 | 0 | 102
03:30 | 3750 | 1950 | 868 | 38 | 25 | 1238.78 | 220 | 4146 | 0 | 402 | 1333.7 | 0 | 0 | 0 | 99
04:00 | 3741 | 1949 | 868 | 38 | 24 | 1258.24 | 220 | 4084 | 0 | 378 | 1239.2 | 0 | 0 | 0 | 96
04:30 | 3723 | 1941.5 | 868 | 38 | 24 | 1256.455 | 220 | 4059 | 0 | 360.5 | 1221.1 | 0 | 0 | 1 | 93.5
05:00 | 3705 | 1934 | 868 | 38 | 24 | 1254.67 | 220 | 4034 | 0 | 343 | 1203 | 0 | 0 | 2 | 91
05:30 | 3720 | 1932 | 868 | 38 | 24 | 1235.215 | 220 | 3938.5 | 11.87 | 279.5 | 1117 | 0 | 0 | 1 | 72.5
06:00 | 3735 | 1930 | 868 | 38 | 24 | 1215.76 | 220 | 3843 | 23.74 | 216 | 1031 | 0 | 0 | 0 | 54
06:30 | 3741 | 1908 | 867.5 | 38 | 23 | 1215.73 | 220 | 3846 | 62.085 | 219 | 926.5 | 0 | 0 | 0 | 62.5
07:00 | 3747 | 1886 | 867 | 38 | 22 | 1215.7 | 220 | 3849 | 100.43 | 222 | 822 | 0 | 0 | 0 | 71
07:30 | 3704.5 | 1819.5 | 868 | 38 | 22 | 1214.85 | 220 | 3863.5 | 156.705 | 220.5 | 832.5 | 0 | 0 | 0 | 69.5
08:00 | 3662 | 1753 | 869 | 38 | 22 | 1214 | 220 | 3878 | 212.98 | 219 | 843 | 0 | 0 | 0 | 68
08:30 | 3696.5 | 1774.5 | 868.5 | 38 | 22 | 1211 | 219.5 | 3873.5 | 257.94 | 219 | 894.5 | 0 | 0 | 0 | 64
09:00 | 3731 | 1796 | 868 | 38 | 22 | 1208 | 219 | 3869 | 302.9 | 219 | 946 | 0 | 0 | 0 | 60
09:30 | 3732.5 | 1821.5 | 872 | 38 | 21 | 1185.5 | 219 | 3829 | 379.5 | 273 | 1169.45 | 0 | 0 | 0 | 49.5
10:00 | 3734 | 1847 | 876 | 38 | 20 | 1163 | 219 | 3789 | 456.1 | 327 | 1392.9 | 0 | 0 | 0 | 39
10:30 | 3693 | 1858.75 | 876.5 | 38 | 22 | 1164 | 218 | 3792 | 532.54 | 338.5 | 1478.25 | 0 | 0 | 0 | 35.5
11:00 | 3652 | 1870.5 | 877 | 38 | 24 | 1165 | 217 | 3795 | 608.98 | 350 | 1563.6 | 0 | 0 | 0 | 32
11:30 | 3645 | 1896.5 | 879.5 | 38 | 25 | 1164 | 217 | 3841 | 622.54 | 357 | 1662.45 | 0 | 0 | 0.5 | 39
12:00 | 3638 | 1922.5 | 882 | 38 | 26 | 1163 | 217 | 3887 | 636.1 | 364 | 1761.3 | 0 | 0 | 1 | 46
12:30 | 3590 | 1917.5 | 882 | 38 | 27 | 1231 | 216.5 | 3866 | 590.97 | 399.9 | 1838.15 | 0 | 0 | 0.5 | 88
13:00 | 3542 | 1912.5 | 882 | 38 | 28 | 1299 | 216 | 3845 | 545.84 | 435.8 | 1915 | 0 | 0 | 0 | 130
13:30 | 3565 | 1896.25 | 871 | 38 | 28 | 1286.795 | 217 | 3843.5 | 499.59 | 444.3 | 1980.1 | 0 | 0 | 0 | 138
14:00 | 3588 | 1880 | 860 | 38 | 28 | 1274.59 | 218 | 3842 | 453.34 | 452.8 | 2045.2 | 0 | 0 | 0 | 146
14:30 | 3601 | 1905.25 | 860 | 38 | 28 | 1267.82 | 218 | 3854 | 458.04 | 466.4 | 2060.65 | 0 | 0 | 7 | 128.5
15:00 | 3614 | 1930.5 | 860 | 38 | 28 | 1261.05 | 218 | 3866 | 462.74 | 480 | 2076.1 | 0 | 0 | 14 | 111
15:30 | 3650.5 | 1930 | 859.5 | 38 | 28 | 1311.58 | 218 | 3835 | 373.8 | 491.5 | 2148.35 | 0 | 0 | 9 | 111.5
16:00 | 3687 | 1929.5 | 859 | 38 | 28 | 1362.11 | 218 | 3804 | 284.86 | 503 | 2220.6 | 0 | 0 | 4 | 112
16:30 | 3680 | 1880 | 859.5 | 38 | 27 | 1360.11 | 218 | 3771.5 | 227.49 | 502.5 | 2189.9 | 0 | 0 | 3 | 74.5
17:00 | 3673 | 1830.5 | 860 | 38 | 26 | 1358.11 | 218 | 3739 | 170.12 | 502 | 2159.2 | 0 | 0 | 2 | 37
17:30 | 3559 | 1766.5 | 858 | 38 | 24 | 1308.98 | 218 | 3663 | 114.64 | 498 | 2174.65 | 0 | 0 | 1 | 18.5
18:00 | 3445 | 1702.5 | 856 | 38 | 22 | 1259.85 | 218 | 3587 | 59.16 | 494 | 2190.1 | 0 | 0 | 0 | 0
18:30 | 3538 | 1804.5 | 856 | 38 | 26 | 1333.425 | 219 | 3751.5 | 29.58 | 570.5 | 2334.05 | 0 | 0 | 1.5 | 47.5
19:00 | 3631 | 1906.5 | 856 | 38 | 30 | 1407 | 220 | 3916 | 0 | 647 | 2478 | 0 | 0 | 3 | 95
19:30 | 3431 | 1865.5 | 855 | 38 | 28 | 1371.57 | 220 | 4096 | 0 | 693 | 2417.2 | 0 | 0 | 4 | 557
20:00 | 3467 | 1878.5 | 855 | 38 | 30 | 1380.22 | 220 | 4113 | 0 | 710 | 2439.7 | 0 | 0 | 0 | 641
20:30 | 3502.5 | 1854.5 | 855.5 | 38 | 28 | 1392.2 | 220 | 4089.5 | 0 | 741 | 2420.55 | 0 | 0 | 0 | 726.5
21:00 | 3538 | 1830.5 | 856 | 38 | 26 | 1404.18 | 220 | 4066 | 0 | 772 | 2401.4 | 0 | 0 | 0 | 812
21:30 | 3549 | 1829.75 | 855.5 | 38 | 26 | 1429.265 | 220 | 4042 | 0 | 773 | 2438.65 | 0 | 0 | 0 | 764.5
22:00 | 3560 | 1829 | 855 | 38 | 26 | 1454.35 | 220 | 4018 | 0 | 774 | 2475.9 | 0 | 0 | 0 | 717
22:30 | 3633 | 1885.5 | 855.5 | 38 | 28 | 1455.075 | 220 | 4063 | 0 | 777 | 2490.9 | 0 | 0 | 0 | 530.5
23:00 | 3706 | 1942 | 856 | 38 | 30 | 1455.8 | 220 | 4108 | 0 | 780 | 2505.9 | 0 | 0 | 0 | 344
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 21-07-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 386 | 18:00 | 379 | 12:00 | Payra | 416 | 07:00 | 413 | 16:00
Ashuganj | 400 | 5:00 | 375 | 12:00 | Rahanpur | 404 | 19:30 | 372 | 13:00
Bhulta | 393 | 02:00 | 366 | 09:00 | Rampal | 406 | 18:00 | 397 | 19:30
Bibiana | 379 | 05:00 | 372 | 09:00
BIPTC | 402 | 06:00 | 393 | 13:00
Bogura | 390 | 19:30 | 358 | 09:00
Gopalganj | 401 | 18:00 | 392 | 23:00
Kaliakoir | 365 | 18:00 | 349 | 09:00
Madunaghat | 394 | 18:00 | 388 | 00:00
Meghnaghat | 386 | 18:00 | 380 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 224 | 06:00 | 218 | 09:00 | Keranigonj | 221 | 06:00 | 216 | 09:00
AKSML | 233 | 18:00 | 222 | 10:00 | Khulna(S) | 232 | 18:00 | 221 | 19:30
Aminbazar | 224 | 04:00 | 219 | 10:00 | Madunaghat | 234 | 18:00 | 228 | 01:00
Ashuganj | 227 | 01:00 | 217 | 09:00 | Madunaghat-400 | 234 | 18:00 | 227 | 10:00
Ashuganj-400 | 227 | 01:00 | 217 | 09:00 | Maniknagar | 218 | 02:00 | 212 | 12:00
Baghabari | 233 | 18:00 | 222 | 09:00 | Meghnaghat | 226 | 05:00 | 220 | 12:00
Barapukuria | 219 | 02:00 | 201 | 07:00 | Meghnaghat-400 | 223 | 18:30 | 218 | 11:00
Barapukuria-230 | 219 | 02:00 | 201 | 07:00 | Mirsorai | 232 | 18:30 | 218 | 03:00
Barishal | 227 | 09:00 | 220 | 21:00 | Rajshahi | 234 | 18:00 | 219 | 10:00
Bheramara | 234 | 18:00 | 221 | 08:00 | Rampal | 232 | 18:30 | 222 | 19:00
Bhulta | 226 | 02:00 | 208 | 09:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 221 | 01:00 | 217 | 15:00 | Rampura | 225 | 02:00 | 205 | 09:00
BIPTC | 236 | 18:00 | 222 | 00:00 | Shikalbaha | 231 | 18:00 | 222 | 11:00
Bogura | 235 | 19:30 | 217 | 13:00 | Shyampur | 220 | 06:00 | 215 | 12:00
Bogura-400 | 237 | 19:30 | 217 | 09:00 | Siddhirganj | 220 | 18:00 | 215 | 10:00
Borhanuddin | 232 | 09:00 | 227 | 19:30 | Sirajgonj | 238 | 18:00 | 228 | 09:00
BSRM | 230 | 18:00 | 218 | 11:00 | Sreepur | 225 | 18:00 | 214 | 09:00
Cumilla(N) | 221 | 18:00 | 215 | 09:00 | Tongi | 224 | 04:00 | 208 | 09:00
Faridpur | 224 | 18:00 | 216 | 22:00
Fenchuganj | 222 | 06:00 | 216 | 15:00
Ghorashal | 230 | 00:00 | 220 | 08:00
Ghorashal-230 | 223 | 02:00 | 208 | 09:00
Gopalganj | 225 | 18:00 | 218 | 23:00
GPH | 231 | 18:00 | 222 | 03:00
Haripur | 219 | 18:30 | 215 | 09:00
Hasnabad | 221 | 01:00 | 215 | 12:00
Hathazari | 233 | 07:00 | 222 | 10:00
Ishurdi | 236 | 18:00 | 223 | 09:00
Jhenaidah | 230 | 18:00 | 216 | 00:00
Kaliakoir | 226 | 18:00 | 216 | 09:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 01:00 | 122 | 09:00 | Lalmonirhat | 132 | 22:00 | 118 | 07:00
Agargaon | 131 | 06:00 | 125 | 11:00 | Madanganj | 128 | 18:00 | 124 | 11:00
Agrabad | 133 | 18:00 | 124 | 11:00 | Madaripur | 135 | 18:00 | 130 | 23:00
AKS | 130 | 18:00 | 125 | 09:00 | Madartek | 133 | 01:00 | 120 | 09:00
Aminbazar | 133 | 03:00 | 129 | 10:00 | Madunaghat | 133 | 17:00 | 127 | 11:00
Amnura | 136 | 16:00 | 125 | 07:00 | Magura | 134 | 18:00 | 122 | 00:00
Ashuganj | 138 | 18:00 | 134 | 09:00 | Mahasthangarh | 137 | 21:00 | 125 | 13:00
Bagerhat | 132 | 18:30 | 121 | 00:00 | Maijdee | 116 | 18:00 | 104 | 03:00
Bajitpur | 129 | 18:30 | 122 | 22:00 | Manikganj | 123 | 02:00 | 115 | 09:00
Bakulia | 135 | 18:00 | 126 | 11:00 | Maniknagar | 130 | 05:00 | 124 | 12:00
Banani | 136 | 02:00 | 122 | 09:00 | Matarbari | 122 | 16:00 | 109 | 00:00
Bangabhaban | 130 | 04:00 | 124 | 12:00 | Matuail | 128 | 18:00 | 124 | 11:00
Barapukuria | 133 | 02:00 | 120 | 07:00 | Millgate | 130 | 01:00 | 120 | 09:00
Barguna | 135 | 18:00 | 130 | 22:00 | Mirpur | 133 | 05:00 | 127 | 10:00
Barishal | 134 | 18:00 | 126 | 23:00 | Mirzapur | 129 | 18:00 | 120 | 09:00
Barishal-230 | 134 | 18:00 | 127 | 23:00 | Mithapukur | 138 | 19:30 | 119 | 07:00
Baroaulia | 132 | 17:00 | 126 | 10:00 | MI_Cement | 129 | 18:00 | 125 | 09:00
Baroirhat | 124 | 18:00 | 115 | 02:00 | Modern | 0 | 00:00 | 0 | 00:00
Bashundhara | 134 | 02:00 | 120 | 08:00 | Mogbazar | 137 | 02:00 | 122 | 08:00
BashundharaCement | 128 | 19:00 | 124 | 11:00 | Mongla | 133 | 18:00 | 122 | 00:00
Beanibazar | 123 | 06:00 | 113 | 19:00 | Motijheel | 130 | 04:00 | 124 | 12:00
Benapole | 133 | 18:30 | 122 | 00:00 | Muktagacha | 134 | 14:00 | 127 | 00:00
Bhaluka | 129 | 17:00 | 120 | 09:00 | Munshiganj | 129 | 18:00 | 124 | 07:00
Bhandaria | 130 | 01:00 | 117 | 23:00 | Muradnagar | 124 | 18:00 | 117 | 15:00
Bhangura | 133 | 18:00 | 127 | 08:00 | Mymensingh | 136 | 18:30 | 114 | 00:00
Bheramara | 137 | 18:00 | 129 | 09:00 | Naogaon | 131 | 18:00 | 121 | 13:00
Bheramara(GK) | 137 | 18:00 | 128 | 10:00 | Narail | 135 | 18:30 | 121 | 00:00
Bhulta | 122 | 01:00 | 117 | 12:00 | Narinda | 130 | 05:00 | 124 | 12:00
Bog-Sherpur | 134 | 18:30 | 126 | 07:00 | Narshingdi | 134 | 00:00 | 118 | 12:00
Bogura | 137 | 21:00 | 128 | 13:00 | Natore | 135 | 18:30 | 125 | 13:00
Bogura-230 | 139 | 19:30 | 128 | 08:00 | Nawabganj | 132 | 05:00 | 128 | 10:00
Brahmanbaria | 137 | 09:00 | 126 | 19:00 | Netrakona | 121 | 17:00 | 111 | 00:00
Cantonment | 131 | 05:00 | 125 | 11:00 | New | 130 | 00:00 | 120 | 09:00
Chandina | 125 | 18:00 | 121 | 03:00 | Niamatpur | 137 | 18:00 | 128 | 00:00
Chandpur | 127 | 18:00 | 111 | 01:00 | Noapara | 135 | 18:00 | 126 | 00:00
Chandraghona | 134 | 18:00 | 129 | 09:00 | Pabna | 133 | 18:00 | 126 | 13:00
Chapai | 136 | 18:00 | 128 | 00:00 | Palashbari | 135 | 21:00 | 119 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 18:00 | 125 | 11:00 | Panchagarh | 132 | 18:30 | 121 | 07:00
Chauddagram | 123 | 18:00 | 115 | 02:00 | Patuakhali | 135 | 13:00 | 131 | 20:00
Chhatak | 122 | 03:00 | 111 | 14:00 | Payra | 137 | 18:00 | 134 | 00:00
Chowmuhani | 117 | 17:00 | 107 | 00:00 | PHP | 122 | 18:00 | 114 | 03:00
Chuadanga | 133 | 18:00 | 120 | 00:00 | Postogola | 131 | 18:00 | 127 | 03:00
Coxsbazar | 121 | 18:00 | 110 | 00:00 | Purbachal | 135 | 01:00 | 120 | 09:00
Cumilla(N) | 127 | 18:00 | 119 | 15:00 | Purbasadipur | 129 | 22:00 | 117 | 08:00
Cumilla(S) | 135 | 05:00 | 119 | 15:00 | Rahanpur | 137 | 17:00 | 129 | 08:00
Daganbhuiyan | 120 | 18:30 | 109 | 02:00 | Rahanpur-400 | 138 | 18:00 | 128 | 08:00
Daudkandi | 122 | 18:00 | 115 | 19:00 | Rahim | 127 | 03:00 | 124 | 10:00
Dhaka | 136 | 01:00 | 123 | 09:00 | Rajbari | 132 | 10:00 | 126 | 19:30
Dhamrai | 127 | 17:00 | 119 | 09:00 | Rajendrapur | 133 | 18:00 | 120 | 00:00
Dhanmondi | 135 | 02:00 | 122 | 09:00 | Rajshahi | 133 | 18:00 | 125 | 13:00
Dohazari | 131 | 18:00 | 122 | 11:00 | Rajshahi-230 | 134 | 17:00 | -82 | 04:00
Faridpur | 133 | 09:00 | 128 | 22:00 | Ramganj | 121 | 18:30 | 105 | 02:00
Fatullah | 130 | 18:30 | 126 | 11:00 | Rampur | 133 | 18:00 | 125 | 10:00
Fenchuganj | 130 | 06:00 | 126 | 00:00 | Rampura | 135 | 02:00 | 121 | 09:00
Feni | 124 | 18:00 | 116 | 15:00 | Rangamati | 132 | 18:00 | 127 | 11:00
Ghatail | 129 | 17:00 | 122 | 00:00 | Rangpur | 132 | 22:00 | 118 | 07:00
Ghorashal | 134 | 00:00 | 126 | 09:00 | Ruppur | 136 | 17:00 | 129 | 09:00
Goalpara | 138 | 18:00 | 129 | 00:00 | Saidpur | 133 | 22:00 | 117 | 19:00
Gollamari | 137 | 18:00 | 130 | 00:00 | Satkhira | 134 | 18:00 | 121 | 00:00
Gopalganj | 135 | 18:00 | 128 | 23:00 | Satmasjid | 131 | 06:00 | 125 | 11:00
Gopalganj-400 | 137 | 18:00 | 133 | 19:30 | Savar | 134 | 04:00 | 128 | 08:00
Gulshan | 135 | 02:00 | 122 | 09:00 | SevenRings | 135 | 02:00 | 124 | 09:00
Halishahar | 134 | 18:00 | 125 | 10:00 | ShahCement | 129 | 18:00 | 125 | 11:00
Haripur | 128 | 18:00 | 124 | 11:00 | Shahjadpur | 135 | 01:00 | 130 | 09:00
HaripurSBU | 128 | 18:00 | 125 | 09:00 | Shahjibazar | 131 | 04:00 | 125 | 19:00
Hasnabad | 130 | 00:00 | 127 | 10:00 | Shahmirpur | 134 | 17:00 | 127 | 11:00
Hathazari | 133 | 18:00 | 129 | 00:00 | Shariatpur | 135 | 18:30 | 128 | 00:00
Ishurdi | 137 | 18:00 | 130 | 13:00 | Sherpur | 137 | 17:00 | 125 | 00:00
Jaldhaka | 131 | 22:00 | 114 | 07:00 | Shikalbaha | 124 | 18:00 | 117 | 10:00
Jamalpur | 140 | 15:00 | 130 | 00:00 | Shikalbaha-230 | 135 | 17:00 | 128 | 11:00
Jashore | 130 | 18:00 | 118 | 00:00 | Shitalakhya | 129 | 18:00 | 125 | 09:00
Jhenaidah | 135 | 18:00 | 119 | 13:00 | Sholosohor | 133 | 18:00 | 127 | 11:00
Jhenaidah-230 | 136 | 18:00 | 124 | 00:00 | Shyampur | 130 | 05:00 | 126 | 09:00
Joydebpur | 132 | 18:00 | 117 | 09:00 | Shyampur-230 | 130 | 18:30 | 126 | 09:00
Joypurhat | 130 | 18:30 | 119 | 13:00 | Siddhirganj | 128 | 01:00 | 125 | 10:00
Juldah | 134 | 18:00 | 126 | 11:00 | Sirajganj | 131 | 18:00 | 126 | 08:00
Kabirpur | 133 | 17:00 | 117 | 08:00 | Sonargaon | 125 | 00:00 | 121 | 10:00
Kachua | 125 | 18:00 | 112 | 01:00 | Sreemongol | 129 | 07:00 | 124 | 00:00
Kaliakoir | 133 | 18:00 | 123 | 09:00 | Sreepur | 130 | 18:00 | 120 | 12:00
Kallyanpur | 133 | 03:00 | 129 | 10:00 | Srinagar | 133 | 05:00 | 128 | 11:00
Kalurghat | 133 | 18:00 | 127 | 11:00 | SSM | 136 | 18:30 | 130 | 12:00
Kamrangirchar | 133 | 05:00 | 127 | 12:00 | Sunamganj | 120 | 07:00 | 109 | 19:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 123 | 06:00 | 114 | 19:00
Kasba | 123 | 18:00 | 117 | 23:00 | Sylhet-132 | 124 | 06:00 | 116 | 15:00
Kazla | 129 | 03:00 | 124 | 12:00 | Tangail | 127 | 17:00 | 120 | 00:00
Keranigonj | 133 | 06:00 | 128 | 11:00 | Taraganj | 135 | 19:30 | 116 | 07:00
Khagrachori | 131 | 04:00 | 127 | 11:00 | Thakurgaon | 131 | 18:30 | 119 | 07:00
Khulna | 136 | 18:00 | 126 | 00:00 | TK | 132 | 18:00 | 128 | 09:00
Khulna(S) | 138 | 18:00 | 130 | 00:00 | Tongi | 133 | 04:00 | 123 | 09:00
Khulshi | 132 | 18:00 | 125 | 09:00 | Ullahpara | 133 | 18:00 | 127 | 08:00
Kishoreganj | 127 | 17:00 | 119 | 19:00 | Ullon | 134 | 01:00 | 122 | 09:00
Kodda | 133 | 00:00 | 118 | 09:00 | Uttara | 133 | 04:00 | 126 | 11:00
KSRM | 134 | 18:00 | 126 | 10:00 | UttaraNew | 133 | 04:00 | 126 | 11:00
Kulaura | 130 | 07:00 | 123 | 19:00 | Zigatola | 132 | 05:00 | 127 | 12:00
Kurigram | 139 | 19:30 | 116 | 07:00
Kushtia | 133 | 18:00 | 123 | 13:00
Laksam | 124 | 18:00 | 111 | 02:00
Lakshmipur | 119 | 18:30 | 107 | 03:00
Lalbag | 132 | 04:00 | 128 | 10:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division