## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 22-07-2025 | [28 empty] | Date: | 22-07-2025 | [28 empty] | Date: | 22-07-2025 | [28 empty] | Date: | 22-07-2025 | [28 empty] | Date: | 22-07-2025 | [11 empty] | Date: | 22-07-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [11 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 7 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 502 | 50 | 19 | 131 | 141 | 261 | 55 | 55 | 158 | 16 | 450 | 299 | 0 | 0 | 55 | 326 | 195 | 0 | 0 | 125 | 21 | 22 | 0 | 0 | 0 | 30 | 70 | 0 | 0 | 65 | 60 | 0 | 12 | 25 | 0 | 218 | 34 | 22 | 685 | 160 | 0 | 50 | 25 | 51 | 218 | 0 | 0 | 0 | 1150 | 0 | 51 | 150 | 45 | 0 | 345 | 340 | 47 | 193 | 29 | 95 | 0 | 168 | 27 | 16 | 95 | 30 | 52.2 | 0 | 36 | 0 | 320 | 371 | 0 | 60 | 145 | 8 | 0 | 85 | 30 | 0 | 18 | 0 | 17 | 111 | 173 | 65 | 0 | 0 | 11 | 9034.2 | 855 | 184 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 17 | 1454.29 | 0 | 47 | 0 | 70 | 0 | 98 | 35 | 36 | 52.2 | 0 | 28 | 0 | 192 | 0 | 192 | 0 | 192 | 0 | 403 | 0 | 0 | 0 | 48 | 46 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 117 | 220 | 0 | 300 | 698 | 0 | 6655.49 | 15689.69 | 99.72
01:00 | 7 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 502 | 46 | 17 | 132 | 141 | 261 | 55 | 55 | 147 | 16 | 450 | 291 | 0 | 0 | 55 | 327 | 196 | 0 | 0 | 125 | 18 | 22 | 0 | 0 | 0 | 30 | 63 | 0 | 0 | 65 | 53 | 0 | 12 | 25 | 0 | 218 | 34 | 22 | 682 | 160 | 0 | 50 | 25.5 | 47 | 219 | 0 | 0 | 0 | 1107 | 0 | 51 | 147 | 45 | 0 | 347 | 335 | 47 | 189 | 29 | 80 | 0 | 51 | 10 | 16 | 95 | 28 | 52.2 | 0 | 36 | 0 | 320 | 338 | 0 | 60 | 133 | 8 | 0 | 85 | 30 | 0 | 18 | 0 | 17 | 110 | 164 | 65 | 0 | 0 | 11 | 8730.7 | 856 | 184 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 988 | 17 | 1448.81 | 0 | 47 | 0 | 70 | 0 | 98 | 35 | 36 | 52.2 | 0 | 28 | 0 | 191 | 0 | 189 | 0 | 192 | 0 | 363 | 0 | 0 | 0 | 46 | 109 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 117 | 220 | 0 | 301 | 695 | 0 | 6602.01 | 15332.71 | 99.77
02:00 | 7 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451 | 46 | 17 | 132 | 141 | 261 | 55 | 55 | 145 | 16 | 450 | 296 | 0 | 0 | 55 | 327 | 195 | 0 | 0 | 125 | 18 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 3 | 65 | 53 | 0 | 12 | 25 | 0 | 220 | 0 | 22 | 681 | 160 | 0 | 50 | 25.5 | 0 | 219 | 0 | 0 | 0 | 1151 | 0 | 51 | 143 | 45 | 0 | 343 | 340 | 48 | 198 | 29 | 72 | 0 | 51 | 0 | 16 | 94 | 28 | 52.2 | 0 | 36 | 0 | 320 | 389 | 0 | 60 | 136 | 8 | 0 | 85 | 30 | 0 | 18 | 0 | 17 | 110 | 163 | 64 | 0 | 0 | 11 | 8617.7 | 856 | 185 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 901 | 17 | 1443.23 | 0 | 47 | 0 | 70 | 0 | 98 | 35 | 36 | 52.2 | 0 | 28 | 0 | 191 | 0 | 189 | 0 | 191 | 0 | 360 | 0 | 0 | 0 | 46 | 109 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 117 | 220 | 0 | 301 | 695 | 0 | 6508.43 | 15126.13 | 99.82
03:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451 | 47 | 17 | 131 | 47 | 161 | 15 | 55 | 150 | 0 | 450 | 306 | 0 | 0 | 55 | 326 | 194 | 0 | 0 | 125 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 53 | 0 | 12 | 25 | 0 | 220 | 0 | 23 | 685 | 17 | 0 | 50 | 0 | 0 | 219 | 0 | 0 | 0 | 1170 | 0 | 51 | 143 | 45 | 0 | 342 | 335 | 48 | 206 | 29 | 73 | 0 | 51 | 0 | 16 | 94 | 26 | 52.2 | 0 | 29 | 0 | 320 | 386 | 0 | 60 | 137 | 8 | 0 | 85 | 30 | 0 | 18 | 0 | 17 | 110 | 164 | 64 | 0 | 0 | 11 | 8180.2 | 855 | 180 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 836 | 17 | 1442.09 | 0 | 47 | 0 | 35 | 0 | 98 | 0 | 36 | 0 | 0 | 28 | 0 | 190 | 0 | 189 | 0 | 191 | 0 | 371 | 0 | 0 | 0 | 46 | 109 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 117 | 220 | 0 | 302 | 695 | 0 | 6326.09 | 14506.29 | 99.87
04:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451 | 50 | 17 | 130 | 32 | 165 | 0 | 55 | 158 | 0 | 450 | 304 | 0 | 0 | 55 | 324 | 194 | 0 | 0 | 125 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 53 | 0 | 12 | 25 | 0 | 220 | 0 | 25 | 684 | 0 | 0 | 50 | 0 | 0 | 219 | 0 | 0 | 0 | 1160 | 0 | 51 | 143 | 45 | 0 | 343 | 340 | 48 | 203 | 29 | 73 | 0 | 51 | 0 | 16 | 94 | 26 | 52.2 | 0 | 30 | 0 | 320 | 389 | 0 | 60 | 144 | 8 | 0 | 85 | 30 | 0 | 18 | 0 | 17 | 110 | 164 | 64 | 0 | 0 | 11 | 8148.2 | 856 | 181 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 868 | 17 | 1448.82 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 28 | 0 | 180 | 0 | 189 | 0 | 191 | 0 | 374 | 0 | 0 | 0 | 47 | 109 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 117 | 220 | 0 | 302 | 700 | 0 | 6228.82 | 14377.02 | 99.92
05:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451 | 50 | 17 | 130 | 32 | 165 | 0 | 55 | 158 | 0 | 450 | 289 | 0 | 0 | 55 | 328 | 197 | 0 | 0 | 125 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 53 | 0 | 12 | 25 | 0 | 220 | 0 | 30 | 687 | 0 | 0 | 40 | 0 | 0 | 220 | 0 | 0 | 0 | 1140 | 0 | 51 | 130 | 45 | 0 | 348 | 340 | 48 | 190 | 29 | 72 | 0 | 51 | 0 | 16 | 94 | 26 | 52.2 | 0 | 37 | 0 | 320 | 361 | 0 | 60 | 141 | 8 | 0 | 85 | 30 | 0 | 18 | 0 | 17 | 110 | 164 | 64 | 0 | 0 | 11 | 8073.2 | 856 | 180 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 860 | 17 | 1462.83 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 28 | 0 | 191 | 0 | 189 | 0 | 191 | 0 | 339 | 0 | 0 | 0 | 47 | 109 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 110 | 220 | 0 | 300 | 698 | 0 | 6184.83 | 14258.03 | 99.97
06:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451 | 42 | 17 | 122 | 31 | 45 | 0 | 55 | 146 | 0 | 450 | 298 | 0 | 0 | 55 | 327 | 133 | 0 | 1 | 125 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 53 | 0 | 12 | 25 | 0.29 | 220 | 0 | 33 | 693 | 0 | 0 | 19 | 0 | 0 | 210 | 0 | 0 | 0 | 1146 | 1 | 43 | 70 | 45 | 0 | 348 | 340 | 48 | 194 | 29 | 75 | 0 | 51 | 5 | 16 | 94 | 24 | 52.2 | 3 | 37 | 0 | 320 | 315 | 0 | 60 | 134 | 0 | 0 | 85 | 30 | 0 | 18 | 0 | 17 | 110 | 164 | 65 | 0 | 0.66 | 4 | 7701.15 | 856 | 180 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 833 | 0 | 1300.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 2.26 | 191 | 0 | 189 | 0 | 191 | 0 | 343 | 0 | 0 | 0 | 47 | 91 | 0 | 113 | 0 | 0 | 0.3 | 0 | 0.03 | 0 | 169 | 110 | 220 | 0 | 302 | 690 | 0 | 5872.23 | 13573.38 | 100.02
07:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451 | 17 | 17 | 69 | 32 | 45 | 0 | 55 | 156 | 0 | 450 | 304 | 0 | 0 | 55 | 327 | 133 | 0 | 0 | 125 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 53 | 0 | 12 | 25 | 1.33 | 220 | 0 | 28 | 726 | 0 | 0 | 19 | 0 | 0 | 219 | 0 | 0 | 0 | 1156 | 4 | 43 | 70 | 45 | 0 | 347 | 340 | 48 | 197 | 29 | 75 | 0 | 51 | 0 | 19 | 94 | 24 | 52.2 | 14 | 36 | 0 | 320 | 330 | 0 | 60 | 141 | 0 | 0 | 85 | 30 | 0 | 18 | 0 | 17 | 110 | 153 | 65 | 0 | 2.57 | 11 | 7720.1 | 856 | 180 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 17 | 859 | 0 | 1314.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 7.54 | 191 | 0 | 189 | 0 | 191 | 0 | 353 | 0 | 0.63 | 0 | 47 | 91 | 0 | 113 | 0 | 0 | 0.9 | 5 | 0.1 | 0 | 170 | 110 | 220 | 0 | 302 | 700 | 0 | 5977.69 | 13697.79 | 100.07
08:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451 | 15.4 | 17 | 68 | 32 | 45 | 0 | 55 | 147 | 4 | 450 | 306 | 0 | 0 | 55 | 326 | 132 | 0 | 0 | 125 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 53 | 0 | 11 | 25 | 1.64 | 220 | 0 | 5 | 729 | 0 | 0 | 19 | 0 | 0 | 220 | 0 | 0 | 0 | 1164 | 7 | 43 | 70 | 45 | 0 | 346 | 340 | 48 | 198 | 29 | 75 | 0 | 51 | 0 | 19 | 94 | 24 | 52.2 | 11 | 37 | 0 | 320 | 330 | 0 | 60 | 134 | 0 | 0 | 85 | 30 | 0 | 18 | 0 | 17 | 109 | 143 | 60 | 1 | 3.39 | 11 | 7680.63 | 856 | 180 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 44 | 797 | 0 | 1326.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 11.68 | 194 | 0 | 189 | 0 | 191 | 0 | 351 | 0 | 0.86 | 0 | 47 | 91 | 0 | 113 | 0 | 0 | 1.6 | 23 | 0.15 | 0 | 172 | 110 | 220 | 0 | 302 | 695 | 0 | 5985.11 | 13665.74 | 100.12
09:00 | 0 | 70 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451 | 23 | 17 | 68 | 63 | 95 | 4 | 55 | 151 | 16 | 450 | 296 | 0 | 0 | 55 | 326 | 194 | 0 | 6 | 125 | 21.8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 53 | 0 | 11 | 25 | 1.11 | 221 | 0 | 2 | 738 | 17 | 0 | 19 | 0 | 0 | 217 | 0 | 0 | 0 | 1118 | 15 | 43 | 85 | 45 | 0 | 345 | 335 | 48 | 193 | 30 | 73 | 0 | 51 | 1 | 15 | 94 | 24 | 52.2 | 54 | 37 | 0 | 320 | 370 | 0 | 60 | 138 | 0 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 109 | 143 | 60 | 1 | 2.54 | 11 | 7883.65 | 856 | 182 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 55 | 833 | 0 | 1310.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 12.43 | 197 | 0 | 187 | 0 | 197 | 0 | 342 | 0 | 0.84 | 0 | 47 | 91 | 1 | 113 | 0 | 0 | 2.3 | 55 | 0.31 | 0 | 169 | 110 | 220 | 0 | 302 | 702 | 0 | 6050.75 | 13934.4 | 100.17
10:00 | 7 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451 | 54 | 17 | 95 | 63 | 195 | 20 | 55 | 147 | 16 | 450 | 302 | 0 | 0 | 55 | 326 | 192 | 0 | 6 | 125 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 53 | 0 | 11 | 25 | 4.03 | 220 | 0 | 2 | 737 | 17 | 0 | 19 | 0 | 0 | 217 | 0 | 0 | 0 | 1098 | 17 | 43 | 133 | 45 | 0 | 343 | 335 | 48 | 194 | 30 | 74 | 0 | 51 | 9 | 17 | 94 | 22 | 47 | 59 | 37 | 0 | 320 | 370 | 0 | 60 | 136 | 0 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 109 | 134 | 60 | 1 | 6.14 | 11 | 8110.67 | 856 | 176 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 19.11 | 837 | 0 | 1305.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 16.1 | 198 | 0 | 189 | 0 | 199 | 0 | 346 | 0 | 1.11 | 0 | 47 | 91 | 5 | 113 | 0 | 0 | 2.3 | 145 | 0.77 | 0 | 171 | 110 | 220 | 0 | 301 | 660 | 0 | 6086.37 | 14197.04 | 100.22
11:00 | 7 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505 | 54 | 17 | 105 | 95 | 210 | 33 | 55 | 154 | 16 | 450 | 305 | 0 | 0 | 55 | 324 | 191 | 0 | 14 | 125 | 21.5 | 22 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 33 | 45 | 0 | 11 | 25 | 4.37 | 219 | 0 | 2 | 738 | 53 | 0 | 29 | 5 | 0 | 215 | 0 | 0 | 0 | 1108 | 8 | 43 | 142 | 45 | 0 | 348 | 340 | 46 | 197 | 31 | 72 | 0 | 51 | 8 | 19 | 94 | 24 | 43 | 61 | 37 | 0 | 320 | 324 | 0 | 60 | 151 | 0 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 92 | 143 | 34 | 1 | 18.86 | 11 | 8260.73 | 856 | 171 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 43.57 | 940 | 0 | 1252.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 18.73 | 195 | 0 | 187 | 0 | 196 | 0 | 350 | 0 | 1.06 | 0 | 47 | 95 | 13 | 113 | 0 | 0 | 2.9 | 101 | 0.81 | 0 | 172 | 110 | 220 | 0 | 301 | 650 | 0 | 6099.76 | 14360.49 | 100.27
12:00 | 7 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505 | 54 | 17 | 129 | 105 | 248 | 55 | 55 | 150 | 16 | 450 | 305 | 0 | 0 | 55 | 322 | 191 | 0 | 30 | 125 | 21.5 | 22 | 0 | 0 | 0 | 0 | 47 | 0 | 11 | 33 | 45 | 0 | 11 | 25 | 4.37 | 217 | 0 | 2 | 746 | 60 | 0 | 50 | 17 | 0 | 215 | 0 | 0 | 0 | 1106 | 8 | 43 | 145 | 8 | 0 | 344 | 335 | 47 | 202 | 29 | 73 | 0 | 51 | 8 | 14 | 94 | 26 | 43 | 57 | 37 | 0 | 320 | 346 | 0 | 60 | 156 | 0 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 93 | 143 | 34 | 1 | 21.13 | 11 | 8451 | 855 | 168 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 102.09 | 959 | 0 | 1354.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 24.43 | 193 | 0 | 185 | 0 | 160 | 0 | 368 | 0 | 1.45 | 0 | 47 | 95 | 29 | 113 | 0 | 0 | 2.5 | 111 | 0.34 | 0 | 174 | 110 | 190 | 0 | 301 | 651 | 0 | 6288.48 | 14739.48 | 100.31
13:00 | 7 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451 | 54 | 17 | 129 | 110 | 248 | 55 | 55 | 151 | 16 | 450 | 298 | 0 | 0 | 55 | 321 | 193 | 0 | 14 | 125 | 21.5 | 22 | 0 | 0 | 0 | 0 | 77 | 0 | 14 | 33 | 45 | 0 | 11 | 25 | 4.15 | 217 | 0 | 5 | 750 | 160 | 0 | 50 | 25.5 | 9 | 216 | 0 | 0 | 0 | 1082 | 18 | 43 | 143 | 8 | 0 | 350 | 340 | 48 | 183 | 35 | 73 | 0 | 51 | 18 | 19 | 94 | 28 | 52.2 | 74 | 35 | 0 | 320 | 361 | 0 | 60 | 153 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 92 | 134 | 34 | 1 | 39.89 | 11 | 8592.24 | 855 | 167 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 98.16 | 911 | 0 | 1409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 19.52 | 189 | 0 | 182 | 0 | 180 | 0 | 330 | 0 | 1.46 | 0 | 47 | 94 | 34 | 113 | 0 | 0 | 3.3 | 164 | 0.9 | 0 | 165 | 110 | 190 | 0 | 302 | 652 | 0 | 6365.34 | 14957.58 | 100.35
14:00 | 7 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451 | 54 | 17 | 126 | 138 | 268 | 55 | 0 | 72 | 16 | 450 | 298 | 0 | 0 | 55 | 331 | 195 | 0 | 31 | 125 | 0 | 22 | 0 | 0 | 0 | 0 | 77 | 0 | 20 | 50 | 56 | 0 | 11 | 25 | 1.77 | 218 | 0 | 2 | 705 | 160 | 0 | 50 | 25.5 | 16 | 214 | 0 | 0 | 0 | 1105 | 15 | 43 | 142 | 8 | 0 | 343 | 335 | 48 | 197 | 32 | 73 | 0 | 51 | 32 | 19 | 94 | 28 | 43 | 63 | 36 | 0 | 320 | 362 | 0 | 60 | 154 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 92 | 143 | 34 | 1 | 39.19 | 11 | 8505.46 | 856 | 162 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 27.19 | 896 | 0 | 1424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 43.36 | 160 | 0 | 150 | 0 | 185 | 0 | 350 | 0 | 5.42 | 0 | 47 | 94 | 10 | 113 | 0 | 0 | 8 | 129 | 0 | 0 | 171 | 110 | 190 | 0 | 302 | 651 | 0 | 6203.97 | 14709.43 | 100.39
15:00 | 7 | 53 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 452 | 54 | 17 | 126 | 138 | 268 | 55 | 0 | 0 | 16 | 450 | 296 | 0 | 0 | 55 | 331 | 200 | 0 | 15 | 125 | 0 | 22 | 0 | 0 | 0 | 0 | 78 | 0 | 7 | 50 | 60 | 0 | 12 | 25 | 2.83 | 218 | 0 | 2 | 732 | 160 | 0 | 50 | 25.5 | 15 | 214 | 0 | 0 | 0 | 1100 | 0 | 51 | 140 | 8 | 0 | 340 | 340 | 48 | 190 | 34 | 73 | 0 | 51 | 35 | 19 | 95 | 28 | 43 | 52 | 37 | 0 | 320 | 362 | 0 | 58 | 154 | 6 | 0 | 80 | 30 | 0 | 18 | 0 | 17 | 91 | 135 | 34 | 1 | 15.92 | 11 | 8381.25 | 855 | 158 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 43.11 | 918 | 0 | 1409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 36.03 | 160 | 0 | 150 | 0 | 160 | 0 | 342 | 0 | 1.85 | 0 | 47 | 94 | 23 | 113 | 0 | 0 | 7.2 | 143 | 0.16 | 0 | 166 | 110 | 190 | 0 | 302 | 653 | 0 | 6156.35 | 14537.6 | 100.43
16:00 | 30 | 53 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 453 | 54 | 17 | 126 | 122 | 270 | 55 | 0 | 0 | 16 | 450 | 304 | 0 | 0 | 35 | 326 | 194 | 0 | 17 | 125 | 0 | 22 | 0 | 0 | 0 | 0 | 87 | 0 | 6 | 50 | 60 | 0 | 36 | 26 | 0.76 | 219 | 0 | 2 | 762 | 160 | 0 | 50 | 25.5 | 15 | 213 | 0 | 0 | 0 | 1125 | 0 | 51 | 140 | 25 | 0 | 335 | 340 | 47 | 206 | 34 | 70 | 0 | 51 | 42 | 19 | 95 | 28 | 52.2 | 40 | 37 | 0 | 320 | 362 | 0 | 58 | 152 | 8 | 0 | 81 | 30 | 0 | 16 | 0 | 17 | 92 | 123 | 34 | 1 | 15.83 | 11 | 8472.29 | 856 | 158 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 21.25 | 848 | 0 | 1421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 22.86 | 160 | 0 | 150 | 0 | 160 | 0 | 370 | 0 | 2.21 | 0 | 46 | 94 | 16 | 113 | 0 | 0 | 4.9 | 20 | 0.21 | 0 | 172 | 110 | 190 | 0 | 302 | 600 | 0 | 5920.43 | 14392.72 | 100.46
17:00 | 48 | 53 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 453 | 54 | 1 | 126 | 138 | 267 | 55 | 0 | 0 | 16 | 450 | 293 | 0 | 0 | 35 | 325 | 193 | 0 | 9 | 125 | 13 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 6 | 50 | 54 | 0 | 36 | 27 | 0.58 | 220 | 0 | 7 | 760 | 160 | 0 | 50 | 25.5 | 16 | 215 | 0 | 0 | 0 | 1134 | 0 | 51 | 142 | 26 | 0 | 338 | 340 | 47 | 190 | 29 | 73 | 0 | 52 | 47 | 19 | 95 | 26 | 52.2 | 16 | 37 | 0 | 320 | 362 | 0 | 58 | 152 | 8 | 0 | 81 | 30 | 0 | 16 | 0 | 17 | 92 | 113 | 34 | 0 | 11.36 | 11 | 8421.64 | 855 | 158 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 15.01 | 804 | 0 | 1410 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 11.87 | 160 | 0 | 150 | 0 | 160 | 0 | 341 | 0 | 1.17 | 0 | 46 | 94 | 10 | 108 | 0 | 0 | 0.7 | 30 | 0.12 | 0 | 167 | 110 | 190 | 0 | 303 | 594 | 0 | 5782.87 | 14204.51 | 100.49
18:00 | 74 | 53 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 54 | 17 | 126 | 122 | 274 | 55 | 0 | 0 | 16 | 450 | 303 | 0 | 0 | 55 | 300 | 76 | 0 | 2 | 108 | 20 | 22 | 0 | 0 | 0 | 0 | 85 | 0 | 1 | 50 | 67 | 0 | 36 | 30 | 0.22 | 220 | 0 | 12 | 708 | 124 | 0 | 50 | 8 | 15 | 215 | 0 | 0 | 0 | 1076 | 1 | 51 | 144 | 26 | 0 | 300 | 300 | 47 | 207 | 35 | 73 | 0 | 58 | 55 | 19 | 95 | 26 | 52.2 | 3 | 37 | 0 | 320 | 362 | 0 | 58 | 145 | 8 | 0 | 81 | 30 | 0 | 16 | 0 | 17 | 92 | 113 | 34 | 0 | 3.93 | 11 | 8080.35 | 855 | 160 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6.34 | 803 | 10 | 1356 | 0 | 0 | 0 | 35 | 0 | 50 | 0 | 0 | 0 | 5 | 0 | 2.44 | 160 | 0 | 150 | 0 | 160 | 0 | 389 | 0 | 0.24 | 0 | 46 | 94 | 1 | 113 | 0 | 0 | 0.2 | 11 | 0.03 | 0 | 179 | 105 | 190 | 0 | 302 | 545 | 0 | 5766.25 | 13846.6 | 100.52
19:00 | 78 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 503 | 52.5 | 17 | 126 | 138 | 262 | 55 | 12 | 118 | 16 | 450 | 298 | 0 | 0 | 55 | 321 | 193 | 0 | 0 | 114 | 1 | 22 | 0 | 0 | 6 | 15 | 65 | 0 | 0 | 50 | 67 | 0 | 36 | 31 | 0 | 220 | 5 | 8 | 753 | 160 | 0 | 50 | 8 | 20 | 215 | 0 | 0 | 0 | 1169 | 0 | 51 | 145 | 68 | 0 | 335 | 340 | 47 | 206 | 31 | 73 | 0 | 144 | 56 | 19 | 95 | 30 | 52.2 | 0 | 36 | 0 | 320 | 362 | 0 | 58 | 151 | 8 | 0 | 82 | 30 | 0 | 16 | 0 | 17 | 100 | 133 | 46 | 0 | 0 | 11 | 8909.7 | 855 | 163 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 865 | 30 | 1344 | 0 | 0 | 0 | 35 | 0 | 85 | 55 | 10 | 38 | 0 | 24 | 0 | 166 | 0 | 184 | 0 | 180 | 0 | 406 | 0 | 0 | 0 | 47 | 94 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 105 | 220 | 0 | 301 | 568 | 0 | 6128 | 15037.7 | 100.55
19:30 | 82 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 503 | 45.5 | 17 | 126 | 138 | 264 | 55 | 35 | 140 | 16 | 450 | 300 | 0 | 0 | 55 | 325 | 194 | 0 | 0 | 125 | 22 | 22 | 0 | 0 | 18 | 30 | 90 | 0 | 0 | 50 | 59 | 0 | 36 | 25 | 0 | 220 | 20 | 12 | 760 | 160 | 0 | 50 | 17 | 45 | 215 | 0 | 0 | 0 | 1150 | 0 | 51 | 147 | 150 | 0 | 341 | 340 | 47 | 195 | 32 | 74 | 0 | 155 | 65 | 19 | 95 | 28 | 52.2 | 0 | 36 | 0 | 320 | 362 | 0 | 58 | 156 | 8 | 0 | 82 | 30 | 0 | 16 | 0 | 17 | 100 | 133 | 46 | 0 | 0 | 11 | 9175.7 | 856 | 159 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1016 | 34 | 1324 | 0 | 0 | 0 | 105 | 0 | 96 | 95 | 15 | 52.2 | 0 | 28 | 0 | 166 | 0 | 187 | 0 | 182 | 0 | 403 | 0 | 0 | 0 | 46 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 115 | 220 | 0 | 302 | 650 | 0 | 6546.2 | 15721.9
20:00 | 90 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 506 | 47.1 | 17 | 126 | 141 | 269 | 55 | 45 | 138 | 16 | 450 | 283 | 0 | 0 | 55 | 325 | 194 | 0 | 0 | 125 | 22 | 22 | 0 | 0 | 27 | 30 | 95 | 0 | 0 | 50 | 59 | 0 | 36 | 25 | 0 | 220 | 30 | 10 | 761 | 160 | 0 | 50 | 25.5 | 47 | 215 | 0 | 0 | 0 | 1142 | 0 | 51 | 145 | 165 | 0 | 345 | 340 | 47 | 183 | 32 | 73 | 0 | 155 | 65 | 19 | 95 | 28 | 52.2 | 0 | 36 | 0 | 320 | 361 | 0 | 60 | 152 | 8 | 0 | 82 | 30 | 0 | 16 | 0 | 17 | 100 | 134 | 47 | 0 | 0 | 11 | 9215.8 | 856 | 158 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1058 | 35 | 1316 | 0 | 41 | 0 | 105 | 0 | 97 | 113 | 25 | 52.2 | 0 | 28 | 0 | 163 | 0 | 187 | 0 | 183 | 0 | 383 | 0 | 0 | 0 | 46 | 95 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 238 | 115 | 220 | 0 | 302 | 650 | 0 | 6616.2 | 15832 | 100.58
21:00 | 82 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505 | 48.6 | 17 | 126 | 141 | 276 | 55 | 55 | 142 | 16 | 450 | 300 | 0 | 0 | 55 | 325 | 194 | 0 | 0 | 125 | 20 | 22 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 50 | 59 | 0 | 36 | 25 | 0 | 220 | 32 | 13 | 761 | 160 | 0 | 50 | 25.5 | 47 | 216 | 0 | 0 | 0 | 1140 | 0 | 51 | 143 | 163 | 0 | 343 | 340 | 48 | 211 | 35 | 73 | 0 | 155 | 65 | 19 | 95 | 30 | 52.2 | 0 | 30 | 0 | 320 | 361 | 0 | 60 | 153 | 8 | 0 | 82 | 30 | 0 | 16 | 0 | 17 | 102 | 135 | 47 | 0 | 0 | 11 | 9224.3 | 856 | 161 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1116 | 45 | 1412.71 | 0 | 47 | 0 | 113 | 0 | 96 | 113 | 37 | 52.2 | 0 | 28 | 0 | 166 | 0 | 188 | 0 | 184 | 0 | 405 | 0 | 0 | 0 | 46 | 94 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 118 | 220 | 0 | 302 | 691 | 0 | 6855.91 | 16080.21 | 100.61
22:00 | 75 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 506 | 45 | 18 | 126 | 141 | 276 | 55 | 55 | 140 | 16 | 450 | 291 | 0 | 0 | 55 | 326 | 194 | 0 | 0 | 125 | 20 | 22 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 50 | 59 | 0 | 36 | 25 | 0 | 220 | 32 | 18 | 762 | 160 | 0 | 50 | 25.5 | 49 | 216 | 0 | 0 | 0 | 1137 | 0 | 51 | 150 | 155 | 0 | 345 | 340 | 47 | 212 | 35 | 73 | 0 | 155 | 66 | 19 | 95 | 30 | 52.2 | 0 | 36 | 0 | 320 | 361 | 0 | 60 | 153 | 8 | 0 | 82 | 30 | 0 | 16 | 0 | 17 | 102 | 136 | 47 | 0 | 0 | 11 | 9211.7 | 856 | 156 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1086 | 51 | 1414.55 | 0 | 47 | 0 | 113 | 0 | 96 | 113 | 37 | 52.2 | 0 | 28 | 0 | 188 | 0 | 185 | 0 | 182 | 0 | 401 | 0 | 0 | 0 | 46 | 94 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 118 | 220 | 0 | 302 | 691 | 0 | 6837.75 | 16049.45 | 100.64
23:00 | 15 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 50 | 35 | 126 | 141 | 276 | 55 | 55 | 143 | 16 | 450 | 290 | 0 | 0 | 55 | 327 | 196 | 0 | 0 | 125 | 21 | 22 | 0 | 0 | 0 | 30 | 90 | 0 | 0 | 50 | 50 | 0 | 36 | 25 | 0 | 220 | 36 | 25 | 761 | 160 | 0 | 50 | 25.5 | 62 | 217 | 0 | 0 | 0 | 1100 | 0 | 51 | 142 | 81 | 0 | 348 | 335 | 44 | 206 | 35 | 79 | 0 | 155 | 65 | 7 | 94 | 30 | 52.2 | 0 | 38 | 0 | 320 | 360 | 0 | 60 | 154 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 100 | 145 | 47 | 0 | 0 | 11 | 9094.7 | 856 | 156 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 51 | 1439.43 | 0 | 40 | 0 | 113 | 0 | 96 | 113 | 37 | 52.2 | 0 | 28 | 0 | 191 | 0 | 183 | 0 | 182 | 0 | 390 | 0 | 0 | 0 | 46 | 94 | 0 | 106 | 16 | 0 | 0 | 0 | 0 | 0 | 206 | 120 | 220 | 0 | 302 | 700 | 0 | 6887.63 | 15982.33 | 100.67
Total KWH | 553392 | 2064960 | 688800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11244970 | 1112760 | 452880 | 2842560 | 2384160 | 5258553 | 950255 | 1049127 | 2882880 | 295680 | 10248500 | 7226182 | 0 | 0 | 1294953 | 7804112 | 4515000 | 0 | 155876 | 2978400 | 406200 | 487080 | 0 | 0 | 46418 | 130473 | 1147200 | 0 | 62880 | 1122839 | 1259760 | 0 | 468480 | 610560 | 28320 | 5112431 | 250073 | 332160 | 17621818.18 | 2412072 | 0 | 1056000 | 375498 | 491782 | 5205410 | 0 | 0 | 0 | 27283634 | 107055 | 1096909 | 3208290 | 1338182 | 0 | 8494500 | 8172000 | 1134720 | 4847000 | 757008 | 1793280 | 0 | 1859520 | 664440 | 385480 | 2267460 | 636480 | 1193184 | 477773 | 868064 | 0 | 7647900 | 8984000 | 0 | 1390080 | 3517118 | 125112 | 0 | 1980480 | 719808 | 0 | 416000 | 0 | 427320 | 2406000 | 3384000 | 1123200 | 7850 | 195310 | 272880 | 203813491.18 | 20727273 | 4280832 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 455760 | 21963640 | 365280 | 33403127 | 0 | 435102 | 0 | 882048 | 0 | 933248 | 681600 | 299403 | 396638 | 506720 | 282036 | 234000 | 4476636 | 0 | 4512564 | 0 | 4664091 | 0 | 8911454 | 0 | 17100 | 0 | 1083927 | 2308996 | 157839 | 2689756 | 18000 | 0 | 35532.24 | 998640 | 3568.5 | 0 | 4362000 | 2713000 | 5251930 | 0 | 7258182 | 16603636.36 | 0 | 152825559.1 | 356639050.28

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 23-07-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-07-2025 | during | 23-07-2025 | during | 23-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 0 | 0 | 0 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 305 | 300 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 191 | 194 | 208.13 | 208.13 | 197 | 197 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 322 | 325 | 335 | 335 | 333 | 333 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 82 | 7 | 102 | 7 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 54 | 48.6 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 105 | 141 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21.5 | 20 | 33 | 33 | 24 | 24 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 33 | 33 | 52.19 | 52.19 | 42 | 42 | Engine Problem
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 248 | 276 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 129 | 126 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 16 | 16 | 104 | 104 | 16 | 16 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 150 | 142 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 25 | 0 | 25 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 35 | 35 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 505 | 505 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 125 | 125 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2965.5 | 3092.6 | 4717.65 | 4787.65 | 3279.33 | 3349.33
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 17 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 8 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 217 | 220 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 216 | 213 | 213 | 213 | 213 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 47 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 45 | 59 | 48 | 72 | 48 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 33 | 50 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 11 | 36 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 13 | 2 | 25 | 2 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 47 | 102 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.37 | 0 | 4.53 | 0 | 4.53 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 32 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 60 | 160 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1106 | 1140 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 11 | 0 | 1 | 1 | 1 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 746 | 761 | 790 | 790 | 790 | 790 | Machine Problem
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 2597.37 | 2936.5 | 3804.25 | 3828.72 | 3804.25 | 3828.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 202 | 211 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 344 | 343 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 335 | 340 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 29 | 35 | 46.7 | 46.7 | 35 | 35 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 47 | 48 | 55 | 55 | 49 | 49 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 163 | 195 | 195 | 81 | 81 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 145 | 143 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 37 | 30 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 155 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 26 | 30 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 19 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 94 | 95 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 65 | 113 | 113 | 18 | 37 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 73 | 73 | 115 | 115 | 95 | 95 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 57 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1556 | 1853.2 | 2434.56 | 2379.56 | 2004.36 | 1968.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-07-2025 | during | 23-07-2025 | during | 23-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 34 | 47 | 157.5 | 157.5 | 67 | 67 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 143 | 135 | 200 | 200 | 186 | 186 | Engine Problem
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 93 | 102 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 21.13 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 11 | 11 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 35 | 35 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 320.13 | 312 | 598.9 | 549 | 464.9 | 415
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 60 | 60 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 153 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 82 | 86 | 86 | 85 | 85 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 16 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 8 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | Plant Shutdown as per schedule HGPI work
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 346 | 361 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | machine problem
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1012 | 1030 | 1087 | 1087 | 1025 | 1025
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 855 | 856 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 168 | 161 | 410 | 410 | 203 | 203 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 45 | 105 | 105 | 60 | 60 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 102.09 | 0 | 70 | 0 | 70 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 959 | 1116 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2122.09 | 2216 | 3622.2 | 3552.2 | 3370 | 3300
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 301 | 302 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 110 | 118 | 120 | 120 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 651 | 691 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 190 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 174 | 220 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.34 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1426.34 | 1551 | 2152 | 2151 | 2152 | 2151
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 47 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 193 | 166 | 214 | 214 | 198 | 198 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 185 | 188 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 160 | 184 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 368 | 405 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 96 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.45 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1354.67 | 1412.71 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 24.43 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 56 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 2342.55 | 2841.91 | 3195.47 | 3028.87 | 3138.09 | 2971.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 47 | 46 | 45 | 45 | 48 | 48 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 113 | 107 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.5 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 95 | 94 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 29 | 0 | 18 | 0 | 18 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 111 | 0 | 141.51 | 0 | 141.51 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 397.5 | 247 | 473.11 | 307 | 476.11 | 310
System Total |  |  |  |  | 28565.2 | 27045.875 | 14739.48 | 16080.21 | 22085.14 | 21671 | 19714.04 | 19318.9
Forecast Scenario (23-07-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 18000 |  | 0 |  | 18000
|  |  |  | 1:00 | 17700 |  | 0 |  | 17700
|  |  |  | 2:00 | 17400 |  | 0 |  | 17400
|  |  |  | 3:00 | 16800 |  | 0 |  | 16800
|  |  |  | 4:00 | 16650 |  | 0 |  | 16650
|  |  |  | 5:00 | 16500 |  | 0 |  | 16500
|  |  |  | 6:00 | 15800 |  | 0 |  | 15800
|  |  |  | 7:00 | 15850 |  | 0 |  | 15850
|  |  |  | 8:00 | 15830 |  | 0 |  | 15830
|  |  |  | 9:00 | 14100 |  | 0 |  | 14100
|  |  |  | 10:00 | 14500 |  | 0 |  | 14500
|  |  |  | 11:00 | 14700 |  | 0 |  | 14700
|  |  |  | 12:00 | 15080 |  | 0 |  | 15080
|  |  |  | 13:00 | 15370 |  | 0 |  | 15370
|  |  |  | 14:00 | 15180 |  | 0 |  | 15180
|  |  |  | 15:00 | 15030 |  | 0 |  | 15030
|  |  |  | 16:00 | 14790 |  | 0 |  | 14790
|  |  |  | 17:00 | 14600 |  | 0 |  | 14600
|  |  |  | 18:00 | 14100 |  | 0 |  | 14100
|  |  |  | 18:30 | 14800 |  | 0 |  | 14800
|  |  |  | 19:00 | 15380 |  | 0 |  | 15380
|  |  |  | 19:30 | 16240 |  | 0 |  | 16240
|  |  |  | 20:00 | 16340 |  | 0 |  | 16340
|  |  |  | 21:00 | 16570 |  | 0 |  | 16570
|  |  |  | 22:00 | 16400 |  | 0 |  | 16400
|  |  |  | 23:00 | 16300 |  | 0 |  | 16300
Probable Maximum Temperature: |  |  | 33.60°C
Probable Maximum Demand at Day Peak: |  |  | 15080.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 16570.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16370.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 368.40588 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:19 hrs on 23-07-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 22-07-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14739.48 | MW | 12:00 Hr. | Energy Generated |  |  | 356.6391 |  | MKWHr.
| Day Peak Demand |  |  | 14883.48 | MW | 12:00 Hr. | Energy Unserverd |  |  | 5.247 |  | MKWHr.
| Evening Peak Generation |  |  | 16080.21 | MW | 21:00 Hr. | Energy Demand |  |  | 361.8861 |  | MKWHr.
| Evening Peak Demand |  |  | 16372.21 | MW | 21:00 Hr. | Maximum Temperature |  |  | 34 |  | °C
| Minimum Generation of the Day |  |  | 13573.38 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 987.67 |  | MMCFD
| Maximum Generation of the Day |  |  | 16080.21 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 7.1487 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 41.932 | 0 | 24.8094 | 0 | 0 | 0.15588 | 0 | 0 | 66.8973 | Gas | 134.4096 | Gas | 458220263.01
| Chattogram Zone |  |  | 5.5376 | 44.9055 | 9.3712 | 0 | 5.1124 | 0.13537 | 0 | 0.06288 | 65.1249 | Coal | 96.1768 | Coal | 580736067.6504
| Cumilla Zone |  |  | 26.2258 | 0 | 11.8542 | 0 | 0 | 0.47777 | 0.63648 | 0 | 39.1943 | HFO | 61.7991 | HFO | 1162230925.87
| Mymensingh Zone |  |  | 1.1232 | 0 | 6.4902 | 0 | 0 | 0.20316 | 0 | 0 | 7.8166 | HSD | 0.018 | HSD | 955080
| Sylhet Zone |  |  | 24.7805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.7805 | Hydro | 5.1124 | Hydro | 511243.1
| Khulna Zone |  |  | 4.2808 | 21.9636 | 0.36528 | 0 | 0 | 0.45576 | 21.6393 | 0 | 48.7048 | Solar | 3.3813 | Solar | 54401645.6914
| Barishal Zone |  |  | 7.9649 | 28.2238 | 0 | 0 | 0 | 0.0035685 | 0 | 0 | 36.1923 | Import | 55.6789 | Import | 291514064.86
| Rajshahi Zone |  |  | 22.5647 | 0 | 3.9101 | 0 | 0 | 0.75782 | 33.4031 | 0 | 60.6358 | Wind | 0.06288 | Wind | 920563.2
| Rangpur Zone |  |  | 0 | 1.0839 | 4.9988 | 0.018 | 0 | 1.192 | 0 | 0 | 7.2927
| Total |  |  | 134.4096 | 96.1768 | 61.7991 | 0.018 | 5.1124 | 3.3813 | 55.6789 | 0.06288 | 356.6391
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 458220263.01 |  | Hydro | 511243.1
|  |  |  | Coal | 580736067.6504 |  | Solar | 54401645.6914
|  |  |  | HFO | 1162230925.87 |  | Import | 291514064.86
|  |  |  | HSD | 955080 |  | Wind | 920563.2
[5 empty] | Total: | 254,94,89,853 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.7273 | Peak Hr Flow | 856.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 33674654.64 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 33.4031 | Peak Hr Flow | 1412.71 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 904 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.63648 | Peak Hr Flow | 30.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 1026 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 54.7669 | Peak Hr Flow | 2298.71 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 65 |  | 5651
|  |  |  | Chattogram |  | 0 |  | 1555
|  |  |  | Cumilla |  | 45 |  | 1505
|  |  |  | Mymensingh |  | 40 |  | 1263
|  |  |  | Sylhet |  | 30 |  | 661
|  |  |  | Khulna |  | 0 |  | 1924
|  |  |  | Barishal |  | 0 |  | 488
|  |  |  | Rajshahi |  | 0 |  | 1686
|  |  |  | Rangpur |  | 99 |  | 1045
|  |  |  | Total |  | 279 |  | 15778
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Bibiana-II 341 MW CCPP (Summit) GT |  |  | 222 | 3 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
|  | 4 | Bibiana-II 341 MW CCPP (Summit) ST |  |  | 119 | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 641 |  |  |  | Total | 707
|  |  |  | Total Unavailable Capacity |  |  |  | 1348
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:21 |  | Jashore 132/33kV S/S JH-2(L1) Scheduled S/D Due to shutdown
| 08:22 |  | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-2 Scheduled S/D
| 10:15 |  | Raozan 25 MW PP Synchronized
|  | 11:25 | Bibiana 400/230kV S/S Summit STG is restored.
|  | 11:28 | Barapukuria S/S-P/S 230 kV Ckt-1 is restored.
|  | 12:04 | Bogura 400/230kV S/S Bogura - Rooppur 400 KV Line-1 is restored.
| 13:26 | 13:43 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-1 Tripped showing Lockout Relay operated, | [7 empty] | 132.0MW load
|  |  | relays Due to Zone-1 operated, Fault Distance location 23km. | [7 empty] | interrup.
| 13:27 | 13:44 | Jashore 132/33kV S/S JH-1(L2) Tripped showing Distance Relay. relays Due to Phase A, Trip | [7 empty] | 128.0MW load
|  |  | ABC | [7 empty] | interrup.
| 13:27 | 14:02 | Jashore 132/33kV S/S Cap. Bank-1 Tripped showing Under Voltage relays Due to Trip
| 14:27 | 18:01 | Aminbazar-Manikgonj PP 132kV Ckt-1 Project Work S/D from Aminbazar 400/230/132kV end Due | [7 empty] | 120.0MW load
|  |  | to Aminbazar-Kaliakoir 400kv conductor repair work. | [7 empty] | interrup. Aminbazar
400/230/132kV end
| 14:27 | 18:37 | Aminbazar-Manikgonj PP 132kV Ckt-2 Project Work S/D from Aminbazar 400/230/132kV end Due | [7 empty] | 120.0MW load
|  |  | to Aminbazar-Kaliakoir 400kv conductor repair work. | [7 empty] | interrup. Aminbazar
400/230/132kV end
| 14:39 |  | Bibiana 400/230kV S/S Summit GTG Scheduled S/D Due to AM
| 14:53 | 17:24 | Coxsbazar 132/33kV S/S T3 HT Tripped showing differential(87T) I-Differential Pickup. | [7 empty] | 58.0MW load
|  |  | relays Due to T-3 Tripped due 33 kV over current Auxiliary Station Transformar Dropout | [7 empty] | interrup.
fuse flashing.
| 15:40 | 17:24 | Gollamari 132/33kV S/S E01 Gollamari-Gopalgonj Line - 1 Forced S/D Due to Ordered by ALDC
khulna.
| 15:41 | 17:24 | Gopalganj 132/33kV S/S Gallamari-1 Scheduled S/D Due to CT Oil Leakage Maintenance
(R-Phase)
| 20:15 | 20:56 | Mahasthangarh 132/33kV S/S 416T MTR 2 LT Forced S/D Due to Due to source blade | [7 empty] | 40.0MW load
|  |  | maintenance of 33 kV Pirob feeder. | [7 empty] | interrup.
| 21:00 |  | Evening peak Generation is 16078 MW
| 06:52 |  | Mahasthangar-Palashbari 132kV Ckt-1 Scheduled S/D from Palashbari 132/33kV end Due to
project work and from Mahasthangarh 132/33kVend.
| 07:00 |  | Minimum Generation: 13971 MW
| 07:00 |  | Baroaulia 132/33kV S/S T-1(405T) HT Scheduled S/D Due to Mainbus DS B phase redhot | [7 empty] | 10.0MW load
|  |  | maintanance | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 22-07-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10248500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 300 | 7226182 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 950255 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 194 | 4515000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 325 | 7804112 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 82 | 553392 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 48.6 | 1112760 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 141 | 2384160 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 1049127 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 1294953 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20 | 406200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 487080 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 33 | 688800 | Engine Problem
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 276 | 5258553 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 126 | 2842560 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2064960 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 295680 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 142 | 2882880 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 155876 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 452880 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 505 | 11244970 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 125 | 2978400 | Engine Problem
Dhaka Area Total |  |  |  |  | 5939.724 | 3092.6 | 66897280
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 375498 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 107055 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1056000 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5112431 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 216 | 5205410 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 47 | 491782 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 59 | 1259760 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 1122839 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 36 | 468480 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 13 | 332160 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 102 | 1147200 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 28320 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 130473 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 32 | 250073 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 610560 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 46418 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 160 | 2412072 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1140 | 27283634 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 62880 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 761 | 17621818.18 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.72 | 2936.5 | 65124863.18
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 211 | 4847000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 343 | 8494500 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 340 | 8172000 | machine problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 35 | 757008 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 48 | 1134720 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 163 | 1338182 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1096909 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 143 | 3208290 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 30 | 868064 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 155 | 1859520 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 30 | 636480 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 1193184 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 385480 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 95 | 2267460 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 65 | 664440 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 73 | 1793280 | FGMO
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 477773 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1853.2 | 39194290
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 47 | 1123200 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7850 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 135 | 3384000 | Engine Problem
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 102 | 2406000 | Engine Problem
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 195310 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 11 | 272880 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 427320 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 312 | 7816560
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1390080 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 153 | 3517118 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 719808 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1980480 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 416000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 125112 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Plant Shutdown as per schedule HGPI work
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 361 | 8984000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7647900 | machine problem
Sylhet Area Total |  |  |  |  | 2325 | 1030 | 24780498
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 856 | 20727273 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 161 | 4280832 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 45 | 365280 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 455760 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1116 | 21963640 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2216 | 48704785
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 302 | 7258182 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 118 | 2713000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 691 | 16603636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5251930 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 220 | 4362000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3568.5 | -
Barishal Area Total |  |  |  |  | 2236 | 1551 | 36192316.86
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 47 | 435102 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 299403 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 166 | 4476636 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 188 | 4512564 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 184 | 4664091 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 405 | 8911454 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 282036 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 396638 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 933248 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 882048 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 681600 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 17100 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1412.71 | 33403127 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 234000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 506720 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2841.91 | 60635767
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 46 | 1083927 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 18000 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 2689756 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 35532.24 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 94 | 2308996 | Engine Problem
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 157839 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 998640 | -
Rangpur Area Total |  |  |  |  | 950 | 247 | 7292690.24
Eastern Grid Total |  |  |  |  | 16667.715 | 9224.3 | 203813491.18
Western Grid Total |  |  |  |  | 10378.16 | 6855.91 | 152825559.1
National Grid Total |  |  |  |  | 27045.875 | 16080.21 | 356639050.28
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 22-07-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10455.45 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5043.8 | MW
i) Dhaka area |  |  | 5586.45 |  | MW | i) Khulna area |  |  |  | 1923.8 | MW
ii) Chattogram area |  |  | 1555 |  | MW | ii) Barishal area |  |  |  | 488 | MW
iii) Cumilla area |  |  | 1460 |  | MW | iii) Rajshahi area |  |  |  | 1686 | MW
iv) Mymensingh area |  |  | 1223 |  | MW | iv) Rangpur area |  |  |  | 946 | MW
v) Sylhet area |  |  | 631 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15499.25 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 91 | 19:00 | 133 | PHP | 9 | 07:00
2 | AKSML | 146.6 | 06:00 | 68 | Ishurdi | 91 | 20:00 | 134 | Pabna | 141 | 21:00
3 | Aftabnagar | 42 | 00:00 | 69 | Jaldhaka | 78 | 18:00 | 135 | Palashbari | 123 | 23:00
4 | Agargaon | 149 | 13:00 | 70 | Jamalpur | 142 | 00:00 | 136 | Panchagarh | 54 | 18:00
5 | Agrabad | 102 | 19:00 | 71 | Jashore | 146 | 00:00 | 137 | Patuakhali | 76 | 21:00
6 | Amnura | 42 | 00:00 | 72 | Jhenaidah | 140 | 19:30 | 138 | Payra | 38 | 00:00
7 | Ashuganj | 100 | 23:00 | 73 | Joydebpur | 145 | 16:00 | 139 | Postogola | 63 | 19:00
8 | BSRM | 202 | 19:30 | 74 | Joypurhat | 73 | 21:00 | 140 | Purbachal | 24 | 22:00
9 | Bagerhat | 89 | 23:00 | 75 | Juldah | 16.5 | 15:00 | 141 | Purbasadipur | 137 | 13:00
10 | Bajitpur | 87 | 22:00 | 76 | KSRM | 22 | 04:00 | 142 | Rahanpur | 33 | 21:00
11 | Bakulia | 99 | 20:00 | 77 | Kabirpur | 258 | 09:00 | 143 | Rahim | 30 | 09:00
12 | Banani | 40.8 | 13:00 | 78 | Kachua | 98 | 22:00 | 144 | Rajbari | 91 | 19:30
13 | Bangabhaban | 18 | 10:00 | 79 | Kallyanpur | 117 | 19:30 | 145 | Rajendrapur | 139 | 19:00
14 | Barapukuria | 71 | 21:00 | 80 | Kalurghat | 42 | 12:00 | 146 | Rajshahi | 139 | 21:00
15 | Barguna | 24 | 00:00 | 81 | Kamrangirchar | 79 | 12:00 | 147 | Rajshahi-230 | 84 | 00:00
16 | Barishal | 120 | 12:00 | 82 | Kaptai | N/A | N/A | 148 | Ramganj | 112 | 19:00
17 | Barishal-230 | 118 | 21:00 | 83 | Kasba | 38 | 20:00 | 149 | Rampur | 45 | 23:00
18 | Baroaulia | 73 | 09:00 | 84 | Kazla | 103 | 13:00 | 150 | Rangamati | 18 | 19:00
19 | Baroirhat | 68 | 23:00 | 85 | Keranigonj | 82 | 18:00 | 151 | Rangpur | 154 | 13:00
20 | Bashundhara | 210 | 12:00 | 86 | Khagrachori | 36 | 19:00 | 152 | Ruppur | 7.4 | 16:00
21 | BashundharaCement | 14 | 01:00 | 87 | Khulna | 84 | 21:00 | 153 | SSM | 2 | 07:00
22 | Beanibazar | 73 | 19:30 | 88 | Khulshi | 189 | 19:30 | 154 | Saidpur | 114 | 08:00
23 | Benapole | 82 | 22:00 | 89 | Kishoreganj | 153 | 23:00 | 155 | Satkhira | 145 | 22:00
24 | Bhaluka | 167 | 19:00 | 90 | Kodda | 316 | 15:00 | 156 | Satmasjid | 119 | 00:00
25 | Bhandaria | 59 | 23:00 | 91 | Kulaura | 53 | 19:00 | 157 | Savar | 235 | 10:00
26 | Bhangura | 42 | 21:00 | 92 | Kurigram | 58 | 13:00 | 158 | SevenRings | 22.14 | 15:00
27 | Bheramara(GK) | 75 | 21:00 | 93 | Kushtia | 174 | 20:00 | 159 | ShahCement | 36 | 22:00
28 | Bhulta | 245 | 00:00 | 94 | Laksam | 38 | 22:00 | 160 | Shahjadpur | 101 | 21:00
29 | Bog-Sherpur | 72 | 20:00 | 95 | Lakshmipur | 33 | 19:00 | 161 | Shahjibazar | 134 | 02:00
30 | Bogura | 179 | 23:00 | 96 | Lalbag | 57 | 17:00 | 162 | Shahmirpur | 64 | 00:00
31 | Borhanuddin | 94 | 19:00 | 97 | Lalmonirhat | 56 | 22:00 | 163 | Shariatpur | 97 | 00:00
32 | Brahmanbaria | 144 | 23:00 | 98 | MI_Cement | 16.1 | 04:00 | 164 | Sherpur | 162 | 23:00
33 | Cantonment | 168 | 13:00 | 99 | Madanganj | 40 | 11:00 | 165 | Shikalbaha | 18 | 12:00
34 | Chandina | 16.4 | 20:00 | 100 | Madaripur | 123 | 00:00 | 166 | Shitalakhya | 88.6 | 12:00
35 | Chandpur | 84 | 22:00 | 101 | Madartek | 101.46 | 23:00 | 167 | Sholosohor | 46 | 19:00
36 | Chandraghona | 38 | 19:30 | 102 | Madunaghat | 58 | 15:00 | 168 | Shyampur | 154 | 13:00
37 | Chapai | 73 | 22:00 | 103 | Magura | 74 | 20:00 | 169 | Siddhirganj | 126 | 12:00
38 | Charsaidpur | 41 | 20:00 | 104 | Mahasthangarh | 104 | 00:00 | 170 | Sirajganj | 132 | 21:00
39 | Chauddagram | 79 | 23:00 | 105 | Maijdee | 15 | 19:00 | 171 | Sonargaon | 118 | 22:00
40 | Chhatak | 37 | 01:00 | 106 | Manikganj | 143 | 20:00 | 172 | Sreemongol | 82 | 18:30
41 | Chowmuhani | 170 | 21:00 | 107 | Maniknagar | 92 | 13:00 | 173 | Sreepur | 106 | 19:00
42 | Chuadanga | 129 | 21:00 | 108 | Matarbari | 55 | 00:00 | 174 | Srinagar | 50.8 | 19:00
43 | Coxsbazar | 125 | 00:00 | 109 | Matuail | 66 | 23:00 | 175 | Sunamganj | 54 | 03:00
44 | Cumilla(N) | 151 | 19:30 | 110 | Millgate | 135 | 15:00 | 176 | Sylhet | 58 | 02:00
45 | Cumilla(S) | 156 | 17:00 | 111 | Mirpur | 133 | 19:00 | 177 | Sylhet-132 | 145 | 20:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 11 | 12:00 | 178 | TK | 36 | 00:00
47 | Daudkandi | 155 | 19:00 | 113 | Mirzapur | 47 | 00:00 | 179 | Tangail | 191 | 19:30
48 | Dhaka | 82 | 13:00 | 114 | Mithapukur | 66 | 18:00 | 180 | Taraganj | 25 | 01:00
49 | Dhamrai | 132 | 18:30 | 115 | Modern | N/A | N/A | 181 | Thakurgaon | 107 | 03:00
50 | Dhanmondi | 141 | 13:00 | 116 | Mogbazar | 158.6 | 13:00 | 182 | Tongi | 137 | 10:00
51 | Dohazari | 110 | 21:00 | 117 | Mongla | 43 | 11:00 | 183 | Ullahpara | 43 | 22:00
52 | Faridpur | 183 | 19:30 | 118 | Motijheel | 48 | 13:00 | 184 | Ullon | 46 | 00:00
53 | Fatullah | 108 | 12:00 | 119 | Muktagacha | 41 | 22:00 | 185 | Uttara | 93 | 16:00
54 | Fenchuganj | 45 | 02:00 | 120 | Munshiganj | 124 | 00:00 | 186 | UttaraNew | 68 | 00:00
55 | Feni | 126 | 18:30 | 121 | Muradnagar | 46 | 21:00 | 187 | Zigatola | 76 | 00:00
56 | GPH | 87 | 00:00 | 122 | Mymensingh | 223 | 23:00
57 | Ghatail | 88 | 06:00 | 123 | Naogaon | 149 | 23:00
58 | Ghorashal | 14 | 04:00 | 124 | Narail | 67 | 19:30
59 | Ghorashal-230 | 91 | 00:00 | 125 | Narinda | 84 | 13:00
60 | Goalpara | 42 | 00:00 | 126 | Narshingdi | 185 | 01:00
61 | Gollamari | 94 | 00:00 | 127 | Natore | 163 | 22:00
62 | Gopalganj | 114 | 22:00 | 128 | Nawabganj | 63 | 19:00
63 | Gulshan | 140 | 12:00 | 129 | Netrakona | 145 | 01:00
64 | Halishahar | 78 | 15:00 | 130 | New | 61 | 15:00
65 | HaripurSBU | 160 | 01:00 | 131 | Niamatpur | 83 | 22:00
66 | Hasnabad | 93 | 00:00 | 132 | Noapara | 64 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 22-07-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15689.69 | 297 |  | 15999.69
1:00 | 15332.71 | 352 |  | 15700.71
2:00 | 15126.13 | 263 |  | 15401.13
3:00 | 14506.29 | 281 |  | 14800.29
4:00 | 14377.02 | 262 |  | 14651.02
5:00 | 14258.03 | 232 |  | 14500.03
6:00 | 13573.38 | 219 |  | 13802.24
7:00 | 13697.79 | 150 |  | 13854.54
8:00 | 13665.74 | 161 |  | 13833.99
9:00 | 13934.4 | 162 |  | 14103.4
10:00 | 14197.04 | 101 |  | 14303.04
11:00 | 14360.49 | 138 |  | 14504.49
12:00 | 14739.48 | 138 |  | 14883.48
13:00 | 14957.58 | 207 |  | 15173.9
14:00 | 14709.43 | 261 |  | 14982.18
15:00 | 14537.6 | 283 |  | 14833.34
16:00 | 14392.72 | 193 |  | 14594.41
17:00 | 14204.51 | 190 |  | 14403.06
18:00 | 13846.6 | 53 |  | 13901.99
19:00 | 15037.7 | 137 |  | 15180.7
19:30 | 15721.9 | 305 |  | 16040.9
20:00 | 15832 | 295 |  | 16140
21:00 | 16080.21 | 279 |  | 16372.21
22:00 | 16049.45 | 269 |  | 16330.56
23:00 | 15982.33 | 324 |  | 16321.33
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 22-07-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 9034.2 | 6655.49 | 15689.69 | DAILY GENERATION CURVE
00:30 | 8882.45 | 6628.75 | 15511.2
01:00 | 8730.7 | 6602.01 | 15332.71 | 22-07-2025
01:30 | 8674.2 | 6555.22 | 15229.42
02:00 | 8617.7 | 6508.43 | 15126.13
02:30 | 8398.95 | 6417.26 | 14816.21
03:00 | 8180.2 | 6326.09 | 14506.29
03:30 | 8164.2 | 6277.455 | 14441.655
04:00 | 8148.2 | 6228.82 | 14377.02
04:30 | 8110.7 | 6206.825 | 14317.525
05:00 | 8073.2 | 6184.83 | 14258.03
05:30 | 7887.175 | 6028.53 | 13915.705
06:00 | 7701.15 | 5872.23 | 13573.38
06:30 | 7710.625 | 5924.96 | 13635.585
07:00 | 7720.1 | 5977.69 | 13697.79
07:30 | 7700.365 | 5981.4 | 13681.765
08:00 | 7680.63 | 5985.11 | 13665.74
08:30 | 7782.14 | 6017.93 | 13800.07
09:00 | 7883.65 | 6050.75 | 13934.4
09:30 | 7997.16 | 6068.56 | 14065.72
10:00 | 8110.67 | 6086.37 | 14197.04
10:30 | 8185.7 | 6093.065 | 14278.765
11:00 | 8260.73 | 6099.76 | 14360.49
11:30 | 8355.865 | 6194.12 | 14549.985
12:00 | 8451 | 6288.48 | 14739.48
12:30 | 8521.62 | 6326.91 | 14848.53
13:00 | 8592.24 | 6365.34 | 14957.58
13:30 | 8548.85 | 6284.655 | 14833.505
14:00 | 8505.46 | 6203.97 | 14709.43
14:30 | 8443.355 | 6180.16 | 14623.515
15:00 | 8381.25 | 6156.35 | 14537.6
15:30 | 8426.77 | 6038.39 | 14465.16
16:00 | 8472.29 | 5920.43 | 14392.72
16:30 | 8446.965 | 5851.65 | 14298.615
17:00 | 8421.64 | 5782.87 | 14204.51
17:30 | 8250.995 | 5774.56 | 14025.555
18:00 | 8080.35 | 5766.25 | 13846.6
18:30 | 8495.025 | 5947.125 | 14442.15
19:00 | 8909.7 | 6128 | 15037.7
19:30 | 9175.7 | 6546.2 | 15721.9
20:00 | 9215.8 | 6616.2 | 15832
20:30 | 9220.05 | 6736.055 | 15956.105 |  | Executive Engineer
21:00 | 9224.3 | 6855.91 | 16080.21 |  | Network Operation Division
21:30 | 9218 | 6846.83 | 16064.83
22:00 | 9211.7 | 6837.75 | 16049.45
22:30 | 9153.2 | 6862.69 | 16015.89
23:00 | 9094.7 | 6887.63 | 15982.33

## En-Curve
QF-LDC-12
Date | 22-07-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3790 | 1933 | 855 | 38 | 30 | 1454.29 | 218 | 4101 | 0 | 774 | 2496.4 | 0 | 0 | 0 | 297 | DAILY ENERGY CURVE
00:30 | 3749.5 | 1921.5 | 855.5 | 38 | 29 | 1451.55 | 218 | 4044 | 0 | 770.5 | 2433.65 | 0 | 0 | 0 | 324.5 | 22-07-2025
01:00 | 3709 | 1910 | 856 | 38 | 28 | 1448.81 | 218 | 3987 | 0 | 767 | 2370.9 | 0 | 0 | 0 | 352
01:30 | 3737 | 1889 | 856 | 38 | 28 | 1446.02 | 219 | 3966.5 | 0 | 767 | 2281.4 | 0 | 0 | 1.5 | 307.5 | Energy Generated | 356.6391 |  | MKWHr
02:00 | 3765 | 1868 | 856 | 38 | 28 | 1443.23 | 220 | 3946 | 0 | 767 | 2191.9 | 0 | 0 | 3 | 263 | Energy not Served | 5.247 |  | MKWHr
02:30 | 3766 | 1874 | 855.5 | 38 | 27 | 1442.66 | 220 | 3926.5 | 0 | 708 | 1957.05 | 0 | 0 | 1.5 | 272 | Total Energy Requirement | 361.8861 |  | MKWHr
03:00 | 3767 | 1880 | 855 | 38 | 26 | 1442.09 | 220 | 3907 | 0 | 649 | 1722.2 | 0 | 0 | 0 | 281
03:30 | 3766 | 1883.5 | 855.5 | 38 | 26 | 1445.455 | 220 | 3920.5 | 0 | 593 | 1693.7 | 0 | 0 | 0 | 271.5
04:00 | 3765 | 1887 | 856 | 38 | 26 | 1448.82 | 220 | 3934 | 0 | 537 | 1665.2 | 0 | 0 | 0 | 262
04:30 | 3735 | 1880.5 | 856 | 38 | 26 | 1455.825 | 220 | 3917.5 | 0 | 532.5 | 1656.2 | 0 | 0 | 0 | 247
05:00 | 3705 | 1874 | 856 | 38 | 26 | 1462.83 | 220 | 3901 | 0 | 528 | 1647.2 | 0 | 0 | 0 | 232
05:30 | 3649 | 1868.5 | 856 | 38 | 25 | 1381.735 | 220 | 3890.5 | 7.27 | 464 | 1515.7 | 0 | 0 | 0 | 225.5
06:00 | 3593 | 1863 | 856 | 38 | 24 | 1300.64 | 220 | 3880 | 14.54 | 400 | 1384.2 | 0 | 0 | 0 | 219
06:30 | 3611 | 1868.5 | 856 | 38 | 24 | 1307.58 | 220 | 3920 | 44.805 | 400 | 1345.7 | 0 | 0 | 0 | 184.5
07:00 | 3629 | 1874 | 856 | 38 | 24 | 1314.52 | 220 | 3960 | 75.07 | 400 | 1307.2 | 0 | 0 | 0 | 150
07:30 | 3626.5 | 1860 | 856 | 38 | 24 | 1320.67 | 220 | 3933 | 105.695 | 400.5 | 1297.4 | 0 | 0 | 0 | 155.5
08:00 | 3624 | 1846 | 856 | 38 | 24 | 1326.82 | 220 | 3906 | 136.32 | 401 | 1287.6 | 0 | 0 | 0 | 161
08:30 | 3668.5 | 1839.9 | 856 | 38 | 24 | 1318.845 | 220.5 | 3907.5 | 184.925 | 400 | 1341.9 | 0 | 0 | 0 | 161.5
09:00 | 3713 | 1833.8 | 856 | 38 | 24 | 1310.87 | 221 | 3909 | 233.53 | 399 | 1396.2 | 0 | 0 | 0 | 162
09:30 | 3713 | 1836.65 | 856 | 38 | 23 | 1308.425 | 220.5 | 3880 | 277.545 | 406.5 | 1506.1 | 0 | 0 | 0 | 131.5
10:00 | 3713 | 1839.5 | 856 | 38 | 22 | 1305.98 | 220 | 3851 | 321.56 | 414 | 1616 | 0 | 0 | 0 | 101
10:30 | 3677 | 1875.5 | 856 | 38 | 23 | 1279.335 | 219.5 | 3903.5 | 317.43 | 426 | 1663.5 | 0 | 0 | 0 | 119.5
11:00 | 3641 | 1911.5 | 856 | 38 | 24 | 1252.69 | 219 | 3956 | 313.3 | 438 | 1711 | 0 | 0 | 0 | 138
11:30 | 3635.5 | 1878.5 | 855.5 | 38 | 25 | 1303.68 | 218 | 3970 | 380.805 | 443 | 1796.5 | 0 | 0 | 5.5 | 138
12:00 | 3630 | 1845.5 | 855 | 38 | 26 | 1354.67 | 217 | 3984 | 448.31 | 448 | 1882 | 0 | 0 | 11 | 138
12:30 | 3624.5 | 1822 | 855 | 38 | 27 | 1381.835 | 217 | 3946.5 | 515.345 | 449.5 | 1959.35 | 0 | 0 | 12.5 | 172.5
13:00 | 3619 | 1798.5 | 855 | 38 | 28 | 1409 | 217 | 3909 | 582.38 | 451 | 2036.7 | 0 | 0 | 14 | 207
13:30 | 3603.5 | 1786.75 | 855.5 | 38 | 28 | 1416.5 | 217.5 | 3893 | 519.155 | 470.5 | 1988.1 | 0 | 0 | 17 | 234
14:00 | 3588 | 1775 | 856 | 38 | 28 | 1424 | 218 | 3877 | 455.93 | 490 | 1939.5 | 0 | 0 | 20 | 261
14:30 | 3569.5 | 1776.5 | 855.5 | 38 | 28 | 1416.5 | 218 | 3897.5 | 417.015 | 493 | 1900.5 | 0 | 0 | 13.5 | 272
15:00 | 3551 | 1778 | 855 | 38 | 28 | 1409 | 218 | 3918 | 378.1 | 496 | 1861.5 | 0 | 0 | 7 | 283
15:30 | 3563.5 | 1791 | 855.5 | 38 | 28 | 1415 | 218.5 | 3886.5 | 292.56 | 488 | 1882.1 | 0 | 0 | 6.5 | 238
16:00 | 3576 | 1804 | 856 | 38 | 28 | 1421 | 219 | 3855 | 207.02 | 480 | 1902.7 | 0 | 0 | 6 | 193
16:30 | 3552.5 | 1797 | 855.5 | 38 | 27 | 1415.5 | 219.5 | 3831.5 | 168.915 | 485 | 1902.2 | 0 | 0 | 6 | 191.5
17:00 | 3529 | 1790 | 855 | 38 | 26 | 1410 | 220 | 3808 | 130.81 | 490 | 1901.7 | 0 | 0 | 6 | 190
17:30 | 3453 | 1783.5 | 855 | 38 | 26 | 1383 | 220 | 3733.5 | 83.605 | 505 | 1941.45 | 0 | 0 | 3.5 | 121.5
18:00 | 3377 | 1777 | 855 | 38 | 26 | 1356 | 220 | 3659 | 36.4 | 520 | 1981.2 | 0 | 0 | 1 | 53
18:30 | 3527 | 1852.5 | 855 | 38 | 28 | 1350 | 220 | 3782 | 18.2 | 591 | 2179.95 | 0 | 0 | 0.5 | 95
19:00 | 3677 | 1928 | 855 | 38 | 30 | 1344 | 220 | 3905 | 0 | 662 | 2378.7 | 0 | 0 | 0 | 137
19:30 | 3686 | 2042 | 856 | 38 | 28 | 1324 | 220 | 4173 | 0 | 685 | 2669.9 | 0 | 0 | 0 | 305
20:00 | 3657 | 2037 | 856 | 38 | 28 | 1316 | 220 | 4197 | 0 | 740 | 2743 | 0 | 0 | 0 | 295
20:30 | 3688.5 | 2045.5 | 856 | 38 | 29 | 1364.355 | 220 | 4236.5 | 0 | 745.5 | 2732.75 | 0 | 0 | 0 | 287
21:00 | 3720 | 2054 | 856 | 38 | 30 | 1412.71 | 220 | 4276 | 0 | 751 | 2722.5 | 0 | 0 | 0 | 279
21:30 | 3726 | 2048 | 856 | 38 | 30 | 1413.63 | 220 | 4258.5 | 0 | 754 | 2720.7 | 0 | 0 | 0 | 274
22:00 | 3732 | 2042 | 856 | 38 | 30 | 1414.55 | 220 | 4241 | 0 | 757 | 2718.9 | 0 | 0 | 0 | 269
22:30 | 3726.5 | 2002 | 856 | 38 | 30 | 1426.99 | 220 | 4234 | 0 | 750 | 2724.4 | 8 | 0 | 0 | 296.5
23:00 | 3721 | 1962 | 856 | 38 | 30 | 1439.43 | 220 | 4227 | 0 | 743 | 2729.9 | 16 | 0 | 0 | 324
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 22-07-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 386 | 05:00 | 380 | 12:00 | Payra | 416 | 06:00 | 414 | 00:00
Ashuganj | 400 | 5:00 | 373 | 12:00 | Rahanpur | 401 | 19:00 | 391 | 03:00
Bhulta | 396 | 05:00 | 372 | 12:00 | Rampal | 406 | 17:00 | 397 | 00:00
Bibiana | 380 | 00:00 | 374 | 16:00
BIPTC | 403 | 06:00 | 392 | 20:00
Bogura | 386 | 19:30 | 372 | 05:00
Gopalganj | 400 | 18:30 | 393 | 00:00
Kaliakoir | 368 | 22:00 | 353 | 09:00
Madunaghat | 392 | 02:00 | 387 | 10:00
Meghnaghat | 386 | 05:00 | 379 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 224 | 04:00 | 217 | 12:00 | Keranigonj | 222 | 05:00 | 215 | 12:00
AKSML | 232 | 17:00 | 224 | 04:00 | Khulna(S) | 232 | 18:30 | 220 | 00:00
Aminbazar | 224 | 01:00 | 218 | 12:00 | Madunaghat | 233 | 17:00 | 228 | 04:00
Ashuganj | 228 | 02:00 | 221 | 13:00 | Madunaghat-400 | 232 | 00:00 | 227 | 11:00
Ashuganj-400 | 228 | 02:00 | 221 | 13:00 | Maniknagar | 217 | 05:00 | 212 | 12:00
Baghabari | 233 | 18:30 | 227 | 13:00 | Meghnaghat | 225 | 04:00 | 220 | 12:00
Barapukuria | 217 | 00:00 | 207 | 22:00 | Meghnaghat-400 | 223 | 05:00 | 218 | 12:00
Barapukuria-230 | 217 | 00:00 | 207 | 22:00 | Mirsorai | 232 | 22:00 | 220 | 04:00
Barishal | 227 | 18:00 | 220 | 00:00 | Rajshahi | 232 | 18:30 | 223 | 13:00
Bheramara | 232 | 18:00 | 226 | 00:00 | Rampal | 232 | 18:00 | 222 | 00:00
Bhulta | 228 | 05:00 | 212 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 223 | 07:00 | 218 | 16:00 | Rampura | 226 | 05:00 | 209 | 12:00
BIPTC | 234 | 18:30 | 226 | 00:00 | Shikalbaha | 230 | 17:00 | 224 | 10:00
Bogura | 232 | 19:30 | 224 | 13:00 | Shyampur | 221 | 06:00 | 215 | 12:00
Bogura-400 | 234 | 19:30 | 225 | 13:00 | Siddhirganj | 219 | 05:00 | 215 | 11:00
Borhanuddin | 232 | 17:00 | 226 | 00:00 | Sirajgonj | 237 | 18:00 | 234 | 21:00
BSRM | 228 | 01:00 | 220 | 09:00 | Sreepur | 225 | 20:00 | 220 | 19:00
Cumilla(N) | 220 | 18:00 | 215 | 12:00 | Tongi | 221 | 04:00 | 212 | 11:00
Faridpur | 224 | 18:00 | 216 | 23:00
Fenchuganj | 223 | 07:00 | 218 | 01:00
Ghorashal | 225 | 00:00 | 220 | 08:00
Ghorashal-230 | 224 | 02:00 | 214 | 17:00
Gopalganj | 224 | 18:00 | 218 | 00:00
GPH | 230 | 01:00 | 224 | 04:00
Haripur | 218 | 02:00 | 214 | 12:00
Hasnabad | 222 | 05:00 | 215 | 12:00
Hathazari | 228 | 13:00 | 222 | 08:00
Ishurdi | 234 | 18:00 | 229 | 00:00
Jhenaidah | 231 | 18:30 | 216 | 00:00
Kaliakoir | 226 | 02:00 | 218 | 09:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 01:00 | 125 | 12:00 | Lalmonirhat | 128 | 00:00 | 118 | 12:00
Agargaon | 131 | 04:00 | 125 | 12:00 | Madanganj | 128 | 18:00 | 124 | 03:00
Agrabad | 132 | 17:00 | 127 | 09:00 | Madaripur | 135 | 18:00 | 130 | 00:00
AKS | 129 | 18:00 | 125 | 10:00 | Madartek | 136 | 02:00 | 125 | 12:00
Aminbazar | 133 | 01:00 | 128 | 12:00 | Madunaghat | 132 | 18:00 | 129 | 04:00
Amnura | 137 | 18:30 | 128 | 13:00 | Magura | 135 | 18:00 | 124 | 01:00
Ashuganj | 138 | 01:00 | 135 | 13:00 | Mahasthangarh | 134 | 19:30 | 128 | 12:00
Bagerhat | 133 | 18:00 | 120 | 00:00 | Maijdee | 116 | 18:30 | 106 | 04:00
Bajitpur | 128 | 09:00 | 123 | 21:00 | Manikganj | 124 | 07:00 | 116 | 09:00
Bakulia | 134 | 19:00 | 127 | 11:00 | Maniknagar | 130 | 04:00 | 124 | 12:00
Banani | 135 | 02:00 | 123 | 13:00 | Matarbari | 126 | 17:00 | 111 | 00:00
Bangabhaban | 129 | 02:00 | 124 | 12:00 | Matuail | 127.5 | 05:00 | 124 | 12:00
Barapukuria | 133 | 00:00 | 124 | 22:00 | Millgate | 129 | 01:00 | 122 | 09:00
Barguna | 135 | 18:00 | 130 | 00:00 | Mirpur | 133 | 05:00 | 124 | 14:00
Barishal | 133 | 18:00 | 127 | 00:00 | Mirzapur | 126 | 00:00 | 121 | 19:30
Barishal-230 | 134 | 18:00 | 128 | 00:00 | Mithapukur | 131 | 03:00 | 124 | 12:00
Baroaulia | 132 | 01:00 | 127 | 10:00 | MI_Cement | 129 | 20:00 | 125 | 12:00
Baroirhat | 122 | 17:00 | 115 | 04:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 136 | 04:00 | 122 | 09:00 | Mogbazar | 138 | 05:00 | 125 | 12:00
BashundharaCement | 128 | 18:00 | 124 | 03:00 | Mongla | 132 | 18:00 | 121 | 00:00
Beanibazar | 123 | 05:00 | 116 | 13:00 | Motijheel | 129 | 02:00 | 124 | 12:00
Benapole | 132 | 18:00 | 119 | 23:00 | Muktagacha | 133 | 10:00 | 121 | 21:00
Bhaluka | 128 | 04:00 | 123 | 19:00 | Munshiganj | 128 | 07:00 | 124 | 12:00
Bhandaria | 129 | 18:30 | 118 | 00:00 | Muradnagar | 123 | 18:00 | 118 | 12:00
Bhangura | 132 | 03:00 | 128 | 13:00 | Mymensingh | 135 | 10:00 | 115 | 21:00
Bheramara | 135 | 05:00 | 133 | 00:00 | Naogaon | 130 | 19:30 | 124 | 13:00
Bheramara(GK) | 135 | 09:00 | 133 | 00:00 | Narail | 135 | 18:30 | 123 | 00:00
Bhulta | 121 | 02:00 | 118 | 11:00 | Narinda | 130 | 04:00 | 124 | 12:00
Bog-Sherpur | 135 | 17:00 | 130 | 11:00 | Narshingdi | 136 | 04:00 | 118 | 12:00
Bogura | 137 | 06:00 | 131 | 13:00 | Natore | 134 | 18:30 | 129 | 13:00
Bogura-230 | 137 | 19:00 | 131 | 13:00 | Nawabganj | 132 | 05:00 | 127 | 12:00
Brahmanbaria | 133 | 07:00 | 128 | 16:00 | Netrakona | 122 | 10:00 | 114 | 21:00
Cantonment | 131 | 05:00 | 124 | 12:00 | New | 129 | 01:00 | 123 | 09:00
Chandina | 126 | 18:30 | 120 | 12:00 | Niamatpur | 136 | 18:30 | 132 | 00:00
Chandpur | 124 | 18:30 | 111 | 12:00 | Noapara | 135 | 18:30 | 124 | 23:00
Chandraghona | 132 | 14:00 | 129 | 11:00 | Pabna | 132 | 06:00 | 128 | 21:00
Chapai | 135 | 18:30 | 131 | 00:00 | Palashbari | 129 | 07:00 | 121 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 128 | 02:00 | 125 | 12:00 | Panchagarh | 135 | 00:00 | 121 | 13:00
Chauddagram | 122 | 18:00 | 115 | 04:00 | Patuakhali | 135 | 10:00 | 131 | 05:00
Chhatak | 125 | 05:00 | 112 | 13:00 | Payra | 137 | 06:00 | 135 | 00:00
Chowmuhani | 115 | 18:30 | 105 | 04:00 | PHP | 122 | 18:30 | 115 | 02:00
Chuadanga | 133 | 18:30 | 119 | 00:00 | Postogola | 130 | 02:00 | 127 | 10:00
Coxsbazar | 127 | 16:00 | 112 | 00:00 | Purbachal | 137 | 04:00 | 122 | 09:00
Cumilla(N) | 125 | 18:00 | 120 | 12:00 | Purbasadipur | 132 | 05:00 | 118 | 13:00
Cumilla(S) | 134 | 04:00 | 119 | 12:00 | Rahanpur | 137 | 17:00 | 132 | 21:00
Daganbhuiyan | 118 | 18:00 | 110 | 02:00 | Rahanpur-400 | 138 | 19:00 | 134 | 00:00
Daudkandi | 122 | 18:00 | 117 | 12:00 | Rahim | 127 | 02:00 | 124 | 12:00
Dhaka | 136 | 03:00 | 124 | 12:00 | Rajbari | 131 | 06:00 | 124 | 22:00
Dhamrai | 128 | 01:00 | 122 | 09:00 | Rajendrapur | 134 | 03:00 | 122 | 19:00
Dhanmondi | 137.4 | 05:00 | 124 | 12:00 | Rajshahi | 133 | 18:00 | 128 | 13:00
Dohazari | 132 | 17:00 | 123 | 09:00 | Rajshahi-230 | 134 | 18:30 | 128 | 13:00
Faridpur | 133 | 18:00 | 128 | 00:00 | Ramganj | 119 | 18:30 | 108 | 12:00
Fatullah | 129 | 02:00 | 125 | 12:00 | Rampur | 130 | 00:00 | 126 | 09:00
Fenchuganj | 131 | 06:00 | 127 | 13:00 | Rampura | 137 | 05:00 | 124 | 12:00
Feni | 122 | 18:00 | 118 | 01:00 | Rangamati | 131 | 17:00 | 128 | 09:00
Ghatail | 129 | 10:00 | 117 | 19:30 | Rangpur | 129 | 03:00 | 119 | 22:00
Ghorashal | 134 | 20:00 | 129 | 10:00 | Ruppur | 135 | 05:00 | 133 | 00:00
Goalpara | 138 | 18:00 | 127 | 00:00 | Saidpur | 131 | 03:00 | 120 | 13:00
Gollamari | 138 | 18:00 | 129 | 00:00 | Satkhira | 134 | 18:00 | 120 | 00:00
Gopalganj | 135 | 17:00 | 128 | 00:00 | Satmasjid | 130 | 02:00 | 124 | 13:00
Gopalganj-400 | 137 | 18:30 | 133 | 00:00 | Savar | 134 | 04:00 | 123 | 14:00
Gulshan | 135 | 04:00 | 124 | 12:00 | SevenRings | 136 | 05:00 | 129 | 09:00
Halishahar | 133 | 23:00 | 126 | 10:00 | ShahCement | 128 | 02:00 | 125 | 12:00
Haripur | 128 | 06:00 | 124 | 12:00 | Shahjadpur | 136 | 19:00 | 133 | 12:00
HaripurSBU | 127 | 00:00 | 124 | 12:00 | Shahjibazar | 131 | 06:00 | 127 | 00:00
Hasnabad | 131 | 04:00 | 127 | 09:00 | Shahmirpur | 133 | 16:00 | 128 | 09:00
Hathazari | 134 | 23:00 | 129 | 07:00 | Shariatpur | 135 | 18:00 | 128 | 00:00
Ishurdi | 137 | 18:30 | 133 | 21:00 | Sherpur | 136 | 10:00 | 120 | 19:30
Jaldhaka | 127 | 00:00 | 116 | 22:00 | Shikalbaha | 124 | 17:00 | 117 | 10:00
Jamalpur | 139 | 10:00 | 124 | 19:30 | Shikalbaha-230 | 134 | 17:00 | 129 | 09:00
Jashore | 133 | 18:00 | 119 | 00:00 | Shitalakhya | 129 | 20:00 | 125 | 12:00
Jhenaidah | 136 | 18:00 | 122 | 19:30 | Sholosohor | 131 | 01:00 | 128 | 09:00
Jhenaidah-230 | 137 | 18:30 | 124 | 00:00 | Shyampur | 130 | 17:00 | 126 | 09:00
Joydebpur | 133 | 00:00 | 124 | 09:00 | Shyampur-230 | 129 | 02:00 | 125 | 12:00
Joypurhat | 128 | 19:30 | 121 | 13:00 | Siddhirganj | 128 | 02:00 | 124 | 12:00
Juldah | 133 | 17:00 | 128 | 09:00 | Sirajganj | 131 | 18:30 | 126 | 13:00
Kabirpur | 130 | 02:00 | 117 | 09:00 | Sonargaon | 126 | 18:30 | 122 | 00:00
Kachua | 122 | 18:00 | 112 | 02:00 | Sreemongol | 129 | 06:00 | 125 | 03:00
Kaliakoir | 132 | 00:00 | 125 | 08:00 | Sreepur | 130 | 17:00 | 127 | 01:00
Kallyanpur | 135 | 06:00 | 128 | 12:00 | Srinagar | 133 | 07:00 | 128 | 11:00
Kalurghat | 132 | 17:00 | 129 | 03:00 | SSM | 133 | 13:00 | 130 | 08:00
Kamrangirchar | 133 | 05:00 | 127 | 12:00 | Sunamganj | 121 | 06:00 | 111 | 14:00
Kaptai | 135 | 23:00 | 132 | 12:00 | Sylhet | 125 | 06:00 | 117 | 14:00
Kasba | 123 | 18:30 | 117 | 12:00 | Sylhet-132 | 125 | 07:00 | 118 | 15:00
Kazla | 129 | 04:00 | 124 | 12:00 | Tangail | 126 | 11:00 | 117 | 19:30
Keranigonj | 133 | 05:00 | 128 | 12:00 | Taraganj | 156 | 04:00 | 119 | 22:00
Khagrachori | 130 | 18:00 | 127 | 10:00 | Thakurgaon | 132 | 00:00 | 118 | 13:00
Khulna | 136 | 18:00 | 126 | 00:00 | TK | 131 | 01:00 | 128 | 10:00
Khulna(S) | 138 | 18:00 | 129 | 00:00 | Tongi | 130 | 04:00 | 124 | 09:00
Khulshi | 130 | 00:00 | 125 | 10:00 | Ullahpara | 133 | 19:00 | 129 | 12:00
Kishoreganj | 127 | 05:00 | 121 | 21:00 | Ullon | 136 | 04:00 | 124 | 12:00
Kodda | 133 | 03:00 | 122 | 08:00 | Uttara | 132 | 02:00 | 126 | 12:00
KSRM | 132 | 19:30 | 127 | 10:00 | UttaraNew | 133 | 05:00 | 126 | 11:00
Kulaura | 130 | 05:00 | 125 | 13:00 | Zigatola | 133 | 05:00 | 128 | 12:00
Kurigram | 128 | 00:00 | 117 | 22:00
Kushtia | 131 | 10:00 | 126 | 21:00
Laksam | 121 | 18:30 | 112 | 03:00
Lakshmipur | 118 | 09:00 | 107 | 12:00
Lalbag | 132 | 04:00 | 127 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division