## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 25-07-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-07-2025 | during | 25-07-2025 | during | 25-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 0 | 0 | 0 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 304 | 299 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 192 | 192 | 208.13 | 208.13 | 196 | 196 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 311 | 305 | 335 | 335 | 328 | 328 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 7 | 7 | 48 | 7 | 48 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 48 | 46 | 53.97 | 53.97 | 48 | 48 | FGMO
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 125 | 149.36 | 149.36 | 138 | 138 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 17 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 25 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 34 | 25 | 52.19 | 52.19 | 16 | 33 | Fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 45 | 145 | 300 | 300 | 277 | 277 | Engine Problem
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 83 | 110 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 25 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 16 | 104 | 104 | 16 | 16 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 158 | 145 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 23 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 23 | 35 | 55 | 55 | 35 | 35 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 604 | 500 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 108 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2436 | 2762 | 4720.65 | 4733.65 | 3159.5 | 3189.5
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 16 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 11 | 0 | 15 | 0 | 15 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 38 | 39 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 220 | 220 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 212 | 217 | 213 | 213 | 213 | 213 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 46 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 46 | 75 | 48 | 72 | 48 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 16 | 65 | 50 | 50 | 50 | 50 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 35 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 17 | 2 | 25 | 33 | 33 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 10 | 80 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3 | 0 | 4.37 | 0 | 4.37 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 42 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 53 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 935 | 958 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 61 | 45 | 54 | 45 | 54 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 780 | 772 | 790 | 790 | 790 | 790 | Machine Problem
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 2326 | 2745.5 | 3830.09 | 3866.72 | 3831.09 | 3844.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 195 | 188 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 344 | 340 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 340 | 340 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 39 | 35 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 40 | 43 | 55 | 55 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 35 | 45 | 195 | 195 | 180 | 180 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 63 | 137 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 179 | 169 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 26 | 26 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 1 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 19 | 20.83 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 75 | 89 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 32 | 36 | 113 | 113 | 65 | 65 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 73 | 75 | 115 | 115 | 95 | 95 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 30 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1584 | 1668 | 2425.89 | 2379.56 | 2087.06 | 2037.06
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-07-2025 | during | 25-07-2025 | during | 25-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 48 | 47 | 157.5 | 157.5 | 48 | 48 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 123 | 194 | 200 | 200 | 160 | 160 | Engine Problem
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 75 | 91 | 115 | 115 | 100 | 100 | Engine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 33 | 0 | 39 | 0 | 39 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 10 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 35 | 35 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 307 | 361 | 590.1 | 549 | 396.1 | 355
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 58 | 60 | 60 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 150 | 150 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 81 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 16 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | Plant Shutdown as per schedule HGPI work
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 323 | 355 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 984 | 1018 | 1087 | 1087 | 1026 | 1026
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 852 | 856 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 173 | 150 | 410 | 410 | 169 | 169 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 51 | 105 | 105 | 60 | 60 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 71 | 0 | 52 | 0 | 52 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 901 | 1113 | 1234.2 | 1234.2 | 1204 | 1204 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2035 | 2208 | 3604.2 | 3552.2 | 3288 | 3236
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 301 | 301 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 117 | 117 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1105 | 1090 | 1244 | 1244 | 1194 | 1194 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 239 | 274 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1983 | 2002 | 2162 | 2161 | 2082 | 2081
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 178 | 202 | 214 | 214 | 200 | 200 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 192 | 169 | 220 | 220 | 188 | 188 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 191 | 171 | 220 | 220 | 187 | 187 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 410 | 387 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 104 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3 | 0 | 3.6 | 0 | 3.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 923 | 1431.69 | 1435.88 | 1435.88 | 1355 | 1355 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 33 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 45 | 0 | 85 | 0 | 85 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 1975 | 2694.69 | 3175.47 | 3025.87 | 2974.21 | 2824.61
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 49 | 46 | 48 | 48 | 48 | 48 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 87 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 8 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 114 | 114 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 206 | 0 | 182.57 | 0 | 182.57 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 494 | 273 | 529.17 | 310 | 529.17 | 310
System Total |  |  |  |  | 28565.2 | 27045.875 | 14124 | 15732.19 | 22124.57 | 21665 | 19373.13 | 18903.89
Forecast Scenario (25-07-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15410 |  | 0 |  | 15410
|  |  |  | 1:00 | 15200 |  | 0 |  | 15200
|  |  |  | 2:00 | 14700 |  | 0 |  | 14700
|  |  |  | 3:00 | 14150 |  | 0 |  | 14150
|  |  |  | 4:00 | 13750 |  | 0 |  | 13750
|  |  |  | 5:00 | 13700 |  | 0 |  | 13700
|  |  |  | 6:00 | 13150 |  | 0 |  | 13150
|  |  |  | 7:00 | 13160 |  | 0 |  | 13160
|  |  |  | 8:00 | 13250 |  | 0 |  | 13250
|  |  |  | 9:00 | 13550 |  | 0 |  | 13550
|  |  |  | 10:00 | 13600 |  | 0 |  | 13600
|  |  |  | 11:00 | 13820 |  | 0 |  | 13820
|  |  |  | 12:00 | 14150 |  | 0 |  | 14150
|  |  |  | 13:00 | 14460 |  | 0 |  | 14460
|  |  |  | 14:00 | 14300 |  | 0 |  | 14300
|  |  |  | 15:00 | 14600 |  | 0 |  | 14600
|  |  |  | 16:00 | 14400 |  | 0 |  | 14400
|  |  |  | 17:00 | 14250 |  | 0 |  | 14250
|  |  |  | 18:00 | 13950 |  | 0 |  | 13950
|  |  |  | 18:30 | 14600 |  | 0 |  | 14600
|  |  |  | 19:00 | 15300 |  | 0 |  | 15300
|  |  |  | 19:30 | 15900 |  | 0 |  | 15900
|  |  |  | 20:00 | 15950 |  | 0 |  | 15950
|  |  |  | 21:00 | 16199 |  | 0 |  | 16199
|  |  |  | 22:00 | 16050 |  | 0 |  | 16050
|  |  |  | 23:00 | 15930 |  | 0 |  | 15930
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 14150.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 16199.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16199.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 346.979 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:19 hrs on 25-07-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 24-07-2025 | [28 empty] | Date: | 24-07-2025 | [28 empty] | Date: | 24-07-2025 | [28 empty] | Date: | 24-07-2025 | [28 empty] | Date: | 24-07-2025 | [11 empty] | Date: | 24-07-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [11 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 7 | 87 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 551 | 54 | 35 | 109 | 138 | 277 | 55 | 55 | 162 | 0 | 450 | 302 | 0 | 0 | 55 | 320 | 192 | 0 | 0 | 108 | 25 | 14 | 0 | 0 | 0 | 0 | 39 | 0 | 10 | 65 | 63 | 0 | 12 | 25 | 0 | 220 | 0 | 23 | 782 | 160 | 0 | 40 | 25 | 17 | 218 | 0 | 0 | 0 | 1160 | 0 | 51 | 143 | 53 | 0 | 332 | 340 | 47 | 198 | 36 | 90 | 0 | 125 | 64 | 19 | 87 | 58 | 43 | 0 | 43 | 0 | 320 | 385 | 0 | 59 | 146 | 6 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 81 | 173 | 46 | 0 | 0 | 0 | 8980 | 860 | 158 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1208 | 34 | 1443 | 0 | 40 | 0 | 70 | 113 | 0 | 95 | 0 | 53 | 0 | 21 | 0 | 196 | 0 | 176 | 0 | 175 | 0 | 403 | 0 | 0 | 0 | 46 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 117 | 220 | 0 | 302 | 1110 | 0 | 7384 | 16364 | 101.51
01:00 | 7 | 50 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553 | 54 | 35 | 105 | 108 | 277 | 55 | 55 | 162 | 0 | 450 | 282 | 0 | 0 | 35 | 322 | 192 | 0 | 0 | 108 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 65 | 45 | 0 | 12 | 25 | 0 | 218 | 0 | 19 | 778 | 160 | 0 | 40 | 26 | 0 | 221 | 0 | 0 | 0 | 1105 | 0 | 51 | 120 | 45 | 0 | 338 | 340 | 47 | 183 | 34 | 75 | 0 | 61 | 40 | 19 | 77 | 46 | 43 | 0 | 45 | 0 | 320 | 300 | 0 | 60 | 136 | 6 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 81 | 163 | 47 | 0 | 0 | 0 | 8460 | 860 | 157 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1175 | 17 | 1441 | 0 | 0 | 0 | 35 | 113 | 0 | 95 | 0 | 0 | 0 | 21 | 0 | 197 | 0 | 176 | 0 | 175 | 0 | 340 | 0 | 0 | 0 | 47 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 117 | 220 | 0 | 302 | 1115 | 0 | 7142 | 15602 | 101.56
02:00 | 0 | 50 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 552 | 54 | 35 | 83 | 108 | 95 | 30 | 17 | 54 | 0 | 450 | 303 | 0 | 0 | 0 | 322 | 191 | 0 | 0 | 108 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 45 | 0 | 12 | 25 | 0 | 218 | 0 | 23 | 780 | 17 | 0 | 20 | 0 | 0 | 218 | 0 | 0 | 0 | 1160 | 0 | 51 | 50 | 53 | 0 | 336 | 340 | 47 | 201 | 36 | 72 | 0 | 59 | 38 | 19 | 60 | 50 | 25 | 0 | 45 | 0 | 320 | 335 | 0 | 60 | 132 | 6 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 81 | 163 | 47 | 0 | 0 | 0 | 7879 | 859 | 157 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1182 | 17 | 1444 | 0 | 0 | 0 | 0 | 113 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 176 | 0 | 176 | 0 | 375 | 0 | 0 | 0 | 47 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 117 | 220 | 0 | 300 | 1110 | 0 | 7085 | 14964 | 101.61
03:00 | 0 | 50 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553 | 54 | 35 | 82 | 108 | 0 | 0 | 0 | 16 | 0 | 450 | 284 | 0 | 0 | 0 | 326 | 196 | 0 | 0 | 108 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 15 | 0 | 12 | 25 | 0 | 218 | 0 | 23 | 776 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1105 | 0 | 51 | 0 | 53 | 0 | 348 | 340 | 44 | 191 | 37 | 84 | 0 | 88 | 39 | 19 | 59 | 48 | 0 | 0 | 0 | 0 | 320 | 333 | 0 | 60 | 133 | 7 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 81 | 163 | 47 | 0 | 0 | 0 | 7450 | 859 | 165 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1131 | 17 | 1384 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 180 | 0 | 177 | 0 | 353 | 0 | 0 | 0 | 47 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 117 | 220 | 0 | 301 | 1115 | 0 | 6827 | 14277 | 101.66
04:00 | 0 | 50 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 0 | 0 | 43 | 95 | 0 | 0 | 0 | 0 | 0 | 400 | 280 | 0 | 0 | 0 | 323 | 96 | 0 | 0 | 108 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 12 | 25 | 0 | 218 | 0 | 24 | 719 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 907 | 0 | 51 | 0 | 53 | 0 | 355 | 340 | 0 | 184 | 0 | 83 | 0 | 100 | 56 | 19 | 60 | 48 | 0 | 0 | 0 | 0 | 320 | 302 | 0 | 60 | 133 | 7 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 75 | 173 | 47 | 0 | 0 | 0 | 6753 | 860 | 167 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1014 | 0 | 1109 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 182 | 0 | 180 | 0 | 338 | 0 | 0 | 0 | 47 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 117 | 220 | 0 | 302 | 1000 | 0 | 6230 | 12983 | 101.71
05:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 300 | 286 | 0 | 0 | 0 | 250 | 96 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 12 | 25 | 0 | 218 | 0 | 30 | 622 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 35 | 0 | 280 | 280 | 0 | 204 | 0 | 73 | 0 | 100 | 57 | 19 | 34 | 48 | 0 | 0 | 0 | 0 | 320 | 346 | 0 | 60 | 137 | 0 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 82 | 166 | 47 | 0 | 0 | 0 | 6064 | 860 | 164 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 0 | 1011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 165 | 0 | 160 | 0 | 386 | 0 | 0 | 0 | 47 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 100 | 180 | 0 | 301 | 810 | 0 | 5688 | 11752 | 101.75
06:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 298 | 0 | 0 | 0 | 290 | 135 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 33 | 0 | 0 | 12 | 25 | 1 | 218 | 0 | 30 | 623 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 840 | 0 | 51 | 0 | 35 | 0 | 280 | 280 | 0 | 186 | 0 | 32 | 0 | 100 | 57 | 19 | 14 | 46 | 0 | 0 | 0 | 0 | 320 | 390 | 0 | 60 | 132 | 0 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 82 | 95 | 49 | 0 | 0 | 10 | 5936 | 859 | 170 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 793 | 0 | 1003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 165 | 0 | 160 | 0 | 392 | 0 | 0 | 0 | 47 | 114 | 2 | 113 | 0 | 0 | 1 | 11 | 0 | 0 | 163 | 100 | 180 | 0 | 301 | 790 | 0 | 5567 | 11503 | 101.79
07:00 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 305 | 0 | 0 | 0 | 290 | 134 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 16 | 0 | 0 | 0 | 12 | 0 | 218 | 0 | 30 | 622 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 844 | 4 | 51 | 0 | 35 | 0 | 280 | 280 | 11 | 207 | 17 | 31 | 0 | 68 | 36 | 19 | 16 | 44 | 0 | 7 | 0 | 0 | 320 | 390 | 0 | 60 | 141 | 0 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 45 | 16 | 49 | 0 | 0 | 0 | 5793 | 852 | 179 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 797 | 0 | 1039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 190 | 0 | 182 | 0 | 414 | 0 | 0 | 0 | 47 | 114 | 7 | 113 | 0 | 0 | 2 | 39 | 1 | 0 | 176 | 100 | 180 | 0 | 302 | 800 | 0 | 5754 | 11547 | 101.83
08:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 301 | 0 | 0 | 0 | 315 | 134 | 0 | 1 | 0 | 26 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 16 | 0 | 0 | 0 | 12 | 3 | 219 | 0 | 5 | 603 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 860 | 10 | 51 | 0 | 35 | 0 | 346 | 340 | 5 | 206 | 36 | 32 | 0 | 66 | 36 | 19 | 15 | 40 | 0 | 19 | 0 | 0 | 320 | 393 | 0 | 60 | 152 | 0 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 8 | 8 | 49 | 0 | 2 | 0 | 6149 | 852 | 181 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5 | 800 | 0 | 1052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 192 | 0 | 191 | 0 | 414 | 0 | 0 | 0 | 46 | 114 | 13 | 113 | 0 | 0 | 4 | 41 | 1 | 0 | 173 | 115 | 220 | 0 | 303 | 795 | 0 | 5858 | 12007 | 101.87
09:00 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 3 | 17 | 0 | 0 | 0 | 10 | 0 | 0 | 420 | 294 | 0 | 0 | 0 | 318 | 196 | 0 | 2 | 0 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 25 | 3 | 220 | 0 | 2 | 623 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 900 | 13 | 51 | 0 | 35 | 0 | 350 | 340 | 26 | 193 | 37 | 40 | 0 | 78 | 33 | 19 | 38 | 44 | 0 | 40 | 0 | 0 | 320 | 376 | 0 | 60 | 157 | 0 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 20 | 39 | 49 | 0 | 6 | 0 | 6463 | 852 | 179 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 23 | 797 | 0 | 984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 194 | 0 | 192 | 0 | 193 | 0 | 353 | 0 | 0 | 0 | 46 | 114 | 15 | 112 | 0 | 0 | 5 | 81 | 1 | 0 | 169 | 117 | 220 | 0 | 301 | 845 | 0 | 5834 | 12297 | 101.91
10:00 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 0 | 35 | 48 | 0 | 0 | 0 | 48 | 15 | 0 | 420 | 308 | 0 | 0 | 0 | 310 | 192 | 0 | 9 | 35 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 12 | 25 | 4 | 220 | 0 | 2 | 780 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 960 | 7 | 43 | 0 | 35 | 0 | 340 | 340 | 37 | 210 | 39 | 69 | 0 | 159 | 31 | 17 | 45 | 24 | 0 | 39 | 0 | 0 | 320 | 383 | 0 | 60 | 156 | 0 | 0 | 80 | 30 | 0 | 18 | 0 | 0 | 64 | 48 | 48 | 0 | 16 | 1 | 6962 | 851 | 176 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 41 | 853 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 5 | 195 | 0 | 192 | 0 | 193 | 0 | 394 | 0 | 1 | 0 | 46 | 113 | 12 | 67 | 0 | 0 | 7 | 143 | 1 | 0 | 176 | 117 | 220 | 0 | 301 | 902 | 0 | 5875 | 12837 | 101.95
11:00 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605 | 10 | 17 | 60 | 0 | 20 | 0 | 55 | 156 | 0 | 420 | 288 | 0 | 0 | 0 | 281 | 197 | 0 | 15 | 52 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 26 | 0 | 12 | 25 | 3 | 220 | 0 | 2 | 781 | 0 | 0 | 26 | 1 | 0 | 214 | 0 | 0 | 0 | 972 | 8 | 51 | 6 | 35 | 0 | 345 | 340 | 37 | 192 | 39 | 71 | 0 | 188 | 31 | 11 | 44 | 26 | 0 | 50 | 0 | 0 | 320 | 351 | 0 | 60 | 158 | 8 | 0 | 80 | 30 | 0 | 18 | 0 | 12 | 75 | 100 | 48 | 1 | 29 | 8 | 7319 | 851 | 176 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 41 | 870 | 0 | 821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 16 | 196 | 0 | 192 | 0 | 193 | 0 | 388 | 0 | 2 | 0 | 49 | 113 | 25 | 54 | 0 | 0 | 8 | 171 | 1 | 0 | 237 | 117 | 220 | 0 | 301 | 1025 | 0 | 6125 | 13444 | 101.99
12:00 | 0 | 25 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 604 | 48 | 23 | 83 | 0 | 45 | 0 | 55 | 158 | 0 | 420 | 304 | 0 | 0 | 17 | 311 | 192 | 0 | 23 | 52 | 20 | 22 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 16 | 46 | 0 | 12 | 25 | 3 | 220 | 0 | 2 | 780 | 0 | 0 | 38 | 16 | 0 | 212 | 0 | 0 | 0 | 935 | 11 | 51 | 63 | 35 | 0 | 344 | 340 | 40 | 195 | 39 | 73 | 50 | 179 | 32 | 11 | 75 | 26 | 1 | 30 | 0 | 0 | 320 | 323 | 0 | 60 | 150 | 8 | 0 | 76 | 30 | 0 | 17 | 0 | 17 | 75 | 123 | 48 | 1 | 33 | 10 | 7637 | 852 | 173 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 71 | 901 | 0 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 33 | 178 | 0 | 192 | 0 | 191 | 0 | 410 | 0 | 3 | 0 | 49 | 114 | 30 | 87 | 0 | 0 | 8 | 206 | 1 | 0 | 239 | 117 | 220 | 0 | 301 | 1105 | 0 | 6487 | 14124 | 102.04
13:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 604 | 49 | 35 | 90 | 0 | 162 | 0 | 55 | 155 | 9 | 420 | 277 | 0 | 0 | 17 | 306 | 193 | 0 | 28 | 70 | 23 | 22 | 0 | 0 | 0 | 0 | 72 | 0 | 4 | 16 | 46 | 0 | 12 | 25 | 4 | 218 | 0 | 3 | 776 | 0 | 0 | 38 | 26 | 0 | 216 | 0 | 0 | 0 | 900 | 11 | 51 | 105 | 35 | 0 | 350 | 340 | 41 | 182 | 39 | 74 | 50 | 181 | 32 | 19 | 78 | 22 | 43 | 59 | 0 | 0 | 320 | 353 | 0 | 60 | 156 | 8 | 0 | 80 | 30 | 0 | 17 | 0 | 17 | 82 | 147 | 46 | 2 | 28 | 9 | 8006 | 851 | 170 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 101 | 937 | 0 | 980 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 70 | 0 | 37 | 176 | 0 | 192 | 0 | 190 | 0 | 383 | 0 | 4 | 0 | 48 | 114 | 29 | 112 | 0 | 0 | 7 | 190 | 1 | 0 | 241 | 117 | 220 | 0 | 301 | 1109 | 0 | 6642 | 14648 | 102.09
14:00 | 0 | 52 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 48 | 35 | 108 | 0 | 262 | 12 | 55 | 153 | 16 | 420 | 287 | 0 | 0 | 17 | 305 | 191 | 0 | 21 | 90 | 24 | 22 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 16 | 46 | 0 | 12 | 25 | 4 | 217 | 0 | 2 | 780 | 0 | 0 | 18 | 25.5 | 0 | 210 | 0 | 0 | 0 | 900 | 20 | 51 | 115 | 35 | 0 | 340 | 300 | 40 | 195 | 38 | 72 | 50 | 180 | 31 | 19 | 78 | 6 | 52.2 | 56 | 0 | 0 | 320 | 380 | 0 | 50 | 141 | 8 | 0 | 76 | 30 | 0 | 16 | 0 | 17 | 84 | 147 | 46 | 2 | 30.07 | 11 | 8074.77 | 856 | 167 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 58 | 871 | 0 | 1152.29 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 58 | 0 | 28.46 | 160 | 0 | 188 | 0 | 190 | 0 | 402 | 0 | 2.6 | 0 | 48 | 114 | 24 | 113 | 0 | 0 | 5.1 | 179 | 0.37 | 0 | 279 | 115 | 220 | 0 | 301 | 1106 | 0 | 6699.82 | 14774.59 | 102.14
15:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 49 | 35 | 110 | 18 | 262 | 16 | 55 | 155 | 16 | 420 | 291 | 0 | 0 | 17 | 305 | 191 | 0 | 21 | 108 | 23.5 | 22 | 0 | 0 | 0 | 0 | 87 | 0 | 11 | 16 | 46 | 0 | 12 | 25 | 2.29 | 217 | 0 | 2 | 775 | 53 | 0 | 39 | 25.5 | 1 | 210 | 0 | 0 | 0 | 930 | 10 | 51 | 118 | 35 | 0 | 336 | 320 | 40 | 200 | 34 | 87 | 68 | 183 | 36 | 19 | 72 | 6 | 52.2 | 50 | 0 | 0 | 320 | 380 | 0 | 50 | 148 | 8 | 0 | 76 | 30 | 0 | 16 | 0 | 17 | 82 | 164 | 46 | 1 | 28.61 | 12 | 8120.1 | 856 | 161 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 56 | 1021 | 0 | 1217.92 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 70 | 0 | 33.15 | 180 | 0 | 183 | 0 | 181 | 0 | 405 | 0 | 3.14 | 0 | 48 | 114 | 12 | 112 | 0 | 0 | 5.8 | 64 | 0.37 | 0 | 278 | 117 | 220 | 0 | 301 | 1108 | 0 | 6809.38 | 14929.48 | 102.19
16:00 | 7 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 49 | 35 | 110 | 27 | 277 | 50 | 55 | 156 | 0 | 420 | 298 | 0 | 0 | 17 | 305 | 191 | 0 | 10 | 108 | 19 | 22 | 0 | 0 | 0 | 0 | 96 | 0 | 24 | 16 | 45 | 0 | 25 | 25 | 2.03 | 217 | 15 | 2 | 779 | 53 | 0 | 37 | 25.5 | 17 | 210 | 0 | 0 | 0 | 935 | 4 | 51 | 120 | 35 | 0 | 322 | 335 | 32 | 205 | 38 | 90 | 50 | 180 | 35 | 19 | 72 | 34 | 52.2 | 25 | 0 | 0 | 320 | 361 | 0 | 50 | 153 | 8 | 0 | 81 | 30 | 0 | 16 | 0 | 17 | 82 | 183 | 46 | 1 | 12.48 | 12 | 8054.21 | 856 | 155 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 23 | 1107 | 0 | 1241.29 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 36 | 0 | 15.84 | 200 | 0 | 178 | 0 | 175 | 0 | 414 | 0 | 1.39 | 0 | 46 | 114 | 7 | 111 | 0 | 0 | 4.8 | 50 | 0.22 | 0 | 289 | 117 | 220 | 0 | 300 | 1106 | 0 | 6829.54 | 14883.75 | 102.26
17:00 | 24 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 46 | 35 | 108 | 30 | 195 | 30 | 55 | 145 | 0 | 420 | 287 | 0 | 0 | 17 | 305 | 187 | 0 | 9 | 108 | 23.5 | 22 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 16 | 65 | 0 | 30 | 25 | 0 | 218 | 17 | 5 | 775 | 17 | 0 | 38 | 20 | 15 | 217 | 0 | 0 | 0 | 930 | 1 | 51 | 113 | 35 | 0 | 335 | 340 | 30 | 198 | 35 | 72 | 50 | 176 | 36 | 19 | 72 | 34 | 52.2 | 15 | 0 | 0 | 320 | 376 | 0 | 50 | 142 | 8 | 0 | 80 | 30 | 0 | 16 | 0 | 17 | 91 | 140 | 47 | 0 | 6.06 | 12 | 7984.76 | 856 | 153 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12 | 1030 | 0 | 1260.74 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 23 | 0 | 8.93 | 200 | 0 | 174 | 0 | 173 | 0 | 363 | 0 | 0.75 | 0 | 46 | 114 | 2 | 111 | 0 | 0 | 1.8 | 40 | 0.12 | 0 | 232 | 117 | 180 | 0 | 301 | 1050 | 0 | 6511.34 | 14496.1 | 102.33
18:00 | 48 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 604 | 47 | 35 | 93 | 30 | 195 | 30 | 55 | 118 | 0 | 370 | 284 | 0 | 0 | 17 | 305 | 75 | 0 | 2 | 108 | 23.5 | 22 | 0 | 0 | 0 | 0 | 97 | 0 | 36 | 16 | 75 | 0 | 32 | 25 | 0 | 218 | 16 | 9 | 768 | 17 | 0 | 39 | 8 | 15 | 218 | 0 | 0 | 0 | 920 | 0 | 51 | 117 | 35 | 0 | 300 | 280 | 38 | 188 | 35 | 71 | 50 | 160 | 35 | 19 | 72 | 30 | 52.2 | 1 | 0 | 0 | 320 | 332 | 0 | 50 | 130 | 8 | 0 | 81 | 30 | 0 | 16 | 0 | 17 | 91 | 140 | 47 | 0 | 1.84 | 12 | 7864.54 | 855 | 152 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7 | 871 | 0 | 1257.79 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 6 | 0 | 3.02 | 160 | 0 | 175 | 0 | 172 | 0 | 340 | 0 | 0.26 | 0 | 46 | 114 | 1 | 110 | 0 | 0 | 0.8 | 16 | 0.46 | 0 | 225 | 117 | 180 | 0 | 301 | 950 | 0 | 6122.33 | 13986.87 | 102.4
19:00 | 82 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 46 | 35 | 101 | 112 | 275 | 31 | 55 | 129 | 16 | 370 | 298 | 0 | 0 | 17 | 305 | 134 | 0 | 0 | 108 | 25 | 22 | 0 | 0 | 0 | 15 | 96 | 0 | 14 | 52 | 75 | 0 | 34 | 25 | 0 | 220 | 15 | 8 | 774 | 160 | 0 | 39 | 12 | 22 | 216 | 0 | 0 | 0 | 930 | 0 | 51 | 127 | 38 | 0 | 333 | 320 | 41 | 206 | 37 | 72 | 50 | 171 | 36 | 19 | 72 | 36 | 52.2 | 0 | 0 | 0 | 320 | 383 | 0 | 70 | 137 | 8 | 0 | 81 | 30 | 0 | 16 | 0 | 17 | 91 | 186 | 46 | 0 | 0 | 12 | 8565.2 | 856 | 152 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 25 | 1367.45 | 0 | 0 | 0 | 60 | 35 | 0 | 60 | 13 | 52.2 | 0 | 0 | 0 | 162 | 0 | 174 | 0 | 171 | 0 | 388 | 0 | 0 | 0 | 46 | 114 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 238 | 117 | 220 | 0 | 302 | 996 | 0 | 6598.65 | 15163.85 | 102.47
19:30 | 48 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 43 | 35 | 116 | 140 | 195 | 55 | 55 | 142 | 16 | 420 | 278 | 0 | 0 | 17 | 305 | 192 | 0 | 0 | 108 | 25 | 22 | 0 | 0 | 0 | 15 | 88 | 0 | 37 | 63 | 75 | 0 | 34 | 25 | 0 | 220 | 34 | 9 | 774 | 108 | 0 | 39 | 25.5 | 43 | 218 | 0 | 0 | 0 | 920 | 0 | 51 | 138 | 35 | 0 | 344 | 340 | 41 | 182 | 38 | 73 | 50 | 157 | 36 | 19 | 89 | 36 | 52.2 | 0 | 0 | 0 | 320 | 354 | 0 | 60 | 149 | 8 | 0 | 81 | 30 | 0 | 16 | 0 | 17 | 91 | 194 | 47 | 0 | 0 | 12 | 8629.7 | 855 | 151 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1065 | 51 | 1423.43 | 0 | 0 | 0 | 100 | 80 | 0 | 90 | 20 | 52.2 | 0 | 21 | 0 | 198 | 0 | 169 | 0 | 170 | 0 | 332 | 0 | 0 | 0 | 46 | 114 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 266 | 117 | 220 | 0 | 302 | 1080 | 0 | 7072.63 | 15702.33
20:00 | 7 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 46 | 35 | 110 | 125 | 145 | 30 | 55 | 145 | 16 | 450 | 299 | 0 | 0 | 17 | 305 | 192 | 0 | 0 | 108 | 25 | 22 | 0 | 0 | 0 | 15 | 80 | 0 | 61 | 65 | 75 | 0 | 35 | 25 | 0 | 220 | 42 | 17 | 772 | 53 | 0 | 39 | 25.5 | 46 | 217 | 0 | 0 | 0 | 958 | 0 | 51 | 137 | 45 | 0 | 340 | 340 | 43 | 188 | 35 | 75 | 50 | 169 | 36 | 19 | 89 | 26 | 25 | 0 | 0 | 0 | 320 | 355 | 0 | 58 | 150 | 8 | 0 | 81 | 30 | 0 | 16 | 0 | 17 | 91 | 194 | 47 | 0 | 0 | 12 | 8554.5 | 856 | 150 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1113 | 51 | 1431.69 | 0 | 0 | 0 | 50 | 104 | 0 | 90 | 37 | 25 | 0 | 28 | 0 | 202 | 0 | 169 | 0 | 171 | 0 | 387 | 0 | 0 | 0 | 46 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 117 | 220 | 0 | 301 | 1090 | 0 | 7177.69 | 15732.19 | 102.54
21:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 45 | 35 | 98 | 110 | 15 | 15 | 55 | 143 | 16 | 350 | 296 | 0 | 0 | 17 | 305 | 193 | 0 | 0 | 108 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 65 | 24 | 0 | 36 | 25 | 0 | 220 | 17 | 18 | 780 | 0 | 0 | 39 | 8 | 17 | 217 | 0 | 0 | 0 | 1050 | 0 | 51 | 80 | 61 | 0 | 340 | 340 | 47 | 188 | 38 | 68 | 50 | 167 | 47 | 0 | 71 | 32 | 8 | 0 | 0 | 0 | 320 | 364 | 0 | 58 | 150 | 8 | 0 | 81 | 30 | 0 | 18 | 0 | 23 | 91 | 194 | 52 | 0 | 0 | 12 | 8142 | 856 | 150 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1191 | 35 | 1434.5 | 0 | 19 | 0 | 100 | 85 | 0 | 90 | 37 | 8 | 0 | 30 | 0 | 203 | 0 | 169 | 0 | 172 | 0 | 365 | 0 | 0 | 0 | 45 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 117 | 221 | 0 | 302 | 1100 | 0 | 7268.5 | 15410.5 | 102.61
22:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 721 | 0 | 0 | 76 | 80 | 0 | 0 | 35 | 108 | 0 | 300 | 285 | 0 | 0 | 0 | 300 | 138 | 0 | 0 | 108 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 50 | 7 | 0 | 37 | 25 | 0 | 218 | 0 | 25 | 780 | 0 | 0 | 26 | 8 | 0 | 217 | 0 | 0 | 0 | 1071 | 0 | 51 | 30 | 63 | 0 | 300 | 280 | 44 | 192 | 38 | 32 | 50 | 164 | 54 | 0 | 70 | 32 | 8 | 0 | 0 | 0 | 320 | 348 | 0 | 57 | 130 | 8 | 0 | 81 | 30 | 0 | 18 | 0 | 35 | 91 | 193 | 79 | 0 | 0 | 12 | 7603 | 856 | 150 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1134 | 17 | 1442.27 | 0 | 30 | 0 | 113 | 100 | 0 | 42 | 0 | 0 | 0 | 28 | 0 | 195 | 0 | 169 | 0 | 172 | 0 | 346 | 0 | 0 | 0 | 45 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 117 | 180 | 0 | 302 | 1020 | 0 | 6951.27 | 14554.27 | 102.68
23:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 721 | 0 | 0 | 57 | 79 | 0 | 0 | 17 | 53 | 0 | 360 | 307 | 0 | 0 | 0 | 300 | 136 | 0 | 0 | 108 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 50 | 7 | 0 | 24 | 25 | 0 | 216 | 0 | 30 | 782 | 0 | 0 | 26 | 8 | 0 | 216 | 0 | 0 | 0 | 1155 | 0 | 51 | 0 | 77 | 0 | 345 | 340 | 47 | 206 | 38 | 40 | 50 | 189 | 64 | 19 | 72 | 32 | 8 | 0 | 0 | 0 | 320 | 363 | 0 | 58 | 148 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 35 | 92 | 184 | 76 | 0 | 0 | 12 | 7839 | 853 | 152 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 17 | 1440.76 | 0 | 32 | 0 | 113 | 113 | 0 | 42 | 0 | 0 | 0 | 28 | 0 | 185 | 0 | 175 | 0 | 172 | 0 | 407 | 0 | 0 | 0 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 252 | 117 | 220 | 0 | 300 | 1027 | 0 | 7037.76 | 14876.76 | 102.75
Total KWH | 182304 | 1181760 | 579840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13170480 | 710640 | 550440 | 1690704 | 1141920 | 2432313 | 406425 | 842007 | 2139840 | 100800 | 9326500 | 7092364 | 0 | 0 | 233534 | 7368785 | 4135000 | 0 | 133547 | 1854000 | 451200 | 429480 | 0 | 0 | 0 | 37636 | 744960 | 0 | 330240 | 783525 | 670312 | 0 | 409920 | 546240 | 27121 | 5250875 | 143855 | 350400 | 17803636.36 | 535273 | 0 | 577920 | 259351.2 | 177309 | 4960404 | 0 | 0 | 0 | 23247270 | 94905 | 1133125 | 1465309 | 1070545 | 0 | 8260500 | 7840000 | 784320 | 4795000 | 750240 | 1632000 | 566000 | 3387840 | 1013880 | 394970 | 1404480 | 825600 | 522778 | 426545 | 108944 | 0 | 7658900 | 8992000 | 0 | 1347480 | 3453136 | 131664 | 0 | 1930560 | 717984 | 0 | 428000 | 0 | 360360 | 1812000 | 3271200 | 1155840 | 7600 | 209970 | 175440 | 181139245.56 | 20716363 | 4053312 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 450000 | 23061820 | 252480 | 28788364 | 0 | 122220 | 0 | 633792 | 935040 | 0 | 678640 | 65084 | 107242 | 338220 | 131349 | 183000 | 4610455 | 0 | 4542818 | 0 | 4526636 | 0 | 9186618 | 0 | 15780 | 0 | 1083927 | 2736636 | 191364 | 2617411 | 0 | 0 | 55156.92 | 1153440 | 4150.5 | 0 | 5599000 | 2744000 | 5176390 | 0 | 7250184 | 25169454.55 | 0 | 158092346.97 | 339231592.53

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 24-07-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14124 | MW | 12:00 Hr. | Energy Generated |  |  | 339.2316 |  | MKWHr.
| Day Peak Demand |  |  | 14124 | MW | 12:00 Hr. | Energy Unserverd |  |  | 2.552 |  | MKWHr.
| Evening Peak Generation |  |  | 15732.19 | MW | 20:00 Hr. | Energy Demand |  |  | 341.7836 |  | MKWHr.
| Evening Peak Demand |  |  | 15900.19 | MW | 20:00 Hr. | Maximum Temperature |  |  | 33 |  | °C
| Minimum Generation of the Day |  |  | 11503 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 981.06 |  | MMCFD
| Maximum Generation of the Day |  |  | 16364 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.4151 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 41.9738 | 0 | 14.0465 | 0 | 0 | 0.13355 | 0 | 0 | 56.1539 | Gas | 133.5351 | Gas | 445908947.32
| Chattogram Zone |  |  | 5.3108 | 41.0509 | 4.8863 | 0 | 5.2509 | 0.12203 | 0 | 0.33024 | 56.9512 | Coal | 103.2153 | Coal | 619972037.9771
| Cumilla Zone |  |  | 25.5947 | 0 | 9.5352 | 0 | 0 | 0.42655 | 0.8256 | 0 | 36.3821 | HFO | 42.367 | HFO | 787933975.944
| Mymensingh Zone |  |  | 1.1558 | 0 | 5.619 | 0 | 0 | 0.21757 | 0 | 0 | 6.9924 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 24.6597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.6597 | Hydro | 5.2509 | Hydro | 525087.5
| Khulna Zone |  |  | 4.0533 | 23.0618 | 0.25248 | 0 | 0 | 0.45 | 21.6284 | 0 | 49.446 | Solar | 3.2908 | Solar | 54151692.2462
| Barishal Zone |  |  | 7.9204 | 38.0186 | 0 | 0 | 0 | 0.0041505 | 0 | 0 | 45.9432 | Import | 51.2423 | Import | 262861194.79
| Rajshahi Zone |  |  | 22.8665 | 0 | 2.6734 | 0 | 0 | 0.537 | 28.7884 | 0 | 54.8653 | Wind | 0.33024 | Wind | 4834713.6
| Rangpur Zone |  |  | 0 | 1.0839 | 5.354 | 0 | 0 | 1.4 | 0 | 0 | 7.8379
| Total |  |  | 133.5351 | 103.2153 | 42.367 | 0 | 5.2509 | 3.2908 | 51.2423 | 0.33024 | 339.2316
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 445908947.32 |  | Hydro | 525087.5
|  |  |  | Coal | 619972037.9771 |  | Solar | 54151692.2462
|  |  |  | HFO | 787933975.944 |  | Import | 262861194.79
|  |  |  | HSD | 0 |  | Wind | 4834713.6
[5 empty] | Total: | 217,61,87,649 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.7164 | Peak Hr Flow | 856.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 42619981.89 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 28.7884 | Peak Hr Flow | 1431.69 MW at 20:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 826 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.8256 | Peak Hr Flow | 26.00 MW at 20:00 hrs.
Maximum Power Flow: |  |  | MW: | 998 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.3303 | Peak Hr Flow | 2313.69 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5540
|  |  |  | Chattogram |  | 0 |  | 1519
|  |  |  | Cumilla |  | 0 |  | 1200
|  |  |  | Mymensingh |  | 0 |  | 1297
|  |  |  | Sylhet |  | 60 |  | 674
|  |  |  | Khulna |  | 0 |  | 1870
|  |  |  | Barishal |  | 0 |  | 487
|  |  |  | Rajshahi |  | 0 |  | 1603
|  |  |  | Rangpur |  | 101 |  | 1054
|  |  |  | Total |  | 161 |  | 15244
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Bibiana-II 341 MW CCPP (Summit) GT |  |  | 222 | 3 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
|  | 4 | Bibiana-II 341 MW CCPP (Summit) ST |  |  | 119 | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 641 |  |  |  | Total | 707
|  |  |  | Total Unavailable Capacity |  |  |  | 1348
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:54 | 10:16 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) LT Project Work S/D | [7 empty] | 10.0MW load
interrup.
| 08:55 | 10:15 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) HT Project Work S/D | [7 empty] | 10.0MW load
interrup.
| 09:01 | 09:14 | Cumilla(S) 132/33kV S/S TR-3 LT Tripped showing 132kv-RET 650 33Kv-REF 615 relays Due to | [7 empty] | 44.0MW load
|  |  | 33Kv Kaliyajhori feeder Fault | [7 empty] | interrup.
|  | 09:47 | Hasnabad 132/33kV S/S 132/33kV 414 T-2 LT is restored.
|  | 09:57 | Feni 132/33kV S/S T-2(415T) HT is restored.
|  | 09:58 | Feni 132/33kV S/S T-2(415T) LT is restored.
| 10:21 |  | Maniknagar 132/33kV S/S Motijheel Ckt-2 Tripped showing Main Protection
Trip, Supervision Ckt-1,2 Trip, Y-phase Trip, Zone -1 Trip relays Due to TT Para
underground cable fault .
| 10:57 |  | Raozan 25 MW PP Synchronized
| 11:10 | 11:35 | Kurigram 132/33kV S/S Transformer T-1 (Tr-403T) LT Forced S/D Due to Tr-01,, 33kv bushing
Red hot remove R-Phase
| 11:11 | 13:16 | BIPTC S/S 20DF21 Scheduled S/D Due to Corrective Maintenance of AC Filter 20DF21
| 11:15 | 13:55 | Brahmanbaria-Narsinghdi 132 kV Ckt-2 Scheduled S/D from Narshingdi 132/33kV end Due to
Line DS and Earth Switch alignment maintenance work.
|  | 11:49 | Cumilla(N)-Shahjibazar 230 kV Ckt-1 is restored.
| 12:00 |  | Day peak generation: 14123 MW
| 12:39 | 16:02 | Maijdee 132/33kV S/S TR-01 LT Scheduled S/D Due to 33kv REB shubornachor CT connector and
breaker maintanance
| 12:39 | 16:02 | Maijdee 132/33kV S/S Tr-02 LT Scheduled S/D Due to 33kv REB shudharam feeder CT connector
and breaker maintanance.
| 12:58 | 13:09 | Baroaulia-Hathazari 132 kV Ckt-1 Tripped from Baroaulia 132/33kV end showing Quadramho
relays Due to Distance trip
| 13:13 | 16:07 | Bogura 400/230kV S/S ATR-03 LT Project Work S/D Due to Painting work
| 13:15 | 16:05 | Bogura 400/230kV S/S ATR-03 HT Project Work S/D Due to Painting work
| 14:34 | 18:14 | Barishal 230/132kV S/S T-5 HT Scheduled S/D | [7 empty] | 16.0MW load
interrup.
| 14:35 | 18:17 | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to 33kv busbar section DS maintenance by | [7 empty] | 16.0MW load
|  |  | Pirojpur PBS | [7 empty] | interrup.
|  | 17:11 | Mahasthangar-Palashbari 132kV Ckt-1 is restored.
|  | 17:43 | Gopalganj 400/132kV S/S 400kV Rooppur is restored.
| 20:00 |  | Evening Peak Generation 15731 MW.
| 20:53 | 21:43 | Chandpur 132/33kV S/S 422T LT Tripped showing O/c and E/f and relays Due to Due to Cdr3 | [7 empty] | 40.0MW load
|  |  | breaker fail and under voltage relay and tcsr relay | [7 empty] | interrup.
| 20:53 | 21:43 | Chandpur 132/33kV S/S 412T LT Tripped showing O/c and E/F And Lockout relay relays Due to | [7 empty] | 40.0MW load
|  |  | Due to cdr3 33kv breaker fail | [7 empty] | interrup.
| 21:50 | 22:06 | Srinagar 132/33kV S/S 33 kV bus Scheduled S/D Due to Red Hot problem in Feeder-4 of 33 KV | [7 empty] | 30.0MW load
|  |  | bus section. | [7 empty] | interrup.
| 21:50 | 22:06 | Srinagar 132/33kV S/S Tr-01 HT Scheduled S/D Due to Red Hot problem in Feeder-4 of 33 KV | [7 empty] | 30.0MW load
|  |  | bus section. | [7 empty] | interrup.
| 21:50 | 22:06 | Srinagar 132/33kV S/S Tr-01 LT Scheduled S/D Due to Red Hot problem in Feeder-4 of 33 KV | [7 empty] | 30.0MW load
|  |  | bus section. | [7 empty] | interrup.
|  | 22:00 | Chandpur 132/33kV S/S 402T LT is restored.
| 23:14 | 23:25 | Sreepur 230/132/33kV S/S 132/33 kV T-1 LT Tripped showing siprotec relays Due to over | [7 empty] | 42.0MW load
|  |  | current | [7 empty] | interrup.
| 23:38 | 01:05 | Bhaluka-Mymensingh 132 kV Ckt-1 Tripped from Mymensingh 132/33kV end showing Distance
(21) relays Due to Due to heavy thunderstorm
| 23:38 | 01:05 | Bhaluka-Mymensingh 132 kV Ckt-2 Tripped from Mymensingh 132/33kV end showing Distance
(21) relays Due to Due to heavy thunderstorm
| 02:32 |  | Raozan 25 MW PP Shutdown
| 03:08 | 04:48 | Chowmuhani 132/33kV S/S TR3-435T HT Forced S/D Due to 33KV PDB Datterhat Feeder BUBBAR | [7 empty] | 50.0MW load
|  |  | end Red hot maintenance. | [7 empty] | interrup.
| 03:08 | 04:49 | Chowmuhani 132/33kV S/S TR3-435T LT Forced S/D Due to 33KV PDB Datterhat Feeder BUBBAR | [7 empty] | 50.0MW load
|  |  | end Red hot maintenance. | [7 empty] | interrup.
| 03:56 |  | Niamatpur 132/33kV S/S 132kV Rahanpur Ckt-1 Tripped showing Distance relay: General
trip R phase trip 21 Z1 Trip VT Fuse Fail AR Success 67 Dir. OC relays Due to R
phase trip CB ( Y,B Phase not tripped)
| 03:56 |  | Rahanpur 400/132kV S/S Rahanpur-Niamatpur 132 KV Line Ckt-01 Tripped showing Distance
relay,Lockout relay relays Due to R phase trip,Zone-02 trip,Relay General trip
| 03:56 |  | Niamatpur 132/33kV S/S 132kV Rahanpur Ckt-1 Tripped showing Distance relay: General
trip R phase trip 21 Z1 Trip VT Fuse Fail AR Success 67 Dir. OC relays Due to R
phase trip CB ( Y,B Phase not tripped)
| 06:19 |  | Madunaghat-TKCL 132kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end Due to For army
project work.
| 06:19 |  | Madunaghat-Sikalbaha 132kV Ckt-2 Scheduled S/D from Madunaghat 132/33kV end Due to for
army project work
| 06:31 |  | Kabirpur 132/33kV S/S XFR, T-I HT Scheduled S/D Due to Loop connection of Auxiliary | [7 empty] | 60.0MW load
|  |  | Transformer -1 | [7 empty] | interrup.
| 06:31 |  | Kabirpur 132/33kV S/S XFR, T-I LT Scheduled S/D Due to Loop connection of Auxiliary | [7 empty] | 60.0MW load
|  |  | Transformer-1 | [7 empty] | interrup.
| 06:37 |  | GPH 230/33kV S/S HATHAZARI Scheduled S/D Due to Maintenance Works.
| 06:40 |  | GPH-Hathazari 230kV Ckt-1 Scheduled S/D from Hathazari 230/132/33kV end Due to Red Hot
Maintenance
| 06:49 |  | Chowmuhani-Feni 132 kV Ckt-2 Scheduled S/D from Chowmuhani 132/33kV end Due to Project
work.
| 06:53 |  | At Bhola-Borhanuddin,( 230/33)Kv transformer is S/D.
| 06:57 |  | Sonargaon 132/33kV S/S Tr-1 LT Scheduled S/D Due to LT side T-Point maintenance | [7 empty] | 45.0MW load
interrup.
| 06:58 |  | Sonargaon 132/33kV S/S Tr-1 HT Scheduled S/D Due to T-point maintenance | [7 empty] | 45.0MW load
interrup.
| 07:25 |  | Gulsan-Rampura 132kV Ckt-1 Scheduled S/D from Gulshan 132/33kV end Due to IVT
replacement work at Rampura Ckt-1
| 07:36 |  | Gulsan-Rampura 132kV Ckt-1 Scheduled S/D from Rampura 230/132kV end Due to S/D taken by
NLDC and Gulshan S/S for IVT change
| 07:36 |  | Mahasthangar-Palashbari 132kV Ckt-2 Scheduled S/D from Palashbari 132/33kV end Due to
Re-conducting work and from Mahasthangarh 132/33kV end Due to STGE Project Work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 24-07-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9326500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 299 | 7092364 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 30 | 406425 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 192 | 4135000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 305 | 7368785 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 7 | 182304 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 46 | 710640 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 125 | 1141920 | machine problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 842007 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 233534 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 25 | 451200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 429480 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 579840 | Fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 2432313 | Machine Problem
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 110 | 1690704 | Machine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1181760 | machine problem
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 100800 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 145 | 2139840 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 133547 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 550440 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 500 | 13170480 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 1854000 | Engine Problem
Dhaka Area Total |  |  |  |  | 5939.724 | 2762 | 56153883
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 259351.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 94905 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 39 | 577920 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5250875 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 4960404 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 46 | 177309 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 75 | 670312 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 783525 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 35 | 409920 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 17 | 350400 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 80 | 744960 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 27121 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 37636 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 42 | 143855 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 546240 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 53 | 535273 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 958 | 23247270 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 61 | 330240 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 772 | 17803636.36 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.72 | 2745.5 | 56951152.56
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 188 | 4795000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 340 | 8260500 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 340 | 7840000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 35 | 750240 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 43 | 784320 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 45 | 1070545 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1133125 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 137 | 1465309 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 108944 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 566000 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 169 | 3387840 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 26 | 825600 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 25 | 522778 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 394970 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 89 | 1404480 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 36 | 1013880 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 75 | 1632000 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 426545 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1668 | 36382076
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 47 | 1155840 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 194 | 3271200 | Machine Problem
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 91 | 1812000 | Machine Problem
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 209970 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 175440 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 360360 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 361 | 6992410
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 58 | 1347480 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 150 | 3453136 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 717984 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1930560 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 428000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 131664 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Plant Shutdown as per schedule HGPI work
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 355 | 8992000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7658900 | Aythority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2325 | 1018 | 24659724
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 856 | 20716363 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 150 | 4053312 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 51 | 252480 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 450000 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1113 | 23061820 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2208 | 49445975
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 301 | 7250184 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 117 | 2744000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1090 | 25169454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5176390 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 274 | 5599000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4150.5 | -
Barishal Area Total |  |  |  |  | 2236 | 2002 | 45943179.05
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 122220 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 65084 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 202 | 4610455 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 169 | 4542818 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 171 | 4526636 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 387 | 9186618 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 131349 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 25 | 107242 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 678640 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 104 | 935040 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 50 | 633792 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 15780 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1431.69 | 28788364 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 183000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 338220 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2694.69 | 54865258
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 46 | 1083927 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 2617411 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 55156.92 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 114 | 2736636 | Engine Problem
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 191364 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1153440 | -
Rangpur Area Total |  |  |  |  | 950 | 273 | 7837934.92
Eastern Grid Total |  |  |  |  | 16667.715 | 8554.5 | 181139245.56
Western Grid Total |  |  |  |  | 10378.16 | 7177.69 | 158092346.97
National Grid Total |  |  |  |  | 27045.875 | 15732.19 | 339231592.53
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 24-07-2025
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10169.78 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4912.3 | MW
i) Dhaka area |  |  | 5540.06 |  | MW | i) Khulna area |  |  |  | 1869.5 | MW
ii) Chattogram area |  |  | 1519 |  | MW | ii) Barishal area |  |  |  | 487.2 | MW
iii) Cumilla area |  |  | 1199.72 |  | MW | iii) Rajshahi area |  |  |  | 1602.6 | MW
iv) Mymensingh area |  |  | 1297 |  | MW | iv) Rangpur area |  |  |  | 953 | MW
v) Sylhet area |  |  | 614 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15082.08 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 84 | 19:00 | 133 | PHP | 10 | 15:00
2 | AKSML | 123 | 06:00 | 68 | Ishurdi | 88 | 19:30 | 134 | Pabna | 137 | 00:00
3 | Aftabnagar | 46 | 00:00 | 69 | Jaldhaka | 96 | 09:00 | 135 | Palashbari | 121 | 21:00
4 | Agargaon | 146 | 00:00 | 70 | Jamalpur | 146 | 23:00 | 136 | Panchagarh | 57 | 18:00
5 | Agrabad | 100 | 16:00 | 71 | Jashore | 149 | 19:30 | 137 | Patuakhali | 79.5 | 19:00
6 | Amnura | 44 | 01:00 | 72 | Jhenaidah | 131 | 00:00 | 138 | Payra | 38 | 00:00
7 | Ashuganj | 105 | 01:00 | 73 | Joydebpur | 150 | 16:00 | 139 | Postogola | 67 | 00:00
8 | BSRM | 204 | 16:00 | 74 | Joypurhat | 75 | 00:00 | 140 | Purbachal | 26 | 00:00
9 | Bagerhat | 89 | 00:00 | 75 | Juldah | 20 | 01:00 | 141 | Purbasadipur | 145 | 22:00
10 | Bajitpur | 87 | 00:00 | 76 | KSRM | 35 | 17:00 | 142 | Rahanpur | 36 | 00:00
11 | Bakulia | 104 | 15:00 | 77 | Kabirpur | 254 | 15:00 | 143 | Rahim | 26 | 13:00
12 | Banani | 54 | 14:00 | 78 | Kachua | 98 | 20:00 | 144 | Rajbari | 93 | 00:00
13 | Bangabhaban | 17 | 11:00 | 79 | Kallyanpur | 123 | 00:00 | 145 | Rajendrapur | 139 | 19:30
14 | Barapukuria | 64 | 13:00 | 80 | Kalurghat | 40 | 10:00 | 146 | Rajshahi | 149 | 00:00
15 | Barguna | 24 | 00:00 | 81 | Kamrangirchar | 82.2 | 12:00 | 147 | Rajshahi-230 | 86 | 00:00
16 | Barishal | 124 | 22:00 | 82 | Kaptai | N/A | N/A | 148 | Ramganj | 110 | 18:30
17 | Barishal-230 | 118 | 00:00 | 83 | Kasba | 39 | 19:30 | 149 | Rampur | 44 | 00:00
18 | Baroaulia | 69 | 11:00 | 84 | Kazla | 104 | 00:00 | 150 | Rangamati | 17 | 18:30
19 | Baroirhat | 64 | 02:00 | 85 | Keranigonj | 86 | 19:00 | 151 | Rangpur | 151 | 13:00
20 | Bashundhara | 203 | 00:00 | 86 | Khagrachori | 30 | 13:00 | 152 | Ruppur | 7 | 16:00
21 | BashundharaCement | 6 | 00:00 | 87 | Khulna | 75 | 11:00 | 153 | SSM | 13 | 06:00
22 | Beanibazar | 75 | 08:00 | 88 | Khulshi | 187 | 15:00 | 154 | Saidpur | 115 | 14:00
23 | Benapole | 82 | 00:00 | 89 | Kishoreganj | 156 | 22:00 | 155 | Satkhira | 142 | 21:00
24 | Bhaluka | 154 | 19:30 | 90 | Kodda | 310 | 15:00 | 156 | Satmasjid | 107 | 21:00
25 | Bhandaria | 60 | 00:00 | 91 | Kulaura | 57 | 19:00 | 157 | Savar | 235 | 16:00
26 | Bhangura | 42 | 01:00 | 92 | Kurigram | 65 | 18:00 | 158 | SevenRings | 8.07 | 17:00
27 | Bheramara(GK) | 76 | 00:00 | 93 | Kushtia | 166 | 00:00 | 159 | ShahCement | 26 | 03:00
28 | Bhulta | 249 | 00:00 | 94 | Laksam | 34 | 19:00 | 160 | Shahjadpur | 90 | 20:00
29 | Bog-Sherpur | 76 | 00:00 | 95 | Lakshmipur | 38 | 19:00 | 161 | Shahjibazar | 136 | 03:00
30 | Bogura | 205 | 00:00 | 96 | Lalbag | 45 | 13:00 | 162 | Shahmirpur | 60 | 00:00
31 | Borhanuddin | 93 | 01:00 | 97 | Lalmonirhat | 70 | 07:00 | 163 | Shariatpur | 102 | 22:00
32 | Brahmanbaria | 153 | 01:00 | 98 | MI_Cement | 11.6 | 15:00 | 164 | Sherpur | 172 | 19:30
33 | Cantonment | 150 | 00:00 | 99 | Madanganj | 52 | 16:00 | 165 | Shikalbaha | 24 | 11:00
34 | Chandina | 42.8 | 19:30 | 100 | Madaripur | 122 | 00:00 | 166 | Shitalakhya | 88.4 | 16:00
35 | Chandpur | 88 | 20:00 | 101 | Madartek | 114 | 00:00 | 167 | Sholosohor | 50 | 16:00
36 | Chandraghona | 35 | 23:00 | 102 | Madunaghat | 59 | 14:00 | 168 | Shyampur | 180 | 16:00
37 | Chapai | 77 | 00:00 | 103 | Magura | 72 | 00:00 | 169 | Siddhirganj | 124 | 16:00
38 | Charsaidpur | 42 | 21:00 | 104 | Mahasthangarh | 106 | 00:00 | 170 | Sirajganj | 120 | 01:00
39 | Chauddagram | 76 | 21:00 | 105 | Maijdee | 21 | 06:00 | 171 | Sonargaon | 112 | 00:00
40 | Chhatak | 35 | 05:00 | 106 | Manikganj | 143 | 20:00 | 172 | Sreemongol | 77 | 01:00
41 | Chowmuhani | 186 | 22:00 | 107 | Maniknagar | 90 | 00:00 | 173 | Sreepur | 101 | 19:00
42 | Chuadanga | 122 | 00:00 | 108 | Matarbari | 51 | 00:00 | 174 | Srinagar | 54.68 | 23:00
43 | Coxsbazar | 133 | 19:30 | 109 | Matuail | 65 | 00:00 | 175 | Sunamganj | 53 | 09:00
44 | Cumilla(N) | 144 | 13:00 | 110 | Millgate | 118 | 15:00 | 176 | Sylhet | 55 | 17:00
45 | Cumilla(S) | 184 | 00:00 | 111 | Mirpur | 131 | 00:00 | 177 | Sylhet-132 | 150 | 21:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 12 | 15:00 | 178 | TK | 37 | 19:30
47 | Daudkandi | 152 | 19:30 | 113 | Mirzapur | 49 | 21:00 | 179 | Tangail | 194 | 22:00
48 | Dhaka | 80 | 13:00 | 114 | Mithapukur | 66 | 06:00 | 180 | Taraganj | 26 | 08:00
49 | Dhamrai | 130 | 19:30 | 115 | Modern | N/A | N/A | 181 | Thakurgaon | 110 | 21:00
50 | Dhanmondi | 155 | 13:00 | 116 | Mogbazar | 159.7 | 14:00 | 182 | Tongi | 134 | 00:00
51 | Dohazari | 115 | 19:30 | 117 | Mongla | 35 | 01:00 | 183 | Ullahpara | 42 | 00:00
52 | Faridpur | 174 | 21:00 | 118 | Motijheel | 46 | 13:00 | 184 | Ullon | 50 | 00:00
53 | Fatullah | 102 | 12:00 | 119 | Muktagacha | 43 | 22:00 | 185 | Uttara | 92 | 13:00
54 | Fenchuganj | 49 | 19:00 | 120 | Munshiganj | 124 | 00:00 | 186 | UttaraNew | 74 | 00:00
55 | Feni | 120 | 21:00 | 121 | Muradnagar | 44 | 19:30 | 187 | Zigatola | 79 | 00:00
56 | GPH | 97 | 15:00 | 122 | Mymensingh | 236 | 03:00
57 | Ghatail | 86 | 22:00 | 123 | Naogaon | 155 | 00:00
58 | Ghorashal | 13 | 00:00 | 124 | Narail | 65 | 00:00
59 | Ghorashal-230 | 91 | 00:00 | 125 | Narinda | 82 | 13:00
60 | Goalpara | 39 | 01:00 | 126 | Narshingdi | 186 | 00:00
61 | Gollamari | 102 | 00:00 | 127 | Natore | 173 | 00:00
62 | Gopalganj | 121 | 19:30 | 128 | Nawabganj | 65.8 | 00:00
63 | Gulshan | 138 | 13:00 | 129 | Netrakona | 139 | 05:00
64 | Halishahar | 86 | 16:00 | 130 | New | 84.6 | 15:00
65 | HaripurSBU | 150 | 12:00 | 131 | Niamatpur | 88 | 00:00
66 | Hasnabad | 100 | 00:00 | 132 | Noapara | 49 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 24-07-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 16364 | 321 |  | 16699.45
1:00 | 15602 | 277 |  | 15891.47
2:00 | 14964 | 198 |  | 15170.91
3:00 | 14277 | 185 |  | 14470.33
4:00 | 12983 | 155 |  | 13144.98
5:00 | 11752 | 122 |  | 11879.49
6:00 | 11503 | 114 |  | 11622.13
7:00 | 11547 | 101 |  | 11652.55
8:00 | 12007 | 0 |  | 12007
9:00 | 12297 | 0 |  | 12297
10:00 | 12837 | 0 |  | 12837
11:00 | 13444 | 0 |  | 13444
12:00 | 14124 | 0 |  | 14124
13:00 | 14648 | 0 |  | 14648
14:00 | 14774.59 | 0 |  | 14774.59
15:00 | 14929.48 | 0 |  | 14929.48
16:00 | 14883.75 | 76 |  | 14963.17
17:00 | 14496.1 | 65 |  | 14564.03
18:00 | 13986.87 | 64 |  | 14053.87
19:00 | 15163.85 | 179 |  | 15350.85
19:30 | 15702.33 | 152 |  | 15861.33
20:00 | 15732.19 | 161 |  | 15900.19
21:00 | 15410.5 | 181 |  | 15599.5
22:00 | 14554.27 | 187 |  | 14749.27
23:00 | 14876.76 | 166 |  | 15049.76
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 24-07-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8980 | 7384 | 16364 | DAILY GENERATION CURVE
00:30 | 8720 | 7263 | 15983
01:00 | 8460 | 7142 | 15602 | 24-07-2025
01:30 | 8169.5 | 7113.5 | 15283
02:00 | 7879 | 7085 | 14964
02:30 | 7664.5 | 6956 | 14620.5
03:00 | 7450 | 6827 | 14277
03:30 | 7101.5 | 6528.5 | 13630
04:00 | 6753 | 6230 | 12983
04:30 | 6408.5 | 5959 | 12367.5
05:00 | 6064 | 5688 | 11752
05:30 | 6000 | 5627.5 | 11627.5
06:00 | 5936 | 5567 | 11503
06:30 | 5864.5 | 5660.5 | 11525
07:00 | 5793 | 5754 | 11547
07:30 | 5971 | 5806 | 11777
08:00 | 6149 | 5858 | 12007
08:30 | 6306 | 5846 | 12152
09:00 | 6463 | 5834 | 12297
09:30 | 6712.5 | 5854.5 | 12567
10:00 | 6962 | 5875 | 12837
10:30 | 7140.5 | 6000 | 13140.5
11:00 | 7319 | 6125 | 13444
11:30 | 7478 | 6306 | 13784
12:00 | 7637 | 6487 | 14124
12:30 | 7821.5 | 6564.5 | 14386
13:00 | 8006 | 6642 | 14648
13:30 | 8040.385 | 6670.91 | 14711.295
14:00 | 8074.77 | 6699.82 | 14774.59
14:30 | 8097.435 | 6754.6 | 14852.035
15:00 | 8120.1 | 6809.38 | 14929.48
15:30 | 8087.155 | 6819.46 | 14906.615
16:00 | 8054.21 | 6829.54 | 14883.75
16:30 | 8019.485 | 6670.44 | 14689.925
17:00 | 7984.76 | 6511.34 | 14496.1
17:30 | 7924.65 | 6316.835 | 14241.485
18:00 | 7864.54 | 6122.33 | 13986.87
18:30 | 8214.87 | 6360.49 | 14575.36
19:00 | 8565.2 | 6598.65 | 15163.85
19:30 | 8629.7 | 7072.63 | 15702.33
20:00 | 8554.5 | 7177.69 | 15732.19
20:30 | 8348.25 | 7223.095 | 15571.345 |  | Executive Engineer
21:00 | 8142 | 7268.5 | 15410.5 |  | Network Operation Division
21:30 | 7872.5 | 7109.885 | 14982.385
22:00 | 7603 | 6951.27 | 14554.27
22:30 | 7721 | 6994.515 | 14715.515
23:00 | 7839 | 7037.76 | 14876.76

## En-Curve
QF-LDC-12
Date | 24-07-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3719 | 1989 | 860 | 38 | 58 | 1443 | 220 | 4887 | 0 | 693 | 2447 | 0 | 0 | 10 | 321 | DAILY ENERGY CURVE
00:30 | 3643 | 1973 | 860 | 38 | 52 | 1442 | 219 | 4841.5 | 0 | 627 | 2282 | 0 | 0 | 5.5 | 299 | 24-07-2025
01:00 | 3567 | 1957 | 860 | 38 | 46 | 1441 | 218 | 4796 | 0 | 561 | 2117 | 0 | 0 | 1 | 277
01:30 | 3610.5 | 1971 | 859.5 | 38 | 48 | 1442.5 | 218 | 4827 | 0 | 527.5 | 1740.5 | 0 | 0 | 0.5 | 237.5 | Energy Generated | 339.2316 |  | MKWHr
02:00 | 3654 | 1985 | 859 | 38 | 50 | 1444 | 218 | 4858 | 0 | 494 | 1364 | 0 | 0 | 0 | 198 | Energy not Served | 2.552 |  | MKWHr
02:30 | 3654.5 | 1975.5 | 859 | 38 | 49 | 1414 | 218 | 4780 | 0 | 416 | 1216.5 | 0 | 0 | 0 | 191.5 | Total Energy Requirement | 341.7836 |  | MKWHr
03:00 | 3655 | 1966 | 859 | 38 | 48 | 1384 | 218 | 4702 | 0 | 338 | 1069 | 0 | 0 | 0 | 185
03:30 | 3566.5 | 1907.5 | 859.5 | 38 | 48 | 1246.5 | 218 | 4443 | 0 | 324 | 979 | 0 | 0 | 0 | 170
04:00 | 3478 | 1849 | 860 | 38 | 48 | 1109 | 218 | 4184 | 0 | 310 | 889 | 0 | 0 | 0 | 155
04:30 | 3365.5 | 1762 | 860 | 38 | 48 | 1060 | 218 | 3944 | 0 | 239.5 | 832.5 | 0 | 0 | 0 | 138.5
05:00 | 3253 | 1675 | 860 | 38 | 48 | 1011 | 218 | 3704 | 0 | 169 | 776 | 0 | 0 | 0 | 122
05:30 | 3313 | 1680.5 | 859.5 | 38 | 47 | 1007 | 218 | 3630.5 | 7.5 | 109.5 | 715 | 0 | 0 | 2 | 118
06:00 | 3373 | 1686 | 859 | 38 | 46 | 1003 | 218 | 3557 | 15 | 50 | 654 | 0 | 0 | 4 | 114
06:30 | 3438 | 1708.5 | 855.5 | 38 | 45 | 1021 | 218 | 3572.5 | 38 | 34 | 552.5 | 0 | 0 | 4 | 107.5
07:00 | 3503 | 1731 | 852 | 38 | 44 | 1039 | 218 | 3588 | 61 | 18 | 451 | 0 | 0 | 4 | 101
07:30 | 3626.5 | 1834.5 | 852 | 38 | 42 | 1045.5 | 218.5 | 3584 | 80 | 25 | 428.5 | 0 | 0 | 2.5 | 50.5
08:00 | 3750 | 1938 | 852 | 38 | 40 | 1052 | 219 | 3580 | 99 | 32 | 406 | 0 | 0 | 1 | 0
08:30 | 3740 | 1944 | 852 | 38 | 42 | 1018 | 219.5 | 3630.5 | 145.5 | 49.5 | 472.5 | 0 | 0 | 0.5 | 0
09:00 | 3730 | 1950 | 852 | 38 | 44 | 984 | 220 | 3681 | 192 | 67 | 539 | 0 | 0 | 0 | 0
09:30 | 3749.5 | 1934.5 | 851.5 | 38 | 34 | 904.5 | 220 | 3849.5 | 241.5 | 84.5 | 659.5 | 0 | 0 | 0 | 0
10:00 | 3769 | 1919 | 851 | 38 | 24 | 825 | 220 | 4018 | 291 | 102 | 780 | 0 | 0 | 0 | 0
10:30 | 3733 | 1928 | 851 | 38 | 25 | 823 | 220 | 4126.5 | 340.5 | 123.5 | 932 | 0 | 0 | 0 | 0
11:00 | 3697 | 1937 | 851 | 38 | 26 | 821 | 220 | 4235 | 390 | 145 | 1084 | 0 | 0 | 0 | 0
11:30 | 3719.5 | 1950 | 851.5 | 38 | 26 | 872 | 220 | 4272.5 | 444 | 159 | 1231.5 | 0 | 0 | 0 | 0
12:00 | 3742 | 1963 | 852 | 38 | 26 | 923 | 220 | 4310 | 498 | 173 | 1379 | 0 | 0 | 0 | 0
12:30 | 3736 | 1961 | 851.5 | 38 | 24 | 951.5 | 219 | 4311 | 534.5 | 198.5 | 1559 | 0 | 0 | 2 | 0
13:00 | 3730 | 1959 | 851 | 38 | 22 | 980 | 218 | 4312 | 571 | 224 | 1739 | 0 | 0 | 4 | 0
13:30 | 3711.5 | 1929.5 | 853.5 | 38 | 14 | 1066.145 | 217.5 | 4298.5 | 529.8 | 243 | 1807.85 | 0 | 0 | 2 | 0
14:00 | 3693 | 1900 | 856 | 38 | 6 | 1152.29 | 217 | 4285 | 488.6 | 262 | 1876.7 | 0 | 0 | 0 | 0
14:30 | 3713 | 1804.75 | 856 | 38 | 6 | 1185.105 | 217 | 4373 | 422.98 | 289 | 1941.7 | 0 | 0 | 5.5 | 0
15:00 | 3733 | 1709.5 | 856 | 38 | 6 | 1217.92 | 217 | 4461 | 357.36 | 316 | 2006.7 | 0 | 0 | 11 | 0
15:30 | 3725.5 | 1634.25 | 856 | 38 | 20 | 1229.605 | 217 | 4511.5 | 275.06 | 320 | 2062.2 | 0 | 0 | 17.5 | 38
16:00 | 3718 | 1559 | 856 | 38 | 34 | 1241.29 | 217 | 4562 | 192.76 | 324 | 2117.7 | 0 | 0 | 24 | 76
16:30 | 3702 | 1615.75 | 856 | 38 | 34 | 1251.015 | 217.5 | 4463 | 156.21 | 325.5 | 2018.95 | 0 | 0 | 12 | 70.5
17:00 | 3686 | 1672.5 | 856 | 38 | 34 | 1260.74 | 218 | 4364 | 119.66 | 327 | 1920.2 | 0 | 0 | 0 | 65
17:30 | 3524 | 1763.5 | 855.5 | 38 | 32 | 1259.265 | 218 | 4222.5 | 79.52 | 332 | 1899.2 | 0 | 0 | 18 | 64.5
18:00 | 3362 | 1854.5 | 855 | 38 | 30 | 1257.79 | 218 | 4081 | 39.38 | 337 | 1878.2 | 0 | 0 | 36 | 64
18:30 | 3496 | 1836.25 | 855.5 | 38 | 33 | 1312.62 | 219 | 4133.5 | 19.69 | 448 | 2158.8 | 0 | 0 | 25 | 121.5
19:00 | 3630 | 1818 | 856 | 38 | 36 | 1367.45 | 220 | 4186 | 0 | 559 | 2439.4 | 0 | 0 | 14 | 179
19:30 | 3633 | 1858 | 855 | 38 | 36 | 1423.43 | 220 | 4453 | 0 | 647 | 2501.9 | 0 | 0 | 37 | 152
20:00 | 3689 | 1930 | 856 | 38 | 26 | 1431.69 | 220 | 4554 | 0 | 658 | 2268.5 | 0 | 0 | 61 | 161
20:30 | 3689 | 1930 | 856 | 38 | 29 | 1433.095 | 220 | 4648 | 0 | 635.5 | 2032.75 | 0 | 0 | 60 | 171
21:00 | 3689 | 1930 | 856 | 38 | 32 | 1434.5 | 220 | 4742 | 0 | 613 | 1797 | 0 | 0 | 59 | 181
21:30 | 3602.5 | 1919 | 856 | 38 | 32 | 1438.385 | 219 | 4660.5 | 0 | 535.5 | 1629.5 | 0 | 0 | 52 | 184
22:00 | 3516 | 1908 | 856 | 38 | 32 | 1442.27 | 218 | 4579 | 0 | 458 | 1462 | 0 | 0 | 45 | 187
22:30 | 3610 | 2007 | 854.5 | 38 | 32 | 1441.515 | 217 | 4610.5 | 0 | 441 | 1419.5 | 0 | 0 | 44.5 | 176.5
23:00 | 3704 | 2106 | 853 | 38 | 32 | 1440.76 | 216 | 4642 | 0 | 424 | 1377 | 0 | 0 | 44 | 166
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 24-07-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 392 | 05:00 | 367 | 15:00 | Payra | 417 | 05:00 | 409 | 00:00
Ashuganj | 410 | 5:00 | 382 | 15:00 | Rahanpur | 409 | 09:00 | 385 | 23:00
Bhulta | 412 | 04:00 | 368 | 15:00 | Rampal | 411 | 05:00 | 392 | 16:00
Bibiana | 392 | 05:00 | 374 | 15:00
BIPTC | 402 | 06:00 | 390 | 00:00
Bogura | 393 | 09:00 | 364 | 22:00
Gopalganj | 404 | 05:00 | 385 | 15:00
Kaliakoir | 388 | 05:00 | 359 | 12:00
Madunaghat | 394 | 06:00 | 384 | 15:00
Meghnaghat | 393 | 05:00 | 371 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 230 | 06:00 | 212 | 15:00 | Keranigonj | 228 | 05:00 | 210 | 15:00
AKSML | 232 | 20:00 | 222 | 11:00 | Khulna(S) | 233 | 06:00 | 217 | 17:00
Aminbazar | 230 | 05:00 | 214 | 12:00 | Madunaghat | 233 | 19:00 | 225 | 23:00
Ashuganj | 237 | 04:00 | 218 | 15:00 | Madunaghat-400 | 233 | 20:00 | 226 | 11:00
Ashuganj-400 | 236 | 5:00 | 220 | 15:00 | Maniknagar | 226 | 04:00 | 208 | 12:00
Baghabari | 234 | 07:00 | 225 | 15:00 | Meghnaghat | 233 | 05:00 | 217 | 12:00
Barapukuria | 223 | 09:00 | 205 | 00:00 | Meghnaghat-400 | 230 | 05:00 | 213 | 15:00
Barapukuria-230 | 223 | 9:00 | 210 | 23:00 | Mirsorai | 232 | 19:30 | 218 | 11:00
Barishal | 232 | 05:00 | 219 | 00:00 | Rajshahi | 231 | 09:00 | 220 | 00:00
Bheramara | 233 | 04:00 | 222 | 15:00 | Rampal | 234 | 05:00 | 219 | 00:00
Bhulta | 238 | 04:00 | 208 | 15:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 233 | 06:00 | 217 | 15:00 | Rampura | 238 | 05:00 | 207 | 15:00
BIPTC | 236 | 04:00 | 222 | 16:00 | Shikalbaha | 231 | 19:30 | 222 | 11:00
Bogura | 238 | 09:00 | 222 | 02:00 | Shyampur | 228 | 05:00 | 210 | 15:00
Bogura-400 | 238 | 09:00 | 222 | 00:00 | Siddhirganj | 231 | 04:00 | 210 | 12:00
Borhanuddin | 235 | 05:00 | 226 | 00:00 | Sirajgonj | 239 | 04:00 | 233 | 15:00
BSRM | 230 | 19:00 | 218 | 11:00 | Sreepur | 234 | 05:00 | 217 | 15:00
Cumilla(N) | 222 | 06:00 | 212 | 11:00 | Tongi | 236 | 04:00 | 211 | 12:00
Faridpur | 230 | 06:00 | 215 | 00:00
Fenchuganj | 233 | 06:00 | 217 | 14:00
Ghorashal | 230 | 22:00 | 220 | 13:00
Ghorashal-230 | 233 | 04:00 | 211 | 15:00
Gopalganj | 231 | 06:00 | 218 | 00:00
GPH | 231 | 19:30 | 221 | 11:00
Haripur | 228 | 05:00 | 209 | 15:00
Hasnabad | 223 | 03:00 | 211 | 12:00
Hathazari | 233 | 09:00 | 219 | 11:00
Ishurdi | 235 | 04:00 | 224 | 15:00
Jhenaidah | 231 | 04:00 | 216 | 00:00
Kaliakoir | 241 | 05:00 | 218 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 141 | 04:00 | 123 | 13:00 | Lalmonirhat | 127 | 09:00 | 113 | 05:00
Agargaon | 135 | 06:00 | 122 | 15:00 | Madanganj | 130 | 07:00 | 121 | 11:00
Agrabad | 131 | 19:30 | 124 | 11:00 | Madaripur | 134 | 08:00 | 128 | 00:00
AKS | 129 | 18:00 | 124 | 10:00 | Madartek | 139 | 05:00 | 121 | 15:00
Aminbazar | 135 | 06:00 | 126 | 11:00 | Madunaghat | 133 | 14:00 | 127 | 23:00
Amnura | 139 | 10:00 | 128 | 21:00 | Magura | 136 | 09:00 | 123 | 00:00
Ashuganj | 144 | 05:00 | 133 | 15:00 | Mahasthangarh | 140 | 09:00 | 125 | 02:00
Bagerhat | 137 | 06:00 | 119 | 00:00 | Maijdee | 126 | 20:00 | 108 | 15:00
Bajitpur | 135 | 05:00 | 122 | 00:00 | Manikganj | 133 | 06:00 | 115 | 21:00
Bakulia | 132 | 06:00 | 126 | 23:00 | Maniknagar | 136 | 05:00 | 122 | 12:00
Banani | 142 | 04:00 | 122 | 15:00 | Matarbari | 120 | 13:00 | 111 | 23:00
Bangabhaban | 135 | 05:00 | 121 | 12:00 | Matuail | 135 | 05:00 | 121 | 12:00
Barapukuria | 136 | 09:00 | 122 | 01:00 | Millgate | 137 | 04:00 | 121 | 11:00
Barguna | 135 | 07:00 | 129 | 00:00 | Mirpur | 134 | 05:00 | 124 | 15:00
Barishal | 137 | 06:00 | 126 | 00:00 | Mirzapur | 136 | 05:00 | 123 | 21:00
Barishal-230 | 137 | 05:00 | 126 | 00:00 | Mithapukur | 133 | 09:00 | 119 | 00:00
Baroaulia | 132 | 19:00 | 127 | 11:00 | MI_Cement | 138 | 05:00 | 121 | 12:00
Baroirhat | 127 | 20:00 | 116 | 11:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 142 | 04:00 | 121 | 10:00 | Mogbazar | 143 | 05:00 | 123 | 15:00
BashundharaCement | 129 | 06:00 | 114 | 01:00 | Mongla | 135 | 06:00 | 120 | 00:00
Beanibazar | 130 | 06:00 | 115 | 13:00 | Motijheel | 135 | 05:00 | 121 | 12:00
Benapole | 134 | 06:00 | 116 | 00:00 | Muktagacha | 138 | 07:00 | 127 | 00:00
Bhaluka | 134 | 05:00 | 120 | 15:00 | Munshiganj | 132 | 06:00 | 120 | 12:00
Bhandaria | 129 | 08:00 | 117 | 00:00 | Muradnagar | 128 | 05:00 | 116 | 15:00
Bhangura | 135 | 08:00 | 127 | 20:00 | Mymensingh | 137 | 07:00 | 110 | 21:00
Bheramara | 136 | 04:00 | 130 | 20:00 | Naogaon | 139 | 09:00 | 121 | 00:00
Bheramara(GK) | 136 | 09:00 | 130 | 00:00 | Narail | 138 | 04:00 | 123 | 00:00
Bhulta | 127 | 06:00 | 115 | 15:00 | Narinda | 136 | 5:00 | 122 | 12:00
Bog-Sherpur | 138 | 09:00 | 127 | 01:00 | Narshingdi | 143 | 04:00 | 116 | 12:00
Bogura | 141 | 09:00 | 130 | 01:00 | Natore | 136 | 09:00 | 127 | 16:00
Bogura-230 | 141 | 09:00 | 130 | 02:00 | Nawabganj | 138 | 05:00 | 124 | 12:00
Brahmanbaria | 137 | 04:00 | 126 | 00:00 | Netrakona | 126 | 06:00 | 107 | 21:00
Cantonment | 135 | 05:00 | 122 | 15:00 | New | 137 | 05:00 | 122 | 12:00
Chandina | 129 | 04:00 | 120 | 11:00 | Niamatpur | 160 | 21:00 | 129 | 23:00
Chandpur | 130 | 20:00 | 117 | 08:00 | Noapara | 136 | 06:00 | 122 | 00:00
Chandraghona | 133 | 19:00 | 128 | 11:00 | Pabna | 134 | 07:00 | 127 | 02:00
Chapai | 139 | 10:00 | 128 | 23:00 | Palashbari | 139 | 09:00 | 118 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 134 | 05:00 | 121 | 12:00 | Panchagarh | 133 | 10:00 | 122 | 00:00
Chauddagram | 127 | 20:00 | 115 | 11:00 | Patuakhali | 135 | 06:00 | 130 | 01:00
Chhatak | 125 | 06:00 | 111 | 17:00 | Payra | 137 | 06:00 | 134 | 00:00
Chowmuhani | 125 | 20:00 | 110 | 11:00 | PHP | 126 | 20:00 | 114 | 15:00
Chuadanga | 134 | 09:00 | 121 | 00:00 | Postogola | 135 | 04:00 | 124 | 12:00
Coxsbazar | 122 | 16:00 | 112 | 23:00 | Purbachal | 141 | 04:00 | 121 | 15:00
Cumilla(N) | 128 | 05:00 | 120 | 11:00 | Purbasadipur | 130 | 10:00 | 116 | 00:00
Cumilla(S) | 133 | 18:00 | 118 | 11:00 | Rahanpur | 141 | 10:00 | 134 | 03:00
Daganbhuiyan | 126 | 20:00 | 111 | 11:00 | Rahanpur-400 | 141 | 10:00 | 132 | 21:00
Daudkandi | 128 | 05:00 | 114 | 15:00 | Rahim | 135 | 05:00 | 121 | 12:00
Dhaka | 141 | 04:00 | 123 | 15:00 | Rajbari | 136 | 06:00 | 125 | 00:00
Dhamrai | 140 | 05:00 | 122 | 15:00 | Rajendrapur | 140 | 05:00 | 120 | 11:00
Dhanmondi | 142 | 04:00 | 123 | 12:00 | Rajshahi | 134 | 08:00 | 126 | 00:00
Dohazari | 128 | 18:00 | 122 | 10:00 | Rajshahi-230 | 134 | 09:00 | 128 | 22:00
Faridpur | 136 | 05:00 | 127 | 00:00 | Ramganj | 127 | 20:00 | 111 | 11:00
Fatullah | 136 | 05:00 | 122 | 12:00 | Rampur | 132 | 19:30 | 125 | 10:00
Fenchuganj | 138 | 06:00 | 126 | 17:00 | Rampura | 144 | 05:00 | 122 | 15:00
Feni | 125 | 20:00 | 113 | 11:00 | Rangamati | 133 | 19:30 | 127 | 11:00
Ghatail | 135 | 07:00 | 122 | 21:00 | Rangpur | 131 | 09:00 | 116 | 00:00
Ghorashal | 137 | 22:00 | 127 | 13:00 | Ruppur | 137 | 08:00 | 131 | 19:00
Goalpara | 141 | 06:00 | 125 | 00:00 | Saidpur | 130 | 09:00 | 118 | 00:00
Gollamari | 140 | 06:00 | 127 | 00:00 | Satkhira | 138 | 06:00 | 119 | 00:00
Gopalganj | 138 | 06:00 | 126 | 00:00 | Satmasjid | 134 | 05:00 | 123 | 14:00
Gopalganj-400 | 139 | 06:00 | 130 | 00:00 | Savar | 132 | 05:00 | 124 | 23:00
Gulshan | 140 | 05:00 | 123 | 15:00 | SevenRings | 141 | 05:00 | 127 | 15:00
Halishahar | 134 | 19:30 | 124 | 16:00 | ShahCement | 134 | 05:00 | 121 | 12:00
Haripur | 134 | 04:00 | 121 | 15:00 | Shahjadpur | 135 | 07:00 | 131 | 00:00
HaripurSBU | 134 | 04:00 | 121 | 15:00 | Shahjibazar | 137 | 05:00 | 125 | 15:00
Hasnabad | 137 | 04:00 | 123 | 12:00 | Shahmirpur | 133 | 19:00 | 127 | 09:00
Hathazari | 135 | 19:30 | 127 | 10:00 | Shariatpur | 138 | 06:00 | 127 | 00:00
Ishurdi | 137 | 04:00 | 131 | 00:00 | Sherpur | 138 | 07:00 | 123 | 08:00
Jaldhaka | 127 | 09:00 | 112 | 00:00 | Shikalbaha | 123 | 19:30 | 117 | 11:00
Jamalpur | 140 | 16:00 | 128 | 03:00 | Shikalbaha-230 | 134 | 19:30 | 127 | 11:00
Jashore | 136 | 06:00 | 120 | 00:00 | Shitalakhya | 138 | 05:00 | 121 | 12:00
Jhenaidah | 137 | 08:00 | 119 | 00:00 | Sholosohor | 132 | 06:00 | 126 | 11:00
Jhenaidah-230 | 138 | 06:00 | 126 | 00:00 | Shyampur | 133 | 04:00 | 121 | 13:00
Joydebpur | 141 | 04:00 | 124 | 10:00 | Shyampur-230 | 135 | 05:00 | 122 | 12:00
Joypurhat | 139 | 09:00 | 117 | 01:00 | Siddhirganj | 135 | 05:00 | 122 | 12:00
Juldah | 133 | 19:00 | 127 | 10:00 | Sirajganj | 135 | 09:00 | 126 | 00:00
Kabirpur | 138 | 05:00 | 117 | 15:00 | Sonargaon | 134 | 04:00 | 118 | 12:00
Kachua | 131 | 21:00 | 116 | 11:00 | Sreemongol | 134 | 05:00 | 124 | 13:00
Kaliakoir | 139 | 05:00 | 125 | 12:00 | Sreepur | 138 | 05:00 | 124 | 15:00
Kallyanpur | 136 | 04:00 | 125 | 16:00 | Srinagar | 139 | 05:00 | 124 | 13:00
Kalurghat | 132 | 18:30 | 128 | 03:00 | SSM | 135 | 20:00 | 130 | 11:00
Kamrangirchar | 138 | 05:00 | 124 | 12:00 | Sunamganj | 124 | 06:00 | 110 | 17:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 129 | 06:00 | 116 | 17:00
Kasba | 127 | 04:00 | 116 | 15:00 | Sylhet-132 | 128 | 06:00 | 117 | 17:00
Kazla | 136 | 05:00 | 121 | 13:00 | Tangail | 134 | 06:00 | 120 | 21:00
Keranigonj | 139 | 05:00 | 125 | 12:00 | Taraganj | 130 | 09:00 | 118 | 00:00
Khagrachori | 132 | 19:30 | 126 | 11:00 | Thakurgaon | 132 | 10:00 | 120 | 00:00
Khulna | 138 | 06:00 | 124 | 00:00 | TK | 131 | 05:00 | 127 | 10:00
Khulna(S) | 140 | 06:00 | 127 | 00:00 | Tongi | 140 | 04:00 | 123 | 12:00
Khulshi | 131 | 19:30 | 124 | 10:00 | Ullahpara | 135 | 08:00 | 128 | 00:00
Kishoreganj | 130 | 05:00 | 118 | 19:00 | Ullon | 140 | 05:00 | 122 | 15:00
Kodda | 137 | 04:00 | 121 | 10:00 | Uttara | 136 | 05:00 | 124 | 15:00
KSRM | 132 | 19:00 | 126 | 10:00 | UttaraNew | 132 | 04:00 | 124 | 23:00
Kulaura | 137 | 06:00 | 125 | 15:00 | Zigatola | 138 | 05:00 | 125 | 13:00
Kurigram | 128 | 10:00 | 115 | 00:00
Kushtia | 133 | 09:00 | 124 | 00:00
Laksam | 131 | 21:00 | 116 | 11:00
Lakshmipur | 126 | 20:00 | 109 | 15:00
Lalbag | 138 | 05:00 | 124 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division