## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 26-07-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 25-07-2025 | during | 26-07-2025 | during | 26-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 0 | 0 | 0 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 280 | 310 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 75 | 196 | 208.13 | 208.13 | 196 | 196 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 7 | 7 | 48 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 32 | 0 | 53.97 | 53.97 | 48 | 48 | FGMO
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 138 | 138 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19 | 19 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 20 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 8 | 52.19 | 52.19 | 16 | 32 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 277 | 277 | Engine Problem
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 32 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 88 | 88 | 105 | 105
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 16 | 16 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 21 | 0 | 0 | 0 | 0 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 35 | 35 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 0 | 0 | 0 | 0 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 724 | 727 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 90 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 1574 | 1855 | 3742.45 | 3742.45 | 2803.5 | 2860.5
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 5 | 0 | 5 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 220 | 221 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 218 | 213 | 213 | 213 | 213 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 7 | 0 | 56 | 72 | 48 | 72 | Machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 33 | 65 | 65 | 50 | 50 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 0 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 35 | 35 | 2 | 25 | 2 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 12 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.84 | 0 | 2.48 | 0 | 2.48 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 700 | 1000 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 65 | 28 | 40 | 35 | 40 | 35 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 606 | 781 | 790 | 790 | 790 | 790 | Machine Problem
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1921.84 | 2316 | 3836.2 | 3862.72 | 3813.2 | 3847.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 184 | 202 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 300 | 347 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 280 | 340 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 31 | 35 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 45 | 49 | 55 | 55 | 51 | 51 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 25 | 87 | 195 | 195 | 100 | 100 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 0 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 51 | 51 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 128 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 24 | 44 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 18 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 38 | 46 | 113 | 113 | 65 | 65 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 16 | 48 | 115 | 115 | 95 | 95 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 31 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1060 | 1445 | 2434.56 | 2379.56 | 2114.06 | 2059.06
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 25-07-2025 | during | 26-07-2025 | during | 26-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 86 | 150 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 85 | 200 | 200 | 200 | 160 | 160 | Engine Problem
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 8 | 0 | 115 | 115 | 100 | 100 | Engine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 32.03 | 0 | 34.35 | 0 | 34.35 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 0 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 35 | 35 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 241.03 | 367 | 585.45 | 549 | 500.95 | 464.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 58 | 57 | 70 | 70 | 60 | 60 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 156 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 11 | 81 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 17 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | Plant Shutdown as per schedule HGPI work
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 316 | 388 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | Aythority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 891 | 1057 | 1097 | 1097 | 1026 | 1026
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 852 | 853 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 197 | 304 | 410 | 410 | 310 | 310 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 60 | 60 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 27 | 0 | 40 | 0 | 40 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 736 | 1055 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1850 | 2250 | 3594.2 | 3554.2 | 3447.2 | 3407.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 300 | 334 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 105 | 117 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 600 | 860 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 165 | 279 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.23 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1350.23 | 1810 | 2162 | 2161 | 2152 | 2151
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 140 | 177 | 214 | 214 | 200 | 200 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 192 | 220 | 220 | 200 | 200 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 197 | 220 | 220 | 220 | 220
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 280 | 407 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 8 | 96 | 96 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.9 | 0 | 3.6 | 0 | 3.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 833.15 | 1208 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 34.08 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 21 | 0 | 90 | 0 | 90 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 1591.13 | 2189 | 3181.47 | 3026.87 | 3105.09 | 2950.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 47 | 45 | 47 | 47 | 48 | 48 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 105 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.9 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 114 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 11 | 0 | 20 | 0 | 20 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 101 | 0 | 147.42 | 0 | 147.42 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 230.9 | 264 | 483.02 | 309 | 484.02 | 310
System Total |  |  |  |  | 28565.2 | 27045.875 | 10710.13 | 13553 | 21116.35 | 20681.8 | 19446.02 | 19076.47
Forecast Scenario (26-07-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13400 |  | 0 |  | 13400
|  |  |  | 1:00 | 12930 |  | 0 |  | 12930
|  |  |  | 2:00 | 12590 |  | 0 |  | 12590
|  |  |  | 3:00 | 12260 |  | 0 |  | 12260
|  |  |  | 4:00 | 11950 |  | 0 |  | 11950
|  |  |  | 5:00 | 11770 |  | 0 |  | 11770
|  |  |  | 6:00 | 11250 |  | 0 |  | 11250
|  |  |  | 7:00 | 11160 |  | 0 |  | 11160
|  |  |  | 8:00 | 11160 |  | 0 |  | 11160
|  |  |  | 9:00 | 12330 |  | 0 |  | 12330
|  |  |  | 10:00 | 12290 |  | 0 |  | 12290
|  |  |  | 11:00 | 12350 |  | 0 |  | 12350
|  |  |  | 12:00 | 13040 |  | 0 |  | 13040
|  |  |  | 13:00 | 13390 |  | 0 |  | 13390
|  |  |  | 14:00 | 13030 |  | 0 |  | 13030
|  |  |  | 15:00 | 13610 |  | 0 |  | 13610
|  |  |  | 16:00 | 13700 |  | 0 |  | 13700
|  |  |  | 17:00 | 13310 |  | 0 |  | 13310
|  |  |  | 18:00 | 12980 |  | 0 |  | 12980
|  |  |  | 18:30 | 13500 |  | 0 |  | 13500
|  |  |  | 19:00 | 14290 |  | 0 |  | 14290
|  |  |  | 19:30 | 15330 |  | 0 |  | 15330
|  |  |  | 20:00 | 15410 |  | 0 |  | 15410
|  |  |  | 21:00 | 15530 |  | 0 |  | 15530
|  |  |  | 22:00 | 15480 |  | 0 |  | 15480
|  |  |  | 23:00 | 15450 |  | 0 |  | 15450
Probable Maximum Temperature: |  |  | 32.40°C
Probable Maximum Demand at Day Peak: |  |  | 13040.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 15530.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14530.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 299.66 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:22 hrs on 26-07-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 25-07-2025 | [28 empty] | Date: | 25-07-2025 | [28 empty] | Date: | 25-07-2025 | [28 empty] | Date: | 25-07-2025 | [28 empty] | Date: | 25-07-2025 | [11 empty] | Date: | 25-07-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [11 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 68 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 721 | 0 | 0.36 | 57 | 79 | 0 | 0 | 24 | 73 | 0 | 360 | 305 | 0 | 0 | 0 | 300 | 135 | 0 | 0 | 108 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 50 | 7 | 0 | 11 | 25 | 0 | 216 | 0 | 32 | 780 | 0 | 0 | 26 | 8 | 0 | 217 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 81 | 0 | 352 | 340 | 47 | 181 | 37 | 63 | 50 | 181 | 64 | 19 | 90 | 34 | 25 | 0 | 0 | 0 | 320 | 312 | 0 | 58 | 139 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 35 | 92 | 200 | 80 | 0 | 0 | 12 | 7802.36 | 852 | 149 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1186 | 17 | 1443.11 | 0 | 32 | 0 | 113 | 113 | 0 | 42 | 0 | 0 | 0 | 28 | 0 | 195 | 0 | 173 | 0 | 172 | 0 | 342 | 0 | 0 | 0 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 267 | 117 | 220 | 0 | 300 | 1100 | 0 | 7173.11 | 14975.47 | 102.82
01:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 721 | 28 | 18 | 57 | 79 | 0 | 4 | 35 | 94 | 0 | 450 | 310 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 108 | 20.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 50 | 7 | 0 | 11 | 25 | 0 | 216 | 0 | 32 | 716 | 0 | 0 | 26 | 8 | 0 | 217 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 81 | 0 | 348 | 340 | 47 | 198 | 34 | 68 | 50 | 167 | 55 | 19 | 76 | 30 | 37 | 0 | 0 | 0 | 320 | 333 | 0 | 58 | 131 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 21 | 65 | 125 | 80 | 0 | 0 | 12 | 7575.2 | 853 | 150 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1206 | 17 | 1369.5 | 0 | 31 | 0 | 113 | 113 | 0 | 42 | 0 | 0 | 0 | 28 | 0 | 170 | 0 | 172 | 0 | 140 | 0 | 352 | 0 | 0 | 0 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 117 | 180 | 0 | 301 | 1100 | 0 | 7045.5 | 14620.7 | 102.86
02:00 | 7 | 69 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 46 | 32 | 57 | 79 | 0 | 45 | 35 | 95 | 0 | 450 | 307 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 108 | 21.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 50 | 7 | 0 | 11 | 12 | 0 | 215 | 0 | 32 | 716 | 0 | 0 | 26 | 8 | 0 | 217 | 0 | 0 | 0 | 1070 | 0 | 51 | 0 | 81 | 0 | 349 | 340 | 47 | 193 | 34 | 79 | 50 | 197 | 55 | 19 | 77 | 28 | 52.2 | 0 | 0 | 0 | 320 | 337 | 0 | 58 | 132 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 65 | 125 | 80 | 0 | 0 | 12 | 7661.4 | 852 | 155 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1206 | 17 | 1358.39 | 0 | 0 | 0 | 35 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 176 | 0 | 140 | 0 | 344 | 0 | 0 | 0 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 117 | 180 | 0 | 301 | 1110 | 0 | 6821.39 | 14482.79 | 102.9
03:00 | 7 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 721 | 46 | 36 | 57 | 48 | 0 | 55 | 35 | 98 | 0 | 450 | 306 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 108 | 21.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 50 | 7 | 0 | 11 | 25 | 0 | 215 | 0 | 32 | 716 | 0 | 0 | 26 | 0 | 0 | 217 | 0 | 0 | 0 | 1090 | 0 | 51 | 0 | 81 | 0 | 348 | 285 | 47 | 193 | 34 | 90 | 50 | 199 | 54 | 19 | 77 | 28 | 52.2 | 0 | 0 | 0 | 320 | 340 | 0 | 58 | 134 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 65 | 125 | 81 | 0 | 0 | 12 | 7627.4 | 853 | 158 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1119 | 0 | 1358.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 183 | 0 | 140 | 0 | 343 | 0 | 0 | 0 | 47 | 70 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 117 | 180 | 0 | 302 | 1110 | 0 | 6499.21 | 14126.61 | 102.94
04:00 | 7 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 45 | 36 | 57 | 31 | 0 | 55 | 0 | 36 | 0 | 450 | 303 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 108 | 21.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 50 | 7 | 0 | 12 | 25 | 0 | 214 | 0 | 32 | 720 | 0 | 0 | 26 | 0 | 0 | 218 | 0 | 0 | 0 | 1075 | 0 | 51 | 0 | 81 | 0 | 349 | 280 | 47 | 190 | 34 | 89 | 50 | 199 | 45 | 19 | 77 | 26 | 52.2 | 0 | 0 | 0 | 320 | 332 | 0 | 58 | 132 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 65 | 125 | 81 | 0 | 0 | 12 | 7440.4 | 853 | 163 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1077 | 0 | 1168.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 187 | 0 | 140 | 0 | 340 | 0 | 0 | 0 | 47 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 117 | 180 | 0 | 301 | 1040 | 0 | 6059.04 | 13499.44 | 102.99
05:00 | 7 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 46 | 36 | 57 | 32 | 0 | 55 | 0 | 33 | 0 | 450 | 306 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 70 | 21.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 50 | 7 | 0 | 12 | 25 | 0 | 216 | 0 | 28 | 720 | 0 | 0 | 26 | 0 | 0 | 218 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 80 | 0 | 347 | 280 | 47 | 194 | 33 | 88 | 50 | 199 | 45 | 19 | 77 | 26 | 52.2 | 0 | 0 | 0 | 320 | 332 | 0 | 57 | 135 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 65 | 125 | 83 | 0 | 0 | 12 | 7338.4 | 852 | 172 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 935 | 0 | 1060.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 188 | 0 | 140 | 0 | 345 | 0 | 0 | 0 | 47 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 117 | 180 | 0 | 301 | 1030 | 0 | 5817.36 | 13155.76 | 103.03
06:00 | 7 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 44 | 36 | 55 | 32 | 0 | 55 | 0 | 31 | 0 | 330 | 299 | 0 | 0 | 0 | 0 | 196 | 0 | 2 | 52 | 20.7 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 50 | 7 | 0 | 12 | 25 | 0.24 | 219 | 0 | 29 | 716 | 0 | 0 | 26 | 0 | 0 | 219 | 0 | 0 | 0 | 884 | 0 | 10 | 0 | 80 | 0 | 300 | 280 | 45 | 184 | 32 | 87 | 50 | 199 | 44 | 19 | 77 | 26 | 52.2 | 4 | 0 | 0 | 320 | 314 | 0 | 57 | 128 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 65 | 125 | 83 | 0 | 1.89 | 10 | 6944.03 | 853 | 175 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4 | 850 | 0 | 933.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 2.63 | 170 | 0 | 160 | 0 | 140 | 0 | 328 | 0 | 0.17 | 0 | 47 | 0 | 1 | 40 | 0 | 0 | 0 | 8 | 0 | 0 | 167 | 117 | 180 | 0 | 302 | 900 | 0 | 5420.25 | 12364.28 | 103.08
07:00 | 7 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 46 | 36 | 32 | 32 | 0 | 55 | 0 | 30 | 0 | 330 | 297 | 0 | 0 | 0 | 0 | 196 | 0 | 6 | 52 | 18 | 22 | 0 | 0 | 0 | 0 | 10 | 0 | 65 | 34 | 7 | 0 | 12 | 25 | 0.84 | 220 | 0 | 32 | 611 | 0 | 0 | 26 | 0 | 0 | 218 | 0 | 0 | 0 | 750 | 0 | 0 | 0 | 86 | 0 | 300 | 280 | 45 | 183 | 32 | 88 | 50 | 199 | 44 | 19 | 77 | 24 | 16 | 15 | 0 | 0 | 320 | 314 | 0 | 57 | 129 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 65 | 125 | 82 | 0 | 7.74 | 6 | 6658.58 | 853 | 183 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 15 | 758 | 0 | 862.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 15.14 | 170 | 0 | 150 | 0 | 140 | 0 | 324 | 0 | 0.77 | 0 | 47 | 0 | 4 | 38 | 0 | 0 | 0.7 | 9 | 0.07 | 0 | 159 | 100 | 180 | 0 | 302 | 800 | 0 | 5173.26 | 11831.84 | 103.12
08:00 | 7 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 718 | 42 | 35 | 32 | 0 | 0 | 15 | 0 | 0 | 0 | 330 | 265 | 0 | 0 | 0 | 0 | 122 | 0 | 12 | 35 | 18 | 22 | 0 | 0 | 0 | 0 | 21 | 0 | 50 | 0 | 7 | 0 | 12 | 25 | 1.17 | 220 | 0 | 34 | 605 | 0 | 0 | 19 | 0 | 0 | 219 | 0 | 0 | 0 | 750 | 0 | 0 | 0 | 76 | 0 | 300 | 280 | 46 | 178 | 32 | 32 | 50 | 100 | 44 | 19 | 14 | 24 | 0 | 38 | 0 | 0 | 320 | 312 | 0 | 57 | 128 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 45 | 105 | 87 | 1 | 9.99 | 7 | 6093.16 | 852 | 187 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 66 | 755 | 0 | 830.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 19.56 | 140 | 0 | 140 | 0 | 140 | 0 | 280 | 0 | 1.71 | 0 | 47 | 35 | 1 | 52 | 0 | 0 | 1.1 | 39 | 0.33 | 0 | 165 | 100 | 180 | 0 | 301 | 785 | 0 | 5180.96 | 11274.12 | 103.16
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 724 | 32 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 280 | 0 | 0 | 0 | 0 | 75 | 0 | 21 | 52 | 19 | 22 | 0 | 0 | 0 | 0 | 12 | 0 | 65 | 0 | 7 | 0 | 12 | 25 | 1.84 | 220 | 0 | 35 | 606 | 0 | 0 | 19 | 0 | 0 | 219 | 0 | 0 | 0 | 700 | 0 | 0 | 0 | 25 | 0 | 300 | 280 | 45 | 184 | 31 | 16 | 50 | 17 | 38 | 19 | 0 | 24 | 0 | 31 | 0 | 0 | 320 | 316 | 0 | 58 | 130 | 8 | 0 | 11 | 30 | 0 | 18 | 0 | 17 | 8 | 85 | 86 | 1 | 32.03 | 12 | 5687.87 | 852 | 197 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 27 | 736 | 0 | 833.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 34.08 | 140 | 0 | 140 | 0 | 140 | 0 | 280 | 0 | 2.9 | 0 | 47 | 35 | 11 | 34 | 0 | 0 | 2.9 | 101 | 0.23 | 0 | 165 | 105 | 180 | 0 | 300 | 600 | 0 | 5022.26 | 10710.13 | 103.2
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 721 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 10 | 300 | 291 | 0 | 0 | 0 | 0 | 76 | 0 | 24 | 52 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 12 | 2.87 | 220 | 0 | 35 | 522 | 0 | 0 | 6 | 0 | 0 | 186 | 0 | 0 | 0 | 670 | 0 | 10 | 0 | 8 | 0 | 280 | 280 | 44 | 180 | 35 | 0 | 50 | 15 | 9 | 10 | 0 | 22 | 0 | 43 | 0 | 0 | 320 | 300 | 0 | 58 | 130 | 8 | 0 | 11 | 20 | 0 | 18 | 0 | 17 | 0 | 85 | 85 | 2 | 44.78 | 12 | 5330.65 | 853 | 206 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 50.03 | 734 | 0 | 831.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 44.07 | 140 | 0 | 140 | 0 | 140 | 0 | 280 | 0 | 4.28 | 0 | 47 | 35 | 21 | 34 | 0 | 0 | 2.5 | 158 | 0.22 | 0 | 158 | 100 | 180 | 0 | 302 | 550 | 0 | 5129.33 | 10459.98 | 103.24
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 300 | 295 | 0 | 0 | 0 | 0 | 38 | 0 | 16 | 52 | 18 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 1.25 | 220 | 0 | 36 | 515 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 610 | 0 | 10 | 0 | 8 | 0 | 280 | 280 | 22 | 200 | 34 | 0 | 50 | 14 | 8 | 16 | 0 | 24 | 0 | 35 | 0 | 0 | 320 | 335 | 0 | 57 | 134 | 8 | 0 | 11 | 20 | 0 | 16 | 0 | 17 | 0 | 85 | 97 | 2 | 49.68 | 12 | 5230.93 | 853 | 216 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 51.17 | 743 | 0 | 828.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 55.29 | 140 | 0 | 140 | 0 | 140 | 0 | 280 | 0 | 5.1 | 0 | 47 | 35 | 15 | 34 | 0 | 0 | 5.2 | 153 | 0.09 | 0 | 168 | 100 | 180 | 0 | 301 | 500 | 0 | 5093.55 | 10324.48 | 103.28
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 300 | 297 | 0 | 0 | 0 | 0 | 93 | 0 | 17 | 52 | 19 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0.19 | 220 | 0 | 36 | 518 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 600 | 0 | 10 | 0 | 8 | 0 | 320 | 280 | 10 | 200 | 34 | 0 | 50 | 16 | 8 | 19 | 0 | 28 | 0 | 47 | 0 | 0 | 320 | 339 | 0 | 58 | 142 | 8 | 0 | 11 | 20 | 0 | 16 | 0 | 17 | 0 | 85 | 95 | 2 | 53.36 | 9 | 5352.55 | 853 | 224 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 66.62 | 766 | 0 | 833.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 59.75 | 140 | 0 | 140 | 0 | 140 | 0 | 385 | 0 | 6.08 | 0 | 48 | 35 | 26 | 34 | 0 | 0 | 5.2 | 186 | 0.05 | 0 | 171 | 100 | 180 | 0 | 301 | 500 | 0 | 5328.09 | 10680.64 | 103.3
13:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 380 | 298 | 0 | 0 | 0 | 0 | 37 | 0 | 13 | 70 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 12 | 12 | 2.87 | 219 | 0 | 40 | 555 | 0 | 0 | 0 | 0 | 6 | 216 | 0 | 0 | 0 | 605 | 9 | 20 | 0 | 8 | 0 | 300 | 300 | 15 | 203 | 36 | 0 | 51 | 23 | 8 | 19 | 0 | 28 | 0 | 46 | 0 | 0 | 320 | 380 | 0 | 58 | 142 | 8 | 0 | 41 | 20 | 0 | 16 | 0 | 17 | 0 | 85 | 95 | 2 | 49.88 | 1 | 5567.75 | 853 | 228 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 33.87 | 753 | 0 | 850.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 45.32 | 160 | 0 | 150 | 0 | 140 | 0 | 388 | 0 | 4.38 | 0 | 48 | 35 | 20 | 34 | 0 | 0 | 6.8 | 201 | 0.03 | 0 | 177 | 115 | 180 | 0 | 301 | 550 | 0 | 5339.62 | 10907.37 | 103.32
14:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 293 | 0 | 0 | 0 | 0 | 74 | 0 | 7 | 70 | 13 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 3.24 | 217 | 0 | 2 | 551 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 610 | 2 | 20 | 0 | 8 | 0 | 300 | 300 | 20 | 198 | 34 | 0 | 50 | 17 | 8 | 12 | 0 | 28 | 0 | 49 | 0 | 0 | 320 | 331 | 0 | 58 | 136 | 8 | 0 | 41 | 20 | 0 | 15 | 0 | 17 | 0 | 85 | 94 | 2 | 28 | 10 | 5394.24 | 853 | 237 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 22.77 | 752 | 0 | 829.33 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 0 | 0 | 28 | 0 | 38.51 | 160 | 0 | 150 | 0 | 140 | 0 | 365 | 0 | 2.08 | 0 | 48 | 35 | 34 | 34 | 0 | 0 | 7.7 | 59 | 0.01 | 0 | 173 | 115 | 180 | 0 | 301 | 550 | 0 | 5157.9 | 10552.14 | 103.34
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 250 | 0 | 0 | 0 | 0 | 76 | 0 | 9 | 35 | 16 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 1.67 | 216 | 0 | 32 | 553 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 605 | 1 | 5 | 0 | 8 | 0 | 280 | 280 | 20 | 178 | 34 | 0 | 50 | 15 | 9 | 12 | 0 | 34 | 0 | 44 | 0 | 0 | 320 | 333 | 0 | 57 | 133 | 8 | 0 | 42 | 20 | 0 | 15 | 0 | 17 | 0 | 93 | 95 | 2 | 43.96 | 6 | 5253.63 | 853 | 211 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 35.89 | 747 | 0 | 833.59 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1 | 0 | 0 | 61 | 0 | 28.66 | 130 | 0 | 130 | 0 | 130 | 0 | 324 | 0 | 1.53 | 0 | 44 | 35 | 21 | 34 | 0 | 0 | 6 | 183 | 0.01 | 0 | 160 | 100 | 180 | 0 | 301 | 550 | 0 | 5145.78 | 10399.41 | 103.36
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 271 | 0 | 0 | 0 | 0 | 77 | 0 | 4 | 10 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0.61 | 216 | 0 | 15 | 518 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 605 | 1 | 5 | 0 | 0 | 0 | 280 | 280 | 5 | 141 | 10 | 0 | 50 | 0 | 0 | 12 | 0 | 34 | 0 | 11 | 0 | 0 | 320 | 315 | 0 | 57 | 140 | 8 | 0 | 11 | 20 | 0 | 15 | 0 | 17 | 0 | 155 | 97 | 1 | 24.68 | 6 | 5039.29 | 853 | 200 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 25.67 | 770 | 0 | 823.3 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 13 | 0 | 19.42 | 140 | 0 | 142 | 0 | 141 | 0 | 343 | 0 | 2.66 | 0 | 43 | 35 | 16 | 0 | 0 | 0 | 4.6 | 48 | 0.04 | 0 | 167 | 100 | 180 | 0 | 301 | 550 | 0 | 4963.69 | 10002.98 | 103.38
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 284 | 0 | 0 | 0 | 0 | 76 | 0 | 4 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0.47 | 217 | 0 | 15 | 518 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 605 | 0 | 5 | 0 | 0 | 0 | 280 | 280 | 5 | 143 | 10 | 0 | 50 | 0 | 0 | 18 | 0 | 36 | 0 | 5 | 0 | 0 | 320 | 284 | 0 | 57 | 130 | 8 | 0 | 11 | 20 | 0 | 15 | 0 | 17 | 0 | 200 | 68 | 0 | 7.39 | 5 | 4953.86 | 853 | 220 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12.79 | 735 | 0 | 823 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 25 | 0 | 6 | 149 | 0 | 161 | 0 | 164 | 0 | 300 | 0 | 0.51 | 0 | 46 | 35 | 11 | 0 | 0 | 0 | 1.9 | 15 | 0.01 | 0 | 140 | 100 | 180 | 0 | 301 | 520 | 0 | 4845.21 | 9799.07 | 103.4
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 721 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 292 | 0 | 0 | 0 | 0 | 78 | 0 | 2 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0.04 | 219 | 0 | 15 | 519 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 605 | 0 | 0 | 0 | 0 | 0 | 280 | 280 | 5 | 184 | 10 | 0 | 50 | 0 | 0 | 18 | 0 | 34 | 0 | 0 | 0 | 0 | 300 | 319 | 0 | 57 | 132 | 8 | 0 | 11 | 20 | 0 | 17 | 0 | 17 | 0 | 200 | 68 | 0 | 4.28 | 6 | 5024.32 | 852 | 220 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1.33 | 741 | 0 | 823.48 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0.97 | 152 | 0 | 164 | 0 | 166 | 0 | 346 | 0 | 0.1 | 0 | 44 | 35 | 4 | 30 | 0 | 0 | 0.4 | 6 | 0 | 0 | 140 | 100 | 180 | 0 | 301 | 520 | 0 | 4873.28 | 9897.6 | 103.42
19:00 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 721 | 0 | 24 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 289 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 19 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 35 | 587 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 842 | 0 | 14 | 0 | 15 | 0 | 337 | 340 | 10 | 209 | 34 | 7 | 50 | 21 | 29 | 18 | 0 | 42 | 0 | 0 | 0 | 0 | 320 | 368 | 0 | 57 | 147 | 8 | 0 | 79 | 30 | 0 | 17 | 0 | 17 | 0 | 200 | 98 | 0 | 0 | 6 | 6105 | 853 | 288 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 863 | 0 | 918.63 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 181 | 0 | 184 | 0 | 399 | 0 | 0 | 0 | 44 | 70 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 211 | 117 | 220 | 0 | 301 | 580 | 0 | 5539.63 | 11644.63 | 103.44
19:30 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 719 | 14 | 35 | 17 | 0 | 0 | 0 | 0 | 47 | 0 | 450 | 306 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 70 | 19 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 33 | 0 | 0 | 36 | 25 | 0 | 220 | 0 | 35 | 717 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 890 | 0 | 51 | 0 | 48 | 0 | 345 | 335 | 47 | 190 | 33 | 44 | 50 | 122 | 55 | 18 | 0 | 42 | 0 | 0 | 0 | 0 | 320 | 321 | 0 | 57 | 152 | 8 | 0 | 81 | 30 | 0 | 17 | 0 | 17 | 16 | 200 | 98 | 0 | 0 | 12 | 6834 | 852 | 288 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 992 | 0 | 1083.45 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 184 | 0 | 191 | 0 | 337 | 0 | 0 | 0 | 44 | 114 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 117 | 220 | 0 | 333 | 690 | 0 | 6021.45 | 12855.45
20:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 721 | 8 | 35 | 17 | 0 | 0 | 0 | 0 | 49 | 0 | 450 | 307 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 70 | 19 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 33 | 0 | 0 | 37 | 25 | 0 | 220 | 0 | 35 | 785 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 53 | 0 | 347 | 340 | 42 | 192 | 35 | 36 | 50 | 108 | 53 | 18 | 0 | 42 | 0 | 0 | 0 | 0 | 320 | 326 | 0 | 57 | 151 | 8 | 0 | 81 | 30 | 0 | 17 | 0 | 17 | 16 | 200 | 103 | 0 | 0 | 0 | 6908 | 853 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1007 | 0 | 1116.09 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 183 | 0 | 190 | 0 | 344 | 0 | 0 | 0 | 45 | 114 | 0 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 117 | 220 | 0 | 333 | 730 | 0 | 6141.09 | 13049.09 | 103.46
21:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 727 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 310 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 90 | 19 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 33 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 35 | 781 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 87 | 0 | 347 | 340 | 49 | 202 | 35 | 48 | 50 | 128 | 46 | 18 | 0 | 44 | 0 | 0 | 0 | 0 | 320 | 388 | 0 | 57 | 156 | 8 | 0 | 81 | 30 | 0 | 17 | 0 | 17 | 0 | 200 | 150 | 0 | 0 | 0 | 7040 | 853 | 304 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1055 | 0 | 1208 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 192 | 0 | 197 | 0 | 407 | 0 | 0 | 0 | 45 | 114 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 117 | 220 | 0 | 334 | 860 | 0 | 6513 | 13553 | 103.48
22:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 725 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 307 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 90 | 18.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 38 | 784 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1008 | 0 | 51 | 0 | 123 | 0 | 345 | 340 | 51 | 207 | 35 | 48 | 50 | 132 | 53 | 18 | 0 | 46 | 0 | 0 | 0 | 0 | 320 | 391 | 0 | 58 | 158 | 8 | 0 | 81 | 30 | 0 | 17 | 0 | 17 | 0 | 200 | 150 | 0 | 0 | 0 | 7112.5 | 853 | 305 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1051 | 0 | 1142 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 193 | 0 | 198 | 0 | 408 | 0 | 0 | 0 | 44 | 114 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 117 | 220 | 0 | 335 | 866 | 0 | 6459 | 13571.5 | 103.5
23:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 726 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 308 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 90 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 33 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 37 | 783 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1023 | 0 | 51 | 0 | 137 | 0 | 345 | 340 | 51 | 209 | 38 | 51 | 50 | 140 | 55 | 19 | 11 | 48 | 0 | 0 | 0 | 0 | 320 | 390 | 0 | 58 | 158 | 8 | 0 | 81 | 30 | 0 | 18 | 0 | 17 | 0 | 200 | 150 | 0 | 0 | 0 | 7181 | 853 | 313 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1139 | 0 | 1312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 201 | 0 | 205 | 0 | 410 | 0 | 0 | 0 | 46 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 117 | 220 | 0 | 333 | 866 | 0 | 6741 | 13922 | 103.52
Total KWH | 56592 | 0 | 112320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17296300 | 411480 | 528840 | 536256 | 356640 | 0 | 376658 | 117322 | 545760 | 61440 | 8923000 | 7155258 | 0 | 0 | 0 | 109564 | 3543000 | 0 | 143748 | 1473600 | 402000 | 469440 | 0 | 0 | 0 | 0 | 48000 | 0 | 1245120 | 511712 | 62352 | 0 | 176640 | 290880 | 19199 | 5234578 | 0 | 760320 | 15440000 | 0 | 0 | 239520 | 19153.8 | 24255 | 4940825 | 0 | 0 | 0 | 19767271 | 9045 | 709779 | 0 | 1254545 | 0 | 7956100 | 7370000 | 816480 | 4643000 | 747216 | 941760 | 1165100 | 2377920 | 811440 | 404030 | 628140 | 758400 | 352896 | 359218 | 0 | 0 | 7626400 | 8402000 | 0 | 1350480 | 3336463.63 | 178920 | 0 | 1304640 | 615840 | 0 | 327000 | 0 | 429480 | 588000 | 3417600 | 2201280 | 15650 | 356250 | 190560 | 153044676.43 | 20651636 | 5448672 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 384480 | 21716360 | 41280 | 24409091 | 0 | 55065 | 0 | 218016 | 246432 | 0 | 148160 | 0 | 0 | 434110 | 44572 | 351752 | 4164136 | 0 | 4278045 | 0 | 4072645 | 0 | 8390400 | 0 | 28620 | 0 | 1083927 | 1414157 | 186117 | 1506460 | 0 | 0 | 42890.04 | 1229040 | 1030 | 0 | 4844000 | 2653000 | 4993540 | 0 | 7410168 | 19035636.36 | 0 | 140395437.4 | 293440113.83

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 25-07-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10710.13 | MW | 09:00 Hr. | Energy Generated |  |  | 293.4401 |  | MKWHr.
| Day Peak Demand |  |  | 10710.13 | MW | 09:00 Hr. | Energy Unserverd |  |  | 0.8 |  | MKWHr.
| Evening Peak Generation |  |  | 13553 | MW | 21:00 Hr. | Energy Demand |  |  | 294.2401 |  | MKWHr.
| Evening Peak Demand |  |  | 13600 | MW | 21:00 Hr. | Maximum Temperature |  |  | 33.6 |  | °C
| Minimum Generation of the Day |  |  | 9799.07 | MW | 17:00 Hr. | Total Gas Supplied |  |  | 975.06 |  | MMCFD
| Maximum Generation of the Day |  |  | 14975.47 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.492 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 37.8986 | 0 | 4.5769 | 0 | 0 | 0.14375 | 0 | 0 | 42.6192 | Gas | 128.0094 | Gas | 409282738.1133
| Chattogram Zone |  |  | 5.7011 | 35.2073 | 1.3725 | 0 | 5.2346 | 0.028244 | 0 | 1.2451 | 48.7889 | Coal | 89.2974 | Coal | 533242361.1196
| Cumilla Zone |  |  | 25.0663 | 0 | 5.1122 | 0 | 0 | 0.35922 | 0.7584 | 0 | 31.296 | HFO | 19.3614 | HFO | 358207002.506
| Mymensingh Zone |  |  | 2.2013 | 0 | 4.6256 | 0 | 0 | 0.3719 | 0 | 0 | 7.1988 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 23.1417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1417 | Hydro | 5.2346 | Hydro | 523457.8
| Khulna Zone |  |  | 5.4487 | 21.7164 | 0.04128 | 0 | 0 | 0.38448 | 21.5636 | 0 | 49.1544 | Solar | 3.5611 | Solar | 58901609.2244
| Barishal Zone |  |  | 7.6465 | 31.2898 | 0 | 0 | 0 | 0.00103 | 0 | 0 | 38.9374 | Import | 46.7311 | Import | 233184190.85
| Rajshahi Zone |  |  | 20.9052 | 0 | 0.71225 | 0 | 0 | 0.81448 | 24.4091 | 0 | 46.841 | Wind | 1.2451 | Wind | 18228556.8
| Rangpur Zone |  |  | 0 | 1.0839 | 2.9206 | 0 | 0 | 1.458 | 0 | 0 | 5.4626
| Total |  |  | 128.0094 | 89.2974 | 19.3614 | 0 | 5.2346 | 3.5611 | 46.7311 | 1.2451 | 293.4401
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 409282738.1133 |  | Hydro | 523457.8
|  |  |  | Coal | 533242361.1196 |  | Solar | 58901609.2244
|  |  |  | HFO | 358207002.506 |  | Import | 233184190.85
|  |  |  | HSD | 0 |  | Wind | 18228556.8
[5 empty] | Total: | 161,15,69,916 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.6516 | Peak Hr Flow | 853.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 42915163.71 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.4091 | Peak Hr Flow | 1208.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 910 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.7584 | Peak Hr Flow | 44.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 1016 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 45.8191 | Peak Hr Flow | 2105.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4541
|  |  |  | Chattogram |  | 0 |  | 1378
|  |  |  | Cumilla |  | 0 |  | 1242
|  |  |  | Mymensingh |  | 0 |  | 1069
|  |  |  | Sylhet |  | 35 |  | 635
|  |  |  | Khulna |  | 0 |  | 1495
|  |  |  | Barishal |  | 0 |  | 368
|  |  |  | Rajshahi |  | 0 |  | 1369
|  |  |  | Rangpur |  | 10 |  | 935
|  |  |  | Total |  | 45 |  | 13032
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Bibiana-II 341 MW CCPP (Summit) GT |  |  | 222 | 3 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
|  | 4 | Bibiana-II 341 MW CCPP (Summit) ST |  |  | 119 | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 641 |  |  |  | Total | 707
|  |  |  | Total Unavailable Capacity |  |  |  | 1348
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:07 | Sonargaon 132/33kV S/S Tr-1 HT is restored.
|  | 08:09 | Sonargaon 132/33kV S/S Tr-1 LT is restored.
| 08:19 |  | Jashore 132/33kV S/S JH-1(L2) Project Work S/D
| 08:20 |  | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-1 Scheduled S/D Due to None
| 08:21 | 13:14 | Sonargaon 132/33kV S/S Tr-2 LT Scheduled S/D Due to Emergency maintenance
| 08:22 | 13:11 | Sonargaon 132/33kV S/S Tr-2 HT Scheduled S/D Due to Emergency Maintenance
| 09:00 |  | Day peak generation 10707 MW
| 09:04 | 10:32 | Rahanpur 400/132kV S/S AT-02 LT Project Work S/D Due to For painting work
| 09:06 | 10:30 | Rahanpur 400/132kV S/S AT-02 HT Project Work S/D Due to For painting work
| 09:12 | 09:51 | Cumilla(S) 132/33kV S/S TR-2 LT Tripped showing 33kv side REF615,132kv side RET 650 | [7 empty] | 25.0MW load
|  |  | relays Due to 33KV laksham REB feeder fult by O/C,E/F | [7 empty] | interrup.
|  | 09:13 | Rahanpur 400/132kV S/S Rahanpur-Niamatpur 132 KV Line Ckt-01 is restored.
|  | 09:15 | Niamatpur 132/33kV S/S 132kV Rahanpur Ckt-1 is restored.
| 09:42 |  | At Borhanuddin ( Bhola) S/S 230/33 KV, 120/140 MVA Transformer S/D Restore.
| 10:06 | 10:22 | Aminbazar-Mirpur 132kV Ckt-1 Tripped from Mirpur 132/33kV end showing E/F, Main
protection opeated relays Due to E/F
| 10:08 | 10:08 | Mirpur-Uttara 132kV Ckt-1 Tripped from Mirpur 132/33kV end showing Distance R, E/E,
Zone-2, Main Prot. relays Due to No
| 10:08 | 10:08 | Mirpur-Uttara 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Line checking
| 10:09 | 11:47 | Mirpur-Uttara 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Right of way
checking
| 10:10 | 13:02 | Chhatak 132/33kV S/S T-3 HT Scheduled S/D Due to Shutdown needed for 33KV T-1 and T-3 | [7 empty] | 10.0MW load
|  |  | Sectionalizer red hot Maintenance Work and 33kV T-3 transformer shutdown needed for | [7 empty] | interrup.
separate the 110v DC from 33kv Companiganj PBS Panel.
| 10:10 | 13:05 | Chhatak 132/33kV S/S T-3 LT Scheduled S/D Due to Shutdown needed for 33KV T-1 and T-3 | [7 empty] | 10.0MW load
|  |  | Sectionalizer red hot Maintenance Work and 33kV T-3 transformer shutdown needed for | [7 empty] | interrup.
separate the 110v DC from 33kv Companiganj PBS Panel.
| 10:10 | 13:03 | Chhatak 132/33kV S/S T-1 HT Scheduled S/D Due to Shutdown needed for 33KV T-1 and T-3 | [7 empty] | 10.0MW load
|  |  | Sectionalizer red hot Maintenance Work and 33kV T-3 transformer shutdown needed for | [7 empty] | interrup.
separate the 110v DC from 33kv Companiganj PBS Panel.
| 10:10 | 13:05 | Chhatak 132/33kV S/S T-1 LT Scheduled S/D Due to Shutdown needed for 33KV T-1 and T-3 | [7 empty] | 10.0MW load
|  |  | Sectionalizer red hot Maintenance Work and 33kV T-3 transformer shutdown needed for | [7 empty] | interrup.
separate the 110v DC from 33kv Companiganj PBS Panel.
|  | 10:15 | Kabirpur 132/33kV S/S XFR, T-I HT is restored.
|  | 10:16 | Kabirpur 132/33kV S/S XFR, T-I LT is restored.
| 10:41 | 18:20 | Rahanpur 400/132kV S/S AT-01 LT Project Work S/D Due to For painting work
| 10:42 | 18:20 | Rahanpur 400/132kV S/S AT-01 HT Project Work S/D Due to For painting work
| 11:01 | 11:43 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing MiCOM P441: PH B, Z2. relays.
| 11:12 | 12:26 | Srinagar 132/33kV S/S Tr-01 HT Scheduled S/D Due to 33 KV Bus Shutdown for Red Hot | [7 empty] | 20.0MW load
|  |  | Maintenance | [7 empty] | interrup.
| 11:12 | 12:26 | Srinagar 132/33kV S/S 33 kV bus Scheduled S/D Due to 33 KV Bus Shutdown for Red Hot | [7 empty] | 20.0MW load
|  |  | Maintenance | [7 empty] | interrup.
| 11:12 | 12:26 | Srinagar 132/33kV S/S Tr-01 LT Scheduled S/D Due to 33 KV Bus Shutdown for Red Hot | [7 empty] | 20.0MW load
|  |  | Maintenance | [7 empty] | interrup.
|  | 11:23 | Madunaghat-TKCL 132kV Ckt-1 is restored.
|  | 11:27 | Madunaghat-Sikalbaha 132kV Ckt-2 is restored.
| 11:50 | 12:18 | Sonargaon 132/33kV S/S Tr-1 LT Tripped showing DIR O/C relays Due to Due to Pbs | [7 empty] | 65.0MW load
|  |  | Anandabazar and Astha feeder. | [7 empty] | interrup.
| 12:09 | 14:33 | Gopalganj (O) - Gopalgan (N) Ckt-1 Tripped from Gopalganj 400/132kV end showing Distance
relays Due to b to c phase to phase fault and from Gopalganj 132/33kV end showing
Siprotec 7sa87 relays Due to Tree broken.
| 12:33 | 21:04 | Bhulta 132/33kV S/S GT1 HT Tripped showing VAJ relays Due to 33 KV feeder Fault
| 12:46 | 12:48 | Aminbazar-Mirpur 132kV Ckt-1 Tripped from Mirpur 132/33kV end showing DEF, Main Prot.
relays Due to NA
| 12:46 | 12:48 | Mirpur-Uttara 132kV Ckt-1 Tripped from Mirpur 132/33kV end showing Distance R. E/E,
Zone-2 relays Due to Unknown
| 12:49 |  | Mirpur-Uttara 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Emergency Right
of Way checking
| 12:49 |  | Aminbazar-Mirpur 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Emergency
Right of Way checking
|  | 13:37 | GPH 230/33kV S/S HATHAZARI is restored.
|  | 13:38 | GPH-Hathazari 230kV Ckt-1 is restored.
| 15:16 | 16:15 | Ghorashal 230kV S/S TARFO-2 HT Forced S/D Due to Emergencey Repear of Incommer-2 CT B | [7 empty] | 52.0MW load
|  |  | Phase icoming clamp conncetor | [7 empty] | interrup.
| 15:19 |  | Bagerhat-Mongla 132 kV Ckt-1 Tripped from Bagerhat 132/33kV end showing Dist B phase,
Z-2, 22.5km relays Due to Unknown and from Mongla 132/33kV end showing AR Lockout relays
Due to B phase or Y phase tear at 30 no tower.
| 15:25 | 18:15 | BIPTC S/S 20DF24 Forced S/D
| 15:45 | 15:45 | Mithapukur 132/33kV S/S TR-1(404T) HT Forced S/D Due to Red hot maintanence | [7 empty] | 25.0MW load
interrup.
| 15:45 | 17:29 | Mithapukur 132/33kV S/S TR-1(404T) LT Forced S/D Due to Red hot maintanence | [7 empty] | 25.0MW load
interrup.
| 15:45 | 15:45 | Mithapukur 132/33kV S/S TR-1(404T) HT Forced S/D Due to Red hot maintanence | [7 empty] | 25.0MW load
interrup.
| 15:55 | 16:24 | Bheramara(GK) 132/33kV S/S TR-2 LT Tripped showing OC/EF relays Due to 33 kV Feeder Fault | [7 empty] | 11.0MW load
interrup.
| 15:55 | 16:20 | Bheramara(GK) 132/33kV S/S TR-2 HT Tripped showing OC/EF relays Due to 33 kV Feeder Fault | [7 empty] | 22.0MW load
interrup.
| 15:55 | 16:22 | Bheramara(GK) 132/33kV S/S TR-1 LT Tripped showing OC/EF relays Due to 33 kV Feeder Fault | [7 empty] | 11.0MW load
interrup.
| 16:04 | 18:18 | Gopalganj 400/132kV S/S 400kV Rooppur Tripped showing DTT relays.
| 16:18 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is ON with remarks:-
| 18:25 | 18:50 | Khulna (C) S/S TR-1 425T LT Tripped showing OC/EF relays Due to 33kv pbs feeder faulty | [7 empty] | 24.0MW load
interrup.
| 18:25 | 18:46 | Khulna (C) S/S Tr-2 415 T HT Tripped showing OC/EF relays Due to 33kv pbs feeder faulty | [7 empty] | 24.0MW load
interrup.
| 18:25 | 18:46 | Khulna (C) S/S Tr-2 415 T LT Tripped showing OC/EF relays Due to 33kv pbs feeder faulty | [7 empty] | 24.0MW load
interrup.
| 18:35 | 19:07 | Madanganj 132/33kV S/S GT-2 HT Tripped showing Back up protection relay relays. | [7 empty] | 30.0MW load
interrup.
| 18:35 |  | Madanganj 132/33kV S/S GT-2 LT Tripped showing Back up protection relay relays. | [7 empty] | 30.0MW load
interrup.
| 18:52 | 20:13 | Chowmuhani-Feni 132 kV Ckt-2 Project Work S/D from Feni 132/33kV end Due to For LILO work
by EEGBPS project.
| 20:10 | 22:18 | Tangail 132/33kV S/S Tr-2 LT Forced S/D Due to due to 33kv bus section DS red hot.(BPDB) | [7 empty] | 30.0MW load
interrup.
| 20:10 | 22:18 | Tangail 132/33kV S/S Tr-2 HT Forced S/D Due to due to 33kv bus section DS red hot.(BPDB) | [7 empty] | 30.0MW load
interrup.
|  | 20:13 | Chowmuhani-Feni 132 kV Ckt-2 is restored.
| 21:00 |  | Evening Peak Generation: 13553 MW.
| 23:05 | 01:59 | Barishal 230/132kV S/S ATR-2 HT Tripped showing RET670 relays Due to OLTC PRD Trip
| 23:05 | 01:55 | Barishal 230/132kV S/S ATR-2 LT Tripped showing No operate 132 kv relay.only 230kv relay
operate relays Due to Oltc prd trip
| 02:22 |  | Barishal 230/132kV S/S ATR-2 LT Tripped showing No operate 132 kv relay.only 230kv relay
operate relays Due to Oltc prd trip
| 02:22 |  | Barishal 230/132kV S/S ATR-2 HT Tripped showing RET670 relays Due to OLTC PRD Trip
| 06:00 |  | Minimum Generation 12085 MW.
| 06:07 |  | Barishal 132/33kV S/S T-1 (405T) LT Scheduled S/D Due to High temperature remedy work | [7 empty] | 25.0MW load
interrup.
| 06:07 |  | Barishal 132/33kV S/S T-1 (405T) LT Scheduled S/D Due to High temperature remedy work | [7 empty] | 25.0MW load
interrup.
| 06:08 |  | Barishal 132/33kV S/S T-1 (405T) HT Scheduled S/D Due to High temperature remedy work | [7 empty] | 25.0MW load
interrup.
| 06:18 |  | Madunaghat-Sikalbaha 132kV Ckt-2 Scheduled S/D from Madunaghat 132/33kV end Due to for
army project work
| 06:18 |  | Madunaghat-TKCL 132kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end Due to for army
project work
| 06:28 |  | Mymensingh 132/33kV S/S Transformer-2 (414T) HT Scheduled S/D Due to To perform high
temperature mitigate works of 132kV B-Bus B-Phase clamp
| 06:29 |  | Mymensingh 132/33kV S/S Transformer-2 (414T) LT Scheduled S/D Due to To perform high
temperature mitigate works of 132kV B-Bus B-Phase clamp.
| 06:40 |  | Chowmuhani-Feni 132 kV Ckt-1 Project Work S/D from Feni 132/33kV end Due to For LILO work
by EEGBPS project
| 06:50 |  | Mymensingh 132/33kV S/S Bus B Scheduled S/D Due to To perform high temperature mitigate
works of 132kV B-Bus B-Phase clamp.
| 07:23 |  | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D
| 07:23 |  | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 25-07-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8923000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 310 | 7155258 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 376658 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 196 | 3543000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 109564 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 56592 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 411480 | FGMO
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 356640 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 117322 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 402000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 469440 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 8 | 112320 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | Engine Problem
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 536256 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 0 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 61440 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 545760 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 143748 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 528840 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 727 | 17296300 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 90 | 1473600 | Engine Problem
Dhaka Area Total |  |  |  |  | 5939.724 | 1855 | 42619218
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 19153.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 9045 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 239520 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 221 | 5234578 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 4940825 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 24255
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 62352 | Machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 33 | 511712 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 176640 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 35 | 760320 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 48000 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 19199 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 290880 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1000 | 19767271 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 28 | 1245120 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 781 | 15440000 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.72 | 2316 | 48788870.8
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 202 | 4643000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 347 | 7956100 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 340 | 7370000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 35 | 747216 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 49 | 816480 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 87 | 1254545 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 709779 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1165100 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 128 | 2377920 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 44 | 758400 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 352896 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 18 | 404030 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 628140 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 46 | 811440 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 48 | 941760 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 359218 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1445 | 31296024
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 150 | 2201280 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15650 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 200 | 3417600 | Engine Problem
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 0 | 588000 | Engine Problem
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 356250 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 190560 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 429480 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 367 | 7198820
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 57 | 1350480 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 156 | 3336463.63 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 615840 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1304640 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 327000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 178920 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Plant Shutdown as per schedule HGPI work
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 388 | 8402000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7626400 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1057 | 23141743.63
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 853 | 20651636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 304 | 5448672 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 41280 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 384480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1055 | 21716360 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2250 | 49154428
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 334 | 7410168 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 117 | 2653000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 860 | 19035636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 4993540
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 279 | 4844000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1030 | -
Barishal Area Total |  |  |  |  | 2236 | 1810 | 38937374.36
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 55065 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 177 | 4164136 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 192 | 4278045 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 197 | 4072645 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 407 | 8390400 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 44572 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 8 | 148160 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 246432 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 218016 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 28620 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1208 | 24409091 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 351752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 434110 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2189 | 46841044
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 45 | 1083927 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 105 | 1506460 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 42890.04 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 114 | 1414157 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 186117 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1229040 | -
Rangpur Area Total |  |  |  |  | 950 | 264 | 5462591.04
Eastern Grid Total |  |  |  |  | 16667.715 | 7040 | 153044676.43
Western Grid Total |  |  |  |  | 10378.16 | 6513 | 140395437.4
National Grid Total |  |  |  |  | 27045.875 | 13553 | 293440113.83
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 25-07-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8830.93 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4156.6 | MW
i) Dhaka area |  |  | 4541.07 |  | MW | i) Khulna area |  |  |  | 1495 | MW
ii) Chattogram area |  |  | 1378.5 |  | MW | ii) Barishal area |  |  |  | 368 | MW
iii) Cumilla area |  |  | 1242.36 |  | MW | iii) Rajshahi area |  |  |  | 1368.6 | MW
iv) Mymensingh area |  |  | 1069 |  | MW | iv) Rangpur area |  |  |  | 925 | MW
v) Sylhet area |  |  | 600 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12987.53 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 79 | 00:00 | 133 | PHP | 8 | 05:00
2 | AKSML | 142 | 00:00 | 68 | Ishurdi | 82 | 00:00 | 134 | Pabna | 122 | 00:00
3 | Aftabnagar | 48 | 19:00 | 69 | Jaldhaka | 86 | 19:30 | 135 | Palashbari | 117 | 01:00
4 | Agargaon | 137 | 18:00 | 70 | Jamalpur | 142 | 00:00 | 136 | Panchagarh | 71 | 02:00
5 | Agrabad | 78 | 00:00 | 71 | Jashore | 142 | 00:00 | 137 | Patuakhali | 71 | 00:00
6 | Amnura | 40 | 00:00 | 72 | Jhenaidah | 126 | 00:00 | 138 | Payra | 34 | 00:00
7 | Ashuganj | 97 | 01:00 | 73 | Joydebpur | 113 | 01:00 | 139 | Postogola | 57 | 00:00
8 | BSRM | 202 | 01:00 | 74 | Joypurhat | 72 | 00:00 | 140 | Purbachal | 22 | 00:00
9 | Bagerhat | 86 | 00:00 | 75 | Juldah | 18 | 00:00 | 141 | Purbasadipur | 142 | 00:00
10 | Bajitpur | 79 | 23:00 | 76 | KSRM | 30 | 09:00 | 142 | Rahanpur | 32 | 00:00
11 | Bakulia | 86 | 00:00 | 77 | Kabirpur | 208 | 21:00 | 143 | Rahim | 18 | 03:00
12 | Banani | 56.6 | 19:30 | 78 | Kachua | 102 | 23:00 | 144 | Rajbari | 88 | 00:00
13 | Bangabhaban | 4 | 00:00 | 79 | Kallyanpur | 105 | 00:00 | 145 | Rajendrapur | 127 | 01:00
14 | Barapukuria | 76 | 03:00 | 80 | Kalurghat | 32 | 00:00 | 146 | Rajshahi | 132 | 00:00
15 | Barguna | 22 | 01:00 | 81 | Kamrangirchar | 76.7 | 00:00 | 147 | Rajshahi-230 | 90 | 23:00
16 | Barishal | 110 | 00:00 | 82 | Kaptai | N/A | N/A | 148 | Ramganj | 104 | 23:00
17 | Barishal-230 | 104 | 00:00 | 83 | Kasba | 34 | 00:00 | 149 | Rampur | 41 | 00:00
18 | Baroaulia | 61 | 21:00 | 84 | Kazla | 90 | 01:00 | 150 | Rangamati | 17 | 19:30
19 | Baroirhat | 67 | 21:00 | 85 | Keranigonj | 78 | 00:00 | 151 | Rangpur | 133 | 14:00
20 | Bashundhara | 178 | 13:00 | 86 | Khagrachori | 30 | 23:00 | 152 | Ruppur | 6.4 | 11:00
21 | BashundharaCement | 6 | 00:00 | 87 | Khulna | 68 | 01:00 | 153 | SSM | 16 | 06:00
22 | Beanibazar | 77 | 19:00 | 88 | Khulshi | 162 | 20:00 | 154 | Saidpur | 108 | 01:00
23 | Benapole | 64 | 00:00 | 89 | Kishoreganj | 130 | 23:00 | 155 | Satkhira | 137 | 00:00
24 | Bhaluka | 136 | 21:00 | 90 | Kodda | 272 | 02:00 | 156 | Satmasjid | 89 | 00:00
25 | Bhandaria | 57 | 02:00 | 91 | Kulaura | 53 | 19:00 | 157 | Savar | 182 | 00:00
26 | Bhangura | 40 | 00:00 | 92 | Kurigram | 64 | 22:00 | 158 | SevenRings | 6.25 | 04:00
27 | Bheramara(GK) | 67 | 00:00 | 93 | Kushtia | 148 | 01:00 | 159 | ShahCement | 31 | 20:00
28 | Bhulta | 240 | 01:00 | 94 | Laksam | 34 | 01:00 | 160 | Shahjadpur | 80 | 01:00
29 | Bog-Sherpur | 70 | 01:00 | 95 | Lakshmipur | 23 | 00:00 | 161 | Shahjibazar | 127 | 00:00
30 | Bogura | 169 | 00:00 | 96 | Lalbag | 43 | 02:00 | 162 | Shahmirpur | 53 | 02:00
31 | Borhanuddin | 92 | 00:00 | 97 | Lalmonirhat | 65 | 22:00 | 163 | Shariatpur | 93 | 00:00
32 | Brahmanbaria | 135 | 00:00 | 98 | MI_Cement | 12.8 | 16:00 | 164 | Sherpur | 170 | 00:00
33 | Cantonment | 130 | 12:00 | 99 | Madanganj | 46 | 00:00 | 165 | Shikalbaha | 20 | 11:00
34 | Chandina | 15.35 | 01:00 | 100 | Madaripur | 126 | 00:00 | 166 | Shitalakhya | 65.5 | 00:00
35 | Chandpur | 73 | 02:00 | 101 | Madartek | 92.5 | 00:00 | 167 | Sholosohor | 42 | 00:00
36 | Chandraghona | 36 | 19:30 | 102 | Madunaghat | 54 | 00:00 | 168 | Shyampur | 156 | 00:00
37 | Chapai | 71 | 00:00 | 103 | Magura | 67 | 00:00 | 169 | Siddhirganj | 103 | 00:00
38 | Charsaidpur | 44 | 02:00 | 104 | Mahasthangarh | 100 | 00:00 | 170 | Sirajganj | 116 | 00:00
39 | Chauddagram | 73 | 00:00 | 105 | Maijdee | 21 | 20:00 | 171 | Sonargaon | 102 | 00:00
40 | Chhatak | 40 | 02:00 | 106 | Manikganj | 132 | 00:00 | 172 | Sreemongol | 86 | 23:00
41 | Chowmuhani | 185 | 00:00 | 107 | Maniknagar | 72 | 23:00 | 173 | Sreepur | 89 | 01:00
42 | Chuadanga | 118 | 00:00 | 108 | Matarbari | 48 | 00:00 | 174 | Srinagar | 49.98 | 00:00
43 | Coxsbazar | 121 | 19:00 | 109 | Matuail | 58 | 00:00 | 175 | Sunamganj | 60 | 19:00
44 | Cumilla(N) | 140 | 01:00 | 110 | Millgate | 102 | 00:00 | 176 | Sylhet | 53 | 23:00
45 | Cumilla(S) | 144 | 00:00 | 111 | Mirpur | 111 | 12:00 | 177 | Sylhet-132 | 146 | 00:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 9 | 14:00 | 178 | TK | 34 | 00:00
47 | Daudkandi | 138 | 03:00 | 113 | Mirzapur | 44 | 00:00 | 179 | Tangail | 184 | 23:00
48 | Dhaka | 34 | 00:00 | 114 | Mithapukur | 74 | 19:30 | 180 | Taraganj | 23 | 19:30
49 | Dhamrai | 120 | 00:00 | 115 | Modern | N/A | N/A | 181 | Thakurgaon | 117 | 02:00
50 | Dhanmondi | 114 | 19:00 | 116 | Mogbazar | 121 | 12:00 | 182 | Tongi | 98 | 23:00
51 | Dohazari | 107 | 00:00 | 117 | Mongla | 35 | 00:00 | 183 | Ullahpara | 40 | 00:00
52 | Faridpur | 161 | 03:00 | 118 | Motijheel | 36 | 13:00 | 184 | Ullon | 40 | 00:00
53 | Fatullah | 83 | 00:00 | 119 | Muktagacha | 38 | 23:00 | 185 | Uttara | 76 | 12:00
54 | Fenchuganj | 45 | 00:00 | 120 | Munshiganj | 108 | 01:00 | 186 | UttaraNew | 60 | 00:00
55 | Feni | 112 | 00:00 | 121 | Muradnagar | 42 | 00:00 | 187 | Zigatola | 80 | 00:00
56 | GPH | 95 | 02:00 | 122 | Mymensingh | 211 | 21:00
57 | Ghatail | 80 | 00:00 | 123 | Naogaon | 142 | 00:00
58 | Ghorashal | 12 | 07:00 | 124 | Narail | 60 | 00:00
59 | Ghorashal-230 | 74 | 21:00 | 125 | Narinda | 55 | 13:00
60 | Goalpara | 42 | 00:00 | 126 | Narshingdi | 169 | 22:00
61 | Gollamari | 90 | 00:00 | 127 | Natore | 153 | 00:00
62 | Gopalganj | 115 | 00:00 | 128 | Nawabganj | 58 | 23:00
63 | Gulshan | 58 | 12:00 | 129 | Netrakona | 139 | 19:30
64 | Halishahar | 45 | 08:00 | 130 | New | 65.9 | 00:00
65 | HaripurSBU | 130 | 22:00 | 131 | Niamatpur | 79 | 00:00
66 | Hasnabad | 77 | 00:00 | 132 | Noapara | 46 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 25-07-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14975.47 | 167 |  | 15149.99
1:00 | 14620.7 | 124 |  | 14750.7
2:00 | 14482.79 | 94 |  | 14580.79
3:00 | 14126.61 | 90 |  | 14220.61
4:00 | 13499.44 | 87 |  | 13590.44
5:00 | 13155.76 | 43 |  | 13200.76
6:00 | 12364.28 | 0 |  | 12364.28
7:00 | 11831.84 | 0 |  | 11831.84
8:00 | 11274.12 | 0 |  | 11274.12
9:00 | 10710.13 | 0 |  | 10710.13
10:00 | 10459.98 | 0 |  | 10459.98
11:00 | 10324.48 | 0 |  | 10324.48
12:00 | 10680.64 | 0 |  | 10680.64
13:00 | 10907.37 | 0 |  | 10907.37
14:00 | 10552.14 | 0 |  | 10552.14
15:00 | 10399.41 | 0 |  | 10399.41
16:00 | 10002.98 | 0 |  | 10002.98
17:00 | 9799.07 | 0 |  | 9799.07
18:00 | 9897.6 | 0 |  | 9897.6
19:00 | 11644.63 | 0 |  | 11644.63
19:30 | 12855.45 | 0 |  | 12855.45
20:00 | 13049.09 | 58 |  | 13110.09
21:00 | 13553 | 45 |  | 13600
22:00 | 13571.5 | 37 |  | 13610.17
23:00 | 13922 | 55 |  | 13979.48
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 25-07-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7802.36 | 7173.11 | 14975.47 | DAILY GENERATION CURVE
00:30 | 7688.78 | 7109.305 | 14798.085
01:00 | 7575.2 | 7045.5 | 14620.7 | 25-07-2025
01:30 | 7618.3 | 6933.445 | 14551.745
02:00 | 7661.4 | 6821.39 | 14482.79
02:30 | 7644.4 | 6660.3 | 14304.7
03:00 | 7627.4 | 6499.21 | 14126.61
03:30 | 7533.9 | 6279.125 | 13813.025
04:00 | 7440.4 | 6059.04 | 13499.44
04:30 | 7389.4 | 5938.2 | 13327.6
05:00 | 7338.4 | 5817.36 | 13155.76
05:30 | 7141.215 | 5618.805 | 12760.02
06:00 | 6944.03 | 5420.25 | 12364.28
06:30 | 6801.305 | 5296.755 | 12098.06
07:00 | 6658.58 | 5173.26 | 11831.84
07:30 | 6375.87 | 5177.11 | 11552.98
08:00 | 6093.16 | 5180.96 | 11274.12
08:30 | 5890.515 | 5101.61 | 10992.125
09:00 | 5687.87 | 5022.26 | 10710.13
09:30 | 5509.26 | 5075.795 | 10585.055
10:00 | 5330.65 | 5129.33 | 10459.98
10:30 | 5280.79 | 5111.44 | 10392.23
11:00 | 5230.93 | 5093.55 | 10324.48
11:30 | 5291.74 | 5210.82 | 10502.56
12:00 | 5352.55 | 5328.09 | 10680.64
12:30 | 5460.15 | 5333.855 | 10794.005
13:00 | 5567.75 | 5339.62 | 10907.37
13:30 | 5480.995 | 5248.76 | 10729.755
14:00 | 5394.24 | 5157.9 | 10552.14
14:30 | 5323.935 | 5151.84 | 10475.775
15:00 | 5253.63 | 5145.78 | 10399.41
15:30 | 5146.46 | 5054.735 | 10201.195
16:00 | 5039.29 | 4963.69 | 10002.98
16:30 | 4996.575 | 4904.45 | 9901.025
17:00 | 4953.86 | 4845.21 | 9799.07
17:30 | 4989.09 | 4859.245 | 9848.335
18:00 | 5024.32 | 4873.28 | 9897.6
18:30 | 5564.66 | 5206.455 | 10771.115
19:00 | 6105 | 5539.63 | 11644.63
19:30 | 6834 | 6021.45 | 12855.45
20:00 | 6908 | 6141.09 | 13049.09
20:30 | 6974 | 6327.045 | 13301.045 |  | Executive Engineer
21:00 | 7040 | 6513 | 13553 |  | Network Operation Division
21:30 | 7076.25 | 6486 | 13562.25
22:00 | 7112.5 | 6459 | 13571.5
22:30 | 7146.75 | 6600 | 13746.75
23:00 | 7181 | 6741 | 13922

## En-Curve
QF-LDC-12
Date | 25-07-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3578 | 2107 | 852 | 38 | 34 | 1443.11 | 216 | 4779 | 0 | 422 | 1457.36 | 0 | 0 | 49 | 167 | DAILY ENERGY CURVE
00:30 | 3450.5 | 2130.6 | 852.5 | 38 | 32 | 1406.305 | 216 | 4763.5 | 0 | 422.5 | 1430.18 | 0 | 0 | 56 | 145.5 | 25-07-2025
01:00 | 3323 | 2154.2 | 853 | 38 | 30 | 1369.5 | 216 | 4748 | 0 | 423 | 1403 | 0 | 0 | 63 | 124
01:30 | 3323.5 | 2153.2 | 852.5 | 38 | 29 | 1363.945 | 215.5 | 4737.5 | 0 | 372 | 1403.1 | 0 | 0 | 63.5 | 109 | Energy Generated | 293.4401 |  | MKWHr
02:00 | 3324 | 2152.2 | 852 | 38 | 28 | 1358.39 | 215 | 4727 | 0 | 321 | 1403.2 | 0 | 0 | 64 | 94 | Energy not Served | 0.8 |  | MKWHr
02:30 | 3303 | 2153.2 | 852.5 | 38 | 28 | 1358.3 | 215 | 4665.5 | 0 | 301.5 | 1325.7 | 0 | 0 | 64 | 92 | Total Energy Requirement | 294.2401 |  | MKWHr
03:00 | 3282 | 2154.2 | 853 | 38 | 28 | 1358.21 | 215 | 4604 | 0 | 282 | 1248.2 | 0 | 0 | 64 | 90
03:30 | 3277.5 | 2151.2 | 853 | 38 | 27 | 1263.125 | 214.5 | 4516 | 0 | 265 | 1149.2 | 0 | 0 | 58.5 | 88.5
04:00 | 3273 | 2148.2 | 853 | 38 | 26 | 1168.04 | 214 | 4428 | 0 | 248 | 1050.2 | 0 | 0 | 53 | 87
04:30 | 3281.5 | 2148.7 | 852.5 | 38 | 26 | 1114.2 | 215 | 4316.5 | 0 | 229.5 | 1048.7 | 0 | 0 | 57 | 65
05:00 | 3290 | 2149.2 | 852 | 38 | 26 | 1060.36 | 216 | 4205 | 0 | 211 | 1047.2 | 0 | 0 | 61 | 43
05:30 | 3231.5 | 2060.95 | 852.5 | 38 | 26 | 996.905 | 217.5 | 4035.5 | 13.965 | 201 | 1027.2 | 0 | 0 | 59 | 21.5
06:00 | 3173 | 1972.7 | 853 | 38 | 26 | 933.45 | 219 | 3866 | 27.93 | 191 | 1007.2 | 0 | 0 | 57 | 0
06:30 | 3160 | 1970.35 | 853 | 38 | 25 | 898.015 | 219.5 | 3646.5 | 63.095 | 183 | 980.6 | 0 | 0 | 61 | 0
07:00 | 3147 | 1968 | 853 | 38 | 24 | 862.58 | 220 | 3427 | 98.26 | 175 | 954 | 0 | 0 | 65 | 0
07:30 | 3069.5 | 1947 | 852.5 | 38 | 24 | 846.42 | 220 | 3417.5 | 157.06 | 117 | 806.5 | 0 | 0 | 57.5 | 0
08:00 | 2992 | 1926 | 852 | 38 | 24 | 830.26 | 220 | 3408 | 215.86 | 59 | 659 | 0 | 0 | 50 | 0
08:30 | 2980.5 | 1862 | 852 | 38 | 24 | 831.705 | 220 | 3281 | 251.42 | 59 | 535 | 0 | 0 | 57.5 | 0
09:00 | 2969 | 1798 | 852 | 38 | 24 | 833.15 | 220 | 3154 | 286.98 | 59 | 411 | 0 | 0 | 65 | 0
09:30 | 2931.5 | 1793 | 852.5 | 38 | 23 | 832.19 | 220 | 3068.5 | 382.365 | 55.5 | 334.5 | 0 | 0 | 54 | 0
10:00 | 2894 | 1788 | 853 | 38 | 22 | 831.23 | 220 | 2983 | 477.75 | 52 | 258 | 0 | 0 | 43 | 0
10:30 | 2911.5 | 1779 | 853 | 38 | 23 | 829.965 | 220 | 2933.5 | 465.765 | 52 | 239.5 | 0 | 0 | 47 | 0
11:00 | 2929 | 1770 | 853 | 38 | 24 | 828.7 | 220 | 2884 | 453.78 | 52 | 221 | 0 | 0 | 51 | 0
11:30 | 3034.5 | 1771 | 853 | 38 | 26 | 831.045 | 220 | 2894 | 506.515 | 52 | 220.5 | 0 | 0 | 56 | 0
12:00 | 3140 | 1772 | 853 | 38 | 28 | 833.39 | 220 | 2904 | 559.25 | 52 | 220 | 0 | 0 | 61 | 0
12:30 | 3176.5 | 1824 | 853 | 38 | 28 | 841.805 | 219.5 | 2946.5 | 510.7 | 65 | 234.5 | 0 | 0 | 56.5 | 0
13:00 | 3213 | 1876 | 853 | 38 | 28 | 850.22 | 219 | 2989 | 462.15 | 78 | 249 | 0 | 0 | 52 | 0
13:30 | 3195 | 1834 | 853 | 38 | 28 | 839.775 | 218 | 2987 | 372.73 | 80.75 | 227.5 | 0 | 0 | 56 | 0
14:00 | 3177 | 1792 | 853 | 38 | 28 | 829.33 | 217 | 2985 | 283.31 | 83.5 | 206 | 0 | 0 | 60 | 0
14:30 | 3062.5 | 1778 | 853 | 38 | 31 | 831.46 | 216.5 | 2972.5 | 361.015 | 63.3 | 207.5 | 0 | 0 | 61 | 0
15:00 | 2948 | 1764 | 853 | 38 | 34 | 833.59 | 216 | 2960 | 438.72 | 43.1 | 209 | 0 | 0 | 62 | 0
15:30 | 2930 | 1735.5 | 853 | 38 | 34 | 828.445 | 216 | 2957 | 305.2 | 30.55 | 211 | 0 | 0 | 62.5 | 0
16:00 | 2912 | 1707 | 853 | 38 | 34 | 823.3 | 216 | 2954 | 171.68 | 18 | 213 | 0 | 0 | 63 | 0
16:30 | 2896 | 1698 | 853 | 38 | 35 | 823.15 | 216.5 | 2909.5 | 130.375 | 13 | 235 | 0 | 0 | 53.5 | 0
17:00 | 2880 | 1689 | 853 | 38 | 36 | 823 | 217 | 2865 | 89.07 | 8 | 257 | 0 | 0 | 44 | 0
17:30 | 2937.5 | 1692.5 | 852.5 | 38 | 35 | 823.24 | 218 | 2867.5 | 54.095 | 8 | 277.5 | 0 | 0 | 44.5 | 0
18:00 | 2995 | 1696 | 852 | 38 | 34 | 823.48 | 219 | 2870 | 19.12 | 8 | 298 | 0 | 0 | 45 | 0
18:30 | 3302.5 | 1855.5 | 852.5 | 38 | 38 | 871.055 | 219.5 | 3149 | 9.56 | 9.5 | 386.5 | 0 | 0 | 39.5 | 0
19:00 | 3610 | 2015 | 853 | 38 | 42 | 918.63 | 220 | 3428 | 0 | 11 | 475 | 0 | 0 | 34 | 0
19:30 | 3497 | 2174 | 852 | 38 | 42 | 1083.45 | 220 | 3922 | 0 | 136 | 859 | 0 | 0 | 32 | 0
20:00 | 3529 | 2176 | 853 | 38 | 42 | 1116.09 | 220 | 4077 | 0 | 136 | 816 | 0 | 0 | 46 | 58
20:30 | 3636.5 | 2203.5 | 853 | 38 | 43 | 1162.045 | 220.5 | 4215.5 | 0 | 137.5 | 754.5 | 0 | 0 | 37 | 51.5
21:00 | 3744 | 2231 | 853 | 38 | 44 | 1208 | 221 | 4354 | 0 | 139 | 693 | 0 | 0 | 28 | 45
21:30 | 3751.5 | 2249.75 | 853 | 38 | 45 | 1175 | 221 | 4361 | 0 | 139 | 698.5 | 0 | 0 | 30.5 | 41
22:00 | 3759 | 2268.5 | 853 | 38 | 46 | 1142 | 221 | 4368 | 0 | 139 | 704 | 0 | 0 | 33 | 37
22:30 | 3779.5 | 2277.25 | 853 | 38 | 47 | 1227 | 221 | 4420 | 0 | 139 | 717.5 | 0 | 0 | 27.5 | 46
23:00 | 3800 | 2286 | 853 | 38 | 48 | 1312 | 221 | 4472 | 0 | 139 | 731 | 0 | 0 | 22 | 55
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 25-07-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 388 | 07:00 | 371 | 23:00 | Payra | 419 | 15:00 | 410 | 00:00
Ashuganj | 404 | 6:00 | 380 | 23:00 | Rahanpur | 403 | 18:00 | 383 | 23:00
Bhulta | 403 | 07:00 | 382 | 23:00 | Rampal | 411 | 14:00 | 393 | 00:00
Bibiana | 387 | 07:00 | 375 | 22:00
BIPTC | 405 | 06:00 | 392 | 23:00
Bogura | 385 | 10:00 | 360 | 23:00
Gopalganj | 406 | 15:00 | 387 | 00:00
Kaliakoir | 380 | 07:00 | 362 | 22:00
Madunaghat | 397 | 11:00 | 383 | 00:00
Meghnaghat | 390 | 12:00 | 375 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 227 | 07:00 | 215 | 22:00 | Keranigonj | 224 | 07:00 | 213 | 22:00
AKSML | 231 | 07:00 | 220 | 23:00 | Khulna(S) | 236 | 17:00 | 220 | 00:00
Aminbazar | 227 | 12:00 | 215 | 23:00 | Madunaghat | 235 | 10:00 | 224 | 22:00
Ashuganj | 233 | 07:00 | 227 | 18:30 | Madunaghat-400 | 235 | 08:00 | 225 | 00:00
Ashuganj-400 | 227 | 7:00 | 220 | 23:00 | Maniknagar | 221 | 14:00 | 209 | 22:00
Baghabari | 236 | 08:00 | 226 | 20:00 | Meghnaghat | 230 | 12:00 | 218 | 22:00
Barapukuria | 220 | 10:00 | 205 | 22:00 | Meghnaghat-400 | 226 | 07:00 | 215 | 22:00
Barapukuria-230 | 220 | 10:00 | 207 | 22:00 | Mirsorai | 230 | 10:00 | 217 | 00:00
Barishal | 235 | 15:00 | 222 | 00:00 | Rajshahi | 232 | 05:00 | 219 | 22:00
Bheramara | 234 | 05:00 | 222 | 20:00 | Rampal | 236 | 17:00 | 220 | 00:00
Bhulta | 233 | 07:00 | 211 | 01:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 227 | 18:30 | 217 | 22:00 | Rampura | 233 | 08:00 | 218 | 23:00
BIPTC | 236 | 05:00 | 222 | 22:00 | Shikalbaha | 233 | 08:00 | 222 | 21:00
Bogura | 238 | 18:00 | 223 | 23:00 | Shyampur | 224 | 07:00 | 212 | 23:00
Bogura-400 | 238 | 10:00 | 223 | 23:00 | Siddhirganj | 223 | 07:00 | 210 | 02:00
Borhanuddin | 238 | 10:00 | 228 | 00:00 | Sirajgonj | 241 | 08:00 | 234 | 22:00
BSRM | 230 | 07:00 | 216 | 23:00 | Sreepur | 230 | 07:00 | 219 | 23:00
Cumilla(N) | 226 | 07:00 | 211 | 23:00 | Tongi | 228 | 10:00 | 218 | 23:00
Faridpur | 233 | 14:00 | 210 | 20:00
Fenchuganj | 227 | 15:00 | 218 | 23:00
Ghorashal | 235 | 03:00 | 225 | 07:00
Ghorashal-230 | 231 | 08:00 | 218 | 23:00
Gopalganj | 233 | 15:00 | 219 | 00:00
GPH | 232 | 08:00 | 220 | 23:00
Haripur | 223 | 14:00 | 211 | 22:00
Hasnabad | 225 | 07:00 | 212 | 23:00
Hathazari | 233 | 09:00 | 220 | 21:00
Ishurdi | 235 | 05:00 | 225 | 20:00
Jhenaidah | 234 | 15:00 | 219 | 00:00
Kaliakoir | 233 | 08:00 | 222 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 141 | 07:00 | 133 | 00:00 | Lalmonirhat | 130 | 10:00 | 117 | 00:00
Agargaon | 133 | 07:00 | 125 | 23:00 | Madanganj | 131 | 07:00 | 122 | 23:00
Agrabad | 134 | 07:00 | 125 | 23:00 | Madaripur | 140 | 16:00 | 130 | 00:00
AKS | 131 | 09:00 | 123 | 23:00 | Madartek | 138 | 05:00 | 131 | 02:00
Aminbazar | 133 | 05:00 | 126 | 23:00 | Madunaghat | 134 | 10:00 | 126 | 23:00
Amnura | 137 | 17:00 | 126 | 22:00 | Magura | 137 | 18:00 | 124 | 21:00
Ashuganj | 140 | 06:00 | 135 | 00:00 | Mahasthangarh | 138 | 18:00 | 126 | 22:00
Bagerhat | 140 | 16:00 | 122 | 01:00 | Maijdee | 131 | 09:00 | 107 | 22:00
Bajitpur | 131 | 14:00 | 122 | 00:00 | Manikganj | 129 | 08:00 | 120 | 00:00
Bakulia | 135 | 09:00 | 126 | 00:00 | Maniknagar | 132 | 07:00 | 125 | 01:00
Banani | 139 | 06:00 | 132 | 21:00 | Matarbari | 133 | 08:00 | 111 | 00:00
Bangabhaban | 132 | 07:00 | 125 | 00:00 | Matuail | 131 | 14:00 | 122 | 23:00
Barapukuria | 133 | 02:00 | 124 | 00:00 | Millgate | 133 | 07:00 | 125 | 22:00
Barguna | 138 | 14:00 | 130 | 01:00 | Mirpur | 132 | 07:00 | 125 | 22:00
Barishal | 140 | 15:00 | 128 | 00:00 | Mirzapur | 132 | 07:00 | 123 | 22:00
Barishal-230 | 139 | 11:00 | 128 | 00:00 | Mithapukur | 134 | 18:00 | 115 | 22:00
Baroaulia | 133 | 09:00 | 126 | 23:00 | MI_Cement | 132 | 08:00 | 123 | 23:00
Baroirhat | 130 | 10:00 | 113 | 22:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 140 | 06:00 | 125 | 21:00 | Mogbazar | 143 | 06:00 | 133 | 21:00
BashundharaCement | 131 | 07:00 | 122 | 23:00 | Mongla | 139 | 15:00 | 121 | 00:00
Beanibazar | 126 | 15:00 | 116 | 23:00 | Motijheel | 132 | 07:00 | 125 | 00:00
Benapole | 136 | 16:00 | 120 | 00:00 | Muktagacha | 134 | 00:00 | 126 | 13:00
Bhaluka | 134 | 00:00 | 121 | 23:00 | Munshiganj | 130 | 08:00 | 122 | 00:00
Bhandaria | 138 | 15:00 | 121 | 00:00 | Muradnagar | 129 | 12:00 | 116 | 22:00
Bhangura | 136 | 15:00 | 128 | 23:00 | Mymensingh | 138 | 00:00 | 114 | 22:00
Bheramara | 138 | 15:00 | 131 | 00:00 | Naogaon | 136 | 10:00 | 122 | 23:00
Bheramara(GK) | 138 | 17:00 | 131 | 00:00 | Narail | 139 | 15:00 | 123 | 21:00
Bhulta | 125 | 08:00 | 115 | 22:00 | Narinda | 132 | 7:00 | 125 | 1:00
Bog-Sherpur | 138 | 18:00 | 127 | 23:00 | Narshingdi | 136 | 07:00 | 116 | 22:00
Bogura | 140 | 18:00 | 129 | 23:00 | Natore | 136 | 18:00 | 127 | 22:00
Bogura-230 | 141 | 18:00 | 129 | 23:00 | Nawabganj | 135 | 12:00 | 126 | 23:00
Brahmanbaria | 134 | 07:00 | 127 | 21:00 | Netrakona | 125 | 17:00 | 111 | 23:00
Cantonment | 133 | 07:00 | 125 | 23:00 | New | 135 | 07:00 | 126 | 21:00
Chandina | 134 | 15:00 | 119 | 22:00 | Niamatpur | 137 | 18:00 | 129 | 00:00
Chandpur | 135 | 07:00 | 114 | 18:00 | Noapara | 140 | 17:00 | 124 | 00:00
Chandraghona | 134 | 07:00 | 127 | 22:00 | Pabna | 137 | 18:00 | 129 | 21:00
Chapai | 137 | 17:00 | 125 | 23:00 | Palashbari | 130 | 17:00 | 114 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 131 | 07:00 | 123 | 00:00 | Panchagarh | 136 | 03:00 | 119 | 13:00
Chauddagram | 130 | 09:00 | 112 | 22:00 | Patuakhali | 137 | 13:00 | 131 | 00:00
Chhatak | 125 | 15:00 | 113 | 23:00 | Payra | 138 | 11:00 | 134 | 00:00
Chowmuhani | 129 | 09:00 | 106 | 23:00 | PHP | 130 | 10:00 | 112 | 23:00
Chuadanga | 136 | 15:00 | 120 | 23:00 | Postogola | 133 | 08:00 | 126 | 00:00
Coxsbazar | 132 | 08:00 | 111 | 23:00 | Purbachal | 140 | 07:00 | 125 | 22:00
Cumilla(N) | 131 | 07:00 | 118 | 23:00 | Purbasadipur | 130 | 03:00 | 118 | 00:00
Cumilla(S) | 133 | 05:00 | 116 | 23:00 | Rahanpur | 138 | 17:00 | 130 | 23:00
Daganbhuiyan | 129 | 10:00 | 109 | 22:00 | Rahanpur-400 | 138 | 08:00 | 131 | 23:00
Daudkandi | 127 | 12:00 | 114 | 23:00 | Rahim | 131 | 07:00 | 122 | 22:00
Dhaka | 140 | 06:00 | 132 | 22:00 | Rajbari | 139 | 16:00 | 125 | 23:00
Dhamrai | 134 | 15:00 | 126 | 21:00 | Rajendrapur | 131 | 08:00 | 123 | 21:00
Dhanmondi | 141 | 07:00 | 132 | 22:00 | Rajshahi | 136 | 18:00 | 126 | 22:00
Dohazari | 135 | 09:00 | 121 | 23:00 | Rajshahi-230 | 134 | 08:00 | 126 | 21:00
Faridpur | 138 | 14:00 | 129 | 00:00 | Ramganj | 131 | 11:00 | 109 | 23:00
Fatullah | 132 | 07:00 | 124 | 23:00 | Rampur | 134 | 07:00 | 124 | 23:00
Fenchuganj | 134 | 15:00 | 127 | 00:00 | Rampura | 141 | 08:00 | 132 | 22:00
Feni | 129 | 10:00 | 114 | 00:00 | Rangamati | 133 | 08:00 | 126 | 23:00
Ghatail | 132 | 16:00 | 122 | 22:00 | Rangpur | 129 | 19:00 | 120 | 00:00
Ghorashal | 137 | 03:00 | 129 | 23:00 | Ruppur | 139 | 18:00 | 131 | 00:00
Goalpara | 142 | 16:00 | 127 | 00:00 | Saidpur | 130 | 03:00 | 118 | 23:00
Gollamari | 142 | 16:00 | 128 | 00:00 | Satkhira | 139 | 17:00 | 120 | 00:00
Gopalganj | 141 | 16:00 | 127 | 00:00 | Satmasjid | 132 | 07:00 | 126 | 00:00
Gopalganj-400 | 140 | 15:00 | 131 | 00:00 | Savar | 131 | 07:00 | 124 | 23:00
Gulshan | 140 | 07:00 | 124 | 13:00 | SevenRings | 138 | 07:00 | 129 | 21:00
Halishahar | 136 | 07:00 | 125 | 23:00 | ShahCement | 131 | 07:00 | 123 | 00:00
Haripur | 131 | 07:00 | 123 | 01:00 | Shahjadpur | 140 | 16:00 | 133 | 00:00
HaripurSBU | 131 | 08:00 | 123 | 22:00 | Shahjibazar | 134 | 08:00 | 125 | 23:00
Hasnabad | 132 | 04:00 | 125 | 00:00 | Shahmirpur | 137 | 07:00 | 126 | 22:00
Hathazari | 135 | 07:00 | 129 | 23:00 | Shariatpur | 140 | 16:00 | 127 | 00:00
Ishurdi | 139 | 15:00 | 132 | 00:00 | Sherpur | 136 | 16:00 | 120 | 13:00
Jaldhaka | 129 | 03:00 | 116 | 23:00 | Shikalbaha | 126 | 08:00 | 115 | 22:00
Jamalpur | 138 | 17:00 | 123 | 13:00 | Shikalbaha-230 | 138 | 08:00 | 127 | 23:00
Jashore | 137 | 15:00 | 119 | 21:00 | Shitalakhya | 132 | 08:00 | 123 | 23:00
Jhenaidah | 140 | 15:00 | 121 | 00:00 | Sholosohor | 133 | 07:00 | 126 | 23:00
Jhenaidah-230 | 139 | 15:00 | 128 | 00:00 | Shyampur | 131 | 07:00 | 125 | 00:00
Joydebpur | 136 | 07:00 | 126 | 21:00 | Shyampur-230 | 132 | 07:00 | 124 | 23:00
Joypurhat | 134 | 18:00 | 119 | 23:00 | Siddhirganj | 131 | 07:00 | 123 | 22:00
Juldah | 136 | 06:00 | 126 | 22:00 | Sirajganj | 137 | 18:00 | 127 | 22:00
Kabirpur | 134 | 07:00 | 121 | 23:00 | Sonargaon | 131 | 12:00 | 119 | 22:00
Kachua | 130 | 08:00 | 114 | 22:00 | Sreemongol | 132 | 08:00 | 123 | 23:00
Kaliakoir | 135 | 07:00 | 126 | 22:00 | Sreepur | 134 | 00:00 | 125 | 23:00
Kallyanpur | 133 | 14:00 | 126 | 23:00 | Srinagar | 136 | 14:00 | 127 | 00:00
Kalurghat | 132 | 07:00 | 126 | 22:00 | SSM | 138 | 10:00 | 130 | 00:00
Kamrangirchar | 136 | 16:00 | 127 | 23:00 | Sunamganj | 122 | 15:00 | 113 | 02:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 126 | 16:00 | 117 | 23:00
Kasba | 128 | 10:00 | 114 | 23:00 | Sylhet-132 | 126 | 16:00 | 118 | 23:00
Kazla | 132 | 08:00 | 124 | 23:00 | Tangail | 130 | 08:00 | 123 | 22:00
Keranigonj | 136 | 14:00 | 127 | 23:00 | Taraganj | 129 | 02:00 | 119 | 00:00
Khagrachori | 133 | 09:00 | 125 | 22:00 | Thakurgaon | 133 | 03:00 | 117 | 13:00
Khulna | 140 | 16:00 | 126 | 00:00 | TK | 133 | 13:00 | 125 | 23:00
Khulna(S) | 142 | 16:00 | 128 | 00:00 | Tongi | 138 | 00:00 | 128 | 23:00
Khulshi | 134 | 07:00 | 124 | 00:00 | Ullahpara | 137 | 17:00 | 130 | 00:00
Kishoreganj | 130 | 18:30 | 117 | 23:00 | Ullon | 140 | 08:00 | 131 | 23:00
Kodda | 131 | 06:00 | 125 | 01:00 | Uttara | 132 | 07:00 | 124 | 21:00
KSRM | 135 | 09:00 | 125 | 22:00 | UttaraNew | 131 | 07:00 | 125 | 22:00
Kulaura | 133 | 15:00 | 125 | 23:00 | Zigatola | 135 | 09:00 | 127 | 00:00
Kurigram | 128 | 02:00 | 117 | 00:00
Kushtia | 138 | 18:00 | 126 | 00:00
Laksam | 130 | 10:00 | 112 | 22:00
Lakshmipur | 130 | 09:00 | 109 | 00:00
Lalbag | 136 | 14:00 | 127 | 23:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division