## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 27-07-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 26-07-2025 | during | 27-07-2025 | during | 27-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 0 | 0 | 0 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 304 | 292 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 34 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 192 | 133 | 208.13 | 208.13 | 208.13 | 208.13 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 0 | 7 | 7 | 7 | 48 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 51 | 45 | 53.97 | 53.97 | 48 | 48 | FGMO
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 46 | 149.36 | 149.36 | 138 | 138 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 54 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 26.5 | 27 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 25 | 52.19 | 52.19 | 16 | 32 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 15 | 145 | 300 | 300 | 277 | 277 | Engine Problem
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 32 | 138 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 70 | 88 | 88 | 105 | 105 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 15 | 16 | 104 | 104 | 16 | 16 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 51 | 141 | 162 | 162 | 146 | 146 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 17 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 20 | 35 | 55 | 55 | 35 | 35 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 727 | 726 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 108 | 108 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2174.5 | 2524 | 4707.65 | 4675.65 | 3809.13 | 3834.13
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 16 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 7 | 0 | 7 | 0 | 7 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 33 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 220 | 221 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 218 | 213 | 213 | 213 | 213 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 78 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 67 | 48 | 72 | 48 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 33 | 65 | 65 | 50 | 50 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 75 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 4 | 21 | 2 | 25 | 2 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 30 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.58 | 0 | 2.48 | 0 | 2.48 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 48 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 25 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 17 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 870 | 1145 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 30 | 30 | 30 | 18 | 30 | 18 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 372 | 692 | 790 | 790 | 790 | 790 | Machine Problem
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1736.58 | 2764 | 3820.2 | 3845.72 | 3805.2 | 3830.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 210 | 197 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 338 | 349 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 340 | 340 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 33 | 34 | 46.7 | 46.7 | 46.7 | 46.7 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 46 | 51 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 172 | 16 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 92 | 80 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 37 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 117 | 181 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 36 | 46 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 16 | 19 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 97 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 52 | 35 | 113 | 113 | 65 | 65 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 66 | 112 | 115 | 115 | 95 | 95 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 7 | 0 | 30 | 0 | 30 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1618 | 1747.2 | 2409.56 | 2379.56 | 2305.56 | 2275.56
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 26-07-2025 | during | 27-07-2025 | during | 27-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 99 | 69 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 3 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 47 | 193 | 200 | 200 | 160 | 160 | Engine Problem
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 73 | 93 | 115 | 115 | 100 | 100 | Engine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 43.7 | 0 | 41 | 0 | 41 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 35 | 35 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 282.7 | 384 | 592.1 | 549 | 507.6 | 464.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 58 | 60 | 60 | 60 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 147 | 131 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 79 | 83 | 83 | 83 | 83 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | Plant Shutdown as per schedule HGPI work
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 389 | 370 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1046 | 1016 | 1086 | 1086 | 1042 | 1042
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 854 | 854 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 332 | 264 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 60 | 60 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 2 | 0 | 69 | 0 | 69 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 922 | 1212 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2148 | 2385 | 3623.2 | 3554.2 | 3576.2 | 3507.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 301 | 301 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 117 | 120 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 820 | 868 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 278 | 278 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.11 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1736.11 | 1787 | 2162 | 2161 | 2162 | 2161
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 39 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 181 | 200 | 214 | 214 | 192 | 192 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 195 | 195 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 182 | 196 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 348 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 8 | 97 | 96 | 96 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.85 | 0 | 3.6 | 0 | 3.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 883.66 | 1375 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 57.28 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 106 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 2031.79 | 2514 | 3191.47 | 3026.87 | 3105.09 | 2940.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 47 | 47 | 50 | 50 | 50 | 50 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 48 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.3 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 112 | 114 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 41 | 0 | 20 | 0 | 20 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 190 | 0 | 161.21 | 0 | 161.21 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 444.3 | 274 | 499.81 | 312 | 499.81 | 312
System Total |  |  |  |  | 28565.2 | 27045.875 | 13217.98 | 15395.2 | 22091.99 | 21590 | 20812.59 | 20367.6
Forecast Scenario (27-07-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15400 |  | 0 |  | 15400
|  |  |  | 1:00 | 14870 |  | 0 |  | 14870
|  |  |  | 2:00 | 14390 |  | 0 |  | 14390
|  |  |  | 3:00 | 13920 |  | 0 |  | 13920
|  |  |  | 4:00 | 13560 |  | 0 |  | 13560
|  |  |  | 5:00 | 13390 |  | 0 |  | 13390
|  |  |  | 6:00 | 12870 |  | 0 |  | 12870
|  |  |  | 7:00 | 12730 |  | 0 |  | 12730
|  |  |  | 8:00 | 12670 |  | 0 |  | 12670
|  |  |  | 9:00 | 12950 |  | 0 |  | 12950
|  |  |  | 10:00 | 13570 |  | 0 |  | 13570
|  |  |  | 11:00 | 13860 |  | 0 |  | 13860
|  |  |  | 12:00 | 14250 |  | 0 |  | 14250
|  |  |  | 13:00 | 14460 |  | 0 |  | 14460
|  |  |  | 14:00 | 14500 |  | 0 |  | 14500
|  |  |  | 15:00 | 14630 |  | 0 |  | 14630
|  |  |  | 16:00 | 14720 |  | 0 |  | 14720
|  |  |  | 17:00 | 14280 |  | 0 |  | 14280
|  |  |  | 18:00 | 13540 |  | 0 |  | 13540
|  |  |  | 18:30 | 14170 |  | 0 |  | 14170
|  |  |  | 19:00 | 14900 |  | 0 |  | 14900
|  |  |  | 19:30 | 15270 |  | 0 |  | 15270
|  |  |  | 20:00 | 15470 |  | 0 |  | 15470
|  |  |  | 21:00 | 15670 |  | 0 |  | 15670
|  |  |  | 22:00 | 15660 |  | 0 |  | 15660
|  |  |  | 23:00 | 15670 |  | 0 |  | 15670
Probable Maximum Temperature: |  |  | 31.70°C
Probable Maximum Demand at Day Peak: |  |  | 14250.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15670.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15670.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 341.93 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:42 hrs on 27-07-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 26-07-2025 | [28 empty] | Date: | 26-07-2025 | [28 empty] | Date: | 26-07-2025 | [28 empty] | Date: | 26-07-2025 | [28 empty] | Date: | 26-07-2025 | [11 empty] | Date: | 26-07-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [11 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 726 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 24 | 6 | 450 | 303 | 0 | 0 | 0 | 0 | 199 | 0 | 0 | 108 | 20 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 33 | 0 | 0 | 12 | 25 | 0 | 221 | 0 | 36 | 600 | 0 | 0 | 0 | 0 | 3 | 220 | 0 | 0 | 0 | 1140 | 0 | 51 | 0 | 137 | 0 | 352 | 340 | 51 | 193 | 38 | 53 | 50 | 146 | 63 | 19 | 44 | 46 | 0 | 0 | 0 | 0 | 320 | 366 | 0 | 58 | 154 | 8 | 0 | 81 | 30 | 0 | 18 | 0 | 17 | 45 | 170 | 150 | 0 | 0 | 0 | 7241 | 853 | 317 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1161 | 0 | 1432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 192 | 0 | 200 | 0 | 396 | 0 | 0 | 0 | 47 | 115 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 117 | 220 | 0 | 352 | 866 | 0 | 6876 | 14117 | 103.54
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 725 | 54 | 35 | 16 | 0 | 0 | 0 | 0 | 30 | 16 | 450 | 302 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 108 | 26.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 33 | 0 | 0 | 11 | 25 | 0 | 221 | 0 | 37 | 515 | 0 | 0 | 0 | 0 | 31 | 220 | 0 | 0 | 0 | 1050 | 0 | 51 | 0 | 137 | 0 | 350 | 340 | 50 | 200 | 38 | 60 | 50 | 134 | 64 | 19 | 46 | 44 | 0 | 0 | 0 | 0 | 320 | 380 | 0 | 58 | 150 | 8 | 0 | 81 | 30 | 0 | 18 | 0 | 17 | 73 | 145 | 151 | 0 | 0 | 0 | 7180.5 | 853 | 323 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1081 | 0 | 1454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 181 | 0 | 189 | 0 | 354 | 0 | 0 | 0 | 48 | 115 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 117 | 220 | 0 | 353 | 870 | 0 | 6707 | 13887.5 | 103.57
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 726 | 54 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 450 | 304 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 108 | 26.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 33 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 37 | 434 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1040 | 0 | 51 | 0 | 137 | 0 | 351 | 340 | 49 | 196 | 38 | 64 | 50 | 144 | 63 | 20 | 46 | 42 | 0 | 0 | 0 | 0 | 320 | 371 | 0 | 58 | 154 | 8 | 0 | 81 | 30 | 0 | 18 | 0 | 17 | 73 | 125 | 151 | 0 | 0 | 0 | 6953.5 | 854 | 335 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 986 | 0 | 1445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 187 | 0 | 192 | 0 | 347 | 0 | 0 | 0 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 117 | 220 | 0 | 299 | 870 | 0 | 6572 | 13525.5 | 103.6
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 727 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 305 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 108 | 26.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 4 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 42 | 367 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1045 | 0 | 51 | 0 | 137 | 0 | 352 | 340 | 51 | 194 | 38 | 63 | 50 | 143 | 57 | 20 | 50 | 42 | 0 | 0 | 0 | 0 | 320 | 362 | 0 | 58 | 153 | 8 | 0 | 81 | 30 | 0 | 18 | 0 | 17 | 75 | 75 | 152 | 0 | 0 | 0 | 6742.5 | 854 | 339 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 934 | 0 | 1352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 186 | 0 | 191 | 0 | 344 | 0 | 0 | 0 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 117 | 220 | 0 | 301 | 870 | 0 | 6426 | 13168.5 | 103.63
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 727 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 305 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 108 | 26.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 42 | 372 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 955 | 0 | 51 | 0 | 137 | 0 | 353 | 340 | 52 | 195 | 38 | 65 | 50 | 146 | 54 | 20 | 47 | 40 | 0 | 0 | 0 | 0 | 320 | 385 | 0 | 60 | 156 | 8 | 0 | 81 | 30 | 0 | 18 | 0 | 17 | 75 | 65 | 152 | 0 | 0 | 0 | 6667.5 | 854 | 350 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 947 | 0 | 1198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 189 | 0 | 194 | 0 | 346 | 0 | 0 | 0 | 48 | 70 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 117 | 220 | 0 | 301 | 870 | 0 | 6243 | 12910.5 | 103.66
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 727 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 304 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 108 | 26.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 42 | 372 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 822 | 0 | 51 | 0 | 133 | 0 | 352 | 340 | 52 | 192 | 38 | 63 | 50 | 143 | 54 | 20 | 46 | 40 | 0 | 0 | 0 | 0 | 320 | 360 | 0 | 60 | 152 | 8 | 0 | 81 | 30 | 0 | 18 | 0 | 17 | 75 | 65 | 152 | 0 | 0 | 0 | 6497.5 | 854 | 351 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 936 | 0 | 1203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 185 | 0 | 190 | 0 | 340 | 0 | 0 | 0 | 47 | 70 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 117 | 220 | 0 | 300 | 870 | 0 | 6218 | 12715.5 | 103.69
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 727 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 305 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 108 | 26.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0.12 | 219 | 0 | 42 | 372 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 702 | 1 | 51 | 0 | 133 | 0 | 300 | 325 | 52 | 198 | 38 | 59 | 50 | 100 | 54 | 20 | 34 | 38 | 0 | 0 | 0 | 0 | 320 | 387 | 0 | 60 | 149 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 55 | 45 | 152 | 0 | 2.26 | 0 | 6193.88 | 853 | 358 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 840 | 0 | 1069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58 | 169 | 0 | 177 | 0 | 183 | 0 | 349 | 0 | 0.06 | 0 | 47 | 70 | 1 | 90 | 0 | 0 | 0.4 | 6 | 0.01 | 0 | 172 | 117 | 180 | 0 | 301 | 870 | 0 | 5893.05 | 12086.93 | 103.72
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 725 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 303 | 0 | 0 | 0 | 0 | 198 | 0 | 10 | 108 | 26.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 12 | 0.15 | 220 | 0 | 35 | 372 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 706 | 4 | 51 | 0 | 133 | 0 | 330 | 300 | 52 | 193 | 35 | 65 | 50 | 98 | 54 | 20 | 33 | 36 | 0 | 9 | 0 | 0 | 320 | 373 | 0 | 60 | 157 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 55 | 45 | 152 | 0 | 9.43 | 0 | 6210.08 | 854 | 362 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 11 | 803 | 0 | 1023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 6.19 | 185 | 0 | 191 | 0 | 197 | 0 | 345 | 0 | 0.53 | 0 | 45 | 70 | 5 | 70 | 0 | 0 | 1.1 | 29 | 0.05 | 0 | 170 | 117 | 180 | 0 | 302 | 870 | 0 | 5880.87 | 12090.95 | 103.75
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 729 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 304 | 0 | 0 | 0 | 0 | 195 | 0 | 7 | 108 | 26.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 12 | 1.21 | 220 | 0 | 13 | 375 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 708 | 4 | 51 | 0 | 133 | 0 | 330 | 300 | 52 | 197 | 35 | 63 | 50 | 95 | 54 | 20 | 31 | 34 | 0 | 4 | 0 | 0 | 320 | 385 | 0 | 60 | 153 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 55 | 45 | 122 | 1 | 8.63 | 0 | 6153.34 | 854 | 361 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 25 | 787 | 0 | 1025.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 29.38 | 181 | 0 | 188 | 0 | 193 | 0 | 348 | 0 | 2.71 | 0 | 47 | 70 | 13 | 70 | 0 | 0 | 3.7 | 84 | 0.07 | 0 | 173 | 117 | 180 | 0 | 301 | 855 | 0 | 5953.46 | 12106.8 | 103.78
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 728 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 309 | 0 | 0 | 0 | 0 | 194 | 0 | 18 | 108 | 26.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 12 | 0.99 | 221 | 0 | 4 | 374 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 705 | 2 | 51 | 0 | 133 | 0 | 300 | 300 | 50 | 200 | 38 | 50 | 50 | 85 | 48 | 19 | 0 | 32 | 0 | 11 | 0 | 0 | 320 | 386 | 0 | 60 | 153 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 7 | 55 | 45 | 117 | 1 | 28.35 | 0 | 6053.84 | 854 | 361 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9 | 785 | 0 | 982.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 26.08 | 186 | 0 | 190 | 0 | 191 | 0 | 363 | 0 | 2.39 | 0 | 47 | 113 | 9 | 70 | 0 | 0 | 3.2 | 113 | 0.07 | 0 | 172 | 117 | 180 | 0 | 302 | 855 | 0 | 6032.15 | 12085.99 | 103.81
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 728 | 0 | 17 | 16 | 0 | 0 | 0 | 10 | 0 | 0 | 450 | 295 | 0 | 0 | 0 | 0 | 196 | 0 | 20 | 108 | 26.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 12 | 1.51 | 221 | 0 | 2 | 375 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 800 | 2 | 43 | 0 | 157 | 0 | 340 | 340 | 48 | 193 | 32 | 48 | 50 | 84 | 52 | 12 | 0 | 32 | 0 | 15 | 0 | 0 | 320 | 361 | 0 | 60 | 158 | 8 | 0 | 79 | 30 | 0 | 16 | 0 | 17 | 55 | 45 | 105 | 3 | 22.68 | 0 | 6269.69 | 854 | 358 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 56 | 819 | 0 | 856.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 42.69 | 192 | 0 | 196 | 0 | 198 | 0 | 397 | 0 | 5.2 | 0 | 47 | 113 | 30 | 70 | 0 | 0 | 2.9 | 152 | 0.28 | 0 | 228 | 117 | 220 | 0 | 301 | 845 | 0 | 6238.65 | 12508.34 | 103.84
11:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 727 | 31 | 17 | 16 | 0 | 0 | 0 | 52 | 50 | 2 | 450 | 307 | 0 | 0 | 0 | 0 | 194 | 0 | 16 | 108 | 26.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 12 | 0.71 | 221 | 0 | 2 | 374 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 805 | 1 | 43 | 22 | 163 | 0 | 334 | 340 | 48 | 207 | 33 | 48 | 50 | 85 | 52 | 12 | 0 | 36 | 0 | 23 | 0 | 0 | 320 | 353 | 0 | 60 | 142 | 8 | 0 | 79 | 30 | 0 | 16 | 0 | 17 | 55 | 45 | 99 | 1 | 26.19 | 0 | 6431.4 | 854 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 50 | 900 | 0 | 893.1 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 24 | 0 | 50.53 | 174 | 0 | 177 | 0 | 175 | 0 | 392 | 0 | 5.8 | 0 | 47 | 113 | 37 | 49 | 0 | 0 | 7.2 | 98 | 0.24 | 0 | 280 | 117 | 220 | 0 | 302 | 830 | 0 | 6140.87 | 12572.27 | 103.87
12:00 | 7 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 727 | 51 | 20 | 32 | 0 | 15 | 34 | 54 | 51 | 15 | 450 | 304 | 0 | 0 | 17 | 0 | 192 | 0 | 17 | 108 | 26.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 12 | 2.58 | 220 | 0 | 4 | 372 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 870 | 7 | 43 | 92 | 172 | 0 | 338 | 340 | 46 | 210 | 33 | 66 | 50 | 117 | 52 | 16 | 0 | 36 | 0 | 7 | 0 | 0 | 320 | 389 | 0 | 58 | 147 | 8 | 0 | 78 | 30 | 0 | 16 | 0 | 17 | 73 | 47 | 99 | 3 | 43.7 | 0 | 6857.78 | 854 | 332 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 922 | 0 | 883.66 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 106 | 0 | 57.28 | 181 | 0 | 195 | 0 | 182 | 0 | 414 | 0 | 4.85 | 0 | 47 | 112 | 41 | 48 | 0 | 0 | 6.3 | 190 | 0.11 | 0 | 278 | 117 | 220 | 0 | 301 | 820 | 0 | 6360.2 | 13217.98 | 103.9
13:00 | 7 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 725 | 48 | 35 | 39 | 16 | 75 | 55 | 55 | 90 | 16 | 450 | 289 | 0 | 0 | 17 | 0 | 197 | 0 | 16 | 108 | 26.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 10 | 25 | 0.59 | 220 | 0 | 9 | 373 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 920 | 12 | 51 | 123 | 177 | 0 | 300 | 335 | 49 | 186 | 33 | 84 | 50 | 145 | 53 | 19 | 17 | 30 | 7 | 9 | 21 | 0 | 320 | 360 | 0 | 58 | 147 | 8 | 0 | 79 | 30 | 0 | 16 | 0 | 17 | 73 | 102 | 96 | 2 | 53.15 | 7 | 7197.24 | 854 | 333 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 22 | 1033 | 0 | 913.78 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 110 | 0 | 49.6 | 186 | 0 | 188 | 0 | 184 | 0 | 385 | 0 | 5.55 | 0 | 47 | 112 | 39 | 49 | 0 | 0 | 7.1 | 116 | 0.15 | 0 | 243 | 117 | 220 | 0 | 301 | 820 | 0 | 6381.18 | 13578.42 | 103.92
14:00 | 7 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 727 | 45 | 35 | 66 | 15 | 75 | 55 | 55 | 97 | 16 | 450 | 294 | 0 | 0 | 17 | 0 | 196 | 0 | 32 | 108 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 12 | 25 | 3.53 | 217 | 0 | 7 | 370 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 955 | 7 | 51 | 132 | 175 | 0 | 300 | 305 | 48 | 202 | 34 | 72 | 50 | 158 | 50 | 19 | 17 | 28 | 8 | 51 | 35 | 0 | 320 | 388 | 0 | 60 | 136 | 8 | 0 | 79 | 30 | 0 | 16 | 0 | 17 | 83 | 105 | 61 | 1 | 21.35 | 12 | 7271.88 | 854 | 329 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 33 | 1093 | 0 | 929 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 13 | 0 | 63.23 | 184 | 0 | 188 | 0 | 171 | 0 | 370 | 0 | 3.67 | 0 | 45 | 112 | 29 | 49 | 0 | 0 | 2.6 | 118 | 0.29 | 0 | 250 | 117 | 220 | 0 | 301 | 820 | 0 | 6340.79 | 13612.67 | 103.94
15:00 | 7 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 729 | 50 | 35 | 66 | 15 | 75 | 55 | 55 | 107 | 0 | 450 | 304 | 0 | 0 | 17 | 0 | 191 | 0 | 26 | 108 | 27 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 25 | 0.57 | 217 | 0 | 3 | 373 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 996 | 5 | 51 | 133 | 117 | 0 | 300 | 305 | 50 | 203 | 35 | 71 | 50 | 180 | 36 | 19 | 17 | 26 | 8 | 10 | 36 | 0 | 320 | 389 | 0 | 60 | 146 | 8 | 0 | 79 | 30 | 0 | 16 | 0 | 17 | 83 | 105 | 61 | 2 | 47.83 | 12 | 7259.4 | 854 | 316 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 23 | 1137 | 0 | 1043 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 107 | 0 | 42.95 | 192 | 0 | 198 | 0 | 181 | 0 | 393 | 0 | 0.94 | 0 | 42 | 112 | 29 | 48 | 0 | 0 | 2.7 | 179 | 0.58 | 0 | 250 | 117 | 220 | 0 | 301 | 830 | 0 | 6665.17 | 13924.57 | 103.95
16:00 | 7 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 727 | 51 | 35 | 58 | 0 | 78 | 55 | 55 | 108 | 0 | 450 | 302 | 0 | 0 | 35 | 0 | 194 | 0 | 21 | 108 | 26.2 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 12 | 25 | 0.94 | 216 | 0 | 3 | 479 | 20 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 970 | 1 | 51 | 130 | 53 | 0 | 300 | 305 | 51 | 194 | 35 | 71 | 50 | 170 | 34 | 19 | 17 | 26 | 8 | 36 | 35 | 0 | 320 | 360 | 0 | 60 | 154 | 5 | 0 | 79 | 30 | 0 | 16 | 0 | 17 | 92 | 105 | 69 | 1 | 21.6 | 12 | 7225.74 | 854 | 304 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 26 | 1160 | 0 | 1107 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 31 | 0 | 30 | 196 | 0 | 198 | 0 | 185 | 0 | 389 | 0 | 2.88 | 0 | 47 | 112 | 22 | 49 | 0 | 0 | 0.4 | 120 | 0.09 | 0 | 245 | 119 | 220 | 0 | 302 | 846 | 0 | 6611.37 | 13837.11 | 103.96
17:00 | 7 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 727 | 44 | 27 | 50 | 0 | 145 | 40 | 55 | 93 | 0 | 350 | 298 | 0 | 0 | 17 | 0 | 98 | 0 | 6 | 70 | 26.2 | 20 | 0 | 0 | 0 | 0 | 1 | 0 | 21 | 32 | 50 | 0 | 50 | 25 | 1.01 | 216 | 5 | 9 | 564 | 34 | 0 | 23 | 13 | 10 | 218 | 0 | 0 | 0 | 890 | 1 | 51 | 133 | 16 | 0 | 300 | 305 | 51 | 193 | 35 | 84 | 50 | 151 | 31 | 19 | 52 | 24 | 15 | 3 | 36 | 0 | 320 | 365 | 0 | 60 | 134 | 8 | 0 | 42 | 30 | 0 | 16 | 0 | 17 | 92 | 75 | 70 | 1 | 5.91 | 12 | 7050.12 | 854 | 295 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 6 | 1122 | 0 | 1115 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 16 | 0 | 15.77 | 173 | 0 | 169 | 0 | 162 | 0 | 338 | 0 | 1.47 | 0 | 44 | 112 | 11 | 49 | 0 | 0 | 2.7 | 57 | 0.15 | 0 | 195 | 119 | 220 | 0 | 300 | 846 | 0 | 6326.09 | 13376.21 | 103.97
18:00 | 7 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 729 | 45 | 30 | 50 | 0 | 145 | 40 | 55 | 95 | 0 | 350 | 294 | 0 | 0 | 17 | 0 | 76 | 0 | 3 | 70 | 26 | 22 | 0 | 0 | 0 | 0 | 24 | 0 | 42 | 32 | 68 | 0 | 63 | 25 | 0.05 | 217 | 15 | 7 | 570 | 34 | 0 | 32 | 16 | 15 | 218 | 0 | 0 | 0 | 900 | 0 | 51 | 133 | 16 | 0 | 300 | 305 | 51 | 200 | 33 | 88 | 50 | 152 | 28 | 19 | 52 | 36 | 25 | 2 | 36 | 0 | 320 | 386 | 0 | 60 | 132 | 8 | 0 | 42 | 30 | 0 | 16 | 0 | 17 | 92 | 75 | 69 | 0 | 2.63 | 12 | 7187.68 | 854 | 292 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 7 | 933 | 0 | 1017 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 5 | 0 | 3.45 | 161 | 0 | 167 | 0 | 167 | 0 | 349 | 0 | 0.32 | 0 | 47 | 112 | 4 | 49 | 0 | 0 | 0.6 | 14 | 0.04 | 0 | 199 | 100 | 180 | 0 | 301 | 785 | 0 | 5850.41 | 13038.09 | 103.98
19:00 | 97 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 727 | 48.5 | 35 | 55 | 15 | 145 | 40 | 55 | 152 | 11 | 420 | 304 | 0 | 0 | 35 | 0 | 193 | 0 | 0 | 70 | 27 | 22 | 0 | 0 | 0 | 0 | 54 | 0 | 26 | 33 | 76 | 0 | 75 | 25 | 0 | 219 | 17 | 14 | 677 | 34 | 0 | 33 | 16 | 16 | 217 | 0 | 0 | 0 | 1115 | 0 | 51 | 135 | 16 | 0 | 330 | 325 | 51 | 209 | 38 | 96 | 50 | 168 | 25 | 19 | 59 | 46 | 25 | 0 | 36 | 0 | 320 | 387 | 0 | 60 | 145 | 8 | 0 | 79 | 30 | 0 | 16 | 0 | 17 | 93 | 84 | 69 | 0 | 0 | 12 | 8147.5 | 853 | 283 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 994 | 0 | 1095 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 12 | 0 | 0 | 20 | 0 | 176 | 0 | 180 | 0 | 182 | 0 | 400 | 0 | 0 | 0 | 45 | 112 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 254 | 120 | 220 | 0 | 302 | 790 | 0 | 6275 | 14422.5 | 103.99
19:30 | 97 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 727 | 45 | 35 | 74 | 35 | 225 | 45 | 55 | 141 | 16 | 450 | 282 | 0 | 0 | 35 | 0 | 196 | 0 | 0 | 108 | 27 | 22 | 0 | 0 | 0 | 15 | 70 | 0 | 31 | 33 | 76 | 0 | 75 | 25 | 0 | 219 | 24 | 14 | 710 | 60 | 0 | 33 | 16 | 20 | 218 | 0 | 0 | 0 | 1100 | 0 | 51 | 140 | 16 | 0 | 351 | 340 | 51 | 185 | 34 | 112 | 50 | 181 | 26 | 19 | 97 | 46 | 26 | 0 | 36 | 0 | 320 | 352 | 0 | 60 | 155 | 8 | 0 | 79 | 30 | 0 | 16 | 0 | 17 | 93 | 196 | 69 | 0 | 0 | 12 | 8572 | 854 | 278 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1170 | 0 | 1209 | 0 | 30 | 0 | 0 | 19 | 0 | 97 | 12 | 0 | 0 | 28 | 0 | 200 | 0 | 192 | 0 | 197 | 0 | 336 | 0 | 0 | 0 | 46 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 267 | 120 | 220 | 0 | 301 | 860 | 0 | 6716 | 15288
20:00 | 30 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 725 | 47 | 35 | 80 | 46 | 225 | 45 | 55 | 150 | 16 | 450 | 284 | 0 | 0 | 35 | 0 | 133 | 0 | 0 | 108 | 27 | 22 | 0 | 0 | 0 | 15 | 57 | 0 | 27 | 33 | 76 | 0 | 75 | 25 | 0 | 220 | 35 | 20 | 739 | 53 | 0 | 33 | 16 | 45 | 218 | 0 | 0 | 0 | 1115 | 0 | 51 | 80 | 16 | 0 | 352 | 340 | 51 | 184 | 34 | 112 | 50 | 182 | 29 | 19 | 97 | 46 | 52.2 | 0 | 36 | 0 | 320 | 350 | 0 | 60 | 142 | 8 | 0 | 79 | 30 | 0 | 16 | 0 | 17 | 93 | 197 | 69 | 0 | 0 | 12 | 8514.2 | 853 | 273 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1178 | 1 | 1284 | 0 | 37 | 0 | 0 | 0 | 0 | 97 | 17 | 0 | 0 | 28 | 0 | 200 | 0 | 193 | 0 | 197 | 0 | 330 | 0 | 0 | 0 | 46 | 114 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 120 | 220 | 0 | 301 | 864 | 0 | 6787 | 15301.2 | 104
21:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 726 | 45 | 35 | 138 | 46 | 145 | 15 | 55 | 141 | 16 | 450 | 292 | 0 | 0 | 35 | 0 | 133 | 0 | 0 | 108 | 27 | 22 | 0 | 0 | 0 | 15 | 30 | 0 | 30 | 33 | 67 | 0 | 75 | 25 | 0 | 221 | 48 | 21 | 692 | 17 | 0 | 33 | 16 | 78 | 218 | 0 | 0 | 0 | 1145 | 0 | 51 | 80 | 16 | 0 | 349 | 340 | 51 | 197 | 34 | 112 | 50 | 181 | 35 | 19 | 97 | 46 | 52.2 | 0 | 37 | 0 | 320 | 370 | 0 | 60 | 131 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 93 | 193 | 69 | 0 | 0 | 12 | 8435.2 | 854 | 264 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1212 | 17 | 1375 | 0 | 39 | 0 | 0 | 0 | 0 | 97 | 36 | 0 | 0 | 28 | 0 | 200 | 0 | 195 | 0 | 196 | 0 | 348 | 0 | 0 | 0 | 47 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 120 | 220 | 0 | 301 | 868 | 0 | 6960 | 15395.2 | 104.01
22:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 726 | 45 | 35 | 149 | 62 | 45 | 15 | 55 | 144 | 16 | 450 | 290 | 0 | 0 | 35 | 0 | 134 | 0 | 0 | 108 | 27 | 22 | 0 | 0 | 0 | 15 | 32 | 0 | 26 | 33 | 67 | 0 | 75 | 25 | 0 | 221 | 46 | 27 | 690 | 17 | 0 | 33 | 16 | 82 | 218 | 0 | 0 | 0 | 1120 | 0 | 51 | 80 | 16 | 0 | 351 | 340 | 51 | 193 | 34 | 111 | 50 | 181 | 36 | 20 | 97 | 40 | 52.2 | 0 | 37 | 0 | 320 | 355 | 0 | 60 | 131 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 102 | 192 | 69 | 0 | 0 | 12 | 8329.2 | 853 | 250 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1210 | 17 | 1375 | 0 | 39 | 0 | 0 | 0 | 0 | 97 | 36 | 0 | 0 | 27 | 0 | 200 | 0 | 195 | 0 | 196 | 0 | 342 | 0 | 0 | 0 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 120 | 220 | 0 | 302 | 870 | 0 | 6934 | 15263.2 | 104.02
23:00 | 7 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 726 | 45 | 35 | 145 | 62 | 45 | 20 | 55 | 143 | 0 | 450 | 288 | 0 | 0 | 35 | 0 | 199 | 0 | 0 | 108 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 33 | 67 | 0 | 63 | 25 | 0 | 222 | 40 | 27 | 701 | 17 | 0 | 33 | 8 | 34 | 220 | 0 | 0 | 0 | 1149 | 0 | 51 | 87 | 16 | 0 | 352 | 340 | 51 | 197 | 34 | 112 | 50 | 181 | 36 | 20 | 97 | 48 | 52.2 | 0 | 37 | 0 | 320 | 365 | 0 | 60 | 133 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 92 | 192 | 72 | 0 | 0 | 12 | 8336.2 | 852 | 244 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1214 | 17 | 1403 | 0 | 39 | 0 | 0 | 0 | 0 | 97 | 30 | 0 | 0 | 27 | 0 | 200 | 0 | 192 | 0 | 191 | 0 | 349 | 0 | 0 | 0 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 120 | 220 | 0 | 299 | 870 | 0 | 6952 | 15288.2 | 104.03
Total KWH | 197712 | 492480 | 167040 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17430209 | 778680 | 686520 | 1271808 | 299040 | 1312505 | 550816 | 782750 | 1550880 | 162240 | 9998000 | 7228189 | 0 | 0 | 335628 | 0 | 4486000 | 0 | 199622 | 2466000 | 591000 | 468000 | 0 | 0 | 0 | 52691 | 224640 | 0 | 737280 | 332882 | 483216 | 0 | 590400 | 384960 | 15359 | 5326553 | 230835 | 536160 | 11563636.36 | 205745 | 0 | 257280 | 115666.2 | 398945 | 5083800 | 0 | 0 | 0 | 22663634 | 42930 | 1132442 | 1550618 | 2458909 | 0 | 8324200 | 7896000 | 1204320 | 4828000 | 854929 | 1852800 | 1197150 | 3452160 | 1098720 | 432970 | 1045380 | 887040 | 336902 | 233973 | 391520 | 0 | 7661900 | 9320000 | 0 | 1382400 | 3503945.46 | 174336 | 0 | 1841280 | 732864 | 0 | 427000 | 0 | 406440 | 1848000 | 2460000 | 2412480 | 13400 | 309130 | 142800 | 172515740.02 | 20674909 | 7773696 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 53856 | 316080 | 24189090 | 74400 | 27512728 | 0 | 181447 | 0 | 0 | 33984 | 0 | 659984 | 120346 | 0 | 551020 | 136318 | 374248 | 4493364 | 0 | 4732482 | 0 | 4733136 | 0 | 8718254 | 0 | 33540 | 0 | 1063854 | 2512229 | 227354 | 1951420 | 0 | 0 | 47541 | 1324080 | 2592 | 0 | 5651000 | 2808000 | 5315560 | 0 | 7344720 | 20928000 | 0 | 155451232 | 327966972.02

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 26-07-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13217.98 | MW | 12:00 Hr. | Energy Generated |  |  | 327.967 |  | MKWHr.
| Day Peak Demand |  |  | 13217.98 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.715 |  | MKWHr.
| Evening Peak Generation |  |  | 15395.2 | MW | 21:00 Hr. | Energy Demand |  |  | 328.682 |  | MKWHr.
| Evening Peak Demand |  |  | 15549.86 | MW | 21:00 Hr. | Maximum Temperature |  |  | 33.1 |  | °C
| Minimum Generation of the Day |  |  | 12085.99 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 1018.16 |  | MMCFD
| Maximum Generation of the Day |  |  | 15395.2 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.0653 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.2014 | 0 | 11.0541 | 0 | 0 | 0.19962 | 0 | 0 | 51.4551 | Gas | 140.181 | Gas | 457562624.3586
| Chattogram Zone |  |  | 5.62 | 34.2273 | 3.2773 | 0 | 5.3266 | 0.058289 | 0 | 0.73728 | 49.2466 | Coal | 93.4039 | Coal | 566215172.7416
| Cumilla Zone |  |  | 28.3289 | 0 | 9.7281 | 0 | 0 | 0.23397 | 0.88704 | 0 | 39.178 | HFO | 34.6407 | HFO | 637636653.274
| Mymensingh Zone |  |  | 2.4125 | 0 | 4.8572 | 0 | 0 | 0.32253 | 0 | 0 | 7.5922 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 25.0437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.0437 | Hydro | 5.3266 | Hydro | 532655.3
| Khulna Zone |  |  | 7.7737 | 24.1891 | 0.12826 | 0 | 0 | 0.31608 | 21.5869 | 0 | 53.994 | Solar | 3.6909 | Solar | 61561514.93
| Barishal Zone |  |  | 8.1236 | 33.9237 | 0 | 0 | 0 | 0.002592 | 0 | 0 | 42.0499 | Import | 49.9867 | Import | 254919490.21
| Rajshahi Zone |  |  | 22.6772 | 0 | 1.1321 | 0 | 0 | 0.95881 | 27.5127 | 0 | 52.2809 | Wind | 0.73728 | Wind | 10793779.2
| Rangpur Zone |  |  | 0 | 1.0639 | 4.4636 | 0 | 0 | 1.599 | 0 | 0 | 7.1265
| Total |  |  | 140.181 | 93.4039 | 34.6407 | 0 | 5.3266 | 3.6909 | 49.9867 | 0.73728 | 327.967
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 457562624.3586 |  | Hydro | 532655.3
|  |  |  | Coal | 566215172.7416 |  | Solar | 61561514.93
|  |  |  | HFO | 637636653.274 |  | Import | 254919490.21
|  |  |  | HSD | 0 |  | Wind | 10793779.2
[5 empty] | Total: | 198,92,21,890 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.6749 | Peak Hr Flow | 854.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 46314618.29 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.5127 | Peak Hr Flow | 1375.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 714 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.88704 | Peak Hr Flow | 46.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 1094 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 49.0747 | Peak Hr Flow | 2275.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5239
|  |  |  | Chattogram |  | 0 |  | 1470
|  |  |  | Cumilla |  | 0 |  | 1394
|  |  |  | Mymensingh |  | 0 |  | 1288
|  |  |  | Sylhet |  | 35 |  | 631
|  |  |  | Khulna |  | 0 |  | 1796
|  |  |  | Barishal |  | 0 |  | 463
|  |  |  | Rajshahi |  | 0 |  | 1595
|  |  |  | Rangpur |  | 113 |  | 1053
|  |  |  | Total |  | 148 |  | 14929
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Bibiana-II 341 MW CCPP (Summit) GT |  |  | 222 | 3 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
|  | 4 | Bibiana-II 341 MW CCPP (Summit) ST |  |  | 119 | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 641 |  |  |  | Total | 707
|  |  |  | Total Unavailable Capacity |  |  |  | 1348
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:18 | 22:10 | Kodda 132/33kV S/S Tr-3 (426T) LT Scheduled S/D | [7 empty] | 50.0MW load
interrup.
| 08:19 | 22:02 | Kodda 132/33kV S/S Tr-3 (426T) HT Scheduled S/D
| 08:20 | 19:20 | Kodda 132/33kV S/S Tr-4 (436T) LT Scheduled S/D | [7 empty] | 50.0MW load
interrup.
| 08:21 | 19:08 | Kodda 132/33kV S/S Tr-4 (436T) HT Scheduled S/D
|  | 08:25 | Barishal 132/33kV S/S T-1 (405T) HT is restored.
|  | 08:25 | Barishal 132/33kV S/S T-1 (405T) LT is restored.
| 08:27 | 12:54 | Mahasthangarh 132/33kV S/S 406T MTR1 LT Scheduled S/D Due to Nesco mahasthangarh 33 kv | [7 empty] | 14.0MW load
|  |  | feeder sky wire maintenance. | [7 empty] | interrup.
| 08:28 | 12:53 | Mahasthangarh 132/33kV S/S 406T MTR1 HT Scheduled S/D Due to Nesco mahasthangarh 33 kv
feeder sky wire maintenance.
| 08:35 | 12:54 | Mahasthangarh 132/33kV S/S 33KV Main bus T-1 Scheduled S/D Due to Nesco mahasthangarh 33 | [7 empty] | 14.0MW load
|  |  | kv feeder sky wire maintenance. | [7 empty] | interrup.
| 08:35 | 14:17 | Barapukuria-Saidpur 132 kV Ckt-2 Scheduled S/D from Barapukuria 230/132/33kV end Due to | [7 empty] | and 10.0MW load
|  |  | 132KV Circuit breaker replacement work ( saidpur -02)at saidpur Sub station. and from | [7 empty] | interrup. Saidpur
|  |  | Saidpur 132/33kV end Due to BP Ckt-2 Breaker Replacement work. | [7 empty] | 132/33kV end
| 08:37 | 18:29 | Rahanpur 400/132kV S/S AT-01 LT Project Work S/D Due to Due to project painting work.
| 08:39 | 18:28 | Rahanpur 400/132kV S/S AT-01 HT Project Work S/D Due to Due to project painting work.
| 08:40 | 10:26 | Barishal 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to High temperature remedy work
| 08:41 | 10:25 | Barishal 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to High temperature remedy work
| 08:48 | 14:35 | Rajbari 132/33kV S/S Bheramara-1 Scheduled S/D Due to CB SF6 pressure manometer
replacement
| 08:57 | 09:50 | Jashore-Noapara 132kV Ckt-1 Tripped from Noapara 132/33kV end showing ALSTOM, EPAC3000
relays Due to Distance Relay Trip and from Jashore 132/33kV end showing Distance relays.
| 08:57 | 15:33 | Bagerhat-Mongla 132 kV Ckt-1 Forced S/D from Mongla 132/33kV end Due to B phase Conductor
tear at 30 no tower.
| 09:00 | 16:00 | KSRM 132/33kV S/S Transformer-01 HT Scheduled S/D Due to 33 KV side Isolator Maintenance
| 09:15 | 15:31 | Ashuganj-Shahjibazar 132kV Ckt-1 Scheduled S/D from Shahjibazar 132/33kV end Due to S/D
Taken By Ashuganj End
|  | 09:18 | Madunaghat-Sikalbaha 132kV Ckt-2 is restored.
|  | 09:18 | Madunaghat-TKCL 132kV Ckt-1 is restored.
| 09:53 | 16:03 | Gopalganj (O) - Gopalgan (N) Ckt-1 Scheduled S/D from Gopalganj 132/33kV end Due to B
phase armoring of North ckt-1 and from Gopalganj 400/132kVend.
| 09:53 | 16:03 | Gopalganj- Gopalganj(N) 132kV Ckt-2 Scheduled S/D from Gopalganj 132/33kV end Due to B
phase armoring of the north ckt-1 and from Gopalganj 400/132kVend.
| 09:56 | 10:20 | Kulaura 132/33kV S/S TR-2 LT Forced S/D Due to PDB Red hot maintenance | [7 empty] | 9.0MW load
interrup.
| 09:57 | 10:20 | Kulaura 132/33kV S/S TR-2 HT Forced S/D Due to PDB Red hot maintenance | [7 empty] | 9.0MW load
interrup.
|  | 10:22 | Mymensingh 132/33kV S/S Transformer-2 (414T) HT is restored.
|  | 10:22 | Mymensingh 132/33kV S/S Transformer-2 (414T) LT is restored.
|  | 10:30 | Mymensingh 132/33kV S/S Bus B is restored.
| 10:46 | 12:04 | Khulna (C) S/S Tr-2 415 T LT Forced S/D Due to 33kv bus section-2 Bus DS red-hot
maintenance.
| 10:47 | 12:03 | Khulna (C) S/S Tr-2 415 T HT Forced S/D Due to 33kv bus section-2 Bus DS red-hot
maintenance.
|  | 11:04 | Mirpur-Uttara 132kV Ckt-1 is restored.
| 12:00 |  | Day peak Generation is 13214 MW
|  | 12:08 | Faridpur 132/33kV S/S Transformer-1 HT is restored.
|  | 12:09 | Faridpur 132/33kV S/S Transformer-1 LT is restored.
| 12:12 | 13:07 | Rajshahi 132/33kV S/S Transformer T-1(405T) LT Forced S/D Due to LT CB clamp high
tempateture
| 12:13 | 13:06 | Rajshahi 132/33kV S/S Transformer T-1(405T) HT Forced S/D Due to T1 LT CB clamp hoigh
temperature
| 12:21 |  | At Gopalgonj(N) S/S 400 KV Pooppur Nuclear PP Line S/D.
| 12:40 |  | At Gopalgonj(N) S/S 400 KV Pooppur Nuclear PP Line S/D Withdrew.
| 13:15 |  | Bakulia-Khulshi 132 kV Ckt-1 Tripped from Bakulia 132/33kV end showing Distance Relay
Trip relays Due to 3Phase fault
|  | 14:51 | Barishal 230/132kV S/S ATR-2 LT is restored.
|  | 14:54 | Barishal 230/132kV S/S ATR-2 HT is restored.
| 15:07 | 15:15 | Cumilla(S) 132/33kV S/S TR-3 LT Tripped showing REF 615 relays Due to 33 KV Kotbari | [7 empty] | 26.0MW load
|  |  | feeder fault. | [7 empty] | interrup.
| 15:31 |  | Bagerhat-Mongla ckt-1 is restored
| 16:03 |  | Raozan 25 MW PP Synchronized
| 16:34 | 16:49 | Brahmanbaria 132/33kV S/S 402T LT Tripped showing OC/EF relays. | [7 empty] | 50.0MW load
interrup.
| 16:51 | 17:00 | Brahmanbaria 132/33kV S/S 402T LT Tripped showing OC/EF relays. | [7 empty] | 50.0MW load
interrup.
|  | 18:45 | Chowmuhani-Feni 132 kV Ckt-1 is restored.
| 21:00 |  | Peak generation 15395 MW
| 23:35 |  | Raozan 25 MW PP Shutdown
| 04:56 | 07:26 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 HT Forced S/D Due to Fenchugonj line | [7 empty] | 70.0MW load
|  |  | red-hot maintenance work | [7 empty] | interrup.
| 04:56 | 07:25 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Forced S/D from Beanibazar 132/33kV end | [7 empty] | 70.0MW load
|  |  | Due to Fenchugonj line shutdown for redhot | [7 empty] | interrup.
Beanibazar 132/33kV
end
| 04:56 | 07:25 | Fenchuganj -Sylhet 132kV Ckt-1 Forced S/D from Beanibazar 132/33kV end Due to | [7 empty] | 70.0MW load
|  |  | Fenchugonj line shutdown for redhot | [7 empty] | interrup.
Beanibazar 132/33kV
end
| 04:56 | 07:45 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 HT Forced S/D Due to Fenchugonj line | [7 empty] | 70.0MW load
|  |  | shutdown for red-hot maintenance work | [7 empty] | interrup.
| 04:57 |  | Beanibazar 132/33kV S/S 132KV Transformer TR-02 LT Forced S/D Due to Fenchugonj line | [7 empty] | 70.0MW load
|  |  | shutdown for hed-hot maintenance | [7 empty] | interrup.
| 04:57 | 07:30 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 LT Forced S/D Due to Fenchugonj line | [7 empty] | 70.0MW load
|  |  | red-hot maintenance work | [7 empty] | interrup.
| 05:20 | 07:10 | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-2 Scheduled S/D Due to REDHOT
| 05:20 | 07:10 | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-1 Scheduled S/D Due to REDHOT | [7 empty] | 15.0MW load
interrup.
| 05:40 | 07:10 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Scheduled S/D from Fenchuganj
230/132/33kV end Due to emergency maintenance
| 05:55 |  | Kishoreganj 132/33kV S/S Tr-1 (404T) LT Scheduled S/D Due to 33/0.4kv Aux Tr-2 DS
Installation work
| 05:56 |  | Kishoreganj 132/33kV S/S Tr-3 (424T) LT Scheduled S/D Due to 33/0.4kv Aux Tr-2 DS | [7 empty] | 40.0MW load
|  |  | Installation work | [7 empty] | interrup.
| 05:57 |  | Kishoreganj 132/33kV S/S Tr-3 (424T) HT Scheduled S/D Due to 33/0.4kv Aux Tr-2 DS
Installation work
| 05:57 |  | Kishoreganj 132/33kV S/S Tr-1 (404T) HT Scheduled S/D Due to 33/0.4kv Aux Tr-2 DS
Installation work
| 07:00 |  | Minimum Generation 12886 MW.
| 07:37 |  | Tangail 132/33kV S/S Tr-1 LT Forced S/D Due to Due 33kv Betka Feeder red hot(BPDB) | [7 empty] | 50.0MW load
interrup.
| 07:37 |  | Tangail 132/33kV S/S Tr-1 HT Forced S/D Due to Due 33kv Betka Feeder red hot(BPDB) | [7 empty] | 50.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 26-07-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9998000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 292 | 7228189 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 550816 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 133 | 4486000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 197712 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 45 | 778680 | FGMO
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 46 | 299040 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 782750 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 335628 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 27 | 591000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 468000 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 167040 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 1312505 | Engine Problem
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 138 | 1271808 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 492480 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 162240 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 141 | 1550880 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 199622 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 686520 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 726 | 17430209 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 2466000 | Engine Problem
Dhaka Area Total |  |  |  |  | 5939.724 | 2524 | 51455119
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 16 | 115666.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 42930 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 257280 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 221 | 5326553 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 5083800 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 78 | 398945 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 67 | 483216 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 33 | 332882 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 75 | 590400 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 21 | 536160 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 30 | 224640 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 15359 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 52691 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 48 | 230835 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 384960 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 17 | 205745 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1145 | 22663634 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 30 | 737280 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 692 | 11563636.36 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.72 | 2764 | 49246612.56
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 197 | 4828000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 349 | 8324200 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 340 | 7896000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 34 | 854929 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 51 | 1204320 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 16 | 2458909 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1132442 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 80 | 1550618 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 37 | 391520 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1197150 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 181 | 3452160 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 46 | 887040 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 336902 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 432970 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 97 | 1045380 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 35 | 1098720 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 112 | 1852800 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 233973 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1747.2 | 39178033
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 69 | 2412480 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13400 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 193 | 2460000 | Engine Problem
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 93 | 1848000 | Engine Problem
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 309130 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 142800 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 406440 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 384 | 7592250
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1382400 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 131 | 3503945.46 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 732864 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 1841280 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 427000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 174336 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Plant Shutdown as per schedule HGPI work
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 370 | 9320000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7661900 | Aythority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2325 | 1016 | 25043725.46
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 854 | 20674909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 264 | 7773696 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 74400 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 53856 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 316080 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1212 | 24189090 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2385 | 53994031
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 301 | 7344720 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2808000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 868 | 20928000 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5315560 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 278 | 5651000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2592 | -
Barishal Area Total |  |  |  |  | 2236 | 1787 | 42049872
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 39 | 181447 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 120346 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 200 | 4493364 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 195 | 4732482 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 196 | 4733136 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 348 | 8718254 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 136318 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 97 | 659984 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 33984 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 33540 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1375 | 27512728 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 374248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 551020 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2514 | 52280851
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 47 | 1063854 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1951420 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 47541 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 114 | 2512229 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 227354 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1324080 | -
Rangpur Area Total |  |  |  |  | 950 | 274 | 7126478
Eastern Grid Total |  |  |  |  | 16667.715 | 8435.2 | 172515740.02
Western Grid Total |  |  |  |  | 10378.16 | 6960 | 155451232
National Grid Total |  |  |  |  | 27045.875 | 15395.2 | 327966972.02
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 26-07-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9986.8 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4794 | MW
i) Dhaka area |  |  | 5238.53 |  | MW | i) Khulna area |  |  |  | 1796 | MW
ii) Chattogram area |  |  | 1470.5 |  | MW | ii) Barishal area |  |  |  | 463 | MW
iii) Cumilla area |  |  | 1393.77 |  | MW | iii) Rajshahi area |  |  |  | 1595 | MW
iv) Mymensingh area |  |  | 1288 |  | MW | iv) Rangpur area |  |  |  | 940 | MW
v) Sylhet area |  |  | 596 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14780.8 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 78 | 19:00 | 133 | PHP | 6 | 00:00
2 | AKSML | 128 | 04:00 | 68 | Ishurdi | 88 | 19:30 | 134 | Pabna | 128 | 21:00
3 | Aftabnagar | 50 | 14:00 | 69 | Jaldhaka | 86 | 00:00 | 135 | Palashbari | 106 | 21:00
4 | Agargaon | 125 | 13:00 | 70 | Jamalpur | 146 | 23:00 | 136 | Panchagarh | 58 | 19:30
5 | Agrabad | 86 | 19:30 | 71 | Jashore | 149 | 19:30 | 137 | Patuakhali | 68.8 | 22:00
6 | Amnura | 40 | 22:00 | 72 | Jhenaidah | 129 | 19:30 | 138 | Payra | 36 | 22:00
7 | Ashuganj | 96 | 00:00 | 73 | Joydebpur | 141 | 12:00 | 139 | Postogola | 59 | 13:00
8 | BSRM | 198 | 20:00 | 74 | Joypurhat | 63 | 21:00 | 140 | Purbachal | 21 | 13:00
9 | Bagerhat | 83 | 20:00 | 75 | Juldah | 18 | 00:00 | 141 | Purbasadipur | 134 | 00:00
10 | Bajitpur | 86 | 22:00 | 76 | KSRM | 32 | 23:00 | 142 | Rahanpur | 34 | 23:00
11 | Bakulia | 93 | 19:30 | 77 | Kabirpur | 249 | 09:00 | 143 | Rahim | 24 | 16:00
12 | Banani | 74 | 13:00 | 78 | Kachua | 98 | 00:00 | 144 | Rajbari | 88 | 19:30
13 | Bangabhaban | 8 | 12:00 | 79 | Kallyanpur | 111 | 23:00 | 145 | Rajendrapur | 143 | 19:00
14 | Barapukuria | 72 | 19:30 | 80 | Kalurghat | 36 | 10:00 | 146 | Rajshahi | 108 | 23:00
15 | Barguna | 22 | 21:00 | 81 | Kamrangirchar | 78 | 13:00 | 147 | Rajshahi-230 | 104 | 13:00
16 | Barishal | 113 | 21:00 | 82 | Kaptai | N/A | N/A | 148 | Ramganj | 120 | 22:00
17 | Barishal-230 | 96 | 21:00 | 83 | Kasba | 37 | 22:00 | 149 | Rampur | 39 | 19:30
18 | Baroaulia | 66 | 10:00 | 84 | Kazla | 97 | 12:00 | 150 | Rangamati | 17 | 19:00
19 | Baroirhat | 73 | 19:30 | 85 | Keranigonj | 83 | 19:30 | 151 | Rangpur | 142 | 19:00
20 | Bashundhara | 197 | 15:00 | 86 | Khagrachori | 34 | 21:00 | 152 | Ruppur | 5 | 12:00
21 | BashundharaCement | 13 | 15:00 | 87 | Khulna | 72 | 13:00 | 153 | SSM | 4 | 23:00
22 | Beanibazar | 84 | 02:00 | 88 | Khulshi | 147 | 16:00 | 154 | Saidpur | 111 | 23:00
23 | Benapole | 62 | 21:00 | 89 | Kishoreganj | 137 | 22:00 | 155 | Satkhira | 128 | 20:00
24 | Bhaluka | 164 | 19:30 | 90 | Kodda | 266 | 23:00 | 156 | Satmasjid | 99 | 19:30
25 | Bhandaria | 54 | 23:00 | 91 | Kulaura | 54 | 15:00 | 157 | Savar | 227 | 16:00
26 | Bhangura | 40 | 20:00 | 92 | Kurigram | 62 | 02:00 | 158 | SevenRings | 9.34 | 16:00
27 | Bheramara(GK) | 66 | 21:00 | 93 | Kushtia | 154 | 19:30 | 159 | ShahCement | 30 | 00:00
28 | Bhulta | 239 | 22:00 | 94 | Laksam | 34 | 23:00 | 160 | Shahjadpur | 90 | 21:00
29 | Bog-Sherpur | 72 | 21:00 | 95 | Lakshmipur | 29 | 02:00 | 161 | Shahjibazar | 130 | 22:00
30 | Bogura | 174 | 23:00 | 96 | Lalbag | 54 | 13:00 | 162 | Shahmirpur | 60.5 | 16:00
31 | Borhanuddin | 93 | 23:00 | 97 | Lalmonirhat | 69 | 19:30 | 163 | Shariatpur | 91 | 23:00
32 | Brahmanbaria | 137 | 23:00 | 98 | MI_Cement | 12.2 | 02:00 | 164 | Sherpur | 164 | 23:00
33 | Cantonment | 146 | 13:00 | 99 | Madanganj | 45 | 12:00 | 165 | Shikalbaha | 22 | 12:00
34 | Chandina | 15.42 | 22:00 | 100 | Madaripur | 118 | 22:00 | 166 | Shitalakhya | 83.7 | 12:00
35 | Chandpur | 85 | 21:00 | 101 | Madartek | 91.15 | 21:00 | 167 | Sholosohor | 45 | 15:00
36 | Chandraghona | 36 | 20:00 | 102 | Madunaghat | 54 | 19:00 | 168 | Shyampur | 166 | 13:00
37 | Chapai | 72 | 21:00 | 103 | Magura | 69 | 19:30 | 169 | Siddhirganj | 119 | 12:00
38 | Charsaidpur | 39 | 04:00 | 104 | Mahasthangarh | 92 | 22:00 | 170 | Sirajganj | 116 | 20:00
39 | Chauddagram | 64 | 21:00 | 105 | Maijdee | 22 | 00:00 | 171 | Sonargaon | 98 | 00:00
40 | Chhatak | 23 | 11:00 | 106 | Manikganj | 129 | 21:00 | 172 | Sreemongol | 85 | 00:00
41 | Chowmuhani | 171 | 20:00 | 107 | Maniknagar | 78 | 13:00 | 173 | Sreepur | 100 | 19:30
42 | Chuadanga | 123 | 19:30 | 108 | Matarbari | 48 | 21:00 | 174 | Srinagar | 49.01 | 00:00
43 | Coxsbazar | 132 | 21:00 | 109 | Matuail | 66 | 15:00 | 175 | Sunamganj | 60 | 19:00
44 | Cumilla(N) | 144 | 22:00 | 110 | Millgate | 118 | 12:00 | 176 | Sylhet | 54 | 00:00
45 | Cumilla(S) | 147 | 19:30 | 111 | Mirpur | 125 | 19:00 | 177 | Sylhet-132 | 138 | 15:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 11 | 15:00 | 178 | TK | 34 | 21:00
47 | Daudkandi | 150 | 21:00 | 113 | Mirzapur | 47 | 22:00 | 179 | Tangail | 192 | 21:00
48 | Dhaka | 62 | 13:00 | 114 | Mithapukur | 66 | 19:30 | 180 | Taraganj | 25 | 19:30
49 | Dhamrai | 128 | 21:00 | 115 | Modern | N/A | N/A | 181 | Thakurgaon | 113 | 00:00
50 | Dhanmondi | 135 | 13:00 | 116 | Mogbazar | 141.8 | 15:00 | 182 | Tongi | 114 | 11:00
51 | Dohazari | 106 | 19:00 | 117 | Mongla | 32 | 01:00 | 183 | Ullahpara | 40 | 19:30
52 | Faridpur | 170 | 19:30 | 118 | Motijheel | 43 | 19:00 | 184 | Ullon | 42 | 21:00
53 | Fatullah | 101 | 16:00 | 119 | Muktagacha | 40 | 19:30 | 185 | Uttara | 82 | 13:00
54 | Fenchuganj | 42 | 01:00 | 120 | Munshiganj | 115 | 23:00 | 186 | UttaraNew | 63 | 23:00
55 | Feni | 109 | 21:00 | 121 | Muradnagar | 43 | 23:00 | 187 | Zigatola | 73 | 19:30
56 | GPH | 96 | 13:00 | 122 | Mymensingh | 208 | 00:00
57 | Ghatail | 86 | 23:00 | 123 | Naogaon | 138 | 23:00
58 | Ghorashal | 13 | 18:00 | 124 | Narail | 60 | 22:00
59 | Ghorashal-230 | 82 | 19:30 | 125 | Narinda | 80 | 13:00
60 | Goalpara | 36 | 12:00 | 126 | Narshingdi | 184 | 20:00
61 | Gollamari | 88 | 13:00 | 127 | Natore | 157 | 22:00
62 | Gopalganj | 112 | 21:00 | 128 | Nawabganj | 60.8 | 22:00
63 | Gulshan | 64 | 13:00 | 129 | Netrakona | 148 | 20:00
64 | Halishahar | 73.5 | 09:00 | 130 | New | 84.4 | 15:00
65 | HaripurSBU | 146 | 23:00 | 131 | Niamatpur | 74 | 21:00
66 | Hasnabad | 84 | 16:00 | 132 | Noapara | 37 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 26-07-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14117 | 79 |  | 14199.56
1:00 | 13887.5 | 51 |  | 13940.8
2:00 | 13525.5 | 0 |  | 13525.5
3:00 | 13168.5 | 0 |  | 13168.5
4:00 | 12910.5 | 0 |  | 12910.5
5:00 | 12715.5 | 0 |  | 12715.5
6:00 | 12086.93 | 0 |  | 12086.93
7:00 | 12090.95 | 0 |  | 12090.95
8:00 | 12106.8 | 0 |  | 12106.8
9:00 | 12085.99 | 0 |  | 12085.99
10:00 | 12508.34 | 0 |  | 12508.34
11:00 | 12572.27 | 0 |  | 12572.27
12:00 | 13217.98 | 0 |  | 13217.98
13:00 | 13578.42 | 0 |  | 13578.42
14:00 | 13612.67 | 0 |  | 13612.67
15:00 | 13924.57 | 0 |  | 13924.57
16:00 | 13837.11 | 0 |  | 13837.11
17:00 | 13376.21 | 0 |  | 13376.21
18:00 | 13038.09 | 0 |  | 13038.09
19:00 | 14422.5 | 0 |  | 14422.5
19:30 | 15288 | 50 |  | 15340
20:00 | 15301.2 | 142 |  | 15449.2
21:00 | 15395.2 | 148 |  | 15549.86
22:00 | 15263.2 | 150 |  | 15420.2
23:00 | 15288.2 | 145 |  | 15439.73
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 26-07-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7241 | 6876 | 14117 | DAILY GENERATION CURVE
00:30 | 7210.75 | 6791.5 | 14002.25
01:00 | 7180.5 | 6707 | 13887.5 | 26-07-2025
01:30 | 7067 | 6639.5 | 13706.5
02:00 | 6953.5 | 6572 | 13525.5
02:30 | 6848 | 6499 | 13347
03:00 | 6742.5 | 6426 | 13168.5
03:30 | 6705 | 6334.5 | 13039.5
04:00 | 6667.5 | 6243 | 12910.5
04:30 | 6582.5 | 6230.5 | 12813
05:00 | 6497.5 | 6218 | 12715.5
05:30 | 6345.69 | 6055.525 | 12401.215
06:00 | 6193.88 | 5893.05 | 12086.93
06:30 | 6201.98 | 5886.96 | 12088.94
07:00 | 6210.08 | 5880.87 | 12090.95
07:30 | 6181.71 | 5917.165 | 12098.875
08:00 | 6153.34 | 5953.46 | 12106.8
08:30 | 6103.59 | 5992.805 | 12096.395
09:00 | 6053.84 | 6032.15 | 12085.99
09:30 | 6161.765 | 6135.4 | 12297.165
10:00 | 6269.69 | 6238.65 | 12508.34
10:30 | 6350.545 | 6189.76 | 12540.305
11:00 | 6431.4 | 6140.87 | 12572.27
11:30 | 6644.59 | 6250.535 | 12895.125
12:00 | 6857.78 | 6360.2 | 13217.98
12:30 | 7027.51 | 6370.69 | 13398.2
13:00 | 7197.24 | 6381.18 | 13578.42
13:30 | 7234.56 | 6360.985 | 13595.545
14:00 | 7271.88 | 6340.79 | 13612.67
14:30 | 7265.64 | 6502.98 | 13768.62
15:00 | 7259.4 | 6665.17 | 13924.57
15:30 | 7242.57 | 6638.27 | 13880.84
16:00 | 7225.74 | 6611.37 | 13837.11
16:30 | 7137.93 | 6468.73 | 13606.66
17:00 | 7050.12 | 6326.09 | 13376.21
17:30 | 7118.9 | 6088.25 | 13207.15
18:00 | 7187.68 | 5850.41 | 13038.09
18:30 | 7667.59 | 6062.705 | 13730.295
19:00 | 8147.5 | 6275 | 14422.5
19:30 | 8572 | 6716 | 15288
20:00 | 8514.2 | 6787 | 15301.2
20:30 | 8474.7 | 6873.5 | 15348.2 |  | Executive Engineer
21:00 | 8435.2 | 6960 | 15395.2 |  | Network Operation Division
21:30 | 8382.2 | 6947 | 15329.2
22:00 | 8329.2 | 6934 | 15263.2
22:30 | 8332.7 | 6943 | 15275.7
23:00 | 8336.2 | 6952 | 15288.2

## En-Curve
QF-LDC-12
Date | 26-07-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3741 | 2277 | 853 | 38 | 46 | 1432 | 221 | 4443 | 0 | 141 | 882 | 0 | 0 | 43 | 79 | DAILY ENERGY CURVE
00:30 | 3714.5 | 2277.25 | 853 | 38 | 45 | 1443 | 221 | 4295.5 | 0 | 141 | 931.5 | 0 | 0 | 42.5 | 65 | 26-07-2025
01:00 | 3688 | 2277.5 | 853 | 38 | 44 | 1454 | 221 | 4148 | 0 | 141 | 981 | 0 | 0 | 42 | 51
01:30 | 3692 | 2281 | 853.5 | 38 | 43 | 1449.5 | 221 | 4027 | 0 | 141 | 931 | 0 | 0 | 29.5 | 25.5 | Energy Generated | 327.967 |  | MKWHr
02:00 | 3696 | 2284.5 | 854 | 38 | 42 | 1445 | 221 | 3906 | 0 | 141 | 881 | 0 | 0 | 17 | 0 | Energy not Served | 0.715 |  | MKWHr
02:30 | 3690.5 | 2288.5 | 854 | 38 | 42 | 1398.5 | 220 | 3849.5 | 0 | 126.5 | 811 | 0 | 0 | 28.5 | 0 | Total Energy Requirement | 328.682 |  | MKWHr
03:00 | 3685 | 2292.5 | 854 | 38 | 42 | 1352 | 219 | 3793 | 0 | 112 | 741 | 0 | 0 | 40 | 0
03:30 | 3709.5 | 2294.5 | 854 | 38 | 41 | 1275 | 219 | 3758 | 0 | 110 | 702 | 0 | 0 | 38.5 | 0
04:00 | 3734 | 2296.5 | 854 | 38 | 40 | 1198 | 219 | 3723 | 0 | 108 | 663 | 0 | 0 | 37 | 0
04:30 | 3711.5 | 2291.5 | 854 | 38 | 40 | 1200.5 | 218.5 | 3648.5 | 0 | 108 | 660 | 0 | 0 | 42.5 | 0
05:00 | 3689 | 2286.5 | 854 | 38 | 40 | 1203 | 218 | 3574 | 0 | 108 | 657 | 0 | 0 | 48 | 0
05:30 | 3668 | 2241 | 853.5 | 38 | 39 | 1136 | 218.5 | 3439 | 6.715 | 108 | 607 | 0 | 0 | 46.5 | 0
06:00 | 3647 | 2195.5 | 853 | 38 | 38 | 1069 | 219 | 3304 | 13.43 | 108 | 557 | 0 | 0 | 45 | 0
06:30 | 3662 | 2194 | 853.5 | 38 | 37 | 1046 | 219.5 | 3286 | 52.44 | 108 | 554.5 | 0 | 0 | 38 | 0
07:00 | 3677 | 2192.5 | 854 | 38 | 36 | 1023 | 220 | 3268 | 91.45 | 108 | 552 | 0 | 0 | 31 | 0
07:30 | 3663.5 | 2182 | 854 | 38 | 35 | 1024.3 | 220 | 3257 | 141.075 | 108 | 540 | 0 | 0 | 36 | 0
08:00 | 3650 | 2171.5 | 854 | 38 | 34 | 1025.6 | 220 | 3246 | 190.7 | 108 | 528 | 0 | 0 | 41 | 0
08:30 | 3645.5 | 2142.5 | 854 | 38 | 33 | 1004.005 | 220.5 | 3243 | 238.89 | 108 | 523 | 0 | 0 | 46 | 0
09:00 | 3641 | 2113.5 | 854 | 38 | 32 | 982.41 | 221 | 3240 | 287.08 | 108 | 518 | 0 | 0 | 51 | 0
09:30 | 3681 | 2180 | 854 | 38 | 32 | 919.495 | 221 | 3327.5 | 370.17 | 108 | 528.5 | 0 | 0 | 37.5 | 0
10:00 | 3721 | 2246.5 | 854 | 38 | 32 | 856.58 | 221 | 3415 | 453.26 | 108 | 539 | 0 | 0 | 24 | 0
10:30 | 3655.5 | 2247 | 854 | 38 | 34 | 874.84 | 221 | 3476.5 | 396.965 | 115.5 | 602.5 | 0 | 0 | 24.5 | 0
11:00 | 3590 | 2247.5 | 854 | 38 | 36 | 893.1 | 221 | 3538 | 340.67 | 123 | 666 | 0 | 0 | 25 | 0
11:30 | 3652.5 | 2255 | 854 | 38 | 36 | 888.38 | 220.5 | 3574 | 414.245 | 136 | 799 | 0 | 0 | 27.5 | 0
12:00 | 3715 | 2262.5 | 854 | 38 | 36 | 883.66 | 220 | 3610 | 487.82 | 149 | 932 | 0 | 0 | 30 | 0
12:30 | 3654 | 2263 | 854 | 38 | 33 | 898.72 | 220 | 3673.5 | 464.98 | 167.5 | 1096.5 | 0 | 0 | 35 | 0
13:00 | 3593 | 2263.5 | 854 | 38 | 30 | 913.78 | 220 | 3737 | 442.14 | 186 | 1261 | 0 | 0 | 40 | 0
13:30 | 3566.5 | 2245.75 | 854 | 38 | 29 | 921.39 | 218.5 | 3785.5 | 410.405 | 201 | 1290.5 | 0 | 0 | 35 | 0
14:00 | 3540 | 2228 | 854 | 38 | 28 | 929 | 217 | 3834 | 378.67 | 216 | 1320 | 0 | 0 | 30 | 0
14:30 | 3556.5 | 2222.5 | 854 | 38 | 27 | 986 | 217 | 3881.5 | 427.62 | 216.5 | 1323 | 0 | 0 | 19 | 0
15:00 | 3573 | 2217 | 854 | 38 | 26 | 1043 | 217 | 3929 | 476.57 | 217 | 1326 | 0 | 0 | 8 | 0
15:30 | 3557 | 2185.6 | 854 | 38 | 26 | 1075 | 216.5 | 3989 | 395.24 | 192.5 | 1341 | 0 | 0 | 11 | 0
16:00 | 3541 | 2154.2 | 854 | 38 | 26 | 1107 | 216 | 4049 | 313.91 | 168 | 1356 | 0 | 0 | 14 | 0
16:30 | 3428.5 | 2062.7 | 854 | 38 | 25 | 1111 | 216 | 4005 | 220.96 | 219 | 1409 | 0 | 0 | 17.5 | 0
17:00 | 3316 | 1971.2 | 854 | 38 | 24 | 1115 | 216 | 3961 | 128.01 | 270 | 1462 | 0 | 0 | 21 | 0
17:30 | 3307.5 | 1949.1 | 854 | 38 | 30 | 1066 | 216.5 | 3848 | 85.05 | 279 | 1502.5 | 0 | 0 | 31.5 | 0
18:00 | 3299 | 1927 | 854 | 38 | 36 | 1017 | 217 | 3735 | 42.09 | 288 | 1543 | 0 | 0 | 42 | 0
18:30 | 3442 | 2015 | 853.5 | 38 | 41 | 1056 | 218 | 3956 | 21.045 | 354.5 | 1701.25 | 0 | 0 | 34 | 0
19:00 | 3585 | 2103 | 853 | 38 | 46 | 1095 | 219 | 4177 | 0 | 421 | 1859.5 | 0 | 0 | 26 | 0
19:30 | 3544 | 2121 | 854 | 38 | 46 | 1209 | 219 | 4454 | 0 | 520 | 2252 | 0 | 0 | 31 | 50
20:00 | 3469 | 2114 | 853 | 38 | 46 | 1284 | 220 | 4517 | 0 | 568 | 2165.2 | 0 | 0 | 27 | 142
20:30 | 3490 | 2113.5 | 853.5 | 38 | 46 | 1329.5 | 220.5 | 4530 | 0 | 577 | 2121.7 | 0 | 0 | 28.5 | 145
21:00 | 3511 | 2113 | 854 | 38 | 46 | 1375 | 221 | 4543 | 0 | 586 | 2078.2 | 0 | 0 | 30 | 148
21:30 | 3493 | 2115.5 | 853.5 | 38 | 43 | 1375 | 221 | 4527 | 0 | 593.5 | 2041.7 | 0 | 0 | 28 | 149
22:00 | 3475 | 2118 | 853 | 38 | 40 | 1375 | 221 | 4511 | 0 | 601 | 2005.2 | 0 | 0 | 26 | 150
22:30 | 3514 | 2118 | 852.5 | 38 | 44 | 1389 | 221.5 | 4533 | 0 | 597 | 1939.2 | 0 | 0 | 29.5 | 147.5
23:00 | 3553 | 2118 | 852 | 38 | 48 | 1403 | 222 | 4555 | 0 | 593 | 1873.2 | 0 | 0 | 33 | 145
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 26-07-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 385 | 06:00 | 373 | 00:00 | Payra | 416 | 08:00 | 411 | 00:00
Ashuganj | 406 | 7:00 | 385 | 19:00 | Rahanpur | 403 | 10:00 | 380 | 23:00
Bhulta | 402 | 07:00 | 382 | 19:00 | Rampal | 408 | 06:00 | 392 | 23:00
Bibiana | 385 | 06:00 | 376 | 00:00
BIPTC | 403 | 06:00 | 392 | 21:00
Bogura | 384 | 10:00 | 355 | 23:00
Gopalganj | 400 | 06:00 | 388 | 00:00
Kaliakoir | 376 | 06:00 | 363 | 00:00
Madunaghat | 395 | 08:00 | 385 | 00:00
Meghnaghat | 387 | 07:00 | 375 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 225 | 06:00 | 216 | 00:00 | Keranigonj | 223 | 06:00 | 213 | 00:00
AKSML | 231 | 07:00 | 222 | 00:00 | Khulna(S) | 232 | 06:00 | 220 | 00:00
Aminbazar | 225 | 06:00 | 217 | 00:00 | Madunaghat | 233 | 18:00 | 226 | 00:00
Ashuganj | 234 | 06:00 | 223 | 00:00 | Madunaghat-400 | 233 | 07:00 | 225 | 00:00
Ashuganj-400 | 234 | 06:00 | 223 | 00:00 | Maniknagar | 218 | 04:00 | 210 | 00:00
Baghabari | 234 | 06:00 | 225 | 22:00 | Meghnaghat | 227 | 06:00 | 219 | 00:00
Barapukuria | 224 | 09:00 | 202 | 19:30 | Meghnaghat-400 | 223 | 06:00 | 215 | 00:00
Barapukuria-230 | 224 | 09:00 | 202 | 19:30 | Mirsorai | 228 | 18:30 | 217 | 00:00
Barishal | 231 | 07:00 | 221 | 21:00 | Rajshahi | 233 | 05:00 | 220 | 00:00
Bheramara | 233 | 05:00 | 223 | 23:00 | Rampal | 231 | 06:00 | 221 | 00:00
Bhulta | 232 | 06:00 | 211 | 10:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 225 | 07:00 | 217 | 00:00 | Rampura | 231 | 07:00 | 217 | 19:00
BIPTC | 236 | 05:00 | 223 | 23:00 | Shikalbaha | 231 | 18:00 | 223 | 15:00
Bogura | 238 | 10:00 | 220 | 23:00 | Shyampur | 222 | 06:00 | 213 | 00:00
Bogura-400 | 238 | 10:00 | 220 | 23:00 | Siddhirganj | 216 | 18:30 | 212 | 15:00
Borhanuddin | 235 | 09:00 | 228 | 22:00 | Sirajgonj | 240 | 08:00 | 233 | 23:00
BSRM | 228 | 18:30 | 216 | 00:00 | Sreepur | 230 | 06:00 | 219 | 00:00
Cumilla(N) | 222 | 07:00 | 212 | 00:00 | Tongi | 225 | 07:00 | 218 | 00:00
Faridpur | 227 | 06:00 | 217 | 22:00
Fenchuganj | 229 | 03:00 | 219 | 00:00
Ghorashal | 225 | 00:00 | 225 | 00:00
Ghorashal-230 | 230 | 06:00 | 219 | 00:00
Gopalganj | 228 | 05:00 | 220 | 21:00
GPH | 230 | 07:00 | 221 | 00:00
Haripur | 219 | 07:00 | 211 | 00:00
Hasnabad | 222 | 07:00 | 214 | 00:00
Hathazari | 230 | 18:00 | 221 | 00:00
Ishurdi | 236 | 06:00 | 225 | 23:00
Jhenaidah | 231 | 06:00 | 219 | 00:00
Kaliakoir | 231 | 05:00 | 222 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 140 | 05:00 | 126 | 0:00 | Lalmonirhat | 130 | 05:00 | 117 | 19:30
Agargaon | 132 | 06:00 | 125 | 15:00 | Madanganj | 128 | 18:30 | 122 | 10:00
Agrabad | 131 | 07:00 | 124 | 15:00 | Madaripur | 135 | 07:00 | 129 | 21:00
AKS | 130 | 18:00 | 124 | 00:00 | Madartek | 140 | 06:00 | 130 | 15:00
Aminbazar | 132 | 05:00 | 126 | 12:00 | Madunaghat | 132 | 17:00 | 127 | 00:00
Amnura | 135 | 18:00 | 125 | 23:00 | Magura | 133 | 06:00 | 120 | 19:00
Ashuganj | 140 | 05:00 | 135 | 00:00 | Mahasthangarh | 136 | 09:00 | 122 | 23:00
Bagerhat | 132 | 06:00 | 121 | 00:00 | Maijdee | 118 | 13:00 | 106 | 00:00
Bajitpur | 134 | 09:00 | 122 | 19:00 | Manikganj | 128 | 04:00 | 120 | 19:00
Bakulia | 134 | 18:00 | 127 | 15:00 | Maniknagar | 131 | 06:00 | 124 | 12:00
Banani | 139 | 06:00 | 129 | 15:00 | Matarbari | 122 | 07:00 | 111 | 00:00
Bangabhaban | 130 | 07:00 | 123 | 16:00 | Matuail | 128.1 | 06:00 | 122 | 00:00
Barapukuria | 137 | 10:00 | 122 | 19:30 | Millgate | 133 | 05:00 | 125 | 00:00
Barguna | 135 | 07:00 | 130 | 22:00 | Mirpur | 131 | 05:00 | 125 | 12:00
Barishal | 134 | 07:00 | 127 | 00:00 | Mirzapur | 129 | 14:00 | 124 | 00:00
Barishal-230 | 134 | 07:00 | 128 | 00:00 | Mithapukur | 127 | 10:00 | 109 | 23:00
Baroaulia | 132 | 08:00 | 126 | 00:00 | MI_Cement | 129 | 19:00 | 124 | 00:00
Baroirhat | 124 | 17:00 | 115 | 00:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 139 | 04:00 | 125 | 00:00 | Mogbazar | 142 | 06:00 | 130 | 16:00
BashundharaCement | 128 | 18:30 | 122 | 10:00 | Mongla | 132 | 08:00 | 122 | 00:00
Beanibazar | 124 | 17:00 | 116 | 02:00 | Motijheel | 130 | 07:00 | 123 | 16:00
Benapole | 131 | 05:00 | 119 | 23:00 | Muktagacha | 133 | 16:00 | 126 | 08:00
Bhaluka | 133 | 07:00 | 120 | 19:00 | Munshiganj | 128 | 18:00 | 123 | 00:00
Bhandaria | 130 | 18:00 | 119 | 22:00 | Muradnagar | 125 | 18:00 | 116 | 00:00
Bhangura | 135 | 06:00 | 127 | 23:00 | Mymensingh | 135 | 16:00 | 111 | 19:00
Bheramara | 138 | 06:00 | 132 | 19:30 | Naogaon | 134 | 09:00 | 121 | 23:00
Bheramara(GK) | 138 | 07:00 | 131 | 23:00 | Narail | 133 | 06:00 | 123 | 00:00
Bhulta | 122 | 13:00 | 116 | 00:00 | Narinda | 0 | 00:00 | N/A | N/A
Bog-Sherpur | 136 | 09:00 | 124 | 23:00 | Narshingdi | 136 | 05:00 | 117 | 00:00
Bogura | 139 | 09:00 | 126 | 23:00 | Natore | 135 | 10:00 | 126 | 23:00
Bogura-230 | 139 | 09:00 | 127 | 23:00 | Nawabganj | 133 | 04:00 | 127 | 00:00
Brahmanbaria | 135 | 06:00 | 128 | 00:00 | Netrakona | 126 | 10:00 | 108 | 21:00
Cantonment | 132 | 05:00 | 125 | 12:00 | New | 133 | 05:00 | 126 | 11:00
Chandina | 127 | 18:00 | 119 | 00:00 | Niamatpur | 137 | 10:00 | 128 | 00:00
Chandpur | 126 | 14:00 | 115 | 00:00 | Noapara | 134 | 08:00 | 125 | 00:00
Chandraghona | 133 | 17:00 | 128 | 00:00 | Pabna | 135 | 06:00 | 127 | 23:00
Chapai | 135 | 08:00 | 127 | 00:00 | Palashbari | 127 | 09:00 | 108 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 18:30 | 123 | 10:00 | Panchagarh | 133 | 06:00 | 116 | 19:30
Chauddagram | 123 | 17:00 | 113 | 00:00 | Patuakhali | 135 | 07:00 | 131 | 22:00
Chhatak | 122 | 06:00 | 112 | 02:00 | Payra | 137 | 07:00 | 134 | 00:00
Chowmuhani | 118 | 08:00 | 106 | 00:00 | PHP | 123 | 17:00 | 112 | 00:00
Chuadanga | 132 | 06:00 | 121 | 00:00 | Postogola | 130 | 05:00 | 126 | 00:00
Coxsbazar | 125 | 18:00 | 111 | 04:00 | Purbachal | 140 | 06:00 | 125 | 10:00
Cumilla(N) | 127 | 18:00 | 119 | 00:00 | Purbasadipur | 130 | 09:00 | 114 | 19:30
Cumilla(S) | 133 | 04:00 | 116 | 00:00 | Rahanpur | 138 | 09:00 | 130 | 21:00
Daganbhuiyan | 118 | 13:00 | 109 | 00:00 | Rahanpur-400 | 137 | 08:00 | 129 | 23:00
Daudkandi | 122 | 07:00 | 115 | 00:00 | Rahim | 128 | 06:00 | 122 | 00:00
Dhaka | 140 | 07:00 | 130 | 06:00 | Rajbari | 134 | 08:00 | 126 | 23:00
Dhamrai | 132 | 04:00 | 124 | 15:00 | Rajendrapur | 135 | 22:00 | 120 | 19:30
Dhanmondi | 140 | 06:00 | 131 | 12:00 | Rajshahi | 133 | 05:00 | 126 | 00:00
Dohazari | 132 | 18:00 | 122 | 00:00 | Rajshahi-230 | 134 | 05:00 | 126 | 00:00
Faridpur | 135 | 06:00 | 129 | 22:00 | Ramganj | 121 | 13:00 | 109 | 00:00
Fatullah | 130 | 06:00 | 125 | 00:00 | Rampur | 131 | 18:00 | 124 | 15:00
Fenchuganj | 132 | 04:00 | 127 | 00:00 | Rampura | 140 | 06:00 | 130 | 15:00
Feni | 124 | 17:00 | 114 | 00:00 | Rangamati | 132 | 18:00 | 127 | 00:00
Ghatail | 129 | 13:00 | 122 | 08:00 | Rangpur | 134 | 09:00 | 117 | 19:30
Ghorashal | 135 | 04:00 | 129 | 00:00 | Ruppur | 138 | 06:00 | 132 | 00:00
Goalpara | 137 | 06:00 | 122 | 0:00 | Saidpur | 131 | 09:00 | 116 | 19:30
Gollamari | 137 | 06:00 | 128 | 15:00 | Satkhira | 133 | 05:00 | 123 | 19:30
Gopalganj | 136 | 08:00 | 124 | 12:00 | Satmasjid | 132 | 06:00 | 125 | 16:00
Gopalganj-400 | 137 | 05:00 | 131 | 22:00 | Savar | 130 | 04:00 | 125 | 00:00
Gulshan | 139 | 05:00 | 130 | 15:00 | SevenRings | 137 | 06:00 | 129 | 00:00
Halishahar | 133 | 18:00 | 125 | 15:00 | ShahCement | 129 | 18:30 | 123 | 10:00
Haripur | 128 | 07:00 | 123 | 00:00 | Shahjadpur | 138 | 10:00 | 132 | 19:30
HaripurSBU | 128 | 06:00 | 123 | 00:00 | Shahjibazar | 134 | 08:00 | 125 | 00:00
Hasnabad | 131 | 05:00 | 125 | 00:00 | Shahmirpur | 134 | 17:00 | 128 | 00:00
Hathazari | 135 | 17:00 | 129 | 00:00 | Shariatpur | 134 | 07:00 | 126 | 23:00
Ishurdi | 138 | 05:00 | 132 | 21:00 | Sherpur | 135 | 16:00 | 122 | 07:00
Jaldhaka | 128 | 06:00 | 111 | 19:00 | Shikalbaha | 124 | 18:00 | 116 | 00:00
Jamalpur | 137 | 16:00 | 124 | 08:00 | Shikalbaha-230 | 135 | 18:00 | 128 | 15:00
Jashore | 132 | 05:00 | 119 | 19:00 | Shitalakhya | 129 | 19:00 | 124 | 00:00
Jhenaidah | 136 | 05:00 | 122 | 22:00 | Sholosohor | 132 | 18:00 | 127 | 00:00
Jhenaidah-230 | 136 | 06:00 | 127 | 22:00 | Shyampur | 128 | 18:00 | 125 | 10:00
Joydebpur | 137 | 13:00 | 123 | 22:00 | Shyampur-230 | 129 | 06:00 | 124 | 16:00
Joypurhat | 132 | 08:00 | 118 | 23:00 | Siddhirganj | 128 | 04:00 | 124 | 00:00
Juldah | 133 | 18:00 | 127 | 00:00 | Sirajganj | 133 | 08:00 | 124 | 21:00
Kabirpur | 130 | 13:00 | 122 | 00:00 | Sonargaon | 127 | 06:00 | 121 | 00:00
Kachua | 124 | 13:00 | 113 | 00:00 | Sreemongol | 131 | 08:00 | 123 | 00:00
Kaliakoir | 134 | 05:00 | 127 | 00:00 | Sreepur | 134 | 07:00 | 124 | 19:00
Kallyanpur | 132 | 06:00 | 126 | 15:00 | Srinagar | 133 | 05:00 | 127 | 00:00
Kalurghat | 132 | 18:00 | 127 | 00:00 | SSM | 135 | 02:00 | 127 | 23:00
Kamrangirchar | 133 | 05:00 | 127 | 00:00 | Sunamganj | 118 | 05:00 | 110 | 19:00
Kaptai | 134 | 4:00 | 132 | 1:00 | Sylhet | 125 | 18:00 | 117 | 02:00
Kasba | 123 | 18:00 | 115 | 00:00 | Sylhet-132 | 125 | 07:00 | 118 | 00:00
Kazla | 130 | 07:00 | 123 | 16:00 | Tangail | 128 | 06:00 | 122 | 23:00
Keranigonj | 134 | 06:00 | 127 | 00:00 | Taraganj | 131 | 05:00 | 111 | 19:00
Khagrachori | 131 | 17:00 | 125 | 00:00 | Thakurgaon | 133 | 09:00 | 114 | 19:30
Khulna | 135 | 06:00 | 126 | 00:00 | TK | 132 | 18:00 | 127 | 00:00
Khulna(S) | 137 | 06:00 | 129 | 00:00 | Tongi | 132 | 07:00 | 128 | 00:00
Khulshi | 130 | 04:00 | 124 | 00:00 | Ullahpara | 135 | 05:00 | 127 | 19:00
Kishoreganj | 129 | 08:00 | 118 | 00:00 | Ullon | 139 | 05:00 | 129 | 16:00
Kodda | 134 | 13:00 | 121 | 00:00 | Uttara | 132 | 06:00 | 124 | 10:00
KSRM | 132 | 04:00 | 127 | 14:00 | UttaraNew | 131 | 05:00 | 125 | 12:00
Kulaura | 132 | 10:00 | 125 | 00:00 | Zigatola | 134 | 07:00 | 127 | 00:00
Kurigram | 130 | 09:00 | 116 | 19:30
Kushtia | 135 | 04:00 | 126 | 23:00
Laksam | 123 | 13:00 | 112 | 00:00
Lakshmipur | 119 | 17:00 | 107 | 00:00
Lalbag | 134 | 06:00 | 126 | 16:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division