## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 24-07-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-07-2025 | during | 24-07-2025 | during | 24-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 0 | 0 | 0 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 294 | 293 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 188 | 188 | 208.13 | 208.13 | 200 | 200 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 320 | 318 | 335 | 335 | 331 | 331 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 82 | 7 | 50 | 7 | 50 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 54 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 137 | 139 | 149.36 | 149.36 | 138 | 138 | machine problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23 | 25 | 33 | 33 | 22 | 22 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 20 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 33 | 33 | 52.19 | 52.19 | 16 | 33 | Fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 277 | 277 | 300 | 300 | 277 | 277 | Machine Problem
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 126 | 133 | 149 | 149 | 149 | 149 | Machine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 105 | 105 | 105 | 70 | 105 | machine problem
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 105 | 0 | 104 | 104 | 16 | 16 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 555 | 602 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 125 | 108 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 3180 | 3189 | 4724.65 | 4735.65 | 3739.47 | 3802.47
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 26 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 13 | 0 | 15 | 0 | 15 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 40 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 219 | 220 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 212 | 213 | 213 | 213 | 213 | 213 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 56 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 8 | 65 | 48 | 72 | 48 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 16 | 66 | 50 | 50 | 50 | 50 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 37 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 21 | 2 | 25 | 2 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 85 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4 | 0 | 4.37 | 0 | 4.37 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 48 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 100 | 160 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1103 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 8 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 784 | 780 | 790 | 790 | 790 | 790 | Machine Problem
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 2525 | 3089 | 3785.09 | 3812.72 | 3785.09 | 3812.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 200 | 196 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 335 | 329 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 340 | 340 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 31 | 37 | 46.7 | 46.7 | 35 | 35 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 42 | 46 | 55 | 55 | 48 | 48 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 86 | 180 | 195 | 195 | 165 | 165 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 137 | 133 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 41 | 42 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 52 | 167 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 52 | 54 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 43 | 53 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 94 | 87 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 45 | 63 | 113 | 113 | 27 | 65 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 76 | 88 | 115 | 115 | 95 | 95 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 41 | 0 | 59 | 0 | 59 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1670 | 1885 | 2275.56 | 2216.56 | 2099.36 | 2078.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-07-2025 | during | 24-07-2025 | during | 24-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 44 | 45 | 157.5 | 157.5 | 65 | 65 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 118 | 162 | 200 | 200 | 160 | 160 | Machine Problem
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 92 | 80 | 115 | 115 | 80 | 80 | Machine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 51 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 11 | 0 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 35 | 35 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 334 | 304 | 600.9 | 549 | 403.9 | 352
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 58 | 60 | 60 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 153 | 151 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 81 | 86 | 86 | 85 | 85 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 18 | 20 | 20 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 6 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | Plant Shutdown as per schedule HGPI work
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 348 | 378 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | Aythority instruction for delayed HGPI
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1017 | 1042 | 1089 | 1089 | 1025 | 1025
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 856 | 921 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 169 | 158 | 410 | 410 | 184 | 184 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 35 | 105 | 105 | 60 | 60 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 85 | 0 | 66 | 0 | 66 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 600 | 1197 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 0 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1748 | 2311 | 3618.2 | 3552.2 | 3347 | 3281
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 301 | 320 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 117 | 117 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 670 | 900 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 221 | 253 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1530 | 1810 | 2162 | 2161 | 2152 | 2151
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 40 | 40 | 40 | 40 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 201 | 199 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 187 | 179 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 180 | 178 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 400 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 21 | 28 | 28 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 53 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 94 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 6 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1266 | 1452 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 53 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 100 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 2393 | 2893 | 3191.47 | 3024.87 | 3150.09 | 2983.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 47 | 46 | 48 | 48 | 48 | 48 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 105 | 111 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 115 | 114 | 115 | 115 | 95 | 95 | Engine Problem
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 156 | 0 | 157.27 | 0 | 157.27 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 462 | 271 | 501.87 | 310 | 481.87 | 290
System Total |  |  |  |  | 28565.2 | 27045.875 | 14859 | 16794 | 21948.74 | 21451 | 20183.78 | 19776.04
Forecast Scenario (24-07-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 16310 |  | 0 |  | 16310
|  |  |  | 1:00 | 16100 |  | 0 |  | 16100
|  |  |  | 2:00 | 15600 |  | 0 |  | 15600
|  |  |  | 3:00 | 15050 |  | 0 |  | 15050
|  |  |  | 4:00 | 14650 |  | 0 |  | 14650
|  |  |  | 5:00 | 14600 |  | 0 |  | 14600
|  |  |  | 6:00 | 14050 |  | 0 |  | 14050
|  |  |  | 7:00 | 14060 |  | 0 |  | 14060
|  |  |  | 8:00 | 14150 |  | 0 |  | 14150
|  |  |  | 9:00 | 14450 |  | 0 |  | 14450
|  |  |  | 10:00 | 14500 |  | 0 |  | 14500
|  |  |  | 11:00 | 14720 |  | 0 |  | 14720
|  |  |  | 12:00 | 15050 |  | 0 |  | 15050
|  |  |  | 13:00 | 15360 |  | 0 |  | 15360
|  |  |  | 14:00 | 15200 |  | 0 |  | 15200
|  |  |  | 15:00 | 15500 |  | 0 |  | 15500
|  |  |  | 16:00 | 15300 |  | 0 |  | 15300
|  |  |  | 17:00 | 15150 |  | 0 |  | 15150
|  |  |  | 18:00 | 14690 |  | 0 |  | 14690
|  |  |  | 18:30 | 15000 |  | 0 |  | 15000
|  |  |  | 19:00 | 15890 |  | 0 |  | 15890
|  |  |  | 19:30 | 16420 |  | 0 |  | 16420
|  |  |  | 20:00 | 16380 |  | 0 |  | 16380
|  |  |  | 21:00 | 16710 |  | 0 |  | 16710
|  |  |  | 22:00 | 16600 |  | 0 |  | 16600
|  |  |  | 23:00 | 16400 |  | 0 |  | 16400
Probable Maximum Temperature: |  |  | 32.30°C
Probable Maximum Demand at Day Peak: |  |  | 15050.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16710.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16710.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 366.47 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:31 hrs on 24-07-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 23-07-2025 | [28 empty] | Date: | 23-07-2025 | [28 empty] | Date: | 23-07-2025 | [28 empty] | Date: | 23-07-2025 | [28 empty] | Date: | 23-07-2025 | [11 empty] | Date: | 23-07-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [11 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 7 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505 | 54 | 35 | 127 | 141 | 276 | 55 | 55 | 144 | 16 | 450 | 307 | 0 | 0 | 55 | 325 | 196 | 0 | 0 | 125 | 21 | 0 | 0 | 0 | 0 | 30 | 67 | 0 | 0 | 50 | 8 | 0 | 12 | 25 | 0 | 220 | 34 | 24 | 759 | 160 | 0 | 50 | 25 | 102 | 217 | 0 | 0 | 0 | 1165 | 0 | 51 | 128 | 81 | 0 | 340 | 340 | 47 | 209 | 29 | 83 | 0 | 149 | 63 | 7 | 94 | 28 | 53 | 0 | 45 | 0 | 320 | 383 | 0 | 60 | 153 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 100 | 146 | 47 | 0 | 0 | 11 | 9094 | 855 | 156 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1117 | 52 | 1468 | 0 | 40 | 0 | 113 | 113 | 0 | 96 | 37 | 53 | 0 | 28 | 0 | 194 | 0 | 180 | 0 | 182 | 0 | 407 | 0 | 0 | 0 | 46 | 94 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 120 | 180 | 0 | 302 | 650 | 0 | 6806 | 15900 | 100.7
01:00 | 7 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 506 | 54 | 35 | 127 | 141 | 276 | 55 | 55 | 142 | 16 | 450 | 301 | 0 | 0 | 55 | 327 | 195 | 0 | 0 | 125 | 21 | 22 | 0 | 0 | 0 | 30 | 64 | 0 | 0 | 50 | 8 | 0 | 12 | 25 | 0 | 220 | 34 | 30 | 761 | 160 | 0 | 50 | 25 | 94 | 220 | 0 | 0 | 0 | 1140 | 0 | 51 | 128 | 81 | 0 | 346 | 335 | 47 | 195 | 32 | 89 | 0 | 55 | 38 | 7 | 94 | 28 | 52 | 0 | 45 | 0 | 320 | 386 | 0 | 60 | 152 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 100 | 146 | 48 | 0 | 0 | 11 | 8964 | 856 | 155 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1056 | 51 | 1453 | 0 | 40 | 0 | 112 | 113 | 0 | 96 | 37 | 52 | 0 | 28 | 0 | 195 | 0 | 180 | 0 | 181 | 0 | 398 | 0 | 0 | 0 | 46 | 94 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 120 | 180 | 0 | 302 | 650 | 0 | 6715 | 15679 | 100.73
02:00 | 7 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 54 | 35 | 126 | 141 | 276 | 55 | 55 | 150 | 16 | 450 | 301 | 0 | 0 | 55 | 328 | 195 | 0 | 0 | 125 | 21 | 22 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 50 | 8 | 0 | 12 | 25 | 0 | 220 | 32 | 30 | 762 | 80 | 0 | 50 | 25 | 51 | 220 | 0 | 0 | 0 | 1130 | 0 | 51 | 142 | 81 | 0 | 347 | 340 | 49 | 193 | 32 | 90 | 0 | 51 | 43 | 7 | 94 | 26 | 52 | 0 | 45 | 0 | 320 | 387 | 0 | 60 | 136 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 100 | 146 | 48 | 0 | 0 | 11 | 8757 | 856 | 157 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1023 | 51 | 1453 | 0 | 40 | 0 | 109 | 113 | 0 | 96 | 37 | 26 | 0 | 28 | 0 | 194 | 0 | 182 | 0 | 181 | 0 | 343 | 0 | 0 | 0 | 46 | 94 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 120 | 180 | 0 | 302 | 640 | 0 | 6592 | 15349 | 100.76
03:00 | 7 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 54 | 35 | 126 | 108 | 145 | 55 | 55 | 144 | 0 | 450 | 309 | 0 | 0 | 55 | 326 | 195 | 0 | 0 | 125 | 21 | 22 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 50 | 8 | 0 | 12 | 25 | 0 | 220 | 0 | 31 | 764 | 0 | 0 | 50 | 25 | 0 | 218 | 0 | 0 | 0 | 1055 | 0 | 51 | 100 | 81 | 0 | 343 | 335 | 49 | 205 | 32 | 92 | 0 | 51 | 38 | 19 | 94 | 26 | 52 | 0 | 45 | 0 | 320 | 386 | 0 | 60 | 147 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 100 | 146 | 48 | 0 | 0 | 11 | 8309 | 856 | 157 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1028 | 51 | 1451 | 0 | 40 | 0 | 50 | 113 | 0 | 0 | 37 | 25 | 0 | 22 | 0 | 195 | 0 | 186 | 0 | 183 | 0 | 384 | 0 | 0 | 0 | 46 | 94 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 120 | 220 | 0 | 303 | 650 | 0 | 6535 | 14844 | 100.79
04:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 506 | 54 | 20 | 126 | 108 | 95 | 30 | 55 | 157 | 0 | 450 | 303 | 0 | 0 | 55 | 323 | 195 | 0 | 0 | 125 | 21 | 22 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 50 | 8 | 0 | 12 | 25 | 0 | 220 | 0 | 31 | 760 | 0 | 0 | 50 | 25 | 0 | 219 | 0 | 0 | 0 | 1055 | 0 | 51 | 100 | 81 | 0 | 343 | 340 | 48 | 206 | 32 | 72 | 0 | 51 | 36 | 19 | 94 | 26 | 52 | 0 | 45 | 0 | 320 | 388 | 0 | 60 | 156 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 100 | 146 | 48 | 0 | 0 | 11 | 8190 | 856 | 157 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1014 | 51 | 1451 | 0 | 40 | 0 | 0 | 35 | 0 | 0 | 37 | 0 | 0 | 22 | 0 | 195 | 0 | 187 | 0 | 186 | 0 | 375 | 0 | 0 | 0 | 46 | 94 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 120 | 220 | 0 | 303 | 650 | 0 | 6364 | 14554 | 100.82
05:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 54 | 17 | 126 | 108 | 95 | 30 | 55 | 156 | 0 | 450 | 295 | 0 | 0 | 55 | 326 | 196 | 0 | 0 | 125 | 21 | 22 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 16 | 8 | 0 | 12 | 25 | 0 | 220 | 0 | 31 | 760 | 0 | 0 | 49 | 25 | 0 | 219 | 0 | 0 | 0 | 1055 | 0 | 51 | 100 | 81 | 0 | 346 | 335 | 49 | 199 | 32 | 70 | 0 | 51 | 37 | 19 | 94 | 26 | 52 | 0 | 45 | 0 | 320 | 389 | 0 | 60 | 156 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 100 | 145 | 48 | 0 | 0 | 11 | 8139 | 856 | 157 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1013 | 51 | 1452 | 0 | 40 | 0 | 0 | 35 | 0 | 0 | 33 | 0 | 0 | 22 | 0 | 195 | 0 | 188 | 0 | 187 | 0 | 355 | 0 | 0 | 0 | 46 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 120 | 220 | 0 | 302 | 650 | 0 | 6358 | 14497 | 100.85
06:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 54 | 17 | 124 | 80 | 45 | 30 | 55 | 144 | 16 | 380 | 290 | 0 | 0 | 55 | 326 | 196 | 0 | 1 | 125 | 21 | 22 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 16 | 8 | 0 | 12 | 25 | 1 | 220 | 0 | 33 | 762 | 0 | 0 | 47 | 8 | 0 | 218 | 0 | 0 | 0 | 1040 | 0 | 51 | 50 | 81 | 0 | 351 | 340 | 49 | 193 | 32 | 70 | 0 | 51 | 37 | 19 | 94 | 24 | 52 | 0 | 45 | 0 | 320 | 390 | 0 | 60 | 149 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 92 | 146 | 48 | 0 | 2 | 11 | 7906 | 856 | 167 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 965 | 17 | 1463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 192 | 0 | 188 | 0 | 187 | 0 | 339 | 0 | 1 | 0 | 46 | 114 | 1 | 100 | 0 | 0 | 1 | 7 | 1 | 0 | 167 | 117 | 180 | 0 | 302 | 635 | 0 | 6092 | 13998 | 100.88
07:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 54 | 17 | 97 | 79 | 45 | 30 | 55 | 146 | 32 | 350 | 290 | 0 | 0 | 55 | 326 | 195 | 0 | 5 | 125 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 0 | 12 | 25 | 0 | 220 | 0 | 31 | 761 | 0 | 0 | 20 | 8 | 0 | 219 | 0 | 0 | 0 | 1035 | 4 | 51 | 50 | 81 | 0 | 348 | 340 | 49 | 193 | 32 | 70 | 0 | 52 | 36 | 19 | 94 | 24 | 52 | 2 | 44 | 0 | 320 | 390 | 0 | 60 | 150 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 92 | 135 | 48 | 0 | 10 | 11 | 7804 | 856 | 167 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 16 | 975 | 17 | 1461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 198 | 0 | 188 | 0 | 187 | 0 | 341 | 0 | 1 | 0 | 47 | 114 | 6 | 94 | 0 | 0 | 2 | 31 | 1 | 0 | 166 | 117 | 180 | 0 | 302 | 637 | 0 | 6173 | 13977 | 100.91
08:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 506 | 54 | 17 | 94 | 78 | 45 | 30 | 55 | 141 | 55 | 350 | 300 | 0 | 0 | 55 | 326 | 194 | 0 | 15 | 125 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | 0 | 12 | 25 | 2 | 220 | 0 | 3 | 760 | 0 | 0 | 19 | 8 | 0 | 218 | 0 | 0 | 0 | 1055 | 5 | 51 | 50 | 81 | 0 | 300 | 340 | 48 | 197 | 34 | 71 | 0 | 53 | 37 | 19 | 77 | 24 | 52 | 10 | 43 | 0 | 320 | 386 | 0 | 60 | 147 | 8 | 0 | 80 | 30 | 0 | 18 | 0 | 17 | 92 | 135 | 47 | 1 | 16 | 11 | 7767 | 857 | 169 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 51 | 965 | 17 | 1450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 20 | 199 | 0 | 188 | 0 | 188 | 0 | 349 | 0 | 2 | 0 | 47 | 114 | 10 | 100 | 0 | 0 | 4 | 82 | 1 | 0 | 171 | 117 | 180 | 0 | 303 | 630 | 0 | 6298 | 14065 | 100.94
09:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505 | 54 | 17 | 92 | 130 | 210 | 30 | 55 | 162 | 105 | 350 | 302 | 0 | 0 | 35 | 324 | 194 | 0 | 20 | 125 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 0 | 12 | 25 | 3 | 220 | 0 | 2 | 760 | 0 | 0 | 19 | 8 | 0 | 218 | 0 | 0 | 0 | 1025 | 8 | 43 | 58 | 81 | 0 | 341 | 340 | 48 | 192 | 26 | 76 | 0 | 51 | 37 | 19 | 77 | 44 | 52 | 28 | 43 | 0 | 320 | 381 | 0 | 60 | 146 | 8 | 0 | 80 | 30 | 0 | 18 | 0 | 17 | 92 | 134 | 47 | 1 | 24 | 11 | 8088 | 856 | 171 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 70 | 1001 | 17 | 1403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 23 | 200 | 0 | 150 | 0 | 150 | 0 | 345 | 0 | 2 | 0 | 47 | 114 | 20 | 103 | 0 | 0 | 6 | 102 | 1 | 0 | 168 | 117 | 180 | 0 | 302 | 600 | 0 | 6253 | 14341 | 100.97
10:00 | 7 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451 | 54 | 30 | 95 | 138 | 277 | 40 | 55 | 162 | 105 | 320 | 307 | 0 | 0 | 55 | 320 | 192 | 0 | 25 | 125 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 0 | 12 | 25 | 4 | 220 | 0 | 2 | 760 | 0 | 0 | 19 | 8 | 0 | 214 | 0 | 0 | 0 | 1055 | 0 | 43 | 110 | 81 | 0 | 332 | 340 | 48 | 205 | 29 | 91 | 0 | 52 | 37 | 12 | 77 | 46 | 43 | 33 | 43 | 0 | 320 | 335 | 0 | 60 | 152 | 8 | 0 | 80 | 30 | 0 | 18 | 0 | 17 | 92 | 134 | 46 | 1 | 16 | 11 | 8191 | 856 | 167 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 92 | 945 | 0 | 1263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 45 | 199 | 0 | 150 | 0 | 150 | 0 | 385 | 0 | 5 | 0 | 47 | 114 | 24 | 103 | 0 | 0 | 7 | 174 | 1 | 0 | 173 | 117 | 180 | 0 | 302 | 600 | 0 | 6226 | 14417 | 101
11:00 | 7 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451 | 54 | 35 | 120 | 138 | 263 | 55 | 55 | 162 | 105 | 450 | 301 | 0 | 0 | 55 | 320 | 188 | 0 | 10 | 125 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 0 | 12 | 25 | 3 | 220 | 0 | 2 | 783 | 5 | 0 | 19 | 8 | 0 | 214 | 0 | 0 | 0 | 1075 | 0 | 43 | 132 | 80 | 0 | 336 | 340 | 47 | 204 | 28 | 78 | 0 | 52 | 36 | 12 | 77 | 46 | 43 | 54 | 43 | 0 | 320 | 322 | 0 | 60 | 155 | 8 | 0 | 82 | 30 | 0 | 16 | 0 | 17 | 92 | 105 | 45 | 2 | 45 | 11 | 8393 | 856 | 168 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 98 | 920 | 0 | 1271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 51 | 200 | 0 | 150 | 0 | 150 | 0 | 372 | 0 | 5 | 0 | 48 | 114 | 25 | 105 | 0 | 0 | 3 | 173 | 1 | 0 | 173 | 117 | 180 | 0 | 300 | 603 | 0 | 6220 | 14613 | 101.03
12:00 | 7 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 54 | 35 | 126 | 137 | 277 | 55 | 55 | 162 | 105 | 450 | 294 | 0 | 0 | 55 | 320 | 188 | 0 | 32 | 125 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 0 | 12 | 25 | 4 | 219 | 0 | 2 | 784 | 100 | 0 | 19 | 8 | 0 | 212 | 0 | 0 | 0 | 1103 | 13 | 43 | 137 | 86 | 0 | 335 | 340 | 42 | 200 | 31 | 76 | 0 | 52 | 45 | 12 | 94 | 52 | 43 | 41 | 41 | 0 | 320 | 348 | 0 | 60 | 153 | 8 | 0 | 82 | 30 | 0 | 16 | 0 | 17 | 92 | 118 | 44 | 1 | 51 | 11 | 8726 | 856 | 169 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 85 | 600 | 0 | 1266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 53 | 201 | 0 | 187 | 0 | 180 | 0 | 400 | 0 | 6 | 0 | 47 | 115 | 32 | 105 | 0 | 0 | 7 | 156 | 1 | 0 | 221 | 117 | 220 | 0 | 301 | 670 | 0 | 6133 | 14859 | 101.06
13:00 | 7 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 54 | 35 | 127 | 137 | 277 | 55 | 55 | 162 | 105 | 450 | 294 | 0 | 0 | 55 | 318 | 188 | 0 | 32 | 125 | 19 | 22 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 44 | 0 | 12 | 25 | 3 | 218 | 0 | 7 | 780 | 160 | 0 | 34 | 17 | 0 | 211 | 0 | 0 | 0 | 1070 | 18 | 43 | 133 | 86 | 0 | 333 | 340 | 44 | 200 | 33 | 91 | 0 | 52 | 48 | 12 | 93 | 54 | 48 | 56 | 33 | 0 | 320 | 356 | 0 | 57 | 152 | 8 | 0 | 81 | 30 | 0 | 16 | 0 | 17 | 92 | 118 | 44 | 2 | 23 | 11 | 8817 | 856 | 163 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 96 | 570 | 0 | 1257 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 102 | 0 | 55 | 195 | 0 | 186 | 0 | 181 | 0 | 386 | 0 | 5 | 0 | 47 | 115 | 25 | 105 | 0 | 0 | 8 | 189 | 1 | 0 | 220 | 117 | 220 | 0 | 302 | 800 | 0 | 6262 | 15079 | 101.09
14:00 | 7 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 54 | 35 | 138 | 136 | 277 | 55 | 55 | 162 | 105 | 450 | 296 | 0 | 0 | 55 | 314 | 131 | 0 | 26 | 125 | 23 | 21 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 16 | 44 | 0 | 12 | 25 | 4 | 218 | 0 | 3 | 780 | 124 | 0 | 40 | 25 | 0 | 211 | 0 | 0 | 0 | 1103 | 9 | 43 | 120 | 85 | 0 | 332 | 340 | 45 | 198 | 33 | 90 | 0 | 52 | 63 | 12 | 93 | 54 | 43 | 33 | 33 | 0 | 320 | 333 | 0 | 57 | 143 | 8 | 0 | 78 | 30 | 0 | 16 | 0 | 17 | 90 | 142 | 44 | 2 | 45 | 11 | 8762 | 861 | 161 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 95 | 575 | 0 | 1278 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 95 | 0 | 50 | 199 | 0 | 179 | 0 | 178 | 0 | 347 | 0 | 5 | 0 | 47 | 115 | 28 | 21 | 0 | 0 | 8 | 100 | 1 | 0 | 219 | 117 | 220 | 0 | 302 | 800 | 0 | 6062 | 14824 | 101.12
15:00 | 7 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 54 | 35 | 141 | 136 | 276 | 55 | 55 | 162 | 105 | 450 | 300 | 0 | 0 | 55 | 315 | 183 | 0 | 21 | 125 | 23 | 21 | 0 | 0 | 0 | 0 | 86 | 0 | 2 | 16 | 50 | 0 | 12 | 25 | 3 | 217 | 0 | 3 | 779 | 160 | 0 | 40 | 25 | 0 | 211 | 0 | 0 | 0 | 1145 | 9 | 51 | 97 | 112 | 0 | 330 | 340 | 43 | 204 | 30 | 91 | 0 | 51 | 63 | 12 | 93 | 54 | 43 | 35 | 33 | 0 | 320 | 378 | 0 | 58 | 149 | 0 | 0 | 78 | 30 | 0 | 16 | 0 | 17 | 89 | 142 | 44 | 2 | 37 | 2 | 8986 | 861 | 159 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 71 | 579 | 0 | 1400 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 82 | 0 | 35 | 196 | 0 | 179 | 0 | 178 | 0 | 398 | 0 | 3 | 0 | 47 | 113 | 12 | 97 | 0 | 0 | 6 | 120 | 1 | 0 | 221 | 117 | 220 | 0 | 301 | 808 | 0 | 6265 | 15251 | 101.15
16:00 | 30 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 523 | 54 | 35 | 142 | 135 | 276 | 55 | 55 | 162 | 55 | 450 | 290 | 0 | 0 | 35 | 315 | 187 | 0 | 12 | 125 | 22 | 21 | 0 | 0 | 0 | 0 | 95 | 0 | 13 | 16 | 50 | 0 | 25 | 25 | 2 | 217 | 0 | 2 | 780 | 160 | 0 | 40 | 25 | 0 | 212 | 0 | 0 | 0 | 1100 | 3 | 51 | 100 | 123 | 0 | 333 | 340 | 44 | 182 | 30 | 90 | 0 | 54 | 56 | 19 | 93 | 56 | 43 | 19 | 33 | 0 | 320 | 353 | 0 | 58 | 150 | 8 | 0 | 78 | 30 | 0 | 16 | 0 | 17 | 88 | 122 | 44 | 1 | 20 | 3 | 8803 | 861 | 155 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 42 | 629 | 0 | 1446 | 0 | 0 | 0 | 25 | 45 | 0 | 23 | 0 | 0 | 53 | 0 | 27 | 196 | 0 | 174 | 0 | 175 | 0 | 372 | 0 | 3 | 0 | 47 | 114 | 15 | 107 | 0 | 0 | 4 | 113 | 1 | 0 | 208 | 117 | 220 | 0 | 301 | 749 | 0 | 6260 | 15063 | 101.19
17:00 | 48 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 502 | 54 | 18 | 142 | 134 | 276 | 55 | 55 | 162 | 34 | 450 | 295 | 0 | 0 | 55 | 316 | 188 | 0 | 7 | 125 | 22 | 12 | 0 | 0 | 0 | 0 | 97 | 0 | 19 | 16 | 50 | 0 | 27 | 25 | 1 | 218 | 0 | 7 | 782 | 160 | 0 | 40 | 25 | 0 | 213 | 0 | 0 | 0 | 1070 | 2 | 51 | 105 | 123 | 0 | 332 | 340 | 44 | 188 | 30 | 89 | 0 | 56 | 58 | 19 | 85 | 56 | 43 | 13 | 33 | 0 | 320 | 352 | 0 | 58 | 149 | 8 | 0 | 80 | 30 | 0 | 16 | 0 | 17 | 89 | 114 | 44 | 1 | 14 | 9 | 8771 | 868 | 155 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 32 | 830 | 0 | 1448 | 0 | 0 | 0 | 35 | 70 | 0 | 23 | 0 | 0 | 27 | 0 | 14 | 196 | 0 | 164 | 0 | 140 | 0 | 335 | 0 | 1 | 0 | 47 | 114 | 9 | 107 | 0 | 0 | 3 | 17 | 1 | 0 | 210 | 117 | 220 | 0 | 300 | 699 | 0 | 6220 | 14991 | 101.22
18:00 | 82 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451 | 51 | 17 | 142 | 134 | 276 | 55 | 55 | 162 | 17 | 400 | 296 | 0 | 0 | 55 | 313 | 132 | 0 | 1 | 125 | 22 | 22 | 0 | 0 | 0 | 0 | 96 | 0 | 23 | 16 | 63 | 0 | 28 | 25 | 1 | 219 | 0 | 11 | 781 | 160 | 0 | 40 | 25 | 0 | 213 | 0 | 0 | 0 | 1035 | 0 | 51 | 123 | 127 | 0 | 300 | 300 | 42 | 188 | 33 | 87 | 0 | 141 | 61 | 19 | 89 | 52 | 43 | 4 | 33 | 0 | 320 | 363 | 0 | 58 | 149 | 6 | 0 | 80 | 30 | 0 | 16 | 0 | 17 | 79 | 140 | 44 | 0 | 4 | 11 | 8657 | 872 | 155 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 8 | 871 | 0 | 1361 | 0 | 0 | 0 | 35 | 70 | 0 | 23 | 0 | 8 | 7 | 0 | 4 | 170 | 0 | 150 | 0 | 140 | 0 | 344 | 0 | 1 | 0 | 47 | 114 | 1 | 106 | 0 | 0 | 1 | 7 | 1 | 0 | 216 | 117 | 180 | 0 | 301 | 694 | 0 | 6042 | 14699 | 101.27
19:00 | 75 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553 | 35 | 35 | 149 | 137 | 277 | 55 | 55 | 162 | 0 | 450 | 296 | 0 | 0 | 55 | 313 | 186 | 0 | 0 | 125 | 22 | 22 | 0 | 0 | 0 | 15 | 93 | 0 | 17 | 50 | 65 | 0 | 37 | 25 | 0 | 220 | 10 | 9 | 778 | 160 | 0 | 40 | 25 | 14 | 212 | 0 | 0 | 0 | 1212 | 0 | 51 | 127 | 145 | 0 | 324 | 335 | 45 | 202 | 37 | 89 | 0 | 164 | 62 | 19 | 89 | 62 | 52 | 0 | 34 | 0 | 320 | 378 | 0 | 58 | 149 | 6 | 0 | 81 | 30 | 0 | 16 | 0 | 17 | 79 | 151 | 44 | 0 | 0 | 11 | 9299 | 883 | 158 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 887 | 33 | 1451 | 0 | 12 | 0 | 95 | 82 | 0 | 80 | 9 | 52 | 0 | 25 | 0 | 180 | 0 | 180 | 0 | 177 | 0 | 392 | 0 | 0 | 0 | 47 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 236 | 117 | 220 | 0 | 302 | 715 | 0 | 6598 | 15897 | 101.31
19:30 | 65 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556 | 35 | 35 | 149 | 137 | 277 | 55 | 55 | 162 | 0 | 450 | 285 | 0 | 0 | 55 | 315 | 189 | 0 | 0 | 125 | 23 | 22 | 0 | 0 | 0 | 15 | 101 | 0 | 12 | 50 | 72 | 0 | 37 | 25 | 0 | 220 | 20 | 13 | 780 | 160 | 0 | 40 | 25 | 45 | 212 | 0 | 0 | 0 | 1224 | 0 | 51 | 130 | 170 | 0 | 328 | 340 | 45 | 202 | 37 | 89 | 0 | 161 | 63 | 19 | 88 | 54 | 52 | 0 | 38 | 0 | 320 | 377 | 0 | 59 | 151 | 6 | 0 | 81 | 30 | 0 | 16 | 0 | 17 | 79 | 160 | 45 | 0 | 0 | 0 | 9387 | 883 | 159 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1116 | 50 | 1446 | 0 | 37 | 0 | 113 | 113 | 0 | 94 | 13 | 52 | 0 | 21 | 0 | 199 | 0 | 181 | 0 | 178 | 0 | 414 | 0 | 0 | 0 | 45 | 114 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 222 | 117 | 220 | 0 | 301 | 800 | 0 | 7038 | 16425 | 101.31
20:00 | 74 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 557 | 54 | 35 | 149 | 138 | 277 | 55 | 55 | 162 | 0 | 450 | 302 | 0 | 0 | 55 | 317 | 189 | 0 | 0 | 125 | 24 | 21 | 0 | 0 | 0 | 15 | 101 | 0 | 13 | 65 | 72 | 0 | 25 | 25 | 0 | 220 | 33 | 16 | 780 | 160 | 0 | 40 | 25 | 48 | 213 | 0 | 0 | 0 | 1224 | 0 | 51 | 129 | 180 | 0 | 334 | 340 | 44 | 194 | 37 | 89 | 0 | 162 | 62 | 19 | 87 | 52 | 52 | 0 | 42 | 0 | 320 | 380 | 0 | 58 | 152 | 6 | 0 | 81 | 30 | 0 | 16 | 0 | 17 | 79 | 169 | 45 | 0 | 0 | 0 | 9479 | 884 | 160 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1101 | 35 | 1444 | 0 | 35 | 0 | 113 | 113 | 0 | 94 | 30 | 52 | 0 | 21 | 0 | 200 | 0 | 181 | 0 | 177 | 0 | 352 | 0 | 0 | 0 | 46 | 114 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 117 | 220 | 0 | 301 | 751 | 0 | 6910 | 16389 | 101.35
21:00 | 82 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 602 | 54 | 35 | 133 | 139 | 277 | 55 | 55 | 162 | 0 | 450 | 293 | 0 | 0 | 55 | 318 | 188 | 0 | 0 | 108 | 25 | 20 | 0 | 0 | 0 | 15 | 85 | 0 | 8 | 66 | 65 | 0 | 37 | 25 | 0 | 220 | 48 | 21 | 780 | 160 | 0 | 40 | 26 | 56 | 213 | 0 | 0 | 0 | 1224 | 0 | 51 | 133 | 180 | 0 | 329 | 340 | 46 | 196 | 37 | 88 | 0 | 167 | 63 | 19 | 87 | 54 | 53 | 0 | 42 | 0 | 320 | 378 | 0 | 58 | 151 | 6 | 0 | 81 | 30 | 0 | 18 | 0 | 17 | 80 | 162 | 45 | 0 | 0 | 0 | 9509 | 883 | 158 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1197 | 35 | 1452 | 0 | 40 | 0 | 113 | 113 | 0 | 94 | 37 | 53 | 0 | 21 | 0 | 199 | 0 | 179 | 0 | 178 | 0 | 414 | 0 | 0 | 0 | 46 | 114 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 253 | 117 | 220 | 0 | 320 | 900 | 0 | 7285 | 16794 | 101.39
22:00 | 50 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 640 | 54 | 35 | 125 | 138 | 277 | 55 | 55 | 162 | 0 | 450 | 280 | 0 | 0 | 55 | 318 | 190 | 0 | 0 | 108 | 24 | 14 | 0 | 0 | 0 | 15 | 84 | 0 | 9 | 66 | 66 | 0 | 37 | 25 | 0 | 220 | 46 | 21 | 776 | 160 | 0 | 40 | 25.5 | 61 | 216 | 0 | 0 | 0 | 1100 | 0 | 51 | 140 | 180 | 0 | 338 | 340 | 46 | 186 | 37 | 89 | 0 | 165 | 60 | 19 | 87 | 54 | 43 | 0 | 43 | 0 | 320 | 350 | 0 | 58 | 149 | 6 | 0 | 81 | 30 | 0 | 18 | 0 | 17 | 80 | 173 | 46 | 0 | 0 | 0 | 9341.5 | 860 | 158 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1199 | 34 | 1438 | 0 | 40 | 0 | 113 | 113 | 0 | 94 | 37 | 52.2 | 0 | 21 | 0 | 198 | 0 | 173 | 0 | 176 | 0 | 414 | 0 | 0 | 0 | 46 | 114 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 267 | 117 | 220 | 0 | 356 | 935 | 0 | 7325.2 | 16666.7 | 101.43
23:00 | 15 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 603 | 54 | 35 | 117 | 139 | 277 | 55 | 55 | 162 | 0 | 450 | 292 | 0 | 0 | 55 | 318 | 130 | 0 | 0 | 108 | 24.5 | 14 | 0 | 0 | 0 | 0 | 79 | 0 | 10 | 65 | 64 | 0 | 37 | 25 | 0 | 220 | 47 | 22 | 778 | 160 | 0 | 40 | 25.5 | 62 | 218 | 0 | 0 | 0 | 1160 | 0 | 51 | 144 | 76 | 0 | 336 | 340 | 47 | 206 | 37 | 89 | 0 | 161 | 63 | 19 | 87 | 60 | 43 | 0 | 43 | 0 | 320 | 380 | 0 | 59 | 134 | 6 | 0 | 81 | 30 | 0 | 18 | 0 | 17 | 80 | 163 | 46 | 0 | 0 | 0 | 9190 | 860 | 158 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1217 | 34 | 1435 | 0 | 40 | 0 | 113 | 113 | 0 | 94 | 37 | 52.2 | 0 | 21 | 0 | 196 | 0 | 176 | 0 | 175 | 0 | 351 | 0 | 0 | 0 | 46 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 117 | 220 | 0 | 300 | 1058 | 0 | 7355.2 | 16545.2 | 101.47
Total KWH | 511488 | 1778880 | 652320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11244970 | 1262160 | 716760 | 3018528 | 3013440 | 5439458 | 1187503 | 1324180 | 3804480 | 993600 | 9744000 | 7180015 | 0 | 0 | 1284009 | 7732812 | 4650000 | 0 | 199089 | 2902800 | 522600 | 454320 | 0 | 0 | 0 | 132982 | 1133760 | 0 | 106080 | 817091 | 762068 | 0 | 427200 | 590400 | 24719 | 5270929 | 306109 | 388320 | 18632727.27 | 2228073 | 0 | 906240 | 492125.4 | 466691 | 5055283 | 0 | 0 | 0 | 26476361 | 76005 | 1105585 | 2754981 | 2458909 | 0 | 8408300 | 8138000 | 1104000 | 4815000 | 776808 | 2022720 | 0 | 1986720 | 1189440 | 389210 | 2134080 | 1012800 | 1148870 | 337891 | 970016 | 0 | 7676000 | 9256000 | 0 | 1376520 | 3582982 | 154440 | 0 | 1939200 | 716928 | 0 | 423000 | 0 | 423000 | 2136000 | 3321600 | 1057920 | 15400 | 310340 | 203040 | 207256275.67 | 20849454 | 4040640 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 753840 | 22552732 | 574080 | 32862909 | 0 | 416021 | 0 | 1005504 | 1362912 | 0 | 866272 | 306374 | 410294 | 769050 | 243055 | 392248 | 4769364 | 0 | 4436291 | 0 | 4428155 | 0 | 8953272 | 0 | 34860 | 0 | 1053818 | 2655511 | 201986 | 2513212 | 0 | 0 | 52220.88 | 1273680 | 4875 | 0 | 4853000 | 2829000 | 5102590 | 0 | 7316364 | 17920000 | 0 | 156715583.88 | 363971859.55

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 23-07-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14859 | MW | 12:00 Hr. | Energy Generated |  |  | 363.9719 |  | MKWHr.
| Day Peak Demand |  |  | 15057.55 | MW | 12:00 Hr. | Energy Unserverd |  |  | 5.146 |  | MKWHr.
| Evening Peak Generation |  |  | 16794 | MW | 21:00 Hr. | Energy Demand |  |  | 369.1179 |  | MKWHr.
| Evening Peak Demand |  |  | 17099.14 | MW | 21:00 Hr. | Maximum Temperature |  |  | 36 |  | °C
| Minimum Generation of the Day |  |  | 13977 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 980.56 |  | MMCFD
| Maximum Generation of the Day |  |  | 16794 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 7.2564 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 41.5287 | 0 | 27.8896 | 0 | 0 | 0.19909 | 0 | 0 | 69.6174 | Gas | 134.9104 | Gas | 460398222.97
| Chattogram Zone |  |  | 5.4436 | 45.1091 | 8.2627 | 0 | 5.2709 | 0.10072 | 0 | 0.10608 | 64.2932 | Coal | 98.805 | Coal | 596115900.7112
| Cumilla Zone |  |  | 27.1958 | 0 | 12.2068 | 0 | 0 | 0.33789 | 1.0128 | 0 | 40.7533 | HFO | 64.796 | HFO | 1217756430.108
| Mymensingh Zone |  |  | 1.0579 | 0 | 6.0836 | 0 | 0 | 0.32574 | 0 | 0 | 7.4673 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 25.1251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.1251 | Hydro | 5.2709 | Hydro | 527092.9
| Khulna Zone |  |  | 4.0406 | 22.5527 | 0.57408 | 0 | 0 | 0.75384 | 21.7615 | 0 | 49.6827 | Solar | 4.4462 | Solar | 72912536.0968
| Barishal Zone |  |  | 7.9316 | 30.0894 | 0 | 0 | 0 | 0.004875 | 0 | 0 | 38.0258 | Import | 55.6372 | Import | 291857344.05
| Rajshahi Zone |  |  | 22.5871 | 0 | 4.6104 | 0 | 0 | 1.1962 | 32.8629 | 0 | 61.2566 | Wind | 0.10608 | Wind | 1553011.2
| Rangpur Zone |  |  | 0 | 1.0538 | 5.1687 | 0 | 0 | 1.5279 | 0 | 0 | 7.7504
| Total |  |  | 134.9104 | 98.805 | 64.796 | 0 | 5.2709 | 4.4462 | 55.6372 | 0.10608 | 363.9719
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 460398222.97 |  | Hydro | 527092.9
|  |  |  | Coal | 596115900.7112 |  | Solar | 72912536.0968
|  |  |  | HFO | 1217756430.108 |  | Import | 291857344.05
|  |  |  | HSD | 0 |  | Wind | 1553011.2
[5 empty] | Total: | 264,11,20,538 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.8495 | Peak Hr Flow | 883.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 33057345.54 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 32.8629 | Peak Hr Flow | 1452.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 820 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.0128 | Peak Hr Flow | 54.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 1002 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 54.7252 | Peak Hr Flow | 2389.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 28 |  | 5842
|  |  |  | Chattogram |  | 0 |  | 1556
|  |  |  | Cumilla |  | 60 |  | 1544
|  |  |  | Mymensingh |  | 64 |  | 1318
|  |  |  | Sylhet |  | 45 |  | 676
|  |  |  | Khulna |  | 0 |  | 2002
|  |  |  | Barishal |  | 0 |  | 518
|  |  |  | Rajshahi |  | 0 |  | 1806
|  |  |  | Rangpur |  | 95 |  | 1073
|  |  |  | Total |  | 292 |  | 16335
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Nababganj 55 MW PP (Southern power ) |  |  | 55
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Bibiana-II 341 MW CCPP (Summit) GT |  |  | 222 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Bibiana-II 341 MW CCPP (Summit) ST |  |  | 119 | 4 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP GT |  |  | 142
[7 empty] | 6 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 641 |  |  |  | Total | 762
|  |  |  | Total Unavailable Capacity |  |  |  | 1403
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:01 | 10:16 | Mithapukur 132/33kV S/S TR-2 (414T) HT Forced S/D Due to By PBS for 33kv mirpur feeder | [7 empty] | 10.0MW load
|  |  | bus DS R-ph emergency red hot maintenance work. | [7 empty] | interrup.
| 09:01 | 10:17 | Mithapukur 132/33kV S/S TR-2 (414T) LT Forced S/D Due to By PBS for 33kv mirpur feeder | [7 empty] | 10.0MW load
|  |  | bus DS R-ph emergency red hot maintenance work. | [7 empty] | interrup.
|  | 09:12 | Baroaulia 132/33kV S/S T-1(405T) HT is restored.
| 09:18 | 10:17 | Mithapukur 132/33kV S/S BUS SECTION-2 (33KV) Forced S/D Due to By PBS for 33kv mirpur
feeder bus DS R-ph emergency red hot maintenance work.
| 09:24 | 09:57 | Coxsbazar 132/33kV S/S T3 HT Scheduled S/D Due to T-3 Tripped due 33 kV over current | [7 empty] | 60.0MW load
|  |  | Auxiliary Station Transformar Dropout fuse flashing. | [7 empty] | interrup.
| 10:00 | 00:17 | Cumilla(N) 230/132/33kV S/S 132KV T-03 LT Forced S/D Due to Underground Cable
maintenance.
| 10:00 | 00:16 | Cumilla(N) 230/132/33kV S/S 132KV T-03 HT Forced S/D
| 11:12 |  | Rampal 1320 MW (BIFPCL) unit-1 tripped.
| 11:12 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U1 tripped-11:12 on 23.7.25
| 11:12 |  | Rampal 1320 MW (BIFPCL) Tripped with remarks:- U1
|  | 11:22 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-2 is restored.
|  | 11:23 | Jashore 132/33kV S/S JH-2(L1) is restored.
| 13:05 |  | Haripur 230/132kV S/S EGCB 412MW Scheduled S/D Due to 412 MW Power Plant Work by EGCB.
| 13:11 | 14:25 | Mahasthangar-Palashbari 132kV Ckt-2 Tripped from Mahasthangarh 132/33kV end showing | [7 empty] | 98.0MW load
|  |  | Distence P443 relays Due to Distance Trip Ia - 4.28 ka In - 3.70 ka | [7 empty] | interrup.
Mahasthangarh
132/33kV end
| 14:47 | 15:58 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Scheduled S/D Due to Due to Dohazari 33 | [7 empty] | 71.0MW load
|  |  | kv feeder redhot maintenance. | [7 empty] | interrup.
| 14:48 | 15:57 | Dohazari 132/33kV S/S Power Transformer -T-2 HT Scheduled S/D Due to Due to Dohazari 33 | [7 empty] | 71.0MW load
|  |  | kv feeder redhot maintenance | [7 empty] | interrup.
| 15:34 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U1
|  | 16:14 | Mahasthangar-Palashbari 132kV Ckt-1 is restored.
|  | 16:14 | Mahasthangar-Palashbari 132kV Ckt-1 is restored.
| 16:28 | 17:28 | Mahasthangar-Palashbari 132kV Ckt-2 Project Work S/D from Mahasthangarh 132/33kV end Due
to project work
| 16:43 |  | Bog-Sherpur 132/33kV S/S Main Bus-1 Project Work S/D
| 17:03 | 19:13 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) LT Project Work S/D
| 17:05 | 19:12 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) HT Project Work S/D
| 20:40 |  | Aminbazar - kaliakoir 400 kv line was switched on.
| 23:59 | 00:15 | Chowmuhani-Ramganj 132 kV Ckt-2 Tripped from Chowmuhani 132/33kV end showing
Zone-1 Distance Relay A,B,C relays Due to Over Thundering
|  | 00:14 | Chowmuhani-Ramganj 132 kV Ckt-1 is restored.
| 01:48 |  | Raozan 25 MW PP Shutdown
| 02:14 |  | Cumilla(N)-Shahjibazar 230 kV Ckt-1 Tripped from Cumilla(N) 230/132/33kV end showing
Distance Relay Y phase Zone-1 relays Due to None
| 03:03 | 04:34 | Daudkandi-Sonargaon 132 kV Ckt-2 Tripped from Sonargaon 132/33kV end showing Line
distance relay relays Due to Bad weather
| 03:18 | 07:05 | Bajitpur 132/33kV S/S Tr-1(404T) LT Tripped showing REC650 relays Due to Over current | [7 empty] | 60.0MW load
|  |  | flow | [7 empty] | interrup.
| 03:18 | 07:06 | Bajitpur 132/33kV S/S Tr-2(414T) LT Tripped showing REC650 relays Due to Over current | [7 empty] | 15.0MW load
|  |  | flow | [7 empty] | interrup.
| 03:23 |  | Bhulta new-Araihazar ckt-2 tripped due to VT fuse fail
| 03:37 | 04:57 | Haripur-Madanganj 132kV Ckt-1 Tripped from Haripur 230/132kV end showing DEF AiDED.
relays Due to Raining & Thundering.
| 03:40 | 04:50 | Madanganj 132/33kV S/S Madanganj-Fatullah 132KV Ckt Tripped showing Line Distance | [7 empty] | 40.0MW load
|  |  | protection relay relays. | [7 empty] | interrup.
| 03:40 | 05:25 | Fatullah-Madanganj 132 kV Ckt-2 Tripped from Fatullah 132/33kV end showing 50/50N Trrip
relays Due to Due to bad weather
| 03:40 | 04:50 | Madanganj 132/33kV S/S Madanganj -Summit 55 MW 132 kv Ckt Tripped showing Trip relay | [7 empty] | 60.0MW load
|  |  | relays. | [7 empty] | interrup.
| 03:40 | 04:50 | Madanganj 132/33kV S/S Madanganj -Haripur 132 kv Ckt-2 Tripped showing Distance | [7 empty] | 28.0MW load
|  |  | protection relay relays. | [7 empty] | interrup.
| 04:00 | 07:10 | Aminbazar-Mirpur 132kV Ckt-1 Tripped from Aminbazar 400/230/132kV end showing REL316*4
relays Due to Trip main-1 diff E/F and from Mirpur 132/33kV end showing main protection
Trip Relay. relays Due to Thundering & rain .
| 04:00 | 05:20 | Aminbazar-Kaliakoir 230kV Ckt-2 Tripped from Aminbazar 400/230/132kV end showing REL316*4
relays Due to Trip main-2 internal relay fail
| 04:05 | 05:33 | Mirpur-Uttara 132kV Ckt-1 Tripped from Mirpur 132/33kV end showing Main Protection trip | [7 empty] | 50.0MW load
|  |  | relay. relays Due to Thundering & rain . | [7 empty] | interrup. Mirpur
132/33kV end
| 05:10 |  | BIPTC S/S 20DF21 Tripped showing 60/61 relays Due to tripped by unbalanced 60/61 instant
trip.
| 05:33 |  | Hasnabad 132/33kV S/S 132/33kV 414 T-2 LT Tripped showing 51, MVAJM, Trip 25 relays Due
to Dir O/C Trip,
| 05:35 | 07:08 | Sylhet 132/33kV S/S Sylhet-90MW P/S Scheduled S/D Due to High temp maintenance of CB | [7 empty] | 32.0MW load
|  |  | terminal(Red phase) | [7 empty] | interrup.
| 06:00 |  | Minimum Generation is 11501 MW
| 06:57 |  | Mahasthangar-Palashbari 132kV Ckt-1 Project Work S/D from Mahasthangarh 132/33kV end Due
to project work
| 07:08 |  | Mahasthangar-Palashbari 132kV Ckt-1 Project Work S/D from Palashbari 132/33kV end.
| 07:23 |  | Feni 132/33kV S/S T-2(415T) HT Scheduled S/D Due to 33KV CT clamp red hot work
| 07:23 |  | Feni 132/33kV S/S T-2(415T) LT Scheduled S/D Due to 33 kv CT Clamp red hot repair work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 23-07-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9744000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 293 | 7180015 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1187503 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 188 | 4650000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 318 | 7732812 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 82 | 511488 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 1262160 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 139 | 3013440 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 1324180 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 1284009 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 25 | 522600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 454320 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 33 | 652320 | Engine Problem
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 277 | 5439458 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 133 | 3018528 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1778880 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 993600 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3804480 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 199089 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 716760 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 602 | 11244970 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 2902800 | Engine Problem
Dhaka Area Total |  |  |  |  | 5939.724 | 3189 | 69617412
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 26 | 492125.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 76005 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 40 | 906240 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5270929 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 213 | 5055283 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 56 | 466691 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 65 | 762068 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 817091 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 37 | 427200 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 21 | 388320 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 85 | 1133760 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 24719 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 132982 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 48 | 306109 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 590400 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 160 | 2228073 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 26476361 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 8 | 106080 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 780 | 18632727.27 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.72 | 3089 | 64293163.67
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 196 | 4815000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 329 | 8408300 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 340 | 8138000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 37 | 776808 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 46 | 1104000 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 180 | 2458909 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1105585 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 133 | 2754981 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 42 | 970016 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 167 | 1986720 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 54 | 1012800 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 53 | 1148870 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 389210 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 87 | 2134080 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 63 | 1189440 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 88 | 2022720 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 337891 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1885 | 40753330
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 45 | 1057920 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15400 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 162 | 3321600 | Engine Problem
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 80 | 2136000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 310340 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 203040 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 423000 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 304 | 7467300
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 58 | 1376520 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 151 | 3582982 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 716928 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1939200 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 423000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 6 | 154440 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Plant Shutdown as per schedule HGPI work
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 378 | 9256000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7676000 | machine problem
Sylhet Area Total |  |  |  |  | 2325 | 1042 | 25125070
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 883 | 20849454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 158 | 4040640 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 574080 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 753840 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1197 | 22552732 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2311 | 49682746
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 320 | 7316364 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 117 | 2829000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 900 | 17920000 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5102590 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 253 | 4853000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4875 | -
Barishal Area Total |  |  |  |  | 2236 | 1810 | 38025829
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 416021 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 306374 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 199 | 4769364 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 179 | 4436291 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 178 | 4428155 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8953272 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 21 | 243055 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 53 | 410294 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 866272 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1362912 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1005504 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 34860 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1452 | 32862909 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 392248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 769050 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2893 | 61256581
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 46 | 1053818 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 111 | 2513212 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 52220.88 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 114 | 2655511 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 201986 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1273680 | -
Rangpur Area Total |  |  |  |  | 950 | 271 | 7750427.88
Eastern Grid Total |  |  |  |  | 16667.715 | 9509 | 207256275.67
Western Grid Total |  |  |  |  | 10378.16 | 7285 | 156715583.88
National Grid Total |  |  |  |  | 27045.875 | 16794 | 363971859.55
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 23-07-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10740.25 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5303.9 | MW
i) Dhaka area |  |  | 5814.5 |  | MW | i) Khulna area |  |  |  | 2001.9 | MW
ii) Chattogram area |  |  | 1556.5 |  | MW | ii) Barishal area |  |  |  | 518 | MW
iii) Cumilla area |  |  | 1484.25 |  | MW | iii) Rajshahi area |  |  |  | 1806 | MW
iv) Mymensingh area |  |  | 1254 |  | MW | iv) Rangpur area |  |  |  | 978 | MW
v) Sylhet area |  |  | 631 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 16044.15 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 88 | 19:30 | 133 | PHP | 9 | 01:00
2 | AKSML | 134.7 | 01:00 | 68 | Ishurdi | 95 | 19:30 | 134 | Pabna | 145 | 19:30
3 | Aftabnagar | 48 | 23:00 | 69 | Jaldhaka | 82 | 04:00 | 135 | Palashbari | 119 | 00:00
4 | Agargaon | 153 | 15:00 | 70 | Jamalpur | 142 | 22:00 | 136 | Panchagarh | 58 | 23:00
5 | Agrabad | 102 | 11:00 | 71 | Jashore | 150 | 21:00 | 137 | Patuakhali | 79.5 | 22:00
6 | Amnura | 45 | 22:00 | 72 | Jhenaidah | 147 | 19:00 | 138 | Payra | 38 | 22:00
7 | Ashuganj | 103 | 23:00 | 73 | Joydebpur | 157 | 19:30 | 139 | Postogola | 67 | 19:30
8 | BSRM | 206 | 11:00 | 74 | Joypurhat | 80 | 21:00 | 140 | Purbachal | 27 | 23:00
9 | Bagerhat | 86 | 00:00 | 75 | Juldah | 17 | 00:00 | 141 | Purbasadipur | 138 | 12:00
10 | Bajitpur | 90 | 22:00 | 76 | KSRM | 33 | 09:00 | 142 | Rahanpur | 36 | 22:00
11 | Bakulia | 102 | 15:00 | 77 | Kabirpur | 262 | 12:00 | 143 | Rahim | 30 | 13:00
12 | Banani | 57.6 | 15:00 | 78 | Kachua | 94 | 22:00 | 144 | Rajbari | 98 | 19:30
13 | Bangabhaban | 19 | 10:00 | 79 | Kallyanpur | 123 | 19:00 | 145 | Rajendrapur | 144 | 20:00
14 | Barapukuria | 66 | 05:00 | 80 | Kalurghat | 42 | 15:00 | 146 | Rajshahi | 151 | 21:00
15 | Barguna | 26 | 22:00 | 81 | Kamrangirchar | 79.8 | 19:00 | 147 | Rajshahi-230 | 85 | 23:00
16 | Barishal | 109 | 21:00 | 82 | Kaptai | N/A | N/A | 148 | Ramganj | 102 | 22:00
17 | Barishal-230 | 124 | 19:30 | 83 | Kasba | 37 | 19:30 | 149 | Rampur | 45 | 00:00
18 | Baroaulia | 74 | 15:00 | 84 | Kazla | 101 | 19:30 | 150 | Rangamati | 18 | 19:00
19 | Baroirhat | 71 | 21:00 | 85 | Keranigonj | 92 | 22:00 | 151 | Rangpur | 150 | 16:00
20 | Bashundhara | 217 | 15:00 | 86 | Khagrachori | 34 | 20:00 | 152 | Ruppur | 7.8 | 16:00
21 | BashundharaCement | 6 | 00:00 | 87 | Khulna | 88 | 21:00 | 153 | SSM | 8 | 22:00
22 | Beanibazar | 76 | 05:00 | 88 | Khulshi | 160 | 21:00 | 154 | Saidpur | 122 | 10:00
23 | Benapole | 85 | 22:00 | 89 | Kishoreganj | 148 | 00:00 | 155 | Satkhira | 141 | 00:00
24 | Bhaluka | 163 | 18:30 | 90 | Kodda | 319 | 12:00 | 156 | Satmasjid | 113 | 19:00
25 | Bhandaria | 60 | 22:00 | 91 | Kulaura | 54 | 02:00 | 157 | Savar | 231 | 21:00
26 | Bhangura | 44 | 20:00 | 92 | Kurigram | 64 | 18:00 | 158 | SevenRings | 21.74 | 11:00
27 | Bheramara(GK) | 78 | 18:30 | 93 | Kushtia | 171 | 00:00 | 159 | ShahCement | 36 | 07:00
28 | Bhulta | 249 | 11:00 | 94 | Laksam | 38 | 23:00 | 160 | Shahjadpur | 103 | 21:00
29 | Bog-Sherpur | 78 | 21:00 | 95 | Lakshmipur | 34 | 19:30 | 161 | Shahjibazar | 134 | 02:00
30 | Bogura | 206 | 23:00 | 96 | Lalbag | 49 | 01:00 | 162 | Shahmirpur | 64 | 00:00
31 | Borhanuddin | 93 | 00:00 | 97 | Lalmonirhat | 64 | 23:00 | 163 | Shariatpur | 104 | 22:00
32 | Brahmanbaria | 149 | 22:00 | 98 | MI_Cement | 16.1 | 08:00 | 164 | Sherpur | 162 | 00:00
33 | Cantonment | 174 | 12:00 | 99 | Madanganj | 40 | 11:00 | 165 | Shikalbaha | 22 | 10:00
34 | Chandina | 22.15 | 12:00 | 100 | Madaripur | 132 | 23:00 | 166 | Shitalakhya | 92.9 | 16:00
35 | Chandpur | 76 | 12:00 | 101 | Madartek | 108 | 23:00 | 167 | Sholosohor | 50 | 18:30
36 | Chandraghona | 39 | 19:00 | 102 | Madunaghat | 61 | 19:00 | 168 | Shyampur | 164 | 12:00
37 | Chapai | 79 | 23:00 | 103 | Magura | 81 | 19:30 | 169 | Siddhirganj | 129 | 12:00
38 | Charsaidpur | 44 | 18:00 | 104 | Mahasthangarh | 104 | 00:00 | 170 | Sirajganj | 136 | 20:00
39 | Chauddagram | 73 | 22:00 | 105 | Maijdee | 16 | 22:00 | 171 | Sonargaon | 123 | 01:00
40 | Chhatak | 40 | 19:00 | 106 | Manikganj | 136 | 01:00 | 172 | Sreemongol | 87 | 21:00
41 | Chowmuhani | 180 | 20:00 | 107 | Maniknagar | 94 | 13:00 | 173 | Sreepur | 105 | 19:00
42 | Chuadanga | 134 | 19:00 | 108 | Matarbari | 54 | 22:00 | 174 | Srinagar | 59.85 | 22:00
43 | Coxsbazar | 145 | 19:00 | 109 | Matuail | 68 | 10:00 | 175 | Sunamganj | 58 | 03:00
44 | Cumilla(N) | 138 | 04:00 | 110 | Millgate | 138 | 16:00 | 176 | Sylhet | 56 | 13:00
45 | Cumilla(S) | 193 | 19:00 | 111 | Mirpur | 141 | 15:00 | 177 | Sylhet-132 | 142 | 16:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 11 | 14:00 | 178 | TK | 38 | 20:00
47 | Daudkandi | 152 | 22:00 | 113 | Mirzapur | 49 | 17:00 | 179 | Tangail | 188 | 23:00
48 | Dhaka | 84 | 13:00 | 114 | Mithapukur | 72 | 18:00 | 180 | Taraganj | 27 | 19:30
49 | Dhamrai | 126 | 08:00 | 115 | Modern | N/A | N/A | 181 | Thakurgaon | 112 | 19:30
50 | Dhanmondi | 162.5 | 14:00 | 116 | Mogbazar | 173.3 | 16:00 | 182 | Tongi | 142 | 11:00
51 | Dohazari | 111 | 19:00 | 117 | Mongla | 44 | 12:00 | 183 | Ullahpara | 46 | 19:30
52 | Faridpur | 194 | 22:00 | 118 | Motijheel | 51 | 13:00 | 184 | Ullon | 50 | 23:00
53 | Fatullah | 110 | 16:00 | 119 | Muktagacha | 43 | 19:30 | 185 | Uttara | 98 | 15:00
54 | Fenchuganj | 50 | 22:00 | 120 | Munshiganj | 124 | 22:00 | 186 | UttaraNew | 77 | 23:00
55 | Feni | 125 | 19:00 | 121 | Muradnagar | 46 | 19:00 | 187 | Zigatola | 80 | 23:00
56 | GPH | 82 | 00:00 | 122 | Mymensingh | 237 | 21:00
57 | Ghatail | 82 | 18:30 | 123 | Naogaon | 160 | 22:00
58 | Ghorashal | 13 | 01:00 | 124 | Narail | 67 | 22:00
59 | Ghorashal-230 | 96 | 22:00 | 125 | Narinda | 85 | 13:00
60 | Goalpara | 42 | 00:00 | 126 | Narshingdi | 193 | 02:00
61 | Gollamari | 100 | 00:00 | 127 | Natore | 175 | 22:00
62 | Gopalganj | 123.7 | 20:00 | 128 | Nawabganj | 73.8 | 22:00
63 | Gulshan | 150 | 14:00 | 129 | Netrakona | 138 | 04:00
64 | Halishahar | 83 | 15:00 | 130 | New | 64 | 10:00
65 | HaripurSBU | 153 | 10:00 | 131 | Niamatpur | 87 | 22:00
66 | Hasnabad | 100 | 23:00 | 132 | Noapara | 66 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 23-07-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15900 | 394 |  | 16311.73
1:00 | 15679 | 403 |  | 16100.14
2:00 | 15349 | 241 |  | 15600.85
3:00 | 14844 | 198 |  | 15050.91
4:00 | 14554 | 93 |  | 14651.19
5:00 | 14497 | 99 |  | 14600.46
6:00 | 13998 | 56 |  | 14056.52
7:00 | 13977 | 85 |  | 14065.83
8:00 | 14065 | 88 |  | 14156.96
9:00 | 14341 | 111 |  | 14457
10:00 | 14417 | 87 |  | 14507.92
11:00 | 14613 | 110 |  | 14727.95
12:00 | 14859 | 190 |  | 15057.55
13:00 | 15079 | 271 |  | 15362.2
14:00 | 14824 | 366 |  | 15206.47
15:00 | 15251 | 244 |  | 15505.98
16:00 | 15063 | 233 |  | 15306.49
17:00 | 14991 | 159 |  | 15157.16
18:00 | 14699 | 151 |  | 14856.8
19:00 | 15897 | 290 |  | 16200.05
19:30 | 16425 | 359 |  | 16800.16
20:00 | 16389 | 441 |  | 16849.85
21:00 | 16794 | 292 |  | 17099.14
22:00 | 16666.7 | 271 |  | 16949.7
23:00 | 16545.2 | 273 |  | 16830.2
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 23-07-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 9094 | 6806 | 15900 | DAILY GENERATION CURVE
00:30 | 9029 | 6760.5 | 15789.5
01:00 | 8964 | 6715 | 15679 | 23-07-2025
01:30 | 8860.5 | 6653.5 | 15514
02:00 | 8757 | 6592 | 15349
02:30 | 8533 | 6563.5 | 15096.5
03:00 | 8309 | 6535 | 14844
03:30 | 8249.5 | 6449.5 | 14699
04:00 | 8190 | 6364 | 14554
04:30 | 8164.5 | 6361 | 14525.5
05:00 | 8139 | 6358 | 14497
05:30 | 8022.5 | 6225 | 14247.5
06:00 | 7906 | 6092 | 13998
06:30 | 7855 | 6132.5 | 13987.5
07:00 | 7804 | 6173 | 13977
07:30 | 7785.5 | 6235.5 | 14021
08:00 | 7767 | 6298 | 14065
08:30 | 7927.5 | 6275.5 | 14203
09:00 | 8088 | 6253 | 14341
09:30 | 8139.5 | 6239.5 | 14379
10:00 | 8191 | 6226 | 14417
10:30 | 8292 | 6223 | 14515
11:00 | 8393 | 6220 | 14613
11:30 | 8559.5 | 6176.5 | 14736
12:00 | 8726 | 6133 | 14859
12:30 | 8771.5 | 6197.5 | 14969
13:00 | 8817 | 6262 | 15079
13:30 | 8789.5 | 6162 | 14951.5
14:00 | 8762 | 6062 | 14824
14:30 | 8874 | 6163.5 | 15037.5
15:00 | 8986 | 6265 | 15251
15:30 | 8894.5 | 6262.5 | 15157
16:00 | 8803 | 6260 | 15063
16:30 | 8787 | 6240 | 15027
17:00 | 8771 | 6220 | 14991
17:30 | 8714 | 6131 | 14845
18:00 | 8657 | 6042 | 14699
18:30 | 8978 | 6320 | 15298
19:00 | 9299 | 6598 | 15897
19:30 | 9387 | 7038 | 16425
20:00 | 9479 | 6910 | 16389
20:30 | 9494 | 7097.5 | 16591.5 |  | Executive Engineer
21:00 | 9509 | 7285 | 16794 |  | Network Operation Division
21:30 | 9425.25 | 7305.1 | 16730.35
22:00 | 9341.5 | 7325.2 | 16666.7
22:30 | 9265.75 | 7340.2 | 16605.95
23:00 | 9190 | 7355.2 | 16545.2

## En-Curve
QF-LDC-12
Date | 23-07-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3753 | 1916 | 855 | 38 | 28 | 1468 | 220 | 4214 | 0 | 700 | 2708 | 0 | 0 | 0 | 394 | DAILY ENERGY CURVE
00:30 | 3747 | 1927 | 855.5 | 38 | 28 | 1460.5 | 220 | 4169 | 0 | 700 | 2644.5 | 0 | 0 | 0 | 398.5 | 23-07-2025
01:00 | 3741 | 1938 | 856 | 38 | 28 | 1453 | 220 | 4124 | 0 | 700 | 2581 | 0 | 0 | 0 | 403
01:30 | 3718 | 1931.5 | 856 | 38 | 27 | 1453 | 220 | 4098.5 | 0 | 682.5 | 2489.5 | 0 | 0 | 0 | 322 | Energy Generated | 363.9719 |  | MKWHr
02:00 | 3695 | 1925 | 856 | 38 | 26 | 1453 | 220 | 4073 | 0 | 665 | 2398 | 0 | 0 | 0 | 241 | Energy not Served | 5.146 |  | MKWHr
02:30 | 3718 | 1961 | 856 | 38 | 26 | 1452 | 220 | 4046 | 0 | 597.5 | 2182 | 0 | 0 | 0 | 219.5 | Total Energy Requirement | 369.1179 |  | MKWHr
03:00 | 3741 | 1997 | 856 | 38 | 26 | 1451 | 220 | 4019 | 0 | 530 | 1966 | 0 | 0 | 0 | 198
03:30 | 3741.5 | 1997.5 | 856 | 38 | 26 | 1451 | 220 | 4010.5 | 0 | 521.5 | 1837 | 0 | 0 | 0 | 145.5
04:00 | 3742 | 1998 | 856 | 38 | 26 | 1451 | 220 | 4002 | 0 | 513 | 1708 | 0 | 0 | 0 | 93
04:30 | 3731 | 1995 | 856 | 38 | 26 | 1451.5 | 220 | 3999.5 | 0 | 494 | 1714.5 | 0 | 0 | 0 | 96
05:00 | 3720 | 1992 | 856 | 38 | 26 | 1452 | 220 | 3997 | 0 | 475 | 1721 | 0 | 0 | 0 | 99
05:30 | 3716 | 1932 | 856 | 38 | 25 | 1457.5 | 220 | 3957 | 11.5 | 417.5 | 1617 | 0 | 0 | 0 | 77.5
06:00 | 3712 | 1872 | 856 | 38 | 24 | 1463 | 220 | 3917 | 23 | 360 | 1513 | 0 | 0 | 0 | 56
06:30 | 3714.5 | 1856.5 | 856 | 38 | 24 | 1462 | 220 | 3920 | 66 | 359 | 1471.5 | 0 | 0 | 0 | 70.5
07:00 | 3717 | 1841 | 856 | 38 | 24 | 1461 | 220 | 3923 | 109 | 358 | 1430 | 0 | 0 | 0 | 85
07:30 | 3698.5 | 1828.5 | 856.5 | 38 | 24 | 1455.5 | 220 | 3927 | 187 | 353 | 1433 | 0 | 0 | 0 | 86.5
08:00 | 3680 | 1816 | 857 | 38 | 24 | 1450 | 220 | 3931 | 265 | 348 | 1436 | 0 | 0 | 0 | 88
08:30 | 3652 | 1811.5 | 856.5 | 38 | 34 | 1426.5 | 220 | 3917 | 320 | 378 | 1549.5 | 0 | 0 | 0 | 99.5
09:00 | 3624 | 1807 | 856 | 38 | 44 | 1403 | 220 | 3903 | 375 | 408 | 1663 | 0 | 0 | 0 | 111
09:30 | 3616.5 | 1768 | 856 | 38 | 45 | 1333 | 220 | 3892.5 | 445.5 | 420.5 | 1744 | 0 | 0 | 0 | 99
10:00 | 3609 | 1729 | 856 | 38 | 46 | 1263 | 220 | 3882 | 516 | 433 | 1825 | 0 | 0 | 0 | 87
10:30 | 3594.5 | 1792.5 | 856 | 38 | 46 | 1267 | 220 | 3892 | 542.5 | 433 | 1833.5 | 0 | 0 | 0 | 98.5
11:00 | 3580 | 1856 | 856 | 38 | 46 | 1271 | 220 | 3902 | 569 | 433 | 1842 | 0 | 0 | 0 | 110
11:30 | 3639 | 1924 | 856 | 38 | 49 | 1268.5 | 219.5 | 3814 | 575.5 | 431.5 | 1921 | 0 | 0 | 0 | 150
12:00 | 3698 | 1992 | 856 | 38 | 52 | 1266 | 219 | 3726 | 582 | 430 | 2000 | 0 | 0 | 0 | 190
12:30 | 3686 | 1992.5 | 856 | 38 | 53 | 1261.5 | 218.5 | 3757.5 | 598.5 | 455.5 | 2052 | 0 | 0 | 0 | 230.5
13:00 | 3674 | 1993 | 856 | 38 | 54 | 1257 | 218 | 3789 | 615 | 481 | 2104 | 0 | 0 | 0 | 271
13:30 | 3607 | 1987.5 | 858.5 | 38 | 54 | 1267.5 | 218 | 3807.5 | 558 | 471.5 | 2084 | 0 | 0 | 0 | 318.5
14:00 | 3540 | 1982 | 861 | 38 | 54 | 1278 | 218 | 3826 | 501 | 462 | 2064 | 0 | 0 | 0 | 366
14:30 | 3613 | 1999.5 | 861 | 38 | 54 | 1339 | 217.5 | 3853 | 469 | 465 | 2127.5 | 0 | 0 | 1 | 305
15:00 | 3686 | 2017 | 861 | 38 | 54 | 1400 | 217 | 3880 | 437 | 468 | 2191 | 0 | 0 | 2 | 244
15:30 | 3647.5 | 2009 | 861 | 38 | 55 | 1423 | 217 | 3847 | 376 | 467.5 | 2208.5 | 0 | 0 | 7.5 | 238.5
16:00 | 3609 | 2001 | 861 | 38 | 56 | 1446 | 217 | 3814 | 315 | 467 | 2226 | 0 | 0 | 13 | 233
16:30 | 3571.5 | 1991.5 | 864.5 | 38 | 56 | 1447 | 217.5 | 3876 | 228.5 | 475.5 | 2245 | 0 | 0 | 16 | 196
17:00 | 3534 | 1982 | 868 | 38 | 56 | 1448 | 218 | 3938 | 142 | 484 | 2264 | 0 | 0 | 19 | 159
17:30 | 3460 | 1919 | 870 | 38 | 54 | 1404.5 | 218.5 | 3941.5 | 91 | 490.5 | 2337 | 0 | 0 | 21 | 155
18:00 | 3386 | 1856 | 872 | 38 | 52 | 1361 | 219 | 3945 | 40 | 497 | 2410 | 0 | 0 | 23 | 151
18:30 | 3522.5 | 1962 | 877.5 | 38 | 57 | 1406 | 219.5 | 4061 | 20 | 586 | 2528.5 | 0 | 0 | 20 | 220.5
19:00 | 3659 | 2068 | 883 | 38 | 62 | 1451 | 220 | 4177 | 0 | 675 | 2647 | 0 | 0 | 17 | 290
19:30 | 3718 | 2092 | 883 | 38 | 54 | 1446 | 220 | 4488 | 0 | 725 | 2749 | 0 | 0 | 12 | 359
20:00 | 3660 | 2123 | 884 | 38 | 52 | 1444 | 220 | 4422 | 0 | 760 | 2773 | 0 | 0 | 13 | 441
20:30 | 3687.5 | 2144 | 883.5 | 38 | 53 | 1448 | 220 | 4571 | 0 | 755 | 2781 | 0 | 0 | 10.5 | 366.5
21:00 | 3715 | 2165 | 883 | 38 | 54 | 1452 | 220 | 4720 | 0 | 750 | 2789 | 0 | 0 | 8 | 292
21:30 | 3699 | 2173 | 871.5 | 38 | 54 | 1445 | 220 | 4699.5 | 0 | 750.5 | 2771.35 | 0 | 0 | 8.5 | 281.5
22:00 | 3683 | 2181 | 860 | 38 | 54 | 1438 | 220 | 4679 | 0 | 751 | 2753.7 | 0 | 0 | 9 | 271
22:30 | 3647 | 2110.25 | 860 | 38 | 57 | 1436.5 | 220 | 4757.5 | 0 | 750 | 2720.2 | 0 | 0 | 9.5 | 272
23:00 | 3611 | 2039.5 | 860 | 38 | 60 | 1435 | 220 | 4836 | 0 | 749 | 2686.7 | 0 | 0 | 10 | 273
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 23-07-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 386 | 05:00 | 371 | 23:00 | Payra | 416 | 06:00 | 409 | 23:00
Ashuganj | 401 | 2:00 | 388 | 12:00 | Rahanpur | 402 | 14:00 | 388 | 21:00
Bhulta | 396 | 02:00 | 367 | 15:00 | Rampal | 407 | 10:00 | 389 | 23:00
Bibiana | 379 | 00:00 | 373 | 19:00
BIPTC | 404 | 08:00 | 388 | 23:00
Bogura | 385 | 14:00 | 368 | 21:00
Gopalganj | 400 | 09:00 | 383 | 23:00
Kaliakoir | 365 | 22:00 | 352 | 08:00
Madunaghat | 391 | 01:00 | 387 | 12:00
Meghnaghat | 386 | 05:00 | 376 | 21:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 225 | 06:00 | 215 | 21:00 | Keranigonj | 222 | 05:00 | 213 | 23:00
AKSML | 231 | 01:00 | 223 | 11:00 | Khulna(S) | 230 | 09:00 | 215 | 23:00
Aminbazar | 255 | 05:00 | 216 | 22:00 | Madunaghat | 232 | 00:00 | 226 | 14:00
Ashuganj | 230 | 01:00 | 221 | 19:00 | Madunaghat-400 | 232 | 01:00 | 228 | 09:00
Ashuganj-400 | 230 | 01:00 | 221 | 19:00 | Maniknagar | 218 | 03:00 | 211 | 23:00
Baghabari | 234 | 08:00 | 225 | 22:00 | Meghnaghat | 226 | 03:00 | 221 | 17:00
Barapukuria | 220 | 14:00 | 205 | 23:00 | Meghnaghat-400 | 223 | 05:00 | 217 | 23:00
Barapukuria-230 | 220 | 14:00 | 205 | 23:00 | Mirsorai | 232 | 18:00 | 221 | 04:00
Barishal | 227 | 08:00 | 215 | 23:00 | Rajshahi | 231 | 02:00 | 220 | 21:00
Bheramara | 233 | 09:00 | 222 | 21:00 | Rampal | 232 | 09:00 | 216 | 23:00
Bhulta | 227 | 01:00 | 209 | 15:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 223 | 18:30 | 218 | 15:00 | Rampura | 227 | 02:00 | 206 | 15:00
BIPTC | 235 | 09:00 | 221 | 21:00 | Shikalbaha | 230 | 02:00 | 224 | 11:00
Bogura | 232 | 14:00 | 222 | 21:00 | Shyampur | 221 | 02:00 | 214 | 23:00
Bogura-400 | 233 | 14:00 | 222 | 21:00 | Siddhirganj | 219 | 00:00 | 214 | 23:00
Borhanuddin | 232 | 07:00 | 224 | 21:00 | Sirajgonj | 239 | 18:30 | 233 | 21:00
BSRM | 230 | 18:00 | 219 | 08:00 | Sreepur | 227 | 02:00 | 218 | 19:00
Cumilla(N) | 220 | 02:00 | 214 | 19:00 | Tongi | 222 | 04:00 | 213 | 18:30
Faridpur | 225 | 09:00 | 211 | 22:00
Fenchuganj | 222 | 09:00 | 217 | 17:00
Ghorashal | 225 | 00:00 | 220 | 08:00
Ghorashal-230 | 225 | 02:00 | 211 | 19:00
Gopalganj | 225 | 09:00 | 213 | 23:00
GPH | 230 | 18:00 | 223 | 08:00
Haripur | 219 | 06:00 | 213 | 23:00
Hasnabad | 220 | 00:00 | 214 | 22:00
Hathazari | 229 | 18:00 | 220 | 11:00
Ishurdi | 234 | 02:00 | 224 | 21:00
Jhenaidah | 231 | 09:00 | 213 | 23:00
Kaliakoir | 227 | 01:00 | 218 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 02:00 | 120 | 15:00 | Lalmonirhat | 127 | 09:00 | 114 | 23:00
Agargaon | 131 | 03:00 | 124 | 15:00 | Madanganj | 128 | 00:00 | 124 | 23:00
Agrabad | 130 | 00:00 | 125 | 12:00 | Madaripur | 135 | 07:00 | 127 | 22:00
AKS | 129 | 18:00 | 124 | 12:00 | Madartek | 137 | 02:00 | 120 | 15:00
Aminbazar | 133 | 02:00 | 126 | 19:00 | Madunaghat | 132 | 18:00 | 128 | 11:00
Amnura | 136 | 00:00 | 129 | 12:00 | Magura | 135 | 09:00 | 120 | 23:00
Ashuganj | 137 | 01:00 | 134 | 16:00 | Mahasthangarh | 135 | 14:00 | 126 | 21:00
Bagerhat | 134 | 09:00 | 118 | 21:00 | Maijdee | 120 | 18:00 | 108 | 05:00
Bajitpur | 128 | 02:00 | 121 | 19:00 | Manikganj | 123 | 00:00 | 117 | 16:00
Bakulia | 132 | 00:00 | 127 | 12:00 | Maniknagar | 130 | 05:00 | 124 | 17:00
Banani | 137 | 02:00 | 120 | 15:00 | Matarbari | 120 | 10:00 | 110 | 19:00
Bangabhaban | 130 | 05:00 | 124 | 16:00 | Matuail | 128 | 02:00 | 124 | 23:00
Barapukuria | 135 | 14:00 | 122 | 23:00 | Millgate | 129 | 01:00 | 121 | 15:00
Barguna | 135 | 08:00 | 129 | 22:00 | Mirpur | 132 | 05:00 | 124 | 21:00
Barishal | 133 | 07:00 | 123 | 23:00 | Mirzapur | 129 | 14:00 | 119 | 19:00
Barishal-230 | 133 | 07:00 | 125 | 21:00 | Mithapukur | 134 | 14:00 | 121 | 21:00
Baroaulia | 132 | 18:00 | 127 | 08:00 | MI_Cement | 129 | 05:00 | 124 | 18:00
Baroirhat | 124 | 18:00 | 116 | 19:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 135 | 01:00 | 119 | 15:00 | Mogbazar | 137 | 03:00 | 122 | 15:00
BashundharaCement | 128 | 00:00 | 124 | 23:00 | Mongla | 132 | 08:00 | 120 | 21:00
Beanibazar | 120 | 00:00 | 113 | 16:00 | Motijheel | 130 | 05:00 | 124 | 16:00
Benapole | 131 | 09:00 | 114 | 23:00 | Muktagacha | 132 | 14:00 | 122 | 19:00
Bhaluka | 128 | 06:00 | 120 | 19:00 | Munshiganj | 128 | 01:00 | 124 | 06:00
Bhandaria | 129 | 18:30 | 115 | 21:00 | Muradnagar | 125 | 13:00 | 118 | 19:00
Bhangura | 133 | 06:00 | 127 | 19:00 | Mymensingh | 133 | 12:00 | 110 | 19:00
Bheramara | 136 | 09:00 | 130 | 23:00 | Naogaon | 131 | 18:30 | 121 | 21:00
Bheramara(GK) | 136 | 09:00 | 130 | 21:00 | Narail | 134 | 09:00 | 119 | 21:00
Bhulta | 120 | 00:00 | 117 | 21:00 | Narinda | 130 | 05:00 | 124 | 17:00
Bog-Sherpur | 134 | 18:30 | 127 | 23:00 | Narshingdi | 136 | 02:00 | 117 | 23:00
Bogura | 137 | 19:00 | 131 | 15:00 | Natore | 133 | 05:00 | 128 | 15:00
Bogura-230 | 137 | 18:30 | 131 | 21:00 | Nawabganj | 132 | 05:00 | 125 | 21:00
Brahmanbaria | 131 | 04:00 | 125 | 19:00 | Netrakona | 120 | 12:00 | 106 | 19:00
Cantonment | 131 | 03:00 | 123 | 19:00 | New | 129 | 03:00 | 122 | 15:00
Chandina | 126 | 13:00 | 120 | 19:00 | Niamatpur | 136 | 09:00 | 131 | 21:00
Chandpur | 126 | 18:30 | 112 | 08:00 | Noapara | 134 | 09:00 | 120 | 23:00
Chandraghona | 132 | 00:00 | 129 | 11:00 | Pabna | 134 | 01:00 | 127 | 19:30
Chapai | 135 | 18:00 | 130 | 21:00 | Palashbari | 129 | 18:30 | 118 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 05:00 | 124 | 23:00 | Panchagarh | 135 | 14:00 | 121 | 23:00
Chauddagram | 124 | 18:00 | 116 | 11:00 | Patuakhali | 134 | 02:00 | 130 | 00:00
Chhatak | 120 | 18:00 | 111 | 15:00 | Payra | 137 | 09:00 | 133 | 23:00
Chowmuhani | 118 | 18:00 | 108 | 07:00 | PHP | 123 | 18:00 | 116 | 03:00
Chuadanga | 132 | 09:00 | 114 | 19:00 | Postogola | 131 | 06:00 | 126 | 23:00
Coxsbazar | 123 | 10:00 | 110 | 19:00 | Purbachal | 136 | 01:00 | 120 | 16:00
Cumilla(N) | 126 | 18:00 | 121 | 08:00 | Purbasadipur | 133 | 14:00 | 116 | 23:00
Cumilla(S) | 134 | 06:00 | 119 | 19:00 | Rahanpur | 137 | 09:00 | 132 | 22:00
Daganbhuiyan | 121 | 18:00 | 111 | 05:00 | Rahanpur-400 | 138 | 14:00 | 133 | 21:00
Daudkandi | 123 | 13:00 | 116 | 19:00 | Rahim | 128 | 05:00 | 123 | 23:00
Dhaka | 136 | 02:00 | 122 | 15:00 | Rajbari | 132 | 09:00 | 122 | 22:00
Dhamrai | 128 | 00:00 | 122 | 19:00 | Rajendrapur | 134 | 03:00 | 121 | 20:00
Dhanmondi | 137 | 02:00 | 121 | 15:00 | Rajshahi | 133 | 03:00 | 126 | 00:00
Dohazari | 127 | 01:00 | 123 | 07:00 | Rajshahi-230 | 133 | 02:00 | 127 | 19:30
Faridpur | 135 | 17:00 | 125 | 22:00 | Ramganj | 122 | 18:00 | 110 | 03:00
Fatullah | 130 | 05:00 | 125 | 23:00 | Rampur | 130 | 00:00 | 125 | 12:00
Fenchuganj | 129 | 00:00 | 126 | 17:00 | Rampura | 136 | 02:00 | 121 | 16:00
Feni | 124 | 18:00 | 116 | 15:00 | Rangamati | 131 | 02:00 | 128 | 12:00
Ghatail | 129 | 14:00 | 117 | 19:00 | Rangpur | 134 | 14:00 | 117 | 23:00
Ghorashal | 135 | 04:00 | 129 | 18:00 | Ruppur | 137 | 09:00 | 131 | 19:30
Goalpara | 137 | 18:30 | 124 | 23:00 | Saidpur | 131 | 14:00 | 115 | 23:00
Gollamari | 137 | 07:00 | 125 | 23:00 | Satkhira | 134 | 11:00 | 117 | 23:00
Gopalganj | 135 | 09:00 | 124 | 23:00 | Satmasjid | 131 | 06:00 | 123 | 23:00
Gopalganj-400 | 137 | 09:00 | 129 | 22:00 | Savar | 133 | 05:00 | 126 | 15:00
Gulshan | 134 | 01:00 | 121 | 15:00 | SevenRings | 135 | 01:00 | 129 | 09:00
Halishahar | 132 | 02:00 | 126 | 12:00 | ShahCement | 129 | 05:00 | 124 | 23:00
Haripur | 127 | 00:00 | 124 | 23:00 | Shahjadpur | 136 | 01:00 | 130 | 21:00
HaripurSBU | 128 | 01:00 | 124 | 23:00 | Shahjibazar | 129 | 06:00 | 124 | 19:00
Hasnabad | 131 | 04:00 | 126 | 23:00 | Shahmirpur | 132 | 00:00 | 127 | 12:00
Hathazari | 134 | 00:00 | 130 | 09:00 | Shariatpur | 134 | 08:00 | 123 | 23:00
Ishurdi | 137 | 09:00 | 131 | 19:30 | Sherpur | 135 | 14:00 | 120 | 21:00
Jaldhaka | 130 | 14:00 | 112 | 00:00 | Shikalbaha | 122 | 00:00 | 117 | 11:00
Jamalpur | 138 | 14:00 | 125 | 01:00 | Shikalbaha-230 | 133 | 02:00 | 128 | 11:00
Jashore | 135 | 18:30 | 117 | 23:00 | Shitalakhya | 129 | 05:00 | 124 | 18:00
Jhenaidah | 136 | 09:00 | 117 | 19:00 | Sholosohor | 131 | 00:00 | 128 | 11:00
Jhenaidah-230 | 136 | 09:00 | 124 | 21:00 | Shyampur | 130 | 06:00 | 126 | 11:00
Joydebpur | 136 | 18:00 | 127 | 08:00 | Shyampur-230 | 129 | 01:00 | 124 | 23:00
Joypurhat | 128 | 18:30 | 116 | 21:00 | Siddhirganj | 128 | 00:00 | 124 | 23:00
Juldah | 132 | 01:00 | 128 | 11:00 | Sirajganj | 133 | 07:00 | 124 | 21:00
Kabirpur | 132 | 14:00 | 117 | 15:00 | Sonargaon | 127 | 09:00 | 122 | 23:00
Kachua | 126 | 18:00 | 114 | 04:00 | Sreemongol | 129 | 11:00 | 123 | 15:00
Kaliakoir | 131 | 00:00 | 125 | 08:00 | Sreepur | 131 | 02:00 | 124 | 19:00
Kallyanpur | 133 | 03:00 | 126 | 19:00 | Srinagar | 133 | 06:00 | 126 | 21:00
Kalurghat | 131 | 01:00 | 128 | 11:00 | SSM | 132 | 00:00 | 128 | 14:00
Kamrangirchar | 133 | 06:00 | 126 | 21:00 | Sunamganj | 117 | 08:00 | 110 | 15:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 121 | 07:00 | 115 | 16:00
Kasba | 123 | 13:00 | 118 | 06:00 | Sylhet-132 | 121 | 00:00 | 117 | 15:00
Kazla | 129 | 04:00 | 124 | 16:00 | Tangail | 128 | 14:00 | 115 | 19:00
Keranigonj | 133 | 05:00 | 126 | 21:00 | Taraganj | 131 | 14:00 | 117 | 23:00
Khagrachori | 131 | 18:00 | 127 | 11:00 | Thakurgaon | 134 | 14:00 | 119 | 21:00
Khulna | 135 | 09:00 | 122 | 22:00 | TK | 131 | 18:00 | 128 | 11:00
Khulna(S) | 138 | 09:00 | 126 | 21:00 | Tongi | 132 | 04:00 | 125 | 15:00
Khulshi | 130 | 18:00 | 126 | 09:00 | Ullahpara | 132 | 01:00 | 127 | 19:30
Kishoreganj | 127 | 04:00 | 117 | 19:00 | Ullon | 136 | 02:00 | 122 | 15:00
Kodda | 133 | 01:00 | 122 | 08:00 | Uttara | 132 | 06:00 | 122 | 12:00
KSRM | 132 | 01:00 | 127 | 08:00 | UttaraNew | 132 | 03:00 | 125 | 14:00
Kulaura | 128 | 10:00 | 125 | 14:00 | Zigatola | 133 | 06:00 | 126 | 23:00
Kurigram | 131 | 14:00 | 115 | 23:00
Kushtia | 131 | 09:00 | 123 | 19:00
Laksam | 125 | 18:00 | 113 | 04:00
Lakshmipur | 120 | 18:00 | 110 | 04:00
Lalbag | 132 | 08:00 | 128 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division