## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 27-07-2025 | [28 empty] | Date: | 27-07-2025 | [28 empty] | Date: | 27-07-2025 | [28 empty] | Date: | 27-07-2025 | [28 empty] | Date: | 27-07-2025 | [11 empty] | Date: | 27-07-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [11 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 7 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 726 | 47 | 35 | 143 | 62 | 95 | 55 | 55 | 147 | 0 | 450 | 294 | 0 | 0 | 35 | 0 | 198 | 0 | 0 | 108 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 33 | 67 | 0 | 63 | 25 | 0 | 221 | 0 | 34 | 691 | 0 | 0 | 33 | 0 | 0 | 220 | 0 | 0 | 0 | 1160 | 0 | 51 | 125 | 18 | 0 | 351 | 340 | 51 | 200 | 34 | 112 | 50 | 181 | 36 | 20 | 97 | 44 | 52.2 | 0 | 37 | 0 | 320 | 385 | 0 | 60 | 136 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 92 | 191 | 72 | 0 | 0 | 12 | 8393.2 | 851 | 237 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1222 | 34 | 1414 | 0 | 39 | 0 | 0 | 0 | 0 | 97 | 28 | 0 | 0 | 27 | 0 | 199 | 0 | 191 | 0 | 188 | 0 | 355 | 0 | 0 | 0 | 46 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 120 | 220 | 0 | 299 | 870 | 0 | 6982 | 15375.2 | 104.04
01:00 | 7 | 68 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 727 | 46 | 17 | 135 | 48 | 0 | 55 | 55 | 146 | 0 | 450 | 296 | 0 | 0 | 35 | 0 | 198 | 0 | 33 | 108 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 33 | 39 | 0 | 12 | 25 | 0 | 221 | 0 | 34 | 610 | 0 | 0 | 19 | 0 | 0 | 220 | 0 | 0 | 0 | 1013 | 0 | 51 | 142 | 35 | 0 | 351 | 340 | 51 | 201 | 34 | 112 | 50 | 181 | 32 | 19 | 96 | 44 | 25 | 0 | 37 | 0 | 320 | 382 | 0 | 60 | 134 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 92 | 192 | 72 | 0 | 0 | 8 | 7944 | 890 | 229 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1216 | 0 | 1406 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 191 | 0 | 188 | 0 | 361 | 0 | 0 | 0 | 47 | 115 | 0 | 113 | 0 | 0 | 7.6 | 0 | 0 | 0 | 278 | 120 | 220 | 0 | 304 | 870 | 0 | 6889.6 | 14833.6 | 104.05
02:00 | 7 | 68 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 725 | 47 | 17 | 68 | 16 | 0 | 55 | 55 | 148 | 0 | 450 | 292 | 0 | 0 | 35 | 0 | 200 | 0 | 0 | 90 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 33 | 39 | 0 | 12 | 25 | 0 | 220 | 0 | 34 | 580 | 0 | 0 | 19 | 0 | 0 | 220 | 0 | 0 | 0 | 875 | 0 | 51 | 143 | 50 | 0 | 355 | 340 | 51 | 191 | 33 | 112 | 50 | 181 | 32 | 20 | 88 | 42 | 25 | 0 | 37 | 0 | 320 | 360 | 0 | 60 | 136 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 93 | 191 | 72 | 0 | 0 | 12 | 7598 | 889 | 221 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1228 | 0 | 1407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 191 | 0 | 188 | 0 | 343 | 0 | 0 | 0 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 120 | 220 | 0 | 301 | 870 | 0 | 6765 | 14363 | 104.06
03:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 725 | 47 | 17 | 48 | 16 | 0 | 0 | 55 | 147 | 0 | 450 | 297 | 0 | 0 | 35 | 0 | 200 | 0 | 0 | 90 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 33 | 39 | 0 | 12 | 25 | 0 | 219 | 0 | 33 | 598 | 0 | 0 | 19 | 0 | 0 | 220 | 0 | 0 | 0 | 845 | 0 | 51 | 30 | 70 | 0 | 355 | 340 | 51 | 201 | 33 | 112 | 50 | 181 | 31 | 20 | 34 | 40 | 25 | 0 | 37 | 0 | 310 | 367 | 0 | 60 | 136 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 93 | 191 | 72 | 0 | 0 | 5 | 7321 | 889 | 214 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1220 | 0 | 1309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 191 | 0 | 188 | 0 | 359 | 0 | 0 | 0 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 120 | 220 | 0 | 301 | 960 | 0 | 6763 | 14084 | 104.07
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 725 | 48 | 17 | 48 | 16 | 0 | 0 | 17 | 126 | 0 | 450 | 308 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 90 | 26.7 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 12 | 25 | 0 | 218 | 0 | 34 | 607 | 0 | 0 | 6 | 0 | 0 | 220 | 0 | 0 | 0 | 856 | 0 | 51 | 10 | 71 | 0 | 350 | 340 | 52 | 208 | 33 | 96 | 50 | 181 | 27 | 20 | 17 | 38 | 8 | 0 | 0 | 0 | 300 | 398 | 0 | 60 | 141 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 93 | 181 | 72 | 0 | 0 | 12 | 7071.7 | 889 | 204 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1054 | 0 | 1319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 190 | 0 | 188 | 0 | 388 | 0 | 0 | 0 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 120 | 220 | 0 | 301 | 1090 | 0 | 6648 | 13719.7 | 104.08
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 728 | 48 | 17 | 48 | 16 | 0 | 0 | 17 | 124 | 0 | 450 | 292 | 0 | 0 | 17 | 0 | 199 | 0 | 0 | 90 | 26.7 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 12 | 25 | 0 | 217 | 0 | 35 | 607 | 0 | 0 | 6 | 0 | 0 | 220 | 0 | 0 | 0 | 850 | 0 | 51 | 10 | 71 | 0 | 355 | 340 | 52 | 192 | 33 | 91 | 50 | 181 | 27 | 20 | 17 | 40 | 8 | 0 | 0 | 0 | 300 | 377 | 0 | 60 | 141 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 93 | 181 | 72 | 0 | 0 | 12 | 7026.7 | 889 | 196 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 0 | 1291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 186 | 0 | 184 | 0 | 344 | 0 | 0 | 0 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 120 | 220 | 0 | 299 | 1110 | 0 | 6520 | 13546.7 | 104.09
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 728 | 48 | 17 | 48 | 16 | 0 | 0 | 17 | 17 | 0 | 380 | 302 | 0 | 0 | 17 | 0 | 198 | 0 | 1 | 90 | 26.7 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 12 | 25 | 0.07 | 217 | 0 | 35 | 612 | 0 | 0 | 6 | 0 | 0 | 220 | 0 | 0 | 0 | 873 | 1 | 51 | 10 | 16 | 0 | 352 | 340 | 51 | 201 | 33 | 90 | 50 | 182 | 27 | 20 | 17 | 38 | 8 | 0 | 0 | 0 | 300 | 388 | 0 | 60 | 136 | 0 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 93 | 160 | 72 | 0 | 1.08 | 12 | 6831.85 | 890 | 194 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1.76 | 846 | 0 | 1208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1.34 | 199 | 0 | 182 | 0 | 182 | 0 | 370 | 0 | 0.11 | 0 | 46 | 94 | 0 | 113 | 0 | 0 | 0.1 | 5 | 0.01 | 0 | 170 | 120 | 220 | 0 | 300 | 1000 | 0 | 6182.32 | 13014.17 | 104.1
07:00 | 0 | 30 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 726 | 48 | 17 | 55 | 16 | 0 | 0 | 17 | 16 | 0 | 380 | 296 | 0 | 0 | 17 | 0 | 197 | 0 | 4 | 70 | 26.7 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 12 | 25 | 0.44 | 218 | 0 | 32 | 607 | 0 | 0 | 6 | 0 | 0 | 220 | 0 | 0 | 0 | 919 | 1 | 51 | 10 | 16 | 0 | 352 | 340 | 52 | 196 | 33 | 91 | 50 | 181 | 28 | 20 | 17 | 36 | 8 | 3 | 0 | 0 | 300 | 381 | 0 | 60 | 139 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 93 | 120 | 63 | 0 | 6.79 | 12 | 6845.93 | 890 | 187 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7.12 | 806 | 0 | 1104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 7.38 | 197 | 0 | 182 | 0 | 182 | 0 | 354 | 0 | 0.58 | 0 | 47 | 94 | 4 | 113 | 0 | 0 | 0.5 | 8 | 0.09 | 0 | 170 | 120 | 220 | 0 | 301 | 1000 | 0 | 6043.67 | 12889.6 | 104.11
08:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 725 | 45 | 17 | 82 | 0 | 0 | 0 | 17 | 15 | 0 | 380 | 296 | 0 | 0 | 35 | 0 | 196 | 0 | 15 | 70 | 26.7 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 12 | 25 | 0.34 | 219 | 0 | 0 | 608 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 995 | 4 | 51 | 13 | 8 | 0 | 349 | 340 | 52 | 196 | 33 | 91 | 50 | 182 | 28 | 20 | 17 | 34 | 8 | 6 | 0 | 0 | 300 | 381 | 0 | 60 | 133 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 0 | 92 | 85 | 62 | 0 | 9.47 | 12 | 6873.51 | 890 | 180 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 19.03 | 780 | 0 | 1108.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 20.9 | 196 | 0 | 179 | 0 | 181 | 0 | 354 | 0 | 1.84 | 0 | 46 | 94 | 8 | 113 | 0 | 0 | 1.5 | 15 | 0.11 | 0 | 172 | 120 | 220 | 0 | 301 | 998 | 0 | 6069.69 | 12943.2 | 104.12
09:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 721 | 48 | 17 | 82 | 15 | 15 | 5 | 24 | 42 | 0 | 380 | 288 | 0 | 0 | 35 | 0 | 194 | 0 | 22 | 70 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 12 | 25 | 0.35 | 220 | 0 | 3 | 589 | 0 | 0 | 7 | 0 | 0 | 221 | 0 | 0 | 0 | 955 | 0 | 51 | 50 | 8 | 0 | 347 | 340 | 52 | 190 | 33 | 91 | 50 | 181 | 28 | 20 | 19 | 34 | 8 | 7 | 0 | 0 | 300 | 363 | 0 | 60 | 138 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 0 | 92 | 104 | 62 | 1 | 26.46 | 12 | 6973.81 | 890 | 164 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 43.89 | 862 | 0 | 1228.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 30.07 | 198 | 0 | 180 | 0 | 178 | 0 | 343 | 0 | 1.64 | 0 | 47 | 94 | 13 | 113 | 0 | 0 | 2.9 | 71 | 0.06 | 0 | 166 | 120 | 220 | 0 | 302 | 992 | 0 | 6357.65 | 13331.46 | 104.13
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 726 | 45 | 27 | 82 | 15 | 15 | 40 | 55 | 46 | 4 | 380 | 303 | 0 | 0 | 35 | 0 | 191 | 0 | 9 | 70 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 12 | 25 | 0.18 | 220 | 0 | 3 | 592 | 0 | 0 | 19 | 0 | 0 | 221 | 0 | 0 | 0 | 1010 | 0 | 51 | 50 | 8 | 0 | 338 | 340 | 50 | 209 | 33 | 107 | 50 | 181 | 27 | 17 | 48 | 36 | 25 | 16 | 0 | 0 | 300 | 393 | 0 | 60 | 133 | 7 | 0 | 79 | 30 | 0 | 16 | 0 | 10 | 92 | 105 | 35 | 1 | 29.38 | 12 | 7202.56 | 852 | 159 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 32 | 890 | 0 | 1224.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 9.36 | 191 | 0 | 150 | 0 | 150 | 0 | 384 | 0 | 1.59 | 0 | 47 | 94 | 10 | 110 | 0 | 0 | 6.4 | 88 | 0.13 | 0 | 173 | 120 | 220 | 0 | 301 | 994 | 0 | 6286.07 | 13488.63 | 104.14
11:00 | 0 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 719 | 49 | 35 | 82 | 15 | 15 | 55 | 55 | 60 | 9 | 380 | 301 | 0 | 0 | 35 | 0 | 189 | 0 | 15 | 70 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 12 | 25 | 0.62 | 220 | 0 | 3 | 635 | 17 | 0 | 22 | 1 | 0 | 221 | 0 | 0 | 0 | 1005 | 5 | 43 | 50 | 11 | 0 | 335 | 340 | 48 | 209 | 33 | 98 | 50 | 180 | 18 | 17 | 49 | 38 | 26 | 7 | 0 | 0 | 300 | 384 | 0 | 60 | 144 | 7 | 0 | 79 | 30 | 0 | 16 | 0 | 17 | 82 | 123 | 35 | 2 | 35.83 | 9 | 7289.45 | 852 | 154 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 58 | 988 | 0 | 1219.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 25.09 | 193 | 0 | 150 | 0 | 150 | 0 | 400 | 0 | 1.59 | 0 | 47 | 94 | 7 | 113 | 0 | 0 | 6.1 | 62 | 0.15 | 0 | 184 | 120 | 220 | 0 | 302 | 994 | 0 | 6452.08 | 13741.53 | 104.15
12:00 | 7 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 719 | 48 | 35 | 86 | 30 | 110 | 55 | 55 | 143 | 16 | 380 | 288 | 0 | 0 | 35 | 0 | 190 | 0 | 16 | 108 | 23 | 22 | 0 | 0 | 0 | 0 | 10 | 0 | 13 | 24 | 4 | 0 | 12 | 25 | 0 | 220 | 0 | 3 | 641 | 53 | 0 | 36 | 8 | 0 | 221 | 0 | 0 | 0 | 1040 | 1 | 51 | 75 | 43 | 0 | 340 | 340 | 51 | 195 | 28 | 90 | 50 | 181 | 21 | 19 | 80 | 36 | 52.2 | 5 | 0 | 0 | 320 | 366 | 0 | 60 | 138 | 8 | 0 | 79 | 30 | 0 | 16 | 0 | 17 | 82 | 140 | 28 | 1 | 41.75 | 5 | 7750.95 | 853 | 147 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 104 | 1062 | 0 | 1333.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 0 | 22.84 | 170 | 0 | 130 | 0 | 130 | 0 | 349 | 0 | 2.13 | 0 | 47 | 94 | 9 | 113 | 0 | 0 | 3.6 | 68 | 0.57 | 0 | 179 | 120 | 220 | 0 | 300 | 1005 | 0 | 6608.35 | 14359.3 | 104.16
13:00 | 7 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 46 | 35 | 110 | 30 | 145 | 55 | 55 | 144 | 16 | 380 | 301 | 0 | 0 | 35 | 0 | 190 | 0 | 33 | 108 | 19 | 22 | 0 | 0 | 0 | 0 | 44 | 0 | 6 | 33 | 34 | 0 | 12 | 25 | 0 | 220 | 0 | 10 | 632 | 53 | 0 | 39 | 8 | 0 | 221 | 0 | 0 | 0 | 1003 | 3 | 51 | 115 | 61 | 0 | 338 | 340 | 47 | 191 | 28 | 90 | 50 | 180 | 28 | 20 | 96 | 40 | 52.2 | 10 | 0 | 0 | 320 | 370 | 0 | 60 | 133 | 8 | 0 | 79 | 30 | 0 | 16 | 0 | 17 | 82 | 140 | 27 | 1 | 48.03 | 8 | 7973.23 | 852 | 144 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 105 | 1082 | 0 | 1306.4 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 62 | 0 | 54.02 | 150 | 0 | 130 | 0 | 130 | 0 | 347 | 0 | 5.88 | 0 | 47 | 94 | 4 | 109 | 0 | 0 | 8 | 64 | 0.27 | 0 | 169 | 120 | 220 | 0 | 301 | 1040 | 0 | 6588.57 | 14561.8 | 104.17
14:00 | 7 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 713 | 46 | 35 | 110 | 30 | 145 | 55 | 55 | 145 | 0 | 380 | 289 | 0 | 0 | 35 | 0 | 190 | 0 | 29 | 108 | 24 | 22 | 0 | 0 | 0 | 0 | 44 | 0 | 7 | 33 | 38 | 0 | 12 | 25 | 0.34 | 219 | 0 | 8 | 642 | 53 | 0 | 39 | 8 | 0 | 221 | 0 | 0 | 0 | 1005 | 2 | 51 | 120 | 70 | 0 | 347 | 340 | 48 | 191 | 35 | 91 | 50 | 180 | 28 | 20 | 96 | 44 | 52.2 | 29 | 10 | 0 | 320 | 365 | 0 | 60 | 133 | 8 | 0 | 79 | 30 | 0 | 16 | 0 | 17 | 82 | 140 | 28 | 1 | 15.6 | 12 | 7966.14 | 852 | 137 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 40 | 1076 | 0 | 1301 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 43 | 0 | 19 | 140 | 0 | 130 | 0 | 130 | 0 | 343 | 0 | 1.75 | 0 | 47 | 94 | 21 | 109 | 0 | 0 | 7.8 | 69 | 0.34 | 0 | 167 | 120 | 180 | 0 | 300 | 1036 | 0 | 6410.39 | 14376.53 | 104.18
15:00 | 5 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 718 | 48 | 17 | 108 | 30 | 145 | 55 | 55 | 154 | 0 | 420 | 302 | 0 | 0 | 35 | 0 | 190 | 0 | 11 | 108 | 23.5 | 22 | 0 | 0 | 0 | 0 | 40 | 0 | 1 | 33 | 38 | 0 | 12 | 25 | 0.24 | 217 | 0 | 4 | 655 | 53 | 0 | 39 | 8 | 0 | 220 | 0 | 0 | 0 | 980 | 0 | 51 | 127 | 103 | 0 | 348 | 340 | 47 | 197 | 35 | 91 | 50 | 180 | 27 | 20 | 96 | 18 | 52.2 | 28 | 22 | 0 | 320 | 389 | 0 | 60 | 151 | 8 | 0 | 79 | 30 | 0 | 16 | 0 | 17 | 82 | 140 | 28 | 0 | 42.67 | 12 | 8061.61 | 852 | 138 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 34 | 1100 | 0 | 1321 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8 | 0 | 0 | 14 | 0 | 23.81 | 140 | 0 | 130 | 0 | 130 | 0 | 355 | 0 | 3.26 | 0 | 47 | 94 | 10 | 113 | 0 | 0 | 7.6 | 67 | 0.41 | 0 | 172 | 120 | 220 | 0 | 302 | 1050 | 0 | 6490.88 | 14552.49 | 104.19
16:00 | 7 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 723 | 46 | 17 | 106 | 30 | 145 | 55 | 55 | 148 | 0 | 420 | 288 | 0 | 0 | 35 | 0 | 192 | 0 | 9 | 108 | 0 | 22 | 0 | 0 | 0 | 0 | 35 | 0 | 3 | 33 | 68 | 0 | 12 | 25 | 0.23 | 216 | 0 | 5 | 650 | 53 | 0 | 39 | 8 | 0 | 220 | 0 | 0 | 0 | 847 | 0 | 51 | 135 | 108 | 0 | 351 | 340 | 49 | 190 | 35 | 96 | 50 | 180 | 26 | 20 | 96 | 20 | 52.2 | 28 | 28 | 0 | 320 | 362 | 0 | 60 | 154 | 8 | 0 | 79 | 30 | 0 | 16 | 0 | 17 | 82 | 140 | 32 | 0 | 12.72 | 12 | 7883.15 | 852 | 138 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 44 | 1078 | 0 | 1461 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8 | 0 | 0 | 25 | 0 | 9.83 | 140 | 0 | 130 | 0 | 130 | 0 | 345 | 0 | 0.91 | 0 | 47 | 94 | 16 | 109 | 0 | 0 | 1.2 | 64 | 0.24 | 0 | 167 | 120 | 220 | 0 | 300 | 1040 | 0 | 6578.98 | 14462.13 | 104.22
17:00 | 7 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 723 | 47 | 17 | 108 | 62 | 145 | 55 | 55 | 147 | 0 | 420 | 293 | 0 | 0 | 35 | 0 | 195 | 0 | 1 | 108 | 23 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 33 | 70 | 0 | 36 | 25 | 0.29 | 216 | 0 | 12 | 590 | 0 | 0 | 39 | 8 | 0 | 220 | 0 | 0 | 0 | 836 | 1 | 51 | 132 | 80 | 0 | 352 | 340 | 49 | 184 | 39 | 103 | 50 | 167 | 27 | 20 | 56 | 20 | 52.2 | 7 | 32 | 0 | 320 | 341 | 0 | 60 | 153 | 8 | 0 | 79 | 30 | 0 | 16 | 0 | 17 | 82 | 133 | 32 | 0 | 6.21 | 12 | 7674.7 | 852 | 138 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 21 | 965 | 0 | 1455 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 10 | 0 | 5.92 | 140 | 0 | 130 | 0 | 130 | 0 | 352 | 0 | 0.8 | 0 | 47 | 94 | 10 | 113 | 0 | 0 | 0.3 | 32 | 0.15 | 0 | 170 | 120 | 220 | 0 | 300 | 950 | 0 | 6344.17 | 14018.87 | 104.24
18:00 | 7 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 722 | 44.5 | 29 | 95 | 62 | 110 | 55 | 43 | 131 | 0 | 420 | 293 | 0 | 0 | 35 | 0 | 195 | 0 | 0 | 70 | 23 | 22 | 0 | 0 | 0 | 0 | 13 | 0 | 4 | 33 | 75 | 0 | 36 | 25 | 0.05 | 217 | 0 | 3 | 584 | 0 | 0 | 27 | 8 | 0 | 220 | 0 | 0 | 0 | 844 | 0 | 51 | 140 | 35 | 0 | 350 | 340 | 50 | 182 | 36 | 89 | 50 | 153 | 26 | 20 | 45 | 18 | 34 | 3 | 36 | 0 | 320 | 320 | 0 | 60 | 137 | 8 | 0 | 79 | 30 | 0 | 16 | 0 | 17 | 92 | 142 | 32 | 0 | 1.21 | 12 | 7452.76 | 852 | 138 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4 | 887 | 0 | 1456 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 2 | 0 | 0.15 | 140 | 0 | 130 | 0 | 130 | 0 | 345 | 0 | 0 | 0 | 47 | 94 | 3 | 98 | 0 | 0 | 0 | 7 | 0.04 | 0 | 168 | 120 | 220 | 0 | 302 | 950 | 0 | 6181.19 | 13633.95 | 104.26
19:00 | 50 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 722 | 48 | 35 | 108 | 95 | 210 | 55 | 37 | 154 | 1 | 450 | 301 | 0 | 0 | 35 | 0 | 194 | 0 | 0 | 142 | 25 | 22 | 0 | 0 | 0 | 10 | 19 | 0 | 4 | 65 | 75 | 0 | 36 | 25 | 0 | 218 | 0 | 14 | 698 | 53 | 0 | 35 | 10 | 1 | 219 | 0 | 0 | 0 | 990 | 0 | 51 | 145 | 8 | 0 | 349 | 340 | 47 | 214 | 35 | 91 | 50 | 151 | 26 | 20 | 76 | 46 | 36 | 0 | 36 | 0 | 320 | 390 | 0 | 60 | 146 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 92 | 152 | 32 | 0 | 0 | 12 | 8316 | 852 | 139 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 993 | 17 | 1484 | 0 | 0 | 0 | 15 | 4 | 0 | 95 | 10 | 25 | 0 | 25 | 0 | 147 | 0 | 130 | 0 | 130 | 0 | 388 | 0 | 0 | 0 | 48 | 94 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 213 | 120 | 220 | 0 | 300 | 972 | 0 | 6562 | 14878 | 104.28
19:30 | 97 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 722 | 46 | 35 | 149 | 110 | 260 | 55 | 55 | 141 | 16 | 450 | 289 | 0 | 0 | 35 | 0 | 75 | 0 | 0 | 142 | 25 | 22 | 0 | 0 | 0 | 30 | 62 | 0 | 5 | 65 | 75 | 0 | 36 | 25 | 0 | 218 | 8 | 18 | 683 | 10 | 0 | 40 | 17 | 17 | 207 | 0 | 0 | 0 | 986 | 0 | 51 | 140 | 8 | 0 | 300 | 330 | 47 | 187 | 36 | 98 | 50 | 180 | 27 | 20 | 84 | 46 | 52.2 | 0 | 36 | 0 | 320 | 348 | 0 | 60 | 150 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 92 | 180 | 47 | 0 | 0 | 12 | 8362.2 | 852 | 138 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1091 | 30 | 1465 | 0 | 0 | 0 | 45 | 30 | 0 | 95 | 15 | 25 | 0 | 27 | 0 | 180 | 0 | 130 | 0 | 130 | 0 | 337 | 0 | 0 | 0 | 48 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 120 | 180 | 0 | 301 | 1070 | 0 | 6815 | 15177.2 | 104.28
20:00 | 80 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 721 | 47 | 35 | 140 | 110 | 195 | 55 | 55 | 150 | 16 | 450 | 297 | 0 | 0 | 35 | 0 | 198 | 0 | 0 | 142 | 26 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 14 | 65 | 75 | 0 | 36 | 25 | 0 | 218 | 17 | 20 | 712 | 0 | 0 | 37 | 8 | 32 | 184 | 0 | 0 | 0 | 976 | 0 | 51 | 142 | 8 | 0 | 300 | 300 | 48 | 200 | 39 | 101 | 50 | 177 | 27 | 20 | 95 | 46 | 52.2 | 0 | 36 | 0 | 320 | 335 | 0 | 60 | 142 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 92 | 190 | 47 | 0 | 0 | 12 | 8355.2 | 852 | 138 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1163 | 30 | 1416 | 0 | 26 | 0 | 0 | 35 | 0 | 95 | 20 | 0 | 0 | 27 | 0 | 160 | 0 | 130 | 0 | 130 | 0 | 367 | 0 | 0 | 0 | 48 | 94 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 120 | 180 | 0 | 301 | 1050 | 0 | 6812 | 15167.2 | 104.3
21:00 | 7 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 722 | 49 | 35 | 108 | 80 | 130 | 55 | 55 | 154 | 18 | 450 | 294 | 0 | 0 | 35 | 0 | 197 | 0 | 0 | 125 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 65 | 31 | 0 | 36 | 25 | 0 | 220 | 0 | 25 | 699 | 0 | 0 | 22 | 0 | 0 | 220 | 0 | 0 | 0 | 1024 | 0 | 51 | 140 | 8 | 0 | 353 | 340 | 48 | 192 | 39 | 104 | 50 | 180 | 26 | 20 | 97 | 44 | 52.2 | 0 | 36 | 0 | 320 | 366 | 0 | 60 | 153 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 92 | 170 | 47 | 0 | 0 | 12 | 8179.2 | 853 | 138 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1176 | 30 | 1460.3 | 0 | 31 | 0 | 0 | 35 | 0 | 95 | 32 | 0 | 0 | 27 | 0 | 160 | 0 | 130 | 0 | 130 | 0 | 345 | 0 | 0 | 0 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 120 | 220 | 0 | 350 | 1120 | 0 | 7042.3 | 15221.5 | 104.32
22:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 721 | 46 | 35 | 105 | 32 | 30 | 15 | 17 | 108 | 16 | 450 | 306 | 0 | 0 | 35 | 0 | 199 | 0 | 0 | 125 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 33 | 24 | 0 | 36 | 25 | 0 | 220 | 0 | 25 | 728 | 0 | 0 | 19 | 0 | 0 | 220 | 0 | 0 | 0 | 1044 | 0 | 51 | 140 | 8 | 0 | 355 | 335 | 48 | 198 | 39 | 99 | 50 | 180 | 27 | 20 | 97 | 48 | 52.2 | 0 | 36 | 0 | 315 | 375 | 0 | 60 | 153 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 93 | 170 | 48 | 0 | 0 | 12 | 7924.2 | 852 | 138 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1179 | 34 | 1421 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 27 | 0 | 160 | 0 | 130 | 0 | 130 | 0 | 357 | 0 | 0 | 0 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 120 | 220 | 0 | 349 | 1105 | 0 | 6863 | 14787.2 | 104.34
23:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 721 | 49 | 35 | 105 | 32 | 30 | 15 | 17 | 107 | 0 | 450 | 307 | 0 | 0 | 35 | 0 | 197 | 0 | 0 | 125 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 18 | 24 | 0 | 36 | 25 | 0 | 221 | 0 | 25 | 751 | 0 | 0 | 19 | 0 | 0 | 218 | 0 | 0 | 0 | 1070 | 0 | 51 | 138 | 8 | 0 | 349 | 340 | 48 | 211 | 39 | 109 | 0 | 181 | 27 | 20 | 97 | 48 | 52.2 | 0 | 36 | 0 | 315 | 394 | 0 | 60 | 158 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 94 | 170 | 48 | 0 | 0 | 12 | 7940.2 | 852 | 144 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1214 | 34 | 1420.73 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 27 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 396 | 0 | 0 | 0 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 283 | 120 | 220 | 0 | 350 | 1113 | 0 | 6926.73 | 14866.93 | 104.36
Total KWH | 212112 | 1268160 | 607200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17324701 | 1145160 | 622800 | 2212992 | 828480 | 1668044 | 871371 | 1017258 | 2738880 | 103680 | 9884500 | 7153251 | 0 | 0 | 777766 | 0 | 4874000 | 0 | 170181 | 2384400 | 582000 | 414360 | 0 | 0 | 8782 | 25091 | 261120 | 0 | 425760 | 554250 | 609792 | 0 | 475200 | 602880 | 3961 | 5243944 | 35963 | 449280 | 15578181.82 | 304436 | 0 | 583200 | 92784.6 | 41818 | 5173644 | 0 | 0 | 0 | 22963634 | 23220 | 1161740 | 2301672 | 970181 | 0 | 8657400 | 8188000 | 1185600 | 4833000 | 835920 | 2366400 | 1092420 | 4276800 | 663600 | 44429 | 1548120 | 878400 | 834922 | 157864 | 454832 | 0 | 7431800 | 9349000 | 0 | 1421640 | 3426790.91 | 179208 | 0 | 1911360 | 719904 | 0 | 425000 | 0 | 401040 | 2126400 | 3672000 | 1124160 | 8100 | 268560 | 271440 | 183505940.33 | 20937454 | 4144032 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 566640 | 24880000 | 199680 | 31822815 | 0 | 50791 | 0 | 42624 | 102912 | 0 | 623104 | 39034 | 20482 | 547840 | 153670 | 235504 | 4219455 | 0 | 3959882 | 0 | 3944182 | 0 | 8746690 | 0 | 24960 | 0 | 1093963 | 2455989 | 125116 | 2703926 | 0 | 0 | 39959.04 | 665280 | 2737 | 0 | 5062000 | 2880000 | 5404110 | 0 | 7403636.36 | 25163636.36 | 0 | 159174103.76 | 342680044.09

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 28-07-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-07-2025 | during | 28-07-2025 | during | 28-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 0 | 0 | 0 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 288 | 294 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 190 | 197 | 208.13 | 208.13 | 200 | 200 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 7 | 7 | 7 | 7 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 48 | 49 | 53.97 | 53.97 | 53.97 | 53.97 | FGMO
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 30 | 80 | 149.36 | 149.36 | 144 | 144 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23 | 26 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 0 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 33 | 33 | 52.19 | 52.19 | 33 | 33 | Fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 110 | 130 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 86 | 108 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 70 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 16 | 18 | 104 | 104 | 16 | 16 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 143 | 154 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 16 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 0 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 719 | 722 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 108 | 125 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 2451 | 2643 | 4120.15 | 4675.15 | 3264.47 | 3236.47
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 1 | 0 | 9 | 0 | 9 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 36 | 22 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 220 | 220 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 221 | 220 | 213 | 213 | 213 | 213 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 4 | 31 | 80 | 80 | 48 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 24 | 65 | 65 | 65 | 50 | 50 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 36 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 3 | 25 | 2 | 25 | 2 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 10 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0 | 0 | 2.45 | 0 | 2.45 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 53 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1040 | 1024 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 13 | 17 | 20 | 42 | 20 | 42 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 641 | 699 | 790 | 790 | 790 | 790 | -
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 2311 | 2384 | 3844.17 | 3877.72 | 3797.17 | 3854.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 195 | 192 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 340 | 353 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 340 | 340 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 28 | 39 | 46.7 | 46.7 | 38 | 38 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 51 | 48 | 55 | 55 | 52 | 52 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 43 | 8 | 195 | 195 | 177 | 177 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 75 | 140 | 150 | 150 | 140 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 36 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 181 | 180 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 36 | 44 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 80 | 97 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 21 | 26 | 113 | 113 | 65 | 65 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 90 | 104 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 5 | 0 | 30 | 0 | 30 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1657.2 | 1780.2 | 2409.56 | 2379.56 | 2188.36 | 2158.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-07-2025 | during | 28-07-2025 | during | 28-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 28 | 47 | 157.5 | 157.5 | 152 | 152 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 140 | 170 | 200 | 200 | 170 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 82 | 92 | 115 | 115 | 100 | 100 | Engine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 41.75 | 0 | 39 | 0 | 39 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 5 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 35 | 35 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 314.75 | 338 | 590.1 | 549 | 510.1 | 499
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 60 | 60 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 138 | 153 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 79 | 83 | 83 | 82 | 82 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 18 | 20 | 20 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | Plant Shutdown as per schedule HGPI work
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 366 | 366 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1017 | 1034 | 1086 | 1086 | 1014 | 1014
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 853 | 853 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 147 | 138 | 410 | 410 | 362 | 362 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 30 | 105 | 105 | 53 | 53 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 104 | 0 | 35 | 0 | 35 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1062 | 1176 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2204 | 2235 | 3587.2 | 3552.2 | 3397.2 | 3362.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 300 | 350 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1005 | 1120 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 179 | 276 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.57 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1824.57 | 2086 | 2162 | 2161 | 2152 | 2151
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 31 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 170 | 160 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 130 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 130 | 130 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 349 | 345 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 27 | 32 | 32 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 95 | 97 | 97 | 97 | 97 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.13 | 0 | 3.5 | 0 | 3.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1333.21 | 1460.3 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 22.84 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 108 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 2245.18 | 2445.3 | 3194.37 | 3029.87 | 3152.99 | 2988.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 47 | 48 | 47 | 47 | 47 | 47 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.6 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 94 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 9 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 68 | 0 | 139.72 | 0 | 139.72 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 334.6 | 276 | 485.32 | 309 | 485.32 | 309
System Total |  |  |  |  | 28565.2 | 27045.875 | 14359.3 | 15221.5 | 21478.87 | 21619.5 | 19961.61 | 19573.24
Forecast Scenario (28-07-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15030 |  | 0 |  | 15030
|  |  |  | 1:00 | 14500 |  | 0 |  | 14500
|  |  |  | 2:00 | 14020 |  | 0 |  | 14020
|  |  |  | 3:00 | 13550 |  | 0 |  | 13550
|  |  |  | 4:00 | 13190 |  | 0 |  | 13190
|  |  |  | 5:00 | 13020 |  | 0 |  | 13020
|  |  |  | 6:00 | 12500 |  | 0 |  | 12500
|  |  |  | 7:00 | 12360 |  | 0 |  | 12360
|  |  |  | 8:00 | 12300 |  | 0 |  | 12300
|  |  |  | 9:00 | 12580 |  | 0 |  | 12580
|  |  |  | 10:00 | 13200 |  | 0 |  | 13200
|  |  |  | 11:00 | 13490 |  | 0 |  | 13490
|  |  |  | 12:00 | 13880 |  | 0 |  | 13880
|  |  |  | 13:00 | 14090 |  | 0 |  | 14090
|  |  |  | 14:00 | 14130 |  | 0 |  | 14130
|  |  |  | 15:00 | 14260 |  | 0 |  | 14260
|  |  |  | 16:00 | 14350 |  | 0 |  | 14350
|  |  |  | 17:00 | 13910 |  | 0 |  | 13910
|  |  |  | 18:00 | 13170 |  | 0 |  | 13170
|  |  |  | 18:30 | 13700 |  | 0 |  | 13700
|  |  |  | 19:00 | 14530 |  | 0 |  | 14530
|  |  |  | 19:30 | 14900 |  | 0 |  | 14900
|  |  |  | 20:00 | 15100 |  | 0 |  | 15100
|  |  |  | 21:00 | 15300 |  | 0 |  | 15300
|  |  |  | 22:00 | 15290 |  | 0 |  | 15290
|  |  |  | 23:00 | 15300 |  | 0 |  | 15300
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 13880.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 15300.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15300.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 333.05 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 11:32 hrs on 28-07-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 27-07-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14359.3 | MW | 12:00 Hr. | Energy Generated |  |  | 342.68 |  | MKWHr.
| Day Peak Demand |  |  | 14359.3 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.748 |  | MKWHr.
| Evening Peak Generation |  |  | 15221.5 | MW | 21:00 Hr. | Energy Demand |  |  | 344.428 |  | MKWHr.
| Evening Peak Demand |  |  | 15320.5 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35 |  | °C
| Minimum Generation of the Day |  |  | 12889.6 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 956.17 |  | MMCFD
| Maximum Generation of the Day |  |  | 15375.2 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.4822 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.2328 | 0 | 16.4583 | 0 | 0 | 0.17018 | 0 | 0 | 56.8613 | Gas | 132.1116 | Gas | 430454922.0981
| Chattogram Zone |  |  | 5.6229 | 38.5418 | 3.5953 | 0 | 5.2439 | 0.027181 | 0 | 0.42576 | 53.4569 | Coal | 102.1451 | Coal | 615358569.2088
| Cumilla Zone |  |  | 26.9687 | 0 | 12.4463 | 0 | 0 | 0.15786 | 0.8784 | 0 | 40.4513 | HFO | 45.3631 | HFO | 837843059.272
| Mymensingh Zone |  |  | 1.1242 | 0 | 6.4709 | 0 | 0 | 0.27666 | 0 | 0 | 7.8717 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 24.8647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.8647 | Hydro | 5.2439 | Hydro | 524394.4
| Khulna Zone |  |  | 4.144 | 24.88 | 0.19968 | 0 | 0 | 0.56664 | 21.8495 | 0 | 51.6398 | Solar | 2.8399 | Solar | 46914206.4144
| Barishal Zone |  |  | 8.2841 | 37.6293 | 0 | 0 | 0 | 0.002737 | 0 | 0 | 45.9161 | Import | 54.5507 | Import | 283978980.59
| Rajshahi Zone |  |  | 20.8702 | 0 | 1.0326 | 0 | 0 | 0.8083 | 31.8228 | 0 | 54.5339 | Wind | 0.42576 | Wind | 6233126.4
| Rangpur Zone |  |  | 0 | 1.094 | 5.1599 | 0 | 0 | 0.83036 | 0 | 0 | 7.0842
| Total |  |  | 132.1116 | 102.1451 | 45.3631 | 0 | 5.2439 | 2.8399 | 54.5507 | 0.42576 | 342.68
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 430454922.0981 |  | Hydro | 524394.4
|  |  |  | Coal | 615358569.2088 |  | Solar | 46914206.4144
|  |  |  | HFO | 837843059.272 |  | Import | 283978980.59
|  |  |  | HSD | 0 |  | Wind | 6233126.4
[5 empty] | Total: | 222,13,07,258 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.9375 | Peak Hr Flow | 853.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 44159072.8 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 31.8228 | Peak Hr Flow | 1460.30 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 726 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.8784 | Peak Hr Flow | 44.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 904 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 53.6387 | Peak Hr Flow | 2357.30 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5013
|  |  |  | Chattogram |  | 0 |  | 1375
|  |  |  | Cumilla |  | 0 |  | 1408
|  |  |  | Mymensingh |  | 0 |  | 1218
|  |  |  | Sylhet |  | 25 |  | 623
|  |  |  | Khulna |  | 0 |  | 1797
|  |  |  | Barishal |  | 0 |  | 488
|  |  |  | Rajshahi |  | 0 |  | 1601
|  |  |  | Rangpur |  | 70 |  | 1034
|  |  |  | Total |  | 95 |  | 14557
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Bibiana-II 341 MW CCPP (Summit) GT |  |  | 222 | 3 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
|  | 4 | Bibiana-II 341 MW CCPP (Summit) ST |  |  | 119 | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 641 |  |  |  | Total | 707
|  |  |  | Total Unavailable Capacity |  |  |  | 1348
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:31 | 18:32 | Rahanpur 400/132kV S/S AT-02 HT Scheduled S/D
| 08:32 | 18:32 | Rahanpur 400/132kV S/S AT-02 LT Scheduled S/D
|  | 09:35 | Tangail 132/33kV S/S Tr-1 LT is restored.
|  | 09:35 | Tangail 132/33kV S/S Tr-1 HT is restored.
| 09:37 | 13:20 | Ullahpara 132/33kV S/S Power Transformer -1 LT Project Work S/D Due to Project Work
| 09:38 | 13:18 | Ullahpara 132/33kV S/S Power Transformer -1 HT Project Work S/D Due to Project Work
|  | 10:16 | Kishoreganj 132/33kV S/S Tr-3 (424T) HT is restored.
|  | 10:17 | Kishoreganj 132/33kV S/S Tr-3 (424T) LT is restored.
|  | 10:18 | Kishoreganj 132/33kV S/S Tr-1 (404T) LT is restored.
|  | 10:18 | Kishoreganj 132/33kV S/S Tr-1 (404T) HT is restored.
| 10:46 |  | Raozan 25 MW PP Synchronized
| 10:50 | 11:19 | Tangail 132/33kV S/S Tr-4 HT Tripped showing SIEMENS SIPROTECH 7UT86 relays Due to 33kv | [7 empty] | 12.0MW load
|  |  | kachuadanga feeder fault.(BPDB) | [7 empty] | interrup.
| 10:50 | 11:19 | Tangail 132/33kV S/S Tr-4 LT Tripped showing N/A relays Due to 33kv kachuadanga feeder | [7 empty] | 12.0MW load
|  |  | fault.(BPDB) | [7 empty] | interrup.
| 11:20 | 13:22 | Bheramara-GK 132kV Ckt-2 Forced S/D from Bheramara(GK) 132/33kV end Due to Loop
maintenance and from Bheramara 230/132kV end Due to DS Loop maintenance work at GK end
| 11:22 | 13:21 | Bheramara-GK 132kV Ckt-2 Forced S/D from Bheramara 230/132kV end Due to DS Loop
maintenance work at GK end
| 11:42 | 13:25 | Tongi 230/132/33kV S/S Tongi-Tongi 80 MW PS Forced S/D
| 12:45 | 13:58 | Rajshahi 132/33kV S/S Transformer T-2(415T) HT Forced S/D Due to For tightening work at
the connector of GCB of 132/33 Kv Tr-2 transformer to minimize high temperature.
| 12:45 | 13:58 | Rajshahi 132/33kV S/S Transformer T-2(415T) LT Forced S/D Due to For tightening work at
the connector of GCB of 132/33 Kv Tr-2 transformer to minimize high temperature.
| 15:19 |  | Gopalgonj (N) S/S - Rooppur PP 400 KV ckt Charge From Gopalganj (N) S/S.
|  | 15:45 | Bog-Sherpur 132/33kV S/S Main Bus-1 is restored.
|  | 17:52 | Bakulia-Khulshi 132 kV Ckt-1 is restored.
| 20:42 |  | Raozan 25 MW PP Shutdown
| 21:00 |  | Evening peak Generation is 15221 MW
| 22:32 | 23:25 | Shahjibazar 132/33kV S/S TR-02 LT Scheduled S/D Due to Red hot Maintenance | [7 empty] | 10.0MW load
interrup.
| 22:33 | 23:23 | Shahjibazar 132/33kV S/S TR-02 HT Scheduled S/D Due to Red Hot Maintenance | [7 empty] | 10.0MW load
interrup.
| 23:35 |  | Raozan 25 MW PP Shutdown
| 00:26 |  | Meghnaghat CCPP(Summit) Shutdown with remarks:- GT2
| 00:26 |  | Meghnaghat CCPP(Summit) GT-2 Shutdown with remarks:- None
| 00:30 |  | Meghnaghat CCPP(Summit) Synchronized
| 00:45 |  | Siddhirganj 335 MW CCPP GT was sync.
| 04:09 |  | Siddhirganj 335 MW CCPP ST was sync.
| 06:00 |  | Minimum generation: 12476 MW
| 07:07 |  | At Narail.SS, T-1 Transformer is S/D due to 33 kv Side R phase DS red hot
| 07:21 |  | Satkhira 132/33kV S/S Transformer-1 (T-1) LT Forced S/D Due to Auxiliary fuse change | [7 empty] | 50.0MW load
interrup.
| 07:21 |  | Satkhira 132/33kV S/S Transformer-1 (T-1) HT Forced S/D Due to Auxiliary fuse change work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 27-07-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9884500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 294 | 7153251 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 871371 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 197 | 4874000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 7 | 212112 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 49 | 1145160 | FGMO
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 80 | 828480 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 1017258 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 777766 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 26 | 582000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 0 | 414360 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 33 | 607200 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 130 | 1668044 | Engine Problem
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 108 | 2212992 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1268160 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 18 | 103680 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 154 | 2738880 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 170181 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 622800 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 722 | 17324701 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 125 | 2384400 | -
Dhaka Area Total |  |  |  |  | 5939.724 | 2643 | 56861296
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 92784.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 23220 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 22 | 583200 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5243944 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 5173644 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 41818 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 31 | 609792 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 554250 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 36 | 475200 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 25 | 449280 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 261120 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 3961 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 25091 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 35963 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 602880 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 8782 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 304436 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1024 | 22963634 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 17 | 425760 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 699 | 15578181.82 | Machine Problem
Chattogram Area Total |  |  |  |  | 4895.72 | 2384 | 53456941.42
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 192 | 4833000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 353 | 8657400 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 340 | 8188000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 39 | 835920 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 48 | 1185600 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 970181 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1161740 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 140 | 2301672 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 454832 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1092420 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 180 | 4276800 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 44 | 878400 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 834922 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 44429 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 97 | 1548120 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 26 | 663600 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 104 | 2366400 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 157864 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1780.2 | 40451300
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 47 | 1124160 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8100 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 170 | 3672000 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 92 | 2126400 | Engine Problem
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 268560 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 271440 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 401040 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 338 | 7871700
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1421640 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 153 | 3426790.91 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 719904 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 1911360 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 425000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 179208 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Plant Shutdown as per schedule HGPI work
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 366 | 9349000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7431800 | -
Sylhet Area Total |  |  |  |  | 2325 | 1034 | 24864702.91
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 853 | 20937454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 138 | 4144032 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 30 | 199680 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 566640 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1176 | 24880000 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2235 | 51639806
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 350 | 7403636.36 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2880000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1120 | 25163636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5404110 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 276 | 5062000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2737 | -
Barishal Area Total |  |  |  |  | 2236 | 2086 | 45916119.72
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 31 | 50791 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 39034 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 160 | 4219455 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 130 | 3959882 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 130 | 3944182 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 345 | 8746690 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 153670 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 20482 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 623104 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 102912 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 42624 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 24960 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1460.3 | 31822815 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 235504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 547840 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2445.3 | 54533945
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 48 | 1093963 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 2703926 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 39959.04 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2455989 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 125116 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 665280 | -
Rangpur Area Total |  |  |  |  | 950 | 276 | 7084233.04
Eastern Grid Total |  |  |  |  | 16667.715 | 8179.2 | 183505940.33
Western Grid Total |  |  |  |  | 10378.16 | 7042.3 | 159174103.76
National Grid Total |  |  |  |  | 27045.875 | 15221.5 | 342680044.09
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 27-07-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9612.24 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4849.1 | MW
i) Dhaka area |  |  | 5012.88 |  | MW | i) Khulna area |  |  |  | 1797 | MW
ii) Chattogram area |  |  | 1375 |  | MW | ii) Barishal area |  |  |  | 487.5 | MW
iii) Cumilla area |  |  | 1408.36 |  | MW | iii) Rajshahi area |  |  |  | 1600.6 | MW
iv) Mymensingh area |  |  | 1218 |  | MW | iv) Rangpur area |  |  |  | 964 | MW
v) Sylhet area |  |  | 598 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14461.34 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hathazari | 76 | 19:00 | 133 | PHP | 7 | 13:00
2 | AKSML | 134 | 06:00 | 68 | Ishurdi | 85 | 19:30 | 134 | Pabna | 130 | 19:30
3 | Aftabnagar | 58 | 13:00 | 69 | Jaldhaka | 81 | 02:00 | 135 | Palashbari | 104 | 01:00
4 | Agargaon | 142 | 15:00 | 70 | Jamalpur | 149 | 00:00 | 136 | Panchagarh | 62 | 21:00
5 | Agrabad | 86 | 20:00 | 71 | Jashore | 143 | 13:00 | 137 | Patuakhali | 73 | 22:00
6 | Amnura | 40 | 00:00 | 72 | Jhenaidah | 126 | 19:00 | 138 | Payra | 36 | 22:00
7 | Ashuganj | 93 | 23:00 | 73 | Joydebpur | 139 | 15:00 | 139 | Postogola | 60 | 18:00
8 | BSRM | 205 | 09:00 | 74 | Joypurhat | 66 | 00:00 | 140 | Purbachal | 22 | 19:00
9 | Bagerhat | 86 | 19:30 | 75 | Juldah | 18 | 19:30 | 141 | Purbasadipur | 133 | 13:00
10 | Bajitpur | 91 | 00:00 | 76 | KSRM | 42 | 16:00 | 142 | Rahanpur | 34 | 00:00
11 | Bakulia | 86 | 13:00 | 77 | Kabirpur | 260 | 16:00 | 143 | Rahim | 31 | 18:00
12 | Banani | 98 | 14:00 | 78 | Kachua | 88 | 22:00 | 144 | Rajbari | 85 | 20:00
13 | Bangabhaban | 19 | 10:00 | 79 | Kallyanpur | 111 | 15:00 | 145 | Rajendrapur | 134 | 15:00
14 | Barapukuria | 69 | 21:00 | 80 | Kalurghat | 40 | 12:00 | 146 | Rajshahi | 132 | 23:00
15 | Barguna | 22 | 19:30 | 81 | Kamrangirchar | 77.4 | 18:00 | 147 | Rajshahi-230 | 90 | 00:00
16 | Barishal | 116 | 21:00 | 82 | Kaptai | N/A | N/A | 148 | Ramganj | 116 | 19:00
17 | Barishal-230 | 104 | 19:00 | 83 | Kasba | 35 | 19:30 | 149 | Rampur | 38 | 00:00
18 | Baroaulia | 67 | 11:00 | 84 | Kazla | 93 | 00:00 | 150 | Rangamati | 15 | 19:00
19 | Baroirhat | 68 | 19:00 | 85 | Keranigonj | 84 | 19:30 | 151 | Rangpur | 153 | 19:00
20 | Bashundhara | 216 | 13:00 | 86 | Khagrachori | 32 | 20:00 | 152 | Ruppur | 6.8 | 10:00
21 | BashundharaCement | 13 | 10:00 | 87 | Khulna | 69 | 13:00 | 153 | SSM | 16 | 03:00
22 | Beanibazar | 80 | 01:00 | 88 | Khulshi | 146 | 13:00 | 154 | Saidpur | 119 | 12:00
23 | Benapole | 62 | 00:00 | 89 | Kishoreganj | 138 | 00:00 | 155 | Satkhira | 137 | 22:00
24 | Bhaluka | 157 | 12:00 | 90 | Kodda | 312 | 19:30 | 156 | Satmasjid | 107 | 13:00
25 | Bhandaria | 57 | 23:00 | 91 | Kulaura | 50 | 02:00 | 157 | Savar | 247 | 12:00
26 | Bhangura | 40 | 20:00 | 92 | Kurigram | 66 | 19:00 | 158 | SevenRings | 9.27 | 12:00
27 | Bheramara(GK) | 68 | 19:30 | 93 | Kushtia | 162 | 19:30 | 159 | ShahCement | 23 | 13:00
28 | Bhulta | 249 | 11:00 | 94 | Laksam | 33 | 00:00 | 160 | Shahjadpur | 90 | 20:00
29 | Bog-Sherpur | 72 | 00:00 | 95 | Lakshmipur | 34 | 21:00 | 161 | Shahjibazar | 125 | 19:30
30 | Bogura | 181 | 22:00 | 96 | Lalbag | 57 | 17:00 | 162 | Shahmirpur | 67 | 19:00
31 | Borhanuddin | 93 | 00:00 | 97 | Lalmonirhat | 66 | 19:00 | 163 | Shariatpur | 92 | 21:00
32 | Brahmanbaria | 137 | 23:00 | 98 | MI_Cement | 15.3 | 12:00 | 164 | Sherpur | 162 | 00:00
33 | Cantonment | 150 | 15:00 | 99 | Madanganj | 46 | 21:00 | 165 | Shikalbaha | 15 | 00:00
34 | Chandina | 39.26 | 19:30 | 100 | Madaripur | 118 | 21:00 | 166 | Shitalakhya | 90.5 | 15:00
35 | Chandpur | 84 | 21:00 | 101 | Madartek | 94.26 | 00:00 | 167 | Sholosohor | 41 | 13:00
36 | Chandraghona | 34 | 19:00 | 102 | Madunaghat | 49 | 19:30 | 168 | Shyampur | 164 | 06:00
37 | Chapai | 75 | 22:00 | 103 | Magura | 67 | 19:00 | 169 | Siddhirganj | 128 | 15:00
38 | Charsaidpur | 40 | 15:00 | 104 | Mahasthangarh | 96 | 00:00 | 170 | Sirajganj | 114 | 20:00
39 | Chauddagram | 65 | 00:00 | 105 | Maijdee | 24 | 04:00 | 171 | Sonargaon | 102 | 01:00
40 | Chhatak | 25 | 18:30 | 106 | Manikganj | 130 | 20:00 | 172 | Sreemongol | 78 | 02:00
41 | Chowmuhani | 176 | 22:00 | 107 | Maniknagar | 90 | 13:00 | 173 | Sreepur | 103 | 19:30
42 | Chuadanga | 116 | 21:00 | 108 | Matarbari | 51 | 19:30 | 174 | Srinagar | 49.9 | 22:00
43 | Coxsbazar | 130 | 18:30 | 109 | Matuail | 66 | 16:00 | 175 | Sunamganj | 60 | 03:00
44 | Cumilla(N) | 137 | 00:00 | 110 | Millgate | 123 | 12:00 | 176 | Sylhet | 51 | 02:00
45 | Cumilla(S) | 147 | 19:00 | 111 | Mirpur | 131 | 14:00 | 177 | Sylhet-132 | 139 | 21:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 11 | 11:00 | 178 | TK | 33 | 19:30
47 | Daudkandi | 143 | 01:00 | 113 | Mirzapur | 46 | 19:30 | 179 | Tangail | 186 | 00:00
48 | Dhaka | 86 | 13:00 | 114 | Mithapukur | 70 | 19:30 | 180 | Taraganj | 26 | 00:00
49 | Dhamrai | 132 | 16:00 | 115 | Modern | N/A | N/A | 181 | Thakurgaon | 101 | 07:00
50 | Dhanmondi | 161 | 13:00 | 116 | Mogbazar | 168.2 | 14:00 | 182 | Tongi | 119 | 12:00
51 | Dohazari | 99 | 23:00 | 117 | Mongla | 34 | 00:00 | 183 | Ullahpara | 39 | 21:00
52 | Faridpur | 170 | 22:00 | 118 | Motijheel | 49 | 13:00 | 184 | Ullon | 42 | 00:00
53 | Fatullah | 104 | 15:00 | 119 | Muktagacha | 40 | 00:00 | 185 | Uttara | 91 | 13:00
54 | Fenchuganj | 43 | 01:00 | 120 | Munshiganj | 115 | 00:00 | 186 | UttaraNew | 63 | 00:00
55 | Feni | 107 | 20:00 | 121 | Muradnagar | 42 | 00:00 | 187 | Zigatola | 78 | 16:00
56 | GPH | 88 | 03:00 | 122 | Mymensingh | 212 | 19:30
57 | Ghatail | 84 | 00:00 | 123 | Naogaon | 137 | 22:00
58 | Ghorashal | 13 | 19:00 | 124 | Narail | 60.5 | 19:30
59 | Ghorashal-230 | 85 | 00:00 | 125 | Narinda | 88 | 13:00
60 | Goalpara | 39 | 21:00 | 126 | Narshingdi | 183 | 01:00
61 | Gollamari | 156 | 05:00 | 127 | Natore | 165 | 19:30
62 | Gopalganj | 120 | 22:00 | 128 | Nawabganj | 61 | 22:00
63 | Gulshan | 78 | 14:00 | 129 | Netrakona | 148 | 20:00
64 | Halishahar | 70 | 15:00 | 130 | New | 87.7 | 12:00
65 | HaripurSBU | 151 | 09:00 | 131 | Niamatpur | 83 | 22:00
66 | Hasnabad | 84 | 14:00 | 132 | Noapara | 44 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 27-07-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15375.2 | 186 |  | 15569.57
1:00 | 14833.6 | 179 |  | 15020.66
2:00 | 14363 | 102 |  | 14470
3:00 | 14084 | 87 |  | 14175
4:00 | 13719.7 | 68 |  | 13790.7
5:00 | 13546.7 | 61 |  | 13610.7
6:00 | 13014.17 | 108 |  | 13127.03
7:00 | 12889.6 | 118 |  | 13012.91
8:00 | 12943.2 | 68 |  | 13014.2
9:00 | 13331.46 | 50 |  | 13383.46
10:00 | 13488.63 | 37 |  | 13527.63
11:00 | 13741.53 | 0 |  | 13741.53
12:00 | 14359.3 | 0 |  | 14359.3
13:00 | 14561.8 | 38 |  | 14601.8
14:00 | 14376.53 | 45 |  | 14423.56
15:00 | 14552.49 | 40 |  | 14594.29
16:00 | 14462.13 | 31 |  | 14494.53
17:00 | 14018.87 | 28 |  | 14048.13
18:00 | 13633.95 | 0 |  | 13633.95
19:00 | 14878 | 21 |  | 14900
19:30 | 15177.2 | 137 |  | 15320.2
20:00 | 15167.2 | 127 |  | 15300.2
21:00 | 15221.5 | 95 |  | 15320.5
22:00 | 14787.2 | 131 |  | 14924.1
23:00 | 14866.93 | 128 |  | 15000.69
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 27-07-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8393.2 | 6982 | 15375.2 | DAILY GENERATION CURVE
00:30 | 8168.6 | 6935.8 | 15104.4
01:00 | 7944 | 6889.6 | 14833.6 | 27-07-2025
01:30 | 7771 | 6827.3 | 14598.3
02:00 | 7598 | 6765 | 14363
02:30 | 7459.5 | 6764 | 14223.5
03:00 | 7321 | 6763 | 14084
03:30 | 7196.35 | 6705.5 | 13901.85
04:00 | 7071.7 | 6648 | 13719.7
04:30 | 7049.2 | 6584 | 13633.2
05:00 | 7026.7 | 6520 | 13546.7
05:30 | 6929.275 | 6351.16 | 13280.435
06:00 | 6831.85 | 6182.32 | 13014.17
06:30 | 6838.89 | 6112.995 | 12951.885
07:00 | 6845.93 | 6043.67 | 12889.6
07:30 | 6859.72 | 6056.68 | 12916.4
08:00 | 6873.51 | 6069.69 | 12943.2
08:30 | 6923.66 | 6213.67 | 13137.33
09:00 | 6973.81 | 6357.65 | 13331.46
09:30 | 7088.185 | 6321.86 | 13410.045
10:00 | 7202.56 | 6286.07 | 13488.63
10:30 | 7246.005 | 6369.075 | 13615.08
11:00 | 7289.45 | 6452.08 | 13741.53
11:30 | 7520.2 | 6530.215 | 14050.415
12:00 | 7750.95 | 6608.35 | 14359.3
12:30 | 7862.09 | 6598.46 | 14460.55
13:00 | 7973.23 | 6588.57 | 14561.8
13:30 | 7969.685 | 6499.48 | 14469.165
14:00 | 7966.14 | 6410.39 | 14376.53
14:30 | 8013.875 | 6450.635 | 14464.51
15:00 | 8061.61 | 6490.88 | 14552.49
15:30 | 7972.38 | 6534.93 | 14507.31
16:00 | 7883.15 | 6578.98 | 14462.13
16:30 | 7778.925 | 6461.575 | 14240.5
17:00 | 7674.7 | 6344.17 | 14018.87
17:30 | 7563.73 | 6262.68 | 13826.41
18:00 | 7452.76 | 6181.19 | 13633.95
18:30 | 7884.38 | 6371.595 | 14255.975
19:00 | 8316 | 6562 | 14878
19:30 | 8362.2 | 6815 | 15177.2
20:00 | 8355.2 | 6812 | 15167.2
20:30 | 8267.2 | 6927.15 | 15194.35 |  | Executive Engineer
21:00 | 8179.2 | 7042.3 | 15221.5 |  | Network Operation Division
21:30 | 8051.7 | 6952.65 | 15004.35
22:00 | 7924.2 | 6863 | 14787.2
22:30 | 7932.2 | 6894.865 | 14827.065
23:00 | 7940.2 | 6926.73 | 14866.93

## En-Curve
QF-LDC-12
Date | 27-07-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3568 | 2136 | 851 | 38 | 44 | 1414 | 221 | 4567 | 0 | 593 | 1917.2 | 0 | 0 | 26 | 186 | DAILY ENERGY CURVE
00:30 | 3566 | 2144.5 | 870.5 | 38 | 44 | 1410 | 221 | 4452.5 | 20.3 | 519.5 | 1797.1 | 0 | 0 | 21 | 182.5 | 27-07-2025
01:00 | 3564 | 2153 | 890 | 38 | 44 | 1406 | 221 | 4338 | 40.6 | 446 | 1677 | 0 | 0 | 16 | 179
01:30 | 3537.5 | 2159 | 889.5 | 38 | 43 | 1406.5 | 220.5 | 4257 | 20.3 | 368.5 | 1643.5 | 0 | 0 | 15 | 140.5 | Energy Generated | 342.68 |  | MKWHr
02:00 | 3511 | 2165 | 889 | 38 | 42 | 1407 | 220 | 4176 | 0 | 291 | 1610 | 0 | 0 | 14 | 102 | Energy not Served | 1.748 |  | MKWHr
02:30 | 3519 | 2177 | 889 | 38 | 41 | 1358 | 219.5 | 4213.5 | 0 | 274 | 1481 | 0 | 0 | 13.5 | 94.5 | Total Energy Requirement | 344.428 |  | MKWHr
03:00 | 3527 | 2189 | 889 | 38 | 40 | 1309 | 219 | 4251 | 0 | 257 | 1352 | 0 | 0 | 13 | 87
03:30 | 3546 | 2198.35 | 889 | 38 | 39 | 1314 | 218.5 | 4189.5 | 0 | 194 | 1260.5 | 0 | 0 | 15 | 77.5
04:00 | 3565 | 2207.7 | 889 | 38 | 38 | 1319 | 218 | 4128 | 0 | 131 | 1169 | 0 | 0 | 17 | 68
04:30 | 3519.5 | 2201.7 | 889 | 38 | 39 | 1305 | 217.5 | 4105.5 | 0 | 131 | 1174 | 0 | 0 | 13 | 64.5
05:00 | 3474 | 2195.7 | 889 | 38 | 40 | 1291 | 217 | 4083 | 0 | 131 | 1179 | 0 | 0 | 9 | 61
05:30 | 3491.5 | 2131.2 | 889.5 | 38 | 39 | 1249.5 | 217 | 3965 | 6.735 | 131 | 1104.5 | 0 | 0 | 17.5 | 84.5
06:00 | 3509 | 2066.7 | 890 | 38 | 38 | 1208 | 217 | 3847 | 13.47 | 131 | 1030 | 0 | 0 | 26 | 108
06:30 | 3485.5 | 2067.2 | 890 | 38 | 37 | 1156 | 217.5 | 3848.5 | 33.685 | 136 | 1013.5 | 0 | 0 | 29 | 113
07:00 | 3462 | 2067.7 | 890 | 38 | 36 | 1104 | 218 | 3850 | 53.9 | 141 | 997 | 0 | 0 | 32 | 118
07:30 | 3453.5 | 2044.2 | 890 | 38 | 35 | 1106.155 | 218.5 | 3875 | 94.045 | 144 | 990 | 0 | 0 | 28 | 93
08:00 | 3445 | 2020.7 | 890 | 38 | 34 | 1108.31 | 219 | 3900 | 134.19 | 147 | 983 | 0 | 0 | 24 | 68
08:30 | 3418 | 2017.35 | 890 | 38 | 34 | 1168.2 | 219.5 | 3906.5 | 206.78 | 154.5 | 1043.5 | 0 | 0 | 41 | 59
09:00 | 3391 | 2014 | 890 | 38 | 34 | 1228.09 | 220 | 3913 | 279.37 | 162 | 1104 | 0 | 0 | 58 | 50
09:30 | 3380.5 | 2018.5 | 871 | 38 | 35 | 1226.34 | 220 | 3960 | 261.705 | 162 | 1185 | 0 | 0 | 52 | 43.5
10:00 | 3370 | 2023 | 852 | 38 | 36 | 1224.59 | 220 | 4007 | 244.04 | 162 | 1266 | 0 | 0 | 46 | 37
10:30 | 3369.5 | 2020 | 852 | 38 | 37 | 1221.87 | 220 | 4081 | 271.71 | 166 | 1298.5 | 0 | 0 | 39.5 | 18.5
11:00 | 3369 | 2017 | 852 | 38 | 38 | 1219.15 | 220 | 4155 | 299.38 | 170 | 1331 | 0 | 0 | 33 | 0
11:30 | 3299.5 | 2030.5 | 852.5 | 38 | 37 | 1276.18 | 220 | 4214.5 | 341.135 | 210.5 | 1507.6 | 0 | 0 | 23 | 0
12:00 | 3230 | 2044 | 853 | 38 | 36 | 1333.21 | 220 | 4274 | 382.89 | 251 | 1684.2 | 0 | 0 | 13 | 0
12:30 | 3216 | 2057.5 | 852.5 | 38 | 38 | 1319.805 | 220 | 4274 | 390.545 | 282.5 | 1762.2 | 0 | 0 | 9.5 | 19
13:00 | 3202 | 2071 | 852 | 38 | 40 | 1306.4 | 220 | 4274 | 398.2 | 314 | 1840.2 | 0 | 0 | 6 | 38
13:30 | 3197.5 | 2048 | 852 | 38 | 42 | 1303.7 | 219.5 | 4273.5 | 338.515 | 312.25 | 1837.7 | 0 | 0 | 6.5 | 41.5
14:00 | 3193 | 2025 | 852 | 38 | 44 | 1301 | 219 | 4273 | 278.83 | 310.5 | 1835.2 | 0 | 0 | 7 | 45
14:30 | 3214.5 | 2096.75 | 852 | 38 | 31 | 1311 | 218 | 4289.5 | 260.41 | 316.65 | 1832.7 | 0 | 0 | 4 | 42.5
15:00 | 3236 | 2168.5 | 852 | 38 | 18 | 1321 | 217 | 4306 | 241.99 | 322.8 | 1830.2 | 0 | 0 | 1 | 40
15:30 | 3218.5 | 2157.75 | 852 | 38 | 19 | 1391 | 216.5 | 4217.5 | 226.56 | 340.8 | 1827.7 | 0 | 0 | 2 | 35.5
16:00 | 3201 | 2147 | 852 | 38 | 20 | 1461 | 216 | 4129 | 211.13 | 358.8 | 1825.2 | 0 | 0 | 3 | 31
16:30 | 3195 | 2139 | 852 | 38 | 20 | 1458 | 216 | 3993.5 | 153.4 | 398.4 | 1775.7 | 0 | 0 | 1.5 | 29.5
17:00 | 3189 | 2131 | 852 | 38 | 20 | 1455 | 216 | 3858 | 95.67 | 438 | 1726.2 | 0 | 0 | 0 | 28
17:30 | 3171.5 | 2107 | 852 | 38 | 19 | 1455.5 | 216.5 | 3820 | 58.06 | 423.5 | 1663.35 | 0 | 0 | 2 | 14
18:00 | 3154 | 2083 | 852 | 38 | 18 | 1456 | 217 | 3782 | 20.45 | 409 | 1600.5 | 0 | 0 | 4 | 0
18:30 | 3229.5 | 2098 | 852 | 38 | 32 | 1470 | 217.5 | 3998 | 10.225 | 517.5 | 1789.25 | 0 | 0 | 4 | 10.5
19:00 | 3305 | 2113 | 852 | 38 | 46 | 1484 | 218 | 4214 | 0 | 626 | 1978 | 0 | 0 | 4 | 21
19:30 | 3043 | 2069 | 852 | 38 | 46 | 1465 | 218 | 4439 | 0 | 648 | 2354.2 | 0 | 0 | 5 | 137
20:00 | 3126 | 2050 | 852 | 38 | 46 | 1416 | 218 | 4529 | 0 | 699 | 2179.2 | 0 | 0 | 14 | 127
20:30 | 3190.5 | 2077 | 852.5 | 38 | 45 | 1438.15 | 219 | 4611 | 0 | 662 | 2045.7 | 0 | 0 | 15.5 | 111
21:00 | 3255 | 2104 | 853 | 38 | 44 | 1460.3 | 220 | 4693 | 0 | 625 | 1912.2 | 0 | 0 | 17 | 95
21:30 | 3266 | 2106.5 | 852.5 | 38 | 46 | 1440.65 | 220 | 4712 | 0 | 527 | 1774.2 | 0 | 0 | 21.5 | 113
22:00 | 3277 | 2109 | 852 | 38 | 48 | 1421 | 220 | 4731 | 0 | 429 | 1636.2 | 0 | 0 | 26 | 131
22:30 | 3273 | 2115 | 852 | 38 | 48 | 1420.865 | 220.5 | 4780 | 0 | 421.5 | 1634.2 | 0 | 0 | 24 | 129.5
23:00 | 3269 | 2121 | 852 | 38 | 48 | 1420.73 | 221 | 4829 | 0 | 414 | 1632.2 | 0 | 0 | 22 | 128
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 27-07-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 385 | 08:00 | 372 | 11:00 | Payra | 415 | 06:00 | 410 | 22:00
Ashuganj | 402 | 7:00 | 377 | 10:00 | Rahanpur | 393 | 08:00 | 380 | 00:00
Bhulta | 398 | 07:00 | 371 | 11:00 | Rampal | 407 | 08:00 | 393 | 23:00
Bibiana | 385 | 08:00 | 377 | 03:00
BIPTC | 399 | 08:00 | 300 | 01:00
Bogura | 374 | 09:00 | 357 | 01:00
Gopalganj | 400 | 08:00 | 386 | 23:00
Kaliakoir | 373 | 07:00 | 362 | 11:00
Madunaghat | 394 | 18:00 | 386 | 00:00
Meghnaghat | 390 | 08:00 | -381 | 19:30
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 223 | 06:00 | 216 | 11:00 | Keranigonj | 221 | 08:00 | 213 | 11:00
AKSML | 230 | 16:00 | 222 | 00:00 | Khulna(S) | 232 | 08:00 | 218 | 23:00
Aminbazar | 223 | 04:00 | 216 | 11:00 | Madunaghat | 233 | 18:00 | 227 | 23:00
Ashuganj | 232 | 07:00 | 222 | 11:00 | Madunaghat-400 | 233 | 18:00 | 227 | 00:00
Ashuganj-400 | 232 | 07:00 | 222 | 11:00 | Maniknagar | 217 | 08:00 | 210 | 12:00
Baghabari | 233 | 07:00 | 224 | 00:00 | Meghnaghat | 226 | 07:00 | 220 | 11:00
Barapukuria | 215 | 09:00 | 202 | 19:00 | Meghnaghat-400 | 223 | 08:00 | 215 | 12:00
Barapukuria-230 | 215 | 09:00 | 202 | 19:00 | Mirsorai | 228 | 14:00 | 219 | 00:00
Barishal | 228 | 07:00 | 220 | 21:00 | Rajshahi | 231 | 08:00 | 219 | 21:00
Bheramara | 233 | 08:00 | 221 | 21:00 | Rampal | 232 | 08:00 | 220 | 23:00
Bhulta | 230 | 07:00 | 210 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 225 | 05:00 | 220 | 00:00 | Rampura | 229 | 07:00 | 209 | 11:00
BIPTC | 235 | 08:00 | 222 | 21:00 | Shikalbaha | 231 | 19:30 | 224 | 23:00
Bogura | 231 | 08:00 | 220 | 01:00 | Shyampur | 221 | 08:00 | 213 | 12:00
Bogura-400 | 232 | 09:00 | 221 | 00:00 | Siddhirganj | 219 | 07:00 | 212 | 11:00
Borhanuddin | 233 | 18:00 | 227 | 23:00 | Sirajgonj | 238 | 09:00 | 233 | 01:00
BSRM | 228 | 14:00 | 218 | 23:00 | Sreepur | 227 | 06:00 | 220 | 00:00
Cumilla(N) | 222 | 08:00 | 216 | 00:00 | Tongi | 226 | 04:00 | 213 | 12:00
Faridpur | 226 | 08:00 | 218 | 00:00
Fenchuganj | 227 | 07:00 | 219 | 23:00
Ghorashal | 230 | 00:00 | 225 | 07:00
Ghorashal-230 | 228 | 07:00 | 213 | 11:00
Gopalganj | 227 | 08:00 | 219 | 23:00
GPH | 230 | 14:00 | 222 | 00:00
Haripur | 219 | 08:00 | 212 | 12:00
Hasnabad | 220 | 07:00 | 215 | 15:00
Hathazari | 230 | 18:00 | 220 | 23:00
Ishurdi | 235 | 08:00 | 224 | 21:00
Jhenaidah | 232 | 08:00 | 218 | 19:30
Kaliakoir | 229 | 05:00 | 220 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 07:00 | 123 | 11:00 | Lalmonirhat | 126 | 17:00 | 119 | 07:00
Agargaon | 131 | 05:00 | 124 | 12:00 | Madanganj | 128 | 19:30 | 124 | 11:00
Agrabad | 133 | 19:30 | 127 | 01:00 | Madaripur | 134 | 08:00 | 128 | 21:00
AKS | 129 | 13:00 | 126 | 00:00 | Madartek | 138 | 06:00 | 122 | 12:00
Aminbazar | 131 | 03:00 | 126 | 11:00 | Madunaghat | 132 | 16:00 | 128 | 23:00
Amnura | 134 | 18:00 | 125 | 01:00 | Magura | 136 | 09:00 | 124 | 21:00
Ashuganj | 140 | 06:00 | 135 | 00:00 | Mahasthangarh | 132 | 09:00 | 123 | 00:00
Bagerhat | 133 | 08:00 | 120 | 23:00 | Maijdee | 117 | 08:00 | 108 | 22:00
Bajitpur | 129 | 05:00 | 123 | 00:00 | Manikganj | 127 | 08:00 | 114 | 12:00
Bakulia | 133 | 17:00 | 127 | 23:00 | Maniknagar | 130 | 08:00 | 122 | 13:00
Banani | 138 | 05:00 | 123 | 12:00 | Matarbari | 125 | 09:00 | 111 | 23:00
Bangabhaban | 129 | 05:00 | 123 | 12:00 | Matuail | 128 | 20:00 | 123 | 12:00
Barapukuria | 132 | 17:00 | 121 | 19:00 | Millgate | 131 | 05:00 | 122 | 12:00
Barguna | 134 | 07:00 | 130 | 23:00 | Mirpur | 131 | 02:00 | 124 | 11:00
Barishal | 133 | 06:00 | 126 | 21:00 | Mirzapur | 129 | 07:00 | 124 | 19:00
Barishal-230 | 133 | 07:00 | 126 | 23:00 | Mithapukur | 123 | 11:00 | 109 | 00:00
Baroaulia | 132 | 13:00 | 128 | 00:00 | MI_Cement | 130 | 20:00 | 124 | 11:00
Baroirhat | 124 | 16:00 | 116 | 23:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 138 | 06:00 | 120 | 17:00 | Mogbazar | 139 | 05:00 | 124 | 12:00
BashundharaCement | 136 | 18:00 | 124 | 11:00 | Mongla | 133 | 08:00 | 121 | 19:30
Beanibazar | 125 | 09:00 | 116 | 02:00 | Motijheel | 129 | 05:00 | 123 | 12:00
Benapole | 130 | 08:00 | 118 | 23:00 | Muktagacha | 134 | 06:00 | 127 | 19:00
Bhaluka | 129 | 07:00 | 122 | 00:00 | Munshiganj | 129 | 20:00 | 123 | 12:00
Bhandaria | 128 | 08:00 | 115 | 23:00 | Muradnagar | 124 | 08:00 | 115 | 22:00
Bhangura | 133 | 08:00 | 127 | 01:00 | Mymensingh | 135 | 06:00 | 113 | 00:00
Bheramara | 137 | 08:00 | 130 | 21:00 | Naogaon | 130 | 08:00 | 121 | 00:00
Bheramara(GK) | 136 | 08:00 | 130 | 19:00 | Narail | 138 | 09:00 | 122 | 21:00
Bhulta | 124 | 19:30 | 117 | 12:00 | Narinda | 130 | 08:00 | 122 | 13:00
Bog-Sherpur | 133 | 08:00 | 125 | 01:00 | Narshingdi | 136 | 07:00 | 118 | 11:00
Bogura | 136 | 09:00 | 127 | 00:00 | Natore | 133 | 09:00 | 125 | 21:00
Bogura-230 | 136 | 08:00 | 127 | 01:00 | Nawabganj | 132 | 04:00 | 125 | 12:00
Brahmanbaria | 134 | 07:00 | 128 | 00:00 | Netrakona | 122 | 07:00 | 112 | 00:00
Cantonment | 130 | 05:00 | 124 | 11:00 | New | 132 | 06:00 | 122 | 12:00
Chandina | 127 | 07:00 | 120 | 23:00 | Niamatpur | 132 | 08:00 | 128 | 00:00
Chandpur | 128 | 09:00 | 117 | 23:00 | Noapara | 134 | 07:00 | 123 | 23:00
Chandraghona | 133 | 16:00 | 129 | 23:00 | Pabna | 134 | 08:00 | 127 | 19:00
Chapai | 131 | 10:00 | 127 | 00:00 | Palashbari | 123 | 18:00 | 107 | 01:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 20:00 | 124 | 12:00 | Panchagarh | 134 | 22:00 | 119 | 19:00
Chauddagram | 122 | 14:00 | 115 | 23:00 | Patuakhali | 135 | 08:00 | 131 | 00:00
Chhatak | 125 | 07:00 | 114 | 06:00 | Payra | 136 | 02:00 | 133 | 22:00
Chowmuhani | 119 | 09:00 | 107 | 22:00 | PHP | 122 | 12:00 | 114 | 23:00
Chuadanga | 136 | 09:00 | 122 | 19:00 | Postogola | 130 | 06:00 | 126 | 11:00
Coxsbazar | 125 | 09:00 | 112 | 23:00 | Purbachal | 138 | 05:00 | 122 | 12:00
Cumilla(N) | 127 | 08:00 | 120 | 23:00 | Purbasadipur | 129 | 17:00 | 116 | 19:00
Cumilla(S) | 134 | 18:00 | 118 | 22:00 | Rahanpur | 134 | 07:00 | 129 | 01:00
Daganbhuiyan | 119 | 13:00 | 110 | 23:00 | Rahanpur-400 | 135 | 08:00 | 130 | 00:00
Daudkandi | 121 | 04:00 | 111 | 22:00 | Rahim | 128 | 20:00 | 123 | 13:00
Dhaka | 138 | 06:00 | 123 | 12:00 | Rajbari | 133 | 08:00 | 126 | 21:00
Dhamrai | 130 | 18:00 | 123 | 12:00 | Rajendrapur | 134 | 08:00 | 121 | 12:00
Dhanmondi | 139 | 07:00 | 123 | 12:00 | Rajshahi | 133 | 09:00 | 126 | 01:00
Dohazari | 132 | 19:30 | 123 | 23:00 | Rajshahi-230 | 132 | 08:00 | 126 | 01:00
Faridpur | 134 | 08:00 | 129 | 00:00 | Ramganj | 121 | 09:00 | 109 | 22:00
Fatullah | 130 | 20:00 | 125 | 11:00 | Rampur | 132 | 19:30 | 127 | 00:00
Fenchuganj | 133 | 07:00 | 128 | 00:00 | Rampura | 138 | 06:00 | 123 | 12:00
Feni | 123 | 13:00 | 116 | 22:00 | Rangamati | 132 | 02:00 | 128 | 23:00
Ghatail | 129 | 07:00 | 122 | 19:00 | Rangpur | 128 | 17:00 | 121 | 04:00
Ghorashal | 136 | 07:00 | 130 | 12:00 | Ruppur | 137 | 07:00 | 130 | 19:30
Goalpara | 138 | 08:00 | 124 | 23:00 | Saidpur | 128 | 17:00 | 120 | 03:00
Gollamari | 137 | 07:00 | 127 | 23:00 | Satkhira | 134 | 09:00 | 119 | 23:00
Gopalganj | 135 | 08:00 | 126 | 22:00 | Satmasjid | 131 | 06:00 | 123 | 13:00
Gopalganj-400 | 138 | 06:00 | 131 | 00:00 | Savar | 132 | 02:00 | 124 | 11:00
Gulshan | 138 | 05:00 | 124 | 12:00 | SevenRings | 137 | 08:00 | 128 | 11:00
Halishahar | 133 | 18:00 | 128 | 00:00 | ShahCement | 130 | 20:00 | 124 | 12:00
Haripur | 129 | 20:00 | 123 | 12:00 | Shahjadpur | 135 | 02:00 | 131 | 23:00
HaripurSBU | 129 | 20:00 | 123 | 12:00 | Shahjibazar | 133 | 08:00 | 127 | 00:00
Hasnabad | 131 | 07:00 | 125 | 12:00 | Shahmirpur | 133 | 18:00 | 129 | 02:00
Hathazari | 134 | 03:00 | 128 | 23:00 | Shariatpur | 133 | 08:00 | 126 | 21:00
Ishurdi | 138 | 08:00 | 131 | 01:00 | Sherpur | 136 | 15:00 | 128 | 19:00
Jaldhaka | 126 | 17:00 | 115 | 07:00 | Shikalbaha | 124 | 19:30 | 117 | 23:00
Jamalpur | 140 | 06:00 | 130 | 19:00 | Shikalbaha-230 | 135 | 19:30 | 129 | 23:00
Jashore | 136 | 08:00 | 120 | 23:00 | Shitalakhya | 130 | 20:00 | 124 | 11:00
Jhenaidah | 138 | 08:00 | 121 | 21:00 | Sholosohor | 131 | 13:00 | 129 | 00:00
Jhenaidah-230 | 138 | 08:00 | 128 | 19:30 | Shyampur | 129 | 20:00 | 124 | 12:00
Joydebpur | 134 | 07:00 | 125 | 11:00 | Shyampur-230 | 130 | 20:00 | 124 | 12:00
Joypurhat | 129 | 18:30 | 117 | 01:00 | Siddhirganj | 129 | 20:00 | 124 | 11:00
Juldah | 134 | 19:30 | 129 | 22:00 | Sirajganj | 131 | 08:00 | 124 | 01:00
Kabirpur | 131 | 18:00 | 118 | 12:00 | Sonargaon | 129 | 20:00 | 122 | 00:00
Kachua | 125 | 07:00 | 116 | 22:00 | Sreemongol | 132 | 07:00 | 126 | 00:00
Kaliakoir | 133 | 17:00 | 126 | 11:00 | Sreepur | 131 | 06:00 | 126 | 00:00
Kallyanpur | 131 | 05:00 | 126 | 13:00 | Srinagar | 133 | 08:00 | 126 | 12:00
Kalurghat | 133 | 19:30 | 128 | 01:00 | SSM | 136 | 18:00 | 130 | 23:00
Kamrangirchar | 132 | 06:00 | 125 | 12:00 | Sunamganj | 120 | 09:00 | 109 | 03:00
Kaptai | 134 | 7:00 | 132 | 11:00 | Sylhet | 126 | 08:00 | 117 | 06:00
Kasba | 122 | 06:00 | 114 | 23:00 | Sylhet-132 | 126 | 05:00 | 119 | 23:00
Kazla | 129 | 08:00 | 122 | 12:00 | Tangail | 128 | 17:00 | 120 | 19:00
Keranigonj | 133 | 08:00 | 127 | 11:00 | Taraganj | 128 | 17:00 | 118 | 19:00
Khagrachori | 131 | 08:00 | 127 | 00:00 | Thakurgaon | 131 | 22:00 | 119 | 07:00
Khulna | 135 | 08:00 | 125 | 23:00 | TK | 132 | 18:00 | 127 | 23:00
Khulna(S) | 138 | 08:00 | 127 | 23:00 | Tongi | 134 | 04:00 | 125 | 12:00
Khulshi | 132 | 19:30 | 126 | 01:00 | Ullahpara | 133 | 07:00 | 127 | 01:00
Kishoreganj | 129 | 08:00 | 118 | 00:00 | Ullon | 138 | 07:00 | 123 | 12:00
Kodda | 133 | 07:00 | 122 | 11:00 | Uttara | 131 | 03:00 | 124 | 11:00
KSRM | 132 | 04:00 | 127 | 23:00 | UttaraNew | 131 | 02:00 | 123 | 11:00
Kulaura | 132 | 07:00 | 127 | 00:00 | Zigatola | 133 | 08:00 | 126 | 12:00
Kurigram | 126 | 17:00 | 114 | 19:00
Kushtia | 133 | 09:00 | 123 | 19:00
Laksam | 124 | 08:00 | 114 | 23:00
Lakshmipur | 119 | 12:00 | 106 | 23:00
Lalbag | 131 | 05:00 | 126 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division