## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 29-07-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-07-2025 | during | 29-07-2025 | during | 29-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 0 | 0 | 0 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 149 | 153 | 150 | 150 | 333.5 | 333.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 197 | 198 | 208.13 | 208.13 | 199 | 199 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 332 | 335 | 335 | 335 | 332 | 332 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 7 | 7 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 32 | 44.5 | 53.97 | 53.97 | 53.97 | 53.97 | FGMO
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 31 | 149.36 | 149.36 | 144 | 144 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 17 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 26.2 | 27 | 33 | 33 | 27 | 27 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 14 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 33 | 33 | 52.19 | 52.19 | 33 | 33 | Fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 75 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 33 | 80 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 87 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 16 | 16 | 104 | 104 | 16 | 16 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 82 | 140 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 19 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 18 | 55 | 55 | 35 | 35 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 142 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 5939.724 | 1978.2 | 1930.5 | 4522.15 | 4490.15 | 3819.97 | 3787.97
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 7 | 0 | 7 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 40 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 220 | 220 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 221 | 220 | 213 | 213 | 213 | 213 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 60 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 75 | 80 | 80 | 80 | 80 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 66 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 36 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 3 | 13 | 2 | 25 | 2 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 52 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.36 | 0 | 2.58 | 0 | 2.58 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 30 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 45 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1135 | 1003 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 9 | 8 | 34 | 34 | 34 | 34 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 712 | 738 | 770 | 770 | 770 | 770 | -
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 2373.36 | 2639 | 3836.3 | 3849.72 | 3836.3 | 3849.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 199 | 195 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 345 | 354 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 325 | 340 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 39 | 39 | 46.7 | 46.7 | 39 | 39 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 49 | 51 | 55 | 55 | 52 | 52 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 80 | 71 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 40 | 80 | 150 | 150 | 140 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 31 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 70 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 145 | 154 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 38 | 44 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 70 | 80 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 14 | 42 | 113 | 113 | 36 | 36 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 68 | 114 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 8 | 0 | 30 | 0 | 30 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1549 | 1761 | 2409.56 | 2379.56 | 2178.36 | 2148.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-07-2025 | during | 29-07-2025 | during | 29-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 47 | 48 | 157.5 | 157.5 | 72 | 72 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 85 | 170 | 200 | 200 | 170.2 | 170.2 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 75 | 93 | 115 | 115 | 100 | 100 | Engine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 28.54 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 35 | 35 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 265.54 | 340 | 595.9 | 549 | 436.1 | 389.2
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 130 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 81 | 83 | 83 | 79 | 79 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 8 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | -
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 367 | 361 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 310 | 300 | 320 | 320 | 320 | 320 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1020 | 988 | 1024 | 1024 | 959 | 959
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 876 | 872 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 220 | 208 | 410 | 410 | 229 | 229 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 34 | 105 | 105 | 53 | 53 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 4.22 | 0 | 25 | 0 | 25 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1071 | 1167 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2209.22 | 2319 | 3577.2 | 3552.2 | 3254.2 | 3229.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 300 | 304 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 117 | 118 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1030 | 1230 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 171 | 274 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.05 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1838.05 | 2146 | 2162 | 2161 | 2152 | 2151
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 32 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 140 | 200 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 170 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 130 | 170 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 396 | 345 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 27 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 96 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.37 | 0 | 3.15 | 0 | 3.15 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1260 | 1446 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 21.24 | 0 | 40 | 0 | 40 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 12 | 0 | 95 | 0 | 95 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 2101.61 | 2486 | 3164.02 | 3025.87 | 3122.64 | 2984.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 47 | 47 | 47 | 47 | 47 | 47 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 26 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 0.5 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 50 | 114 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 12 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 176 | 0 | 177.33 | 0 | 177.33 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 311.5 | 274 | 517.93 | 309 | 517.93 | 309
System Total |  |  |  |  | 28565.2 | 27045.875 | 13646.48 | 14883.5 | 21809.06 | 21340.5 | 20276.5 | 19807.94
Forecast Scenario (29-07-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14900 |  | 0 |  | 14900
|  |  |  | 1:00 | 14600 |  | 0 |  | 14600
|  |  |  | 2:00 | 14300 |  | 0 |  | 14300
|  |  |  | 3:00 | 13700 |  | 0 |  | 13700
|  |  |  | 4:00 | 13550 |  | 0 |  | 13550
|  |  |  | 5:00 | 13400 |  | 0 |  | 13400
|  |  |  | 6:00 | 12700 |  | 0 |  | 12700
|  |  |  | 7:00 | 12750 |  | 0 |  | 12750
|  |  |  | 8:00 | 12730 |  | 0 |  | 12730
|  |  |  | 9:00 | 13000 |  | 0 |  | 13000
|  |  |  | 10:00 | 13200 |  | 0 |  | 13200
|  |  |  | 11:00 | 13400 |  | 0 |  | 13400
|  |  |  | 12:00 | 13780 |  | 0 |  | 13780
|  |  |  | 13:00 | 14070 |  | 0 |  | 14070
|  |  |  | 14:00 | 13880 |  | 0 |  | 13880
|  |  |  | 15:00 | 13730 |  | 0 |  | 13730
|  |  |  | 16:00 | 13490 |  | 0 |  | 13490
|  |  |  | 17:00 | 13300 |  | 0 |  | 13300
|  |  |  | 18:00 | 12800 |  | 0 |  | 12800
|  |  |  | 18:30 | 13300 |  | 0 |  | 13300
|  |  |  | 19:00 | 14080 |  | 0 |  | 14080
|  |  |  | 19:30 | 14940 |  | 0 |  | 14940
|  |  |  | 20:00 | 15040 |  | 0 |  | 15040
|  |  |  | 21:00 | 15270 |  | 0 |  | 15270
|  |  |  | 22:00 | 15230 |  | 0 |  | 15230
|  |  |  | 23:00 | 15220 |  | 0 |  | 15220
Probable Maximum Temperature: |  |  | 31.10°C
Probable Maximum Demand at Day Peak: |  |  | 13780.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15270.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15270.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 332.12 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:40 hrs on 29-07-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 28-07-2025 | [28 empty] | Date: | 28-07-2025 | [28 empty] | Date: | 28-07-2025 | [28 empty] | Date: | 28-07-2025 | [28 empty] | Date: | 28-07-2025 | [11 empty] | Date: | 28-07-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [11 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 721 | 50 | 17 | 108 | 32 | 95 | 15 | 29 | 125 | 0 | 450 | 269 | 0 | 0 | 35 | 0 | 197 | 0 | 0 | 125 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 33 | 24 | 0 | 25 | 25 | 0 | 221 | 0 | 30 | 698 | 0 | 0 | 19 | 0 | 0 | 218 | 0 | 0 | 0 | 1100 | 0 | 51 | 140 | 40 | 0 | 355 | 340 | 47 | 185 | 39 | 114 | 30 | 180 | 21 | 20 | 97 | 48 | 52.2 | 0 | 29 | 0 | 310 | 394 | 0 | 60 | 153 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 94 | 181 | 48 | 0 | 0 | 12 | 8013.4 | 852 | 147 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1206 | 34 | 1418.23 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 27 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 340 | 0 | 0 | 0 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 120 | 220 | 0 | 349 | 1109 | 0 | 6847.23 | 14860.63 | 104.38
01:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505 | 45 | 17 | 145 | 16 | 45 | 15 | 55 | 143 | 0 | 450 | 152 | 0 | 0 | 35 | 12 | 131 | 0 | 0 | 108 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 33 | 24 | 0 | 12 | 25 | 0 | 220 | 0 | 30 | 708 | 0 | 0 | 19 | 0 | 0 | 219 | 0 | 0 | 0 | 1121 | 0 | 51 | 142 | 45 | 0 | 320 | 340 | 48 | 193 | 39 | 106 | 70 | 181 | 18 | 20 | 97 | 46 | 52.2 | 0 | 29 | 0 | 310 | 322 | 0 | 60 | 130 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 93 | 182 | 49 | 0 | 0 | 9 | 7551 | 854 | 155 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1167 | 34 | 1415.14 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 27 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 346 | 0 | 0 | 0 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 120 | 220 | 0 | 351 | 1110 | 0 | 6827.14 | 14378.14 | 104.41
02:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 45 | 17 | 130 | 0 | 15 | 15 | 55 | 144 | 0 | 450 | 152 | 0 | 0 | 35 | 1 | 131 | 0 | 0 | 90 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 24 | 0 | 12 | 25 | 0 | 220 | 0 | 30 | 724 | 0 | 0 | 19 | 0 | 0 | 218 | 0 | 0 | 0 | 1059 | 0 | 51 | 140 | 45 | 0 | 320 | 340 | 49 | 195 | 39 | 92 | 70 | 180 | 17 | 20 | 97 | 44 | 52.2 | 0 | 29 | 0 | 310 | 322 | 0 | 60 | 132 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 93 | 182 | 49 | 0 | 0 | 11 | 7178 | 855 | 160 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1175 | 0 | 1416.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 354 | 0 | 0 | 0 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 120 | 220 | 0 | 350 | 1110 | 0 | 6741.12 | 13919.12 | 104.44
03:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 45 | 17 | 118 | 0 | 0 | 0 | 55 | 143 | 0 | 450 | 152 | 0 | 0 | 0 | 1 | 134 | 0 | 0 | 70 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 12 | 25 | 0 | 219 | 0 | 32 | 724 | 0 | 0 | 6 | 0 | 0 | 219 | 0 | 0 | 0 | 1053 | 0 | 51 | 110 | 45 | 0 | 320 | 340 | 48 | 196 | 39 | 92 | 70 | 180 | 18 | 20 | 97 | 42 | 52.2 | 0 | 29 | 0 | 310 | 341 | 0 | 60 | 132 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 93 | 125 | 49 | 0 | 0 | 12 | 6957 | 855 | 166 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1168 | 0 | 1413.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 361 | 0 | 0 | 0 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 120 | 220 | 0 | 351 | 1111 | 0 | 6725.69 | 13682.69 | 104.47
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 43 | 17 | 89 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 155 | 0 | 0 | 0 | 6 | 134 | 0 | 0 | 52 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 12 | 25 | 0 | 218 | 0 | 32 | 729 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1052 | 0 | 51 | 30 | 45 | 0 | 320 | 340 | 48 | 199 | 39 | 92 | 70 | 181 | 17 | 20 | 97 | 42 | 25 | 0 | 29 | 0 | 310 | 329 | 0 | 60 | 134 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 93 | 105 | 49 | 0 | 0 | 12 | 6591.8 | 855 | 172 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1088 | 0 | 1416.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 362 | 0 | 0 | 0 | 47 | 90 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 120 | 220 | 0 | 350 | 1110 | 0 | 6578.63 | 13170.43 | 104.5
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 17 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 154 | 0 | 0 | 0 | 182 | 133 | 0 | 0 | 52 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 12 | 25 | 0 | 217 | 0 | 34 | 710 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1031 | 0 | 51 | 0 | 45 | 0 | 320 | 340 | 49 | 193 | 39 | 92 | 70 | 180 | 17 | 20 | 97 | 42 | 25 | 0 | 29 | 0 | 300 | 317 | 0 | 60 | 135 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 83 | 105 | 49 | 0 | 0 | 12 | 6550.8 | 855 | 175 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 0 | 1302.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 350 | 0 | 0 | 0 | 47 | 90 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 120 | 220 | 0 | 351 | 1110 | 0 | 6397.99 | 12948.79 | 104.53
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 17 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 154 | 0 | 0 | 0 | 330 | 75 | 0 | 0 | 52 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 12 | 25 | 0 | 217 | 0 | 34 | 714 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1050 | 0 | 51 | 0 | 45 | 0 | 320 | 340 | 48 | 195 | 39 | 93 | 70 | 181 | 18 | 20 | 97 | 32 | 25 | 3 | 0 | 0 | 300 | 318 | 0 | 60 | 134 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 85 | 85 | 49 | 0 | 0 | 12 | 6600.8 | 855 | 177 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 930 | 0 | 1109.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64 | 130 | 0 | 130 | 0 | 130 | 0 | 352 | 0 | 0.08 | 0 | 47 | 50 | 0 | 34 | 0 | 0 | 0.1 | 0 | 0.02 | 0 | 171 | 120 | 220 | 0 | 309 | 1070 | 0 | 5875.19 | 12475.99 | 104.56
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 153 | 0 | 0 | 0 | 332 | 73 | 0 | 0 | 35 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 12 | 25 | 0 | 219 | 0 | 32 | 758 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 972 | 1 | 51 | 0 | 45 | 0 | 320 | 340 | 45 | 209 | 39 | 105 | 70 | 180 | 17 | 20 | 70 | 30 | 8 | 9 | 0 | 0 | 300 | 356 | 0 | 60 | 143 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 84 | 65 | 48 | 0 | 1.09 | 12 | 6536.59 | 855 | 200 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 11 | 919 | 0 | 1160.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3.23 | 130 | 0 | 130 | 0 | 130 | 0 | 392 | 0 | 0.17 | 0 | 48 | 50 | 2 | 34 | 0 | 0 | 0 | 3 | 0.12 | 0 | 174 | 120 | 220 | 0 | 300 | 1016 | 0 | 5947.55 | 12484.14 | 104.59
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 17 | 30 | 0 | 0 | 0 | 11 | 0 | 0 | 450 | 153 | 0 | 0 | 0 | 332 | 73 | 0 | 6 | 35 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 25 | 0 | 219 | 0 | 7 | 725 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 948 | 3 | 51 | 0 | 45 | 0 | 320 | 340 | 45 | 197 | 39 | 113 | 70 | 181 | 18 | 20 | 70 | 36 | 8 | 12 | 0 | 0 | 300 | 338 | 0 | 60 | 142 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 84 | 65 | 45 | 0 | 2.03 | 12 | 6451.53 | 855 | 210 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 30 | 903 | 0 | 1117.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 5.35 | 130 | 0 | 130 | 0 | 130 | 0 | 360 | 0 | 0.25 | 0 | 47 | 50 | 3 | 34 | 0 | 0 | 0.1 | 18 | 0.22 | 0 | 172 | 120 | 220 | 0 | 301 | 1018 | 0 | 5920.18 | 12371.71 | 104.63
09:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 17 | 30 | 0 | 0 | 0 | 24 | 30 | 0 | 450 | 151 | 0 | 0 | 0 | 330 | 134 | 0 | 10 | 17 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 25 | 0.04 | 219 | 0 | 2 | 758 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 994 | 3 | 51 | 0 | 61 | 0 | 340 | 340 | 46 | 213 | 37 | 90 | 70 | 155 | 17 | 20 | 70 | 34 | 8 | 25 | 0 | 0 | 300 | 337 | 0 | 60 | 147 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 84 | 85 | 45 | 1 | 6.27 | 12 | 6673.31 | 864 | 216 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 24 | 930 | 0 | 1130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 3.49 | 130 | 0 | 130 | 0 | 130 | 0 | 396 | 0 | 0.36 | 0 | 47 | 50 | 5 | 34 | 0 | 0 | 0.7 | 84 | 0.44 | 0 | 175 | 120 | 220 | 0 | 301 | 1009 | 0 | 6068.99 | 12742.3 | 104.67
10:00 | 0 | 17 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 17 | 30 | 0 | 0 | 0 | 52 | 34 | 0 | 450 | 149 | 0 | 0 | 0 | 327 | 192 | 0 | 13 | 17 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 12 | 25 | 0.17 | 219 | 0 | 2 | 761 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1061 | 15 | 51 | 0 | 63 | 0 | 346 | 340 | 47 | 210 | 38 | 68 | 70 | 155 | 15 | 20 | 70 | 34 | 8 | 33 | 0 | 0 | 300 | 387 | 0 | 60 | 148 | 0 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 84 | 85 | 48 | 0 | 15.66 | 12 | 6912.53 | 864 | 216 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6.83 | 941 | 0 | 1132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11.25 | 130 | 0 | 130 | 0 | 130 | 0 | 390 | 0 | 0.85 | 0 | 47 | 50 | 9 | 34 | 0 | 0 | 3.1 | 37 | 0.25 | 0 | 175 | 120 | 220 | 0 | 301 | 1009 | 0 | 6017.28 | 12929.81 | 104.71
11:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 15 | 17 | 30 | 0 | 0 | 0 | 55 | 60 | 14 | 450 | 150 | 0 | 0 | 25 | 331 | 198 | 0 | 27 | 17 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 12 | 25 | 0.57 | 220 | 0 | 2 | 700 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1010 | 9 | 51 | 4 | 73 | 0 | 354 | 340 | 49 | 194 | 39 | 68 | 70 | 153 | 8 | 20 | 70 | 34 | 8 | 35 | 0 | 0 | 310 | 362 | 0 | 60 | 157 | 0 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 83 | 85 | 48 | 1 | 19.24 | 12 | 6918.31 | 876 | 219 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 38.21 | 1078 | 0 | 1222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 12.97 | 140 | 0 | 130 | 0 | 130 | 0 | 383 | 0 | 1.14 | 0 | 47 | 50 | 12 | 34 | 0 | 0 | 3.2 | 40 | 0.02 | 0 | 163 | 120 | 220 | 0 | 299 | 1020 | 0 | 6329.54 | 13247.85 | 104.76
12:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 32 | 17 | 33 | 0 | 0 | 0 | 55 | 82 | 16 | 450 | 149 | 0 | 0 | 35 | 332 | 197 | 0 | 19 | 52 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 12 | 25 | 1.36 | 220 | 0 | 3 | 712 | 0 | 0 | 18 | 0 | 0 | 221 | 0 | 0 | 0 | 1135 | 17 | 51 | 40 | 80 | 0 | 345 | 325 | 49 | 199 | 39 | 68 | 50 | 145 | 14 | 20 | 70 | 38 | 8 | 8 | 0 | 0 | 310 | 367 | 0 | 60 | 156 | 0 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 75 | 85 | 47 | 1 | 28.54 | 12 | 7186.1 | 876 | 220 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4.22 | 1071 | 0 | 1260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 21.24 | 140 | 0 | 140 | 0 | 130 | 0 | 396 | 0 | 2.37 | 0 | 47 | 50 | 12 | 26 | 0 | 0 | 0.5 | 176 | 0.05 | 0 | 171 | 117 | 220 | 0 | 300 | 1030 | 0 | 6460.38 | 13646.48 | 104.81
13:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 46 | 17 | 63 | 0 | 60 | 0 | 55 | 130 | 16 | 450 | 152 | 0 | 0 | 35 | 328 | 196 | 0 | 5 | 52 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 18 | 0 | 12 | 25 | 1.76 | 221 | 0 | 9 | 706 | 0 | 0 | 19 | 0 | 0 | 221 | 0 | 0 | 0 | 1130 | 5 | 51 | 87 | 107 | 0 | 345 | 340 | 51 | 192 | 38 | 72 | 50 | 139 | 17 | 19 | 70 | 36 | 8 | 9 | 14 | 0 | 310 | 348 | 0 | 60 | 149 | 8 | 0 | 78 | 30 | 0 | 18 | 0 | 17 | 73 | 85 | 47 | 2 | 4.4 | 12 | 7325.36 | 885 | 219 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7.94 | 1064 | 0 | 1261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 31.48 | 140 | 0 | 140 | 0 | 130 | 0 | 340 | 0 | 3.4 | 0 | 46 | 50 | 9 | 34 | 0 | 0 | 0.2 | 61 | 0.12 | 0 | 168 | 118 | 220 | 0 | 300 | 1100 | 0 | 6397.14 | 13722.5 | 104.86
14:00 | 0 | 70 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 17 | 63 | 0 | 30 | 0 | 55 | 147 | 16 | 450 | 150 | 0 | 0 | 35 | 335 | 137 | 0 | 11 | 52 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 12 | 25 | 1.38 | 221 | 0 | 2 | 715 | 0 | 0 | 19 | 0 | 0 | 221 | 0 | 0 | 0 | 1151 | 2 | 51 | 122 | 108 | 0 | 300 | 285 | 49 | 199 | 38 | 97 | 50 | 158 | 18 | 19 | 44 | 48 | 8 | 11 | 32 | 0 | 310 | 335 | 0 | 60 | 136 | 8 | 0 | 78 | 30 | 0 | 18 | 0 | 17 | 66 | 85 | 47 | 1 | 7.04 | 12 | 6931.62 | 886 | 218 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 10 | 1075 | 0 | 1265.78 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 20 | 0 | 30.17 | 140 | 0 | 140 | 0 | 130 | 0 | 343 | 0 | 1.4 | 0 | 48 | 50 | 21 | 34 | 0 | 0 | 5.5 | 61 | 0.05 | 0 | 170 | 118 | 220 | 0 | 301 | 1101 | 0 | 6466.9 | 13398.52 | 104.91
15:00 | 0 | 70 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 47.5 | 17 | 50 | 31 | 30 | 0 | 55 | 153 | 0 | 450 | 151 | 0 | 0 | 30 | 335 | 135 | 0 | 8 | 52 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 48 | 0 | 12 | 25 | 1.1 | 221 | 0 | 3 | 715 | 0 | 0 | 30 | 0 | 0 | 221 | 0 | 0 | 0 | 1105 | 0 | 51 | 80 | 108 | 0 | 354 | 280 | 48 | 186 | 38 | 68 | 50 | 161 | 17 | 11 | 42 | 58 | 8 | 15 | 32 | 0 | 310 | 315 | 0 | 60 | 137 | 8 | 0 | 77 | 30 | 0 | 18 | 0 | 17 | 65 | 105 | 48 | 1 | 8.75 | 12 | 6951.55 | 886 | 218 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3.06 | 1090 | 0 | 1262.6 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 30 | 0 | 7.95 | 140 | 0 | 140 | 0 | 130 | 0 | 327 | 0 | 0.81 | 0 | 48 | 50 | 4 | 34 | 0 | 0 | 4.3 | 68 | 0.04 | 0 | 164 | 118 | 220 | 0 | 301 | 1105 | 0 | 6429.76 | 13381.31 | 104.96
16:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 38.4 | 17 | 50 | 31 | 15 | 0 | 55 | 54 | 0 | 450 | 151 | 0 | 0 | 0 | 335 | 199 | 0 | 3 | 34 | 26.2 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 60 | 0 | 12 | 25 | 0.69 | 218 | 0 | 7 | 702 | 0 | 0 | 39 | 0 | 0 | 221 | 0 | 0 | 0 | 1050 | 0 | 51 | 12 | 108 | 0 | 354 | 340 | 49 | 191 | 38 | 32 | 50 | 144 | 26 | 20 | 30 | 54 | 8 | 15 | 31 | 0 | 310 | 319 | 0 | 60 | 131 | 7 | 0 | 77 | 30 | 0 | 18 | 0 | 17 | 65 | 105 | 48 | 1 | 8.79 | 12 | 7013.08 | 886 | 217 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9.57 | 1031 | 0 | 1225.17 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 35 | 0 | 15.74 | 140 | 0 | 140 | 0 | 130 | 0 | 332 | 0 | 1.4 | 0 | 47 | 50 | 7 | 48 | 0 | 0 | 3.5 | 20 | 0.06 | 0 | 168 | 118 | 220 | 0 | 302 | 1050 | 0 | 6274.44 | 13287.52 | 105.01
17:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.7 | 17 | 50 | 31 | 15 | 0 | 55 | 49 | 0 | 450 | 151 | 0 | 0 | 0 | 333 | 198 | 0 | 4 | 34 | 26.2 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 75 | 0 | 24 | 25 | 0.34 | 218 | 0 | 10 | 714 | 0 | 0 | 39 | 0 | 0 | 221 | 0 | 0 | 0 | 1006 | 0 | 51 | 12 | 108 | 0 | 352 | 340 | 50 | 199 | 38 | 32 | 30 | 147 | 27 | 20 | 32 | 52 | 8 | 10 | 31 | 0 | 310 | 357 | 0 | 60 | 138 | 7 | 0 | 78 | 30 | 0 | 18 | 0 | 17 | 65 | 105 | 48 | 0 | 0.55 | 12 | 6685.79 | 886 | 217 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7.92 | 948 | 0 | 1219.58 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 10 | 0 | 7.13 | 140 | 0 | 140 | 0 | 170 | 0 | 403 | 0 | 0.64 | 0 | 47 | 50 | 4 | 49 | 0 | 0 | 0.9 | 16 | 0.04 | 0 | 171 | 118 | 220 | 0 | 300 | 1040 | 0 | 6243.21 | 12929 | 105.04
18:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.4 | 17 | 65 | 31 | 15 | 0 | 55 | 48 | 0 | 380 | 154 | 0 | 0 | 0 | 332 | 196 | 0 | 1 | 34 | 20.2 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 7 | 0 | 75 | 0 | 36 | 25 | 0.05 | 218 | 0 | 3 | 754 | 0 | 0 | 39 | 0 | 0 | 220 | 0 | 0 | 0 | 1000 | 0 | 51 | 12 | 108 | 0 | 347 | 340 | 50 | 207 | 38 | 32 | 70 | 148 | 29 | 20 | 32 | 52 | 8 | 1 | 31 | 0 | 310 | 347 | 0 | 60 | 137 | 7 | 0 | 79 | 30 | 0 | 18 | 0 | 17 | 83 | 105 | 48 | 0 | 0.16 | 12 | 6710.81 | 873 | 217 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3.44 | 941 | 0 | 1220 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 5 | 0 | 0.99 | 140 | 0 | 140 | 0 | 140 | 0 | 414 | 0 | 0.11 | 0 | 49 | 50 | 1 | 49 | 0 | 0 | 0.3 | 4 | 0.03 | 0 | 174 | 118 | 180 | 0 | 303 | 1000 | 0 | 6100.87 | 12811.68 | 105.05
19:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.2 | 17 | 81 | 31 | 70 | 5 | 55 | 152 | 16 | 420 | 152 | 0 | 0 | 17 | 330 | 198 | 0 | 0 | 142 | 26.2 | 0 | 0 | 0 | 0 | 15 | 35 | 0 | 10 | 66 | 75 | 0 | 36 | 25 | 0 | 218 | 13 | 10 | 756 | 0 | 0 | 40 | 0 | 16 | 220 | 0 | 0 | 0 | 1030 | 0 | 51 | 45 | 108 | 0 | 349 | 340 | 51 | 207 | 38 | 44 | 70 | 156 | 28 | 20 | 72 | 64 | 18 | 0 | 31 | 0 | 310 | 386 | 0 | 60 | 142 | 8 | 0 | 81 | 30 | 0 | 18 | 0 | 17 | 93 | 132 | 48 | 0 | 0 | 12 | 7458.4 | 873 | 209 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1078 | 34 | 1383.55 | 0 | 0 | 0 | 0 | 4 | 0 | 90 | 0 | 0 | 0 | 27 | 0 | 148 | 0 | 170 | 0 | 170 | 0 | 414 | 0 | 0 | 0 | 49 | 113 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 245 | 118 | 220 | 0 | 301 | 1025 | 0 | 6822.55 | 14280.95 | 105.05
19:30 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.2 | 17 | 80 | 31 | 75 | 15 | 55 | 141 | 16 | 450 | 152 | 0 | 0 | 17 | 330 | 198 | 0 | 0 | 142 | 26.2 | 0 | 0 | 0 | 0 | 30 | 52 | 0 | 9 | 66 | 75 | 0 | 36 | 25 | 0 | 218 | 20 | 13 | 723 | 0 | 0 | 40 | 1 | 34 | 220 | 0 | 0 | 0 | 990 | 0 | 51 | 80 | 80 | 0 | 354 | 340 | 51 | 193 | 37 | 114 | 70 | 142 | 28 | 20 | 84 | 42 | 25 | 0 | 31 | 0 | 310 | 357 | 0 | 60 | 136 | 8 | 0 | 81 | 30 | 0 | 18 | 0 | 17 | 93 | 170 | 48 | 0 | 0 | 12 | 7531.4 | 872 | 209 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1163 | 34 | 1438.33 | 0 | 11 | 0 | 0 | 35 | 0 | 96 | 0 | 0 | 0 | 27 | 0 | 185 | 0 | 170 | 0 | 170 | 0 | 343 | 0 | 0 | 0 | 47 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 118 | 220 | 0 | 305 | 1160 | 0 | 7141.33 | 14672.73
20:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.6 | 17 | 80 | 31 | 75 | 15 | 55 | 147 | 16 | 450 | 153 | 0 | 0 | 17 | 335 | 198 | 0 | 0 | 142 | 27 | 0 | 0 | 0 | 0 | 30 | 51 | 0 | 4 | 66 | 75 | 0 | 36 | 25 | 0 | 220 | 43 | 16 | 722 | 0 | 0 | 39 | 2 | 70 | 220 | 0 | 0 | 0 | 970 | 0 | 51 | 80 | 71 | 0 | 355 | 340 | 51 | 193 | 39 | 104 | 70 | 145 | 27 | 20 | 78 | 42 | 25 | 0 | 31 | 0 | 310 | 353 | 0 | 60 | 132 | 8 | 0 | 81 | 30 | 0 | 18 | 0 | 17 | 93 | 170 | 48 | 0 | 0 | 12 | 7550.6 | 872 | 209 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1168 | 34 | 1429.43 | 0 | 39 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 27 | 0 | 193 | 0 | 170 | 0 | 170 | 0 | 340 | 0 | 0 | 0 | 49 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 118 | 220 | 0 | 305 | 1180 | 0 | 7158.43 | 14709.03 | 105.06
21:00 | 0 | 87 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.5 | 18 | 80 | 31 | 75 | 15 | 55 | 140 | 16 | 450 | 153 | 0 | 0 | 17 | 335 | 198 | 0 | 0 | 142 | 27 | 14 | 0 | 0 | 0 | 30 | 52 | 0 | 8 | 66 | 75 | 0 | 36 | 25 | 0 | 220 | 45 | 13 | 738 | 0 | 0 | 40 | 8 | 60 | 220 | 0 | 0 | 0 | 1003 | 0 | 51 | 80 | 71 | 0 | 354 | 340 | 51 | 195 | 39 | 114 | 70 | 154 | 42 | 20 | 80 | 44 | 25 | 0 | 31 | 0 | 300 | 361 | 0 | 60 | 130 | 8 | 0 | 81 | 30 | 0 | 18 | 0 | 17 | 93 | 170 | 48 | 0 | 0 | 12 | 7658.5 | 872 | 208 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1167 | 34 | 1446 | 0 | 32 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 27 | 0 | 200 | 0 | 170 | 0 | 170 | 0 | 345 | 0 | 0 | 0 | 47 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 118 | 220 | 0 | 304 | 1230 | 0 | 7225 | 14883.5 | 105.06
22:00 | 0 | 87 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 75 | 31 | 15 | 0 | 55 | 126 | 16 | 450 | 153 | 0 | 0 | 0 | 335 | 198 | 0 | 0 | 125 | 27 | 14 | 0 | 0 | 0 | 0 | 50 | 0 | 8 | 66 | 75 | 0 | 36 | 25 | 0 | 220 | 15 | 21 | 721 | 0 | 0 | 40 | 8 | 61 | 221 | 0 | 0 | 0 | 1008 | 0 | 51 | 40 | 71 | 0 | 354 | 340 | 51 | 198 | 39 | 111 | 70 | 153 | 46 | 20 | 91 | 44 | 25 | 0 | 31 | 0 | 300 | 367 | 0 | 60 | 132 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 102 | 170 | 48 | 0 | 0 | 12 | 7468 | 856 | 214 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1180 | 34 | 1463 | 0 | 32 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 27 | 0 | 200 | 0 | 170 | 0 | 170 | 0 | 351 | 0 | 0 | 0 | 48 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 118 | 220 | 0 | 304 | 1230 | 0 | 7256 | 14724 | 105.07
23:00 | 0 | 87 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.5 | 35 | 65 | 31 | 15 | 0 | 55 | 118 | 0 | 450 | 153 | 0 | 0 | 0 | 335 | 198 | 0 | 0 | 125 | 21 | 14 | 0 | 0 | 0 | 0 | 51 | 0 | 10 | 51 | 75 | 0 | 36 | 12 | 0 | 220 | 15 | 22 | 737 | 0 | 0 | 40 | 8 | 63 | 221 | 0 | 0 | 0 | 1060 | 0 | 51 | 40 | 71 | 0 | 355 | 335 | 49 | 196 | 39 | 109 | 50 | 162 | 45 | 20 | 91 | 44 | 25 | 0 | 31 | 0 | 300 | 367 | 0 | 60 | 135 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 1 | 102 | 170 | 48 | 0 | 0 | 10 | 7448.5 | 856 | 209 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1193 | 34 | 1468 | 0 | 32 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 27 | 0 | 200 | 0 | 170 | 0 | 170 | 0 | 345 | 0 | 0 | 0 | 48 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 118 | 220 | 0 | 304 | 1180 | 0 | 7211 | 14659.5 | 105.07
Total KWH | 0 | 1017600 | 535680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5875000 | 782640 | 488880 | 1597968 | 304320 | 623258 | 77833 | 1062585 | 2053440 | 134400 | 10325000 | 3665280 | 0 | 0 | 295372 | 6326675 | 4104000 | 0 | 94315 | 1652400 | 542400 | 47880 | 0 | 0 | 0 | 95345 | 344640 | 0 | 299520 | 400076 | 710460 | 0 | 451200 | 586560 | 8301 | 5275402 | 163926 | 396480 | 17687272.73 | 0 | 0 | 489120 | 36734.4 | 337055 | 5199818 | 0 | 0 | 0 | 25265452 | 47790 | 1145080 | 1371636 | 1739636 | 0 | 8414200 | 8086000 | 1173600 | 4860000 | 935640 | 2114880 | 1459480 | 3924000 | 575400 | 445320 | 1757880 | 1023360 | 484805 | 178355 | 492576 | 0 | 7349700 | 8755000 | 0 | 1407840 | 3338345.46 | 159696 | 0 | 1916160 | 718272 | 0 | 432000 | 0 | 407520 | 1990800 | 2889600 | 1089600 | 7750 | 117590 | 284640 | 170448439.59 | 20977454 | 4988160 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 147600 | 25476370 | 235680 | 31117213 | 0 | 146254 | 0 | 0 | 31488 | 0 | 765904 | 0 | 0 | 282970 | 189000 | 153000 | 3652818 | 0 | 3742118 | 0 | 3719464 | 0 | 8877163 | 0 | 15000 | 0 | 1144145 | 1950828 | 86637 | 1708819 | 0 | 0 | 23150.52 | 425280 | 1563 | 0 | 5127000 | 2846000 | 5364830 | 0 | 7549090.91 | 26667636.36 | 0 | 158324635.79 | 328773075.38

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 28-07-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13646.48 | MW | 12:00 Hr. | Energy Generated |  |  | 328.7731 |  | MKWHr.
| Day Peak Demand |  |  | 13646.48 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.57 |  | MKWHr.
| Evening Peak Generation |  |  | 14883.5 | MW | 21:00 Hr. | Energy Demand |  |  | 329.3431 |  | MKWHr.
| Evening Peak Demand |  |  | 14935.5 | MW | 21:00 Hr. | Maximum Temperature |  |  | 30 |  | °C
| Minimum Generation of the Day |  |  | 12371.71 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 945.59 |  | MMCFD
| Maximum Generation of the Day |  |  | 14883.5 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.2558 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 30.8862 | 0 | 10.6264 | 0 | 0 | 0.094315 | 0 | 0 | 41.6069 | Gas | 123.0987 | Gas | 436263209.7986
| Chattogram Zone |  |  | 5.5963 | 42.9527 | 3.6151 | 0 | 5.2754 | 0.056091 | 0 | 0.29952 | 57.7952 | Coal | 108.917 | Coal | 656404519.8084
| Cumilla Zone |  |  | 28.259 | 0 | 10.7212 | 0 | 0 | 0.17836 | 1.0234 | 0 | 40.1818 | HFO | 35.5632 | HFO | 652696939.088
| Mymensingh Zone |  |  | 1.0896 | 0 | 5.5726 | 0 | 0 | 0.12534 | 0 | 0 | 6.7875 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 24.077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.077 | Hydro | 5.2754 | Hydro | 527540.2
| Khulna Zone |  |  | 4.9882 | 25.4764 | 0.23568 | 0 | 0 | 0.1476 | 21.8895 | 0 | 52.7373 | Solar | 1.5893 | Solar | 25660950.6072
| Barishal Zone |  |  | 8.2108 | 39.3437 | 0 | 0 | 0 | 0.001563 | 0 | 0 | 47.5561 | Import | 54.03 | Import | 280812785.01
| Rajshahi Zone |  |  | 19.9916 | 0 | 1.1326 | 0 | 0 | 0.45097 | 31.1172 | 0 | 52.6924 | Wind | 0.29952 | Wind | 4384972.8
| Rangpur Zone |  |  | 0 | 1.1441 | 3.6596 | 0 | 0 | 0.53507 | 0 | 0 | 5.3389
| Total |  |  | 123.0987 | 108.917 | 35.5632 | 0 | 5.2754 | 1.5893 | 54.03 | 0.29952 | 328.7731
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 436263209.7986 |  | Hydro | 527540.2
|  |  |  | Coal | 656404519.8084 |  | Solar | 25660950.6072
|  |  |  | HFO | 652696939.088 |  | Import | 280812785.01
|  |  |  | HSD | 0 |  | Wind | 4384972.8
[5 empty] | Total: | 205,67,50,917 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.9775 | Peak Hr Flow | 872.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 48505036.45 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 31.1172 | Peak Hr Flow | 1446.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 870 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.0234 | Peak Hr Flow | 44.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 988 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 53.118 | Peak Hr Flow | 2362.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5016
|  |  |  | Chattogram |  | 0 |  | 1410
|  |  |  | Cumilla |  | 0 |  | 1366
|  |  |  | Mymensingh |  | 0 |  | 1202
|  |  |  | Sylhet |  | 0 |  | 622
|  |  |  | Khulna |  | 0 |  | 1712
|  |  |  | Barishal |  | 0 |  | 450
|  |  |  | Rajshahi |  | 0 |  | 1531
|  |  |  | Rangpur |  | 50 |  | 1005
|  |  |  | Total |  | 50 |  | 14314
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Bibiana-II 341 MW CCPP (Summit) GT |  |  | 222 | 3 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
|  | 4 | Bibiana-II 341 MW CCPP (Summit) ST |  |  | 119 | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 641 |  |  |  | Total | 707
|  |  |  | Total Unavailable Capacity |  |  |  | 1348
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:24 | Satkhira 132/33kV S/S Transformer-1 (T-1) HT is restored.
|  | 08:26 | Satkhira 132/33kV S/S Transformer-1 (T-1) LT is restored.
|  | 08:34 | Narail 132/33kV S/S TR1 (403-T) HT is restored.
|  | 08:35 | Narail 132/33kV S/S TR1 (403-T) LT is restored.
| 12:00 |  | Day Peak Generation 13644 MW.
| 13:07 |  | JERA 718 MW CCPP conducted load rejection test. | [7 empty] | 370MW generation
interrup.
| 13:14 |  | JERA CCPP GT-12 was synch.
| 13:18 |  | JERA CCPP GT-11 was synch.
| 13:35 |  | JERA CCPP GT-11 was shut down due to gas line leakage.
| 13:41 |  | JERA CCPP GT-12 was shut down due to gas line leakage
| 13:45 | 14:04 | Brahmanbaria 132/33kV S/S 402T LT Tripped showing OC/EF relays. | [7 empty] | 50.0MW load
interrup.
| 16:49 | 19:00 | Rajshahi 132/33kV S/S Station Aux. Transformer-1 HT Forced S/D Due to High temperature
maintenance
| 16:51 | 18:51 | Rajshahi 132/33kV S/S Transformer T-1(405T) LT Forced S/D Due to High temperature
maintenance
| 16:52 | 18:50 | Rajshahi 132/33kV S/S Transformer T-1(405T) HT Forced S/D Due to High temperature
maintenance
| 17:23 | 20:29 | Fatullah 132/33kV S/S 132 kV Hasnabad Scheduled S/D Due to The Line isolator at the
Hasnabad substation is overheating
|  | 17:32 | Hasnabad 132/33kV S/S 132kV Reserve Bus is restored.
| 17:32 | 20:28 | Hasnabad 132/33kV S/S Fatulla (Pre-Brahmongaon) Scheduled S/D Due to Red hot at line
Yellow phase line D/S
| 17:42 | 17:58 | Brahmanbaria 132/33kV S/S 402T LT Tripped showing O/C & E/F Relay relays. | [7 empty] | 20.0MW load
interrup.
|  | 17:56 | Haripur 230/132kV S/S EGCB 412MW is restored.
| 19:24 | 19:42 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Tripped showing Over current pro. | [7 empty] | 70.0MW load
|  |  | trip, Lockout Relay K861 trip, Lockout Relay K862 trip, relays Due to Due to Lohaghara | [7 empty] | interrup.
& Banshkhali 33 kv feeder (O/C & E/F)
| 19:26 |  | Raozan 25 MW PP Synchronized
| 20:22 | 21:40 | Hathazari 230/132/33kV S/S MT-04 LT Forced S/D Due to Red hot maintainance
| 20:22 | 21:40 | Hathazari 230/132/33kV S/S MT-04 HT Forced S/D Due to Red hot maintainance
| 00:36 |  | Raozan 25 MW PP Shutdown
| 04:30 |  | Sathia - Pabna 65MW solar Power plant 132 KV Line-1 has tripped ( Distance Relay R-ph ).
| 06:00 |  | Minimum Generation is 12343 MW
| 06:15 |  | Kodda 132/33kV S/S Tr-3 (426T) LT Scheduled S/D Due to 33 kV LDS maintenance
| 06:17 |  | Kodda 132/33kV S/S Tr-3 (426T) HT Scheduled S/D Due to 33kV LDS maintenance
| 07:15 |  | Beanibazar 132/33kV S/S 132KV Transformer TR-02 HT Forced S/D Due to Incommer 2 DS RED | [7 empty] | 13.0MW load
|  |  | HOT Maintenance. | [7 empty] | interrup.
| 07:15 |  | Beanibazar 132/33kV S/S 132KV Transformer TR-02 LT Forced S/D Due to Incommer 2 DS RED | [7 empty] | 13.0MW load
|  |  | HOT Maintenance. | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 28-07-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10325000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 153 | 3665280 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 77833 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 198 | 4104000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 6326675 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 44.5 | 782640 | FGMO
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 31 | 304320 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 1062585 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 295372 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 27 | 542400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 47880 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 33 | 535680 | Fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 75 | 623258 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 80 | 1597968 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 87 | 1017600 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 134400 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 140 | 2053440 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 94315 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 18 | 488880 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 5875000 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 142 | 1652400 | Engine Problem
Dhaka Area Total |  |  |  |  | 5939.724 | 1930.5 | 41606926
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 36734.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 47790 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 40 | 489120 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5275402 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 5199818 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 60 | 337055 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 75 | 710460 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 400076 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 36 | 451200 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 13 | 396480 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 52 | 344640 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 8301 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 30 | 95345 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 45 | 163926 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 586560 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1003 | 25265452 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 8 | 299520 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 738 | 17687272.73 | -
Chattogram Area Total |  |  |  |  | 4895.72 | 2639 | 57795152.13
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 195 | 4860000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 354 | 8414200 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 340 | 8086000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 39 | 935640 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 51 | 1173600 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 71 | 1739636 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1145080 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 80 | 1371636 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 31 | 492576 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1459480 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 154 | 3924000 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 44 | 1023360 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 25 | 484805 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 445320 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 80 | 1757880 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 42 | 575400 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 114 | 2114880 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 178355 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1761 | 40181848
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 48 | 1089600 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7750 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 170 | 2889600 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 93 | 1990800 | Engine Problem
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 117590 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 284640 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 407520 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 340 | 6787500
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1407840 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3338345.46 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 718272 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1916160 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 432000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 159696 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Plant Shutdown as per schedule HGPI work
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 361 | 8755000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 300 | 7349700 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 988 | 24077013.46
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 872 | 20977454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 208 | 4988160 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 34 | 235680 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 147600 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1167 | 25476370 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2319 | 52737264
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 304 | 7549090.91 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 118 | 2846000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1230 | 26667636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5364830 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 274 | 5127000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1563 | -
Barishal Area Total |  |  |  |  | 2236 | 2146 | 47556120.27
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 146254 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 200 | 3652818 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 170 | 3742118 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 170 | 3719464 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 345 | 8877163 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 189000 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 765904 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 31488 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 15000 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1446 | 31117213 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 153000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 282970 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2486 | 52692392
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 47 | 1144145 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1708819 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 23150.52 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 114 | 1950828 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 86637 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 425280 | -
Rangpur Area Total |  |  |  |  | 950 | 274 | 5338859.52
Eastern Grid Total |  |  |  |  | 16667.715 | 7658.5 | 170448439.59
Western Grid Total |  |  |  |  | 10378.16 | 7225 | 158324635.79
National Grid Total |  |  |  |  | 27045.875 | 14883.5 | 328773075.38
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 28-07-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9615.48 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4647.7 | MW
i) Dhaka area |  |  | 5015.76 |  | MW | i) Khulna area |  |  |  | 1711.6 | MW
ii) Chattogram area |  |  | 1410 |  | MW | ii) Barishal area |  |  |  | 450.5 | MW
iii) Cumilla area |  |  | 1365.72 |  | MW | iii) Rajshahi area |  |  |  | 1530.6 | MW
iv) Mymensingh area |  |  | 1202 |  | MW | iv) Rangpur area |  |  |  | 955 | MW
v) Sylhet area |  |  | 622 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14263.18 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 10 | 23:00 | 67 | Hathazari | 73 | 19:00 | 133 | PHP | 8 | 18:00
2 | AKSML | 128 | 12:00 | 68 | Ishurdi | 84 | 09:00 | 134 | Pabna | 126 | 19:30
3 | Aftabnagar | 52 | 12:00 | 69 | Jaldhaka | 76 | 03:00 | 135 | Palashbari | 102 | 01:00
4 | Agargaon | 132 | 13:00 | 70 | Jamalpur | 134 | 21:00 | 136 | Panchagarh | 60 | 22:00
5 | Agrabad | 136 | 11:00 | 71 | Jashore | 136 | 19:00 | 137 | Patuakhali | 71 | 00:00
6 | Amnura | 40 | 00:00 | 72 | Jhenaidah | 126 | 19:00 | 138 | Payra | 36 | 00:00
7 | Ashuganj | 95 | 00:00 | 73 | Joydebpur | 135 | 12:00 | 139 | Postogola | 60 | 13:00
8 | BSRM | 197 | 18:00 | 74 | Joypurhat | 63 | 00:00 | 140 | Purbachal | 20 | 00:00
9 | Bagerhat | 86 | 00:00 | 75 | Juldah | 18 | 01:00 | 141 | Purbasadipur | 127 | 00:00
10 | Bajitpur | 76 | 23:00 | 76 | KSRM | 46 | 14:00 | 142 | Rahanpur | 34 | 00:00
11 | Bakulia | 90 | 21:00 | 77 | Kabirpur | 241 | 15:00 | 143 | Rahim | 24 | 11:00
12 | Banani | 86.4 | 13:00 | 78 | Kachua | 94 | 01:00 | 144 | Rajbari | 82 | 19:30
13 | Bangabhaban | 17 | 10:00 | 79 | Kallyanpur | 105 | 00:00 | 145 | Rajendrapur | 129 | 19:30
14 | Barapukuria | 66 | 20:00 | 80 | Kalurghat | 38 | 09:00 | 146 | Rajshahi | 130 | 00:00
15 | Barguna | 22 | 00:00 | 81 | Kamrangirchar | 78 | 13:00 | 147 | Rajshahi-230 | 96 | 13:00
16 | Barishal | 111 | 00:00 | 82 | Kaptai | N/A | N/A | 148 | Ramganj | 116 | 23:00
17 | Barishal-230 | 102 | 00:00 | 83 | Kasba | 36 | 19:30 | 149 | Rampur | 38 | 00:00
18 | Baroaulia | 63 | 15:00 | 84 | Kazla | 92 | 01:00 | 150 | Rangamati | 15 | 19:30
19 | Baroirhat | 70 | 19:30 | 85 | Keranigonj | 87 | 19:30 | 151 | Rangpur | 138 | 00:00
20 | Bashundhara | 195 | 12:00 | 86 | Khagrachori | 32 | 19:00 | 152 | Ruppur | 7 | 11:00
21 | BashundharaCement | 7 | 09:00 | 87 | Khulna | 68 | 21:00 | 153 | SSM | 2 | 00:00
22 | Beanibazar | 78 | 21:00 | 88 | Khulshi | 185 | 15:00 | 154 | Saidpur | 108 | 19:30
23 | Benapole | 63 | 21:00 | 89 | Kishoreganj | 136 | 00:00 | 155 | Satkhira | 129 | 00:00
24 | Bhaluka | 148 | 00:00 | 90 | Kodda | 301 | 11:00 | 156 | Satmasjid | 98 | 12:00
25 | Bhandaria | 56 | 00:00 | 91 | Kulaura | 52 | 23:00 | 157 | Savar | 229 | 16:00
26 | Bhangura | 37 | 20:00 | 92 | Kurigram | 60 | 03:00 | 158 | SevenRings | 15.46 | 23:00
27 | Bheramara(GK) | 68 | 19:30 | 93 | Kushtia | 152 | 19:00 | 159 | ShahCement | 30 | 22:00
28 | Bhulta | 229 | 23:00 | 94 | Laksam | 33 | 00:00 | 160 | Shahjadpur | 88 | 20:00
29 | Bog-Sherpur | 68 | 00:00 | 95 | Lakshmipur | 34.5 | 00:00 | 161 | Shahjibazar | 131 | 23:00
30 | Bogura | 170 | 00:00 | 96 | Lalbag | 56 | 13:00 | 162 | Shahmirpur | 59 | 00:00
31 | Borhanuddin | 93 | 00:00 | 97 | Lalmonirhat | 56 | 00:00 | 163 | Shariatpur | 93 | 00:00
32 | Brahmanbaria | 132 | 01:00 | 98 | MI_Cement | 13.4 | 23:00 | 164 | Sherpur | 150 | 00:00
33 | Cantonment | 141 | 13:00 | 99 | Madanganj | 37 | 19:30 | 165 | Shikalbaha | 15 | 00:00
34 | Chandina | 37.21 | 00:00 | 100 | Madaripur | 112 | 23:00 | 166 | Shitalakhya | 82.1 | 12:00
35 | Chandpur | 86 | 00:00 | 101 | Madartek | 90 | 00:00 | 167 | Sholosohor | 43 | 19:00
36 | Chandraghona | 33 | 19:30 | 102 | Madunaghat | 56 | 19:30 | 168 | Shyampur | 150 | 03:00
37 | Chapai | 75 | 12:00 | 103 | Magura | 64 | 19:30 | 169 | Siddhirganj | 123 | 11:00
38 | Charsaidpur | 41 | 01:00 | 104 | Mahasthangarh | 84 | 00:00 | 170 | Sirajganj | 110 | 21:00
39 | Chauddagram | 69 | 22:00 | 105 | Maijdee | 17 | 00:00 | 171 | Sonargaon | 102 | 00:00
40 | Chhatak | 37 | 19:00 | 106 | Manikganj | 124 | 20:00 | 172 | Sreemongol | 81 | 19:00
41 | Chowmuhani | 176 | 19:30 | 107 | Maniknagar | 84 | 13:00 | 173 | Sreepur | 102 | 12:00
42 | Chuadanga | 113 | 00:00 | 108 | Matarbari | 49 | 22:00 | 174 | Srinagar | 48.85 | 00:00
43 | Coxsbazar | 128 | 19:00 | 109 | Matuail | 60 | 12:00 | 175 | Sunamganj | 58 | 21:00
44 | Cumilla(N) | 136 | 22:00 | 110 | Millgate | 112 | 15:00 | 176 | Sylhet | 49 | 00:00
45 | Cumilla(S) | 154 | 19:00 | 111 | Mirpur | 126 | 13:00 | 177 | Sylhet-132 | 128 | 15:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 11 | 21:00 | 178 | TK | 31 | 22:00
47 | Daudkandi | 142 | 19:00 | 113 | Mirzapur | 45 | 20:00 | 179 | Tangail | 176 | 20:00
48 | Dhaka | 76 | 13:00 | 114 | Mithapukur | 68 | 19:30 | 180 | Taraganj | 22 | 00:00
49 | Dhamrai | 118 | 13:00 | 115 | Modern | N/A | N/A | 181 | Thakurgaon | 107 | 23:00
50 | Dhanmondi | 139.8 | 14:00 | 116 | Mogbazar | 154.5 | 12:00 | 182 | Tongi | 110 | 10:00
51 | Dohazari | 98 | 19:00 | 117 | Mongla | 32 | 06:00 | 183 | Ullahpara | 39 | 19:30
52 | Faridpur | 160 | 20:00 | 118 | Motijheel | 43 | 13:00 | 184 | Ullon | 42 | 00:00
53 | Fatullah | 97 | 10:00 | 119 | Muktagacha | 37 | 00:00 | 185 | Uttara | 84 | 11:00
54 | Fenchuganj | 44 | 23:00 | 120 | Munshiganj | 122 | 00:00 | 186 | UttaraNew | 58 | 13:00
55 | Feni | 103 | 00:00 | 121 | Muradnagar | 41 | 00:00 | 187 | Zigatola | 70 | 00:00
56 | GPH | 85 | 06:00 | 122 | Mymensingh | 203 | 00:00
57 | Ghatail | 80 | 22:00 | 123 | Naogaon | 137 | 00:00
58 | Ghorashal | 14 | 18:30 | 124 | Narail | 58 | 00:00
59 | Ghorashal-230 | 83 | 22:00 | 125 | Narinda | 78 | 13:00
60 | Goalpara | 39 | 00:00 | 126 | Narshingdi | 176 | 23:00
61 | Gollamari | 82 | 12:00 | 127 | Natore | 156 | 00:00
62 | Gopalganj | 114 | 00:00 | 128 | Nawabganj | 57.8 | 00:00
63 | Gulshan | 72 | 12:00 | 129 | Netrakona | 137 | 00:00
64 | Halishahar | 69.5 | 10:00 | 130 | New | 83.7 | 11:00
65 | HaripurSBU | 144 | 02:00 | 131 | Niamatpur | 73 | 00:00
66 | Hasnabad | 80 | 00:00 | 132 | Noapara | 43 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 28-07-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14860.63 | 134 |  | 15000.66
1:00 | 14378.14 | 127 |  | 14511.14
2:00 | 13919.12 | 102 |  | 14026.12
3:00 | 13682.69 | 0 |  | 13682.69
4:00 | 13170.43 | 0 |  | 13170.43
5:00 | 12948.79 | 0 |  | 12948.79
6:00 | 12475.99 | 0 |  | 12475.99
7:00 | 12484.14 | 0 |  | 12484.14
8:00 | 12371.71 | 0 |  | 12371.71
9:00 | 12742.3 | 0 |  | 12742.3
10:00 | 12929.81 | 0 |  | 12929.81
11:00 | 13247.85 | 0 |  | 13247.85
12:00 | 13646.48 | 0 |  | 13646.48
13:00 | 13722.5 | 0 |  | 13722.5
14:00 | 13398.52 | 0 |  | 13398.52
15:00 | 13381.31 | 0 |  | 13381.31
16:00 | 13287.52 | 0 |  | 13287.52
17:00 | 12929 | 0 |  | 12929
18:00 | 12811.68 | 0 |  | 12811.68
19:00 | 14280.95 | 43 |  | 14325.95
19:30 | 14672.73 | 37 |  | 14711.73
20:00 | 14709.03 | 59 |  | 14771.03
21:00 | 14883.5 | 50 |  | 14935.5
22:00 | 14724 | 30 |  | 14755
23:00 | 14659.5 | 25 |  | 14685.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 28-07-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8013.4 | 6847.23 | 14860.63 | DAILY GENERATION CURVE
00:30 | 7782.2 | 6837.185 | 14619.385
01:00 | 7551 | 6827.14 | 14378.14 | 28-07-2025
01:30 | 7364.5 | 6784.13 | 14148.63
02:00 | 7178 | 6741.12 | 13919.12
02:30 | 7067.5 | 6733.405 | 13800.905
03:00 | 6957 | 6725.69 | 13682.69
03:30 | 6774.4 | 6652.16 | 13426.56
04:00 | 6591.8 | 6578.63 | 13170.43
04:30 | 6571.3 | 6488.31 | 13059.61
05:00 | 6550.8 | 6397.99 | 12948.79
05:30 | 6575.8 | 6136.59 | 12712.39
06:00 | 6600.8 | 5875.19 | 12475.99
06:30 | 6568.695 | 5911.37 | 12480.065
07:00 | 6536.59 | 5947.55 | 12484.14
07:30 | 6494.06 | 5933.865 | 12427.925
08:00 | 6451.53 | 5920.18 | 12371.71
08:30 | 6562.42 | 5994.585 | 12557.005
09:00 | 6673.31 | 6068.99 | 12742.3
09:30 | 6792.92 | 6043.135 | 12836.055
10:00 | 6912.53 | 6017.28 | 12929.81
10:30 | 6915.42 | 6173.41 | 13088.83
11:00 | 6918.31 | 6329.54 | 13247.85
11:30 | 7052.205 | 6394.96 | 13447.165
12:00 | 7186.1 | 6460.38 | 13646.48
12:30 | 7255.73 | 6428.76 | 13684.49
13:00 | 7325.36 | 6397.14 | 13722.5
13:30 | 7128.49 | 6432.02 | 13560.51
14:00 | 6931.62 | 6466.9 | 13398.52
14:30 | 6941.585 | 6448.33 | 13389.915
15:00 | 6951.55 | 6429.76 | 13381.31
15:30 | 6982.315 | 6352.1 | 13334.415
16:00 | 7013.08 | 6274.44 | 13287.52
16:30 | 6849.435 | 6258.825 | 13108.26
17:00 | 6685.79 | 6243.21 | 12929
17:30 | 6698.3 | 6172.04 | 12870.34
18:00 | 6710.81 | 6100.87 | 12811.68
18:30 | 7084.605 | 6461.71 | 13546.315
19:00 | 7458.4 | 6822.55 | 14280.95
19:30 | 7531.4 | 7141.33 | 14672.73
20:00 | 7550.6 | 7158.43 | 14709.03
20:30 | 7604.55 | 7191.715 | 14796.265 |  | Executive Engineer
21:00 | 7658.5 | 7225 | 14883.5 |  | Network Operation Division
21:30 | 7563.25 | 7240.5 | 14803.75
22:00 | 7468 | 7256 | 14724
22:30 | 7458.25 | 7233.5 | 14691.75
23:00 | 7448.5 | 7211 | 14659.5

## En-Curve
QF-LDC-12
Date | 28-07-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3221 | 2114.2 | 852 | 38 | 48 | 1418.23 | 221 | 4782 | 0 | 423 | 1713.2 | 0 | 0 | 30 | 134 | DAILY ENERGY CURVE
00:30 | 3172.5 | 1937.5 | 853 | 38 | 47 | 1416.685 | 220.5 | 4781 | 0 | 406.5 | 1714.2 | 0 | 0 | 32.5 | 130.5 | 28-07-2025
01:00 | 3124 | 1760.8 | 854 | 38 | 46 | 1415.14 | 220 | 4780 | 0 | 390 | 1715.2 | 0 | 0 | 35 | 127
01:30 | 3125.5 | 1708.3 | 854.5 | 38 | 45 | 1415.63 | 220 | 4761.5 | 0 | 275 | 1668.2 | 0 | 0 | 37 | 114.5 | Energy Generated | 328.7731 |  | MKWHr
02:00 | 3127 | 1655.8 | 855 | 38 | 44 | 1416.12 | 220 | 4743 | 0 | 160 | 1621.2 | 0 | 0 | 39 | 102 | Energy not Served | 0.57 |  | MKWHr
02:30 | 3145.5 | 1655.8 | 855 | 38 | 43 | 1414.905 | 219.5 | 4727 | 0 | 138 | 1533.2 | 0 | 0 | 31 | 51 | Total Energy Requirement | 329.3431 |  | MKWHr
03:00 | 3164 | 1655.8 | 855 | 38 | 42 | 1413.69 | 219 | 4711 | 0 | 116 | 1445.2 | 0 | 0 | 23 | 0
03:30 | 3165.5 | 1658.8 | 855 | 38 | 42 | 1415.16 | 218.5 | 4658.5 | 0 | 98.5 | 1248.6 | 0 | 0 | 28 | 0
04:00 | 3167 | 1661.8 | 855 | 38 | 42 | 1416.63 | 218 | 4606 | 0 | 81 | 1052 | 0 | 0 | 33 | 0
04:30 | 3236 | 1663.3 | 855 | 38 | 42 | 1359.81 | 217.5 | 4567 | 0 | 81 | 978 | 0 | 0 | 22 | 0
05:00 | 3305 | 1664.8 | 855 | 38 | 42 | 1302.99 | 217 | 4528 | 0 | 81 | 904 | 0 | 0 | 11 | 0
05:30 | 3353.5 | 1663.8 | 855 | 38 | 37 | 1206.17 | 217 | 4409.5 | 2.92 | 66.5 | 850.5 | 0 | 0 | 12.5 | 0
06:00 | 3402 | 1662.8 | 855 | 38 | 32 | 1109.35 | 217 | 4291 | 5.84 | 52 | 797 | 0 | 0 | 14 | 0
06:30 | 3458 | 1665.65 | 855 | 38 | 31 | 1134.69 | 218 | 4239 | 24.225 | 43.5 | 762.5 | 0 | 0 | 10.5 | 0
07:00 | 3514 | 1668.5 | 855 | 38 | 30 | 1160.03 | 219 | 4187 | 42.61 | 35 | 728 | 0 | 0 | 7 | 0
07:30 | 3487 | 1655.5 | 855 | 38 | 33 | 1138.645 | 219 | 4150.5 | 75.28 | 35 | 737.5 | 0 | 0 | 3.5 | 0
08:00 | 3460 | 1642.5 | 855 | 38 | 36 | 1117.26 | 219 | 4114 | 107.95 | 35 | 747 | 0 | 0 | 0 | 0
08:30 | 3526.5 | 1652.25 | 859.5 | 38 | 35 | 1123.63 | 219 | 4164 | 151.125 | 34.5 | 753.5 | 0 | 0 | 0 | 0
09:00 | 3593 | 1662 | 864 | 38 | 34 | 1130 | 219 | 4214 | 194.3 | 34 | 760 | 0 | 0 | 0 | 0
09:30 | 3646 | 1658.85 | 864 | 38 | 34 | 1131 | 219 | 4254.5 | 180.705 | 40 | 764 | 0 | 0 | 6 | 0
10:00 | 3699 | 1655.7 | 864 | 38 | 34 | 1132 | 219 | 4295 | 167.11 | 46 | 768 | 0 | 0 | 12 | 0
10:30 | 3698 | 1666.6 | 870 | 38 | 34 | 1177 | 219.5 | 4306 | 209.73 | 52.5 | 806.5 | 0 | 0 | 11 | 0
11:00 | 3697 | 1677.5 | 876 | 38 | 34 | 1222 | 220 | 4317 | 252.35 | 59 | 845 | 0 | 0 | 10 | 0
11:30 | 3690 | 1680.35 | 876 | 38 | 36 | 1241 | 220 | 4391.5 | 277.815 | 97 | 890 | 0 | 0 | 9.5 | 0
12:00 | 3683 | 1683.2 | 876 | 38 | 38 | 1260 | 220 | 4466 | 303.28 | 135 | 935 | 0 | 0 | 9 | 0
12:30 | 3646.5 | 1668.7 | 880.5 | 38 | 37 | 1260.5 | 220.5 | 4490 | 237.29 | 161 | 1038.5 | 0 | 0 | 6 | 0
13:00 | 3610 | 1654.2 | 885 | 38 | 36 | 1261 | 221 | 4514 | 171.3 | 187 | 1142 | 0 | 0 | 3 | 0
13:30 | 3532 | 1472.7 | 885.5 | 38 | 42 | 1263.39 | 221 | 4537.5 | 176.92 | 231 | 1159 | 0 | 0 | 1.5 | 0
14:00 | 3454 | 1291.2 | 886 | 38 | 48 | 1265.78 | 221 | 4561 | 182.54 | 275 | 1176 | 0 | 0 | 0 | 0
14:30 | 3453.5 | 1322.7 | 886 | 38 | 53 | 1264.19 | 221 | 4544.5 | 167.275 | 295.5 | 1142.25 | 0 | 0 | 2 | 0
15:00 | 3453 | 1354.2 | 886 | 38 | 58 | 1262.6 | 221 | 4528 | 152.01 | 316 | 1108.5 | 0 | 0 | 4 | 0
15:30 | 3521.5 | 1498.2 | 886 | 38 | 56 | 1243.885 | 219.5 | 4439 | 136.38 | 307.5 | 986.45 | 0 | 0 | 2 | 0
16:00 | 3590 | 1642.2 | 886 | 38 | 54 | 1225.17 | 218 | 4350 | 120.75 | 299 | 864.4 | 0 | 0 | 0 | 0
16:30 | 3656 | 1475.7 | 886 | 38 | 53 | 1222.375 | 218 | 4288 | 91.135 | 296.5 | 883.55 | 0 | 0 | 0 | 0
17:00 | 3722 | 1309.2 | 886 | 38 | 52 | 1219.58 | 218 | 4226 | 61.52 | 294 | 902.7 | 0 | 0 | 0 | 0
17:30 | 3727 | 1249.2 | 879.5 | 38 | 52 | 1219.79 | 218 | 4223.5 | 39.3 | 294 | 926.55 | 0 | 0 | 3.5 | 0
18:00 | 3732 | 1189.2 | 873 | 38 | 52 | 1220 | 218 | 4221 | 17.08 | 294 | 950.4 | 0 | 0 | 7 | 0
18:30 | 3782.5 | 1239.2 | 873 | 38 | 58 | 1301.775 | 218 | 4352.5 | 8.54 | 429.5 | 1236.8 | 0 | 0 | 8.5 | 21.5
19:00 | 3833 | 1289.2 | 873 | 38 | 64 | 1383.55 | 218 | 4484 | 0 | 565 | 1523.2 | 0 | 0 | 10 | 43
19:30 | 3760 | 1288.2 | 872 | 38 | 42 | 1438.33 | 218 | 4661 | 0 | 582 | 1764.2 | 0 | 0 | 9 | 37
20:00 | 3769 | 1280 | 872 | 38 | 42 | 1429.43 | 220 | 4668 | 0 | 610 | 1776.6 | 0 | 0 | 4 | 59
20:30 | 3774 | 1284.5 | 872 | 38 | 43 | 1437.715 | 220 | 4715.5 | 0 | 615 | 1790.55 | 0 | 0 | 6 | 54.5
21:00 | 3779 | 1289 | 872 | 38 | 44 | 1446 | 220 | 4763 | 0 | 620 | 1804.5 | 0 | 0 | 8 | 50
21:30 | 3790 | 1294.5 | 864 | 38 | 44 | 1454.5 | 220 | 4766 | 0 | 611.5 | 1713.25 | 0 | 0 | 8 | 40
22:00 | 3801 | 1300 | 856 | 38 | 44 | 1463 | 220 | 4769 | 0 | 603 | 1622 | 0 | 0 | 8 | 30
22:30 | 3782.5 | 1298 | 856 | 38 | 44 | 1465.5 | 220 | 4783.5 | 0 | 595.5 | 1599.75 | 0 | 0 | 9 | 27.5
23:00 | 3764 | 1296 | 856 | 38 | 44 | 1468 | 220 | 4798 | 0 | 588 | 1577.5 | 0 | 0 | 10 | 25
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 28-07-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 382 | 06:00 | 372 | 15:00 | Payra | 414 | 08:00 | 409 | 22:00
Ashuganj | 402 | 06:00 | 392 | 11:00 | Rahanpur | 397 | 06:00 | 382 | 23:00
Bhulta | 397 | 06:00 | 373 | 11:00 | Rampal | 405 | 08:00 | 393 | 23:00
Bibiana | 384 | 07:00 | 377 | 23:00
BIPTC | 402 | 06:00 | 393 | 00:00
Bogura | 377 | 06:00 | 360 | 00:00
Gopalganj | 397 | 06:00 | 386 | 22:00
Kaliakoir | 373 | 06:00 | 363 | 11:00
Madunaghat | 390 | 06:00 | 386 | 13:00
Meghnaghat | 381 | 06:00 | 372 | 23:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 222 | 06:00 | 215 | 12:00 | Keranigonj | 221 | 06:00 | 213 | 12:00
AKSML | 229 | 21:00 | 222 | 11:00 | Khulna(S) | 232 | 08:00 | 219 | 00:00
Aminbazar | 223 | 03:00 | 216 | 11:00 | Madunaghat | 232 | 19:30 | 227 | 12:00
Ashuganj | 231 | 05:00 | 223 | 11:00 | Madunaghat-400 | 231 | 20:00 | 227 | 11:00
Ashuganj-400 | 231 | 05:00 | 223 | 11:00 | Maniknagar | 218 | 04:00 | 211 | 12:00
Baghabari | 235 | 05:00 | 227 | 00:00 | Meghnaghat | 225 | 05:00 | 220 | 00:00
Barapukuria | 217 | 16:00 | 206 | 23:00 | Meghnaghat-400 | 222 | 06:00 | 216 | 10:00
Barapukuria-230 | 217 | 16:00 | 206 | 23:00 | Mirsorai | 224 | 08:00 | 220 | 00:00
Barishal | 228 | 08:00 | 220 | 23:00 | Rajshahi | 234 | 18:00 | 222 | 00:00
Bheramara | 234 | 06:00 | 224 | 00:00 | Rampal | 232 | 08:00 | 221 | 00:00
Bhulta | 228 | 06:00 | 211 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 225 | 06:00 | 219 | 22:00 | Rampura | 227 | 06:00 | 208 | 11:00
BIPTC | 236 | 06:00 | 225 | 00:00 | Shikalbaha | 230 | 20:00 | 224 | 12:00
Bogura | 233 | 06:00 | 222 | 23:00 | Shyampur | 219 | 06:00 | 213 | 12:00
Bogura-400 | 233 | 06:00 | 223 | 00:00 | Siddhirganj | 219 | 07:00 | 213 | 12:00
Borhanuddin | 233 | 08:00 | 227 | 00:00 | Sirajgonj | 240 | 06:00 | 235 | 00:00
BSRM | 225 | 08:00 | 220 | 00:00 | Sreepur | 229 | 06:00 | 221 | 11:00
Cumilla(N) | 221 | 07:00 | 215 | 11:00 | Tongi | 225 | 04:00 | 213 | 10:00
Faridpur | 226 | 08:00 | 218 | 22:00
Fenchuganj | 225 | 07:00 | 219 | 22:00
Ghorashal | 232 | 01:00 | 222 | 13:00
Ghorashal-230 | 227 | 06:00 | 212 | 11:00
Gopalganj | 226 | 06:00 | 219 | 22:00
GPH | 227 | 21:00 | 223 | 00:00
Haripur | 219 | 06:00 | 213 | 12:00
Hasnabad | 220 | 06:00 | 213 | 12:00
Hathazari | 228 | 19:30 | 211 | 00:00
Ishurdi | 236 | 06:00 | 227 | 00:00
Jhenaidah | 232 | 08:00 | 220 | 00:00
Kaliakoir | 230 | 06:00 | 220 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 06:00 | 123 | 11:00 | Lalmonirhat | 128 | 17:00 | 120 | 20:00
Agargaon | 131 | 06:00 | 125 | 11:00 | Madanganj | 127 | 01:00 | 123 | 12:00
Agrabad | 131 | 21:00 | 126 | 10:00 | Madaripur | 133 | 10:00 | 128 | 22:00
AKS | 128 | 19:30 | 125 | 10:00 | Madartek | 135 | 05:00 | 122 | 11:00
Aminbazar | 132 | 02:00 | 127 | 08:00 | Madunaghat | 131 | 19:30 | 128 | 01:00
Amnura | 136 | 17:00 | 125 | 22:00 | Magura | 136 | 16:00 | 125 | 00:00
Ashuganj | 140 | 06:00 | 135 | 23:00 | Mahasthangarh | 135 | 17:00 | 125 | 00:00
Bagerhat | 134 | 08:00 | 121 | 00:00 | Maijdee | 119 | 13:00 | 108 | 01:00
Bajitpur | 131 | 05:00 | 125 | 00:00 | Manikganj | 125 | 00:00 | 119 | 12:00
Bakulia | 132 | 19:30 | 128 | 00:00 | Maniknagar | 130 | 06:00 | 124 | 12:00
Banani | 136 | 06:00 | 123 | 11:00 | Matarbari | 123 | 19:30 | 114 | 19:00
Bangabhaban | 129 | 05:00 | 124 | 11:00 | Matuail | 128 | 04:00 | 123 | 12:00
Barapukuria | 133 | 16:00 | 125 | 23:00 | Millgate | 132 | 06:00 | 123 | 10:00
Barguna | 134 | 09:00 | 130 | 00:00 | Mirpur | 130 | 00:00 | 124 | 12:00
Barishal | 132 | 11:00 | 126 | 23:00 | Mirzapur | 129 | 01:00 | 124 | 11:00
Barishal-230 | 132 | 05:00 | 127 | 00:00 | Mithapukur | 127 | 17:00 | 112 | 00:00
Baroaulia | 132 | 19:30 | 128 | 10:00 | MI_Cement | 128 | 03:00 | 124 | 10:00
Baroirhat | 125 | 00:00 | 118 | 02:00 | Modern | 0 | 00:00 | 0 | 00:00
Bashundhara | 136 | 06:00 | 121 | 17:00 | Mogbazar | 137 | 06:00 | 125 | 11:00
BashundharaCement | 127 | 01:00 | 123 | 12:00 | Mongla | 134 | 18:30 | 122 | 00:00
Beanibazar | 125 | 07:00 | 117 | 21:00 | Motijheel | 130 | 06:00 | 124 | 11:00
Benapole | 131 | 07:00 | 119 | 00:00 | Muktagacha | 133 | 01:00 | 128 | 13:00
Bhaluka | 129 | 07:00 | 125 | 00:00 | Munshiganj | 127 | 02:00 | 123 | 10:00
Bhandaria | 128 | 11:00 | 116 | 00:00 | Muradnagar | 124 | 06:00 | 115 | 01:00
Bhangura | 133 | 06:00 | 128 | 00:00 | Mymensingh | 135 | 05:00 | 117 | 00:00
Bheramara | 137 | 06:00 | 131 | 00:00 | Naogaon | 133 | 17:00 | 123 | 00:00
Bheramara(GK) | 137 | 09:00 | 131 | 00:00 | Narail | 135 | 09:00 | 123 | 00:00
Bhulta | 124 | 03:00 | 117 | 12:00 | Narinda | 130 | 06:00 | 124 | 12:00
Bog-Sherpur | 135 | 06:00 | 127 | 00:00 | Narshingdi | 135 | 03:00 | 119 | 12:00
Bogura | 138 | 17:00 | 129 | 00:00 | Natore | 135 | 17:00 | 127 | 00:00
Bogura-230 | 138 | 17:00 | 130 | 00:00 | Nawabganj | 132 | 05:00 | 126 | 11:00
Brahmanbaria | 135 | 07:00 | 128 | 22:00 | Netrakona | 125 | 08:00 | 116 | 00:00
Cantonment | 131 | 05:00 | 124 | 12:00 | New | 132 | 02:00 | 123 | 11:00
Chandina | 126 | 06:00 | 121 | 00:00 | Niamatpur | 135 | 06:00 | 129 | 00:00
Chandpur | 128 | 07:00 | 118 | 00:00 | Noapara | 135 | 17:00 | 124 | 00:00
Chandraghona | 132 | 19:30 | 129 | 12:00 | Pabna | 135 | 06:00 | 128 | 00:00
Chapai | 134 | 17:00 | 128 | 00:00 | Palashbari | 127 | 09:00 | 112 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 128 | 03:00 | 124 | 10:00 | Panchagarh | 133 | 18:30 | 124 | 07:00
Chauddagram | 123 | 08:00 | 116 | 01:00 | Patuakhali | 134 | 07:00 | 131 | 19:30
Chhatak | 125 | 08:00 | 112 | 23:00 | Payra | 136 | 07:00 | 133 | 00:00
Chowmuhani | 119 | 08:00 | 108 | 00:00 | PHP | 122 | 08:00 | 115 | 00:00
Chuadanga | 136 | 17:00 | 124 | 00:00 | Postogola | 131 | 06:00 | 126 | 10:00
Coxsbazar | 124 | 19:30 | 116 | 00:00 | Purbachal | 136 | 05:00 | 123 | 11:00
Cumilla(N) | 126 | 07:00 | 120 | 01:00 | Purbasadipur | 129 | 18:30 | 121 | 08:00
Cumilla(S) | 133 | 06:00 | 119 | 00:00 | Rahanpur | 136 | 06:00 | 131 | 00:00
Daganbhuiyan | 120 | 08:00 | 112 | 00:00 | Rahanpur-400 | 136 | 06:00 | 131 | 00:00
Daudkandi | 122 | 06:00 | 112 | 00:00 | Rahim | 128 | 03:00 | 123 | 12:00
Dhaka | 138 | 10:00 | 124 | 11:00 | Rajbari | 133 | 08:00 | 125 | 04:00
Dhamrai | 130 | 06:00 | 123 | 12:00 | Rajendrapur | 136 | 01:00 | 123 | 00:00
Dhanmondi | 137 | 06:00 | 123 | 11:00 | Rajshahi | 134 | 17:00 | 126 | 00:00
Dohazari | 129 | 21:00 | 123 | 11:00 | Rajshahi-230 | 134 | 07:00 | 127 | 00:00
Faridpur | 134 | 08:00 | 128 | 23:00 | Ramganj | 122 | 13:00 | 111 | 00:00
Fatullah | 129 | 05:00 | 125 | 10:00 | Rampur | 131 | 20:00 | 126 | 10:00
Fenchuganj | 133 | 09:00 | 127 | 23:00 | Rampura | 136 | 06:00 | 122 | 11:00
Feni | 123 | 07:00 | 117 | 00:00 | Rangamati | 131 | 06:00 | 129 | 00:00
Ghatail | 130 | 04:00 | 124 | 14:00 | Rangpur | 130 | 18:30 | 122 | 20:00
Ghorashal | 135 | 01:00 | 127 | 11:00 | Ruppur | 138 | 15:00 | 131 | 00:00
Goalpara | 138 | 17:00 | 128 | 00:00 | Saidpur | 129 | 06:00 | 121 | 20:00
Gollamari | 138 | 07:00 | 129 | 01:00 | Satkhira | 136 | 08:00 | 121 | 00:00
Gopalganj | 135 | 08:00 | 127 | 00:00 | Satmasjid | 131 | 06:00 | 125 | 11:00
Gopalganj-400 | 135 | 06:00 | 131 | 00:00 | Savar | 132 | 03:00 | 124 | 16:00
Gulshan | 136 | 06:00 | 123 | 11:00 | SevenRings | 137 | 06:00 | 127 | 11:00
Halishahar | 133 | 19:30 | 127 | 09:00 | ShahCement | 128 | 03:00 | 124 | 10:00
Haripur | 128 | 05:00 | 123 | 12:00 | Shahjadpur | 137 | 06:00 | 133 | 00:00
HaripurSBU | 128 | 05:00 | 124 | 10:00 | Shahjibazar | 134 | 07:00 | 126 | 23:00
Hasnabad | 131 | 00:00 | 125 | 12:00 | Shahmirpur | 134 | 20:00 | 128 | 09:00
Hathazari | 132 | 19:30 | 127 | 03:00 | Shariatpur | 133 | 08:00 | 125 | 22:00
Ishurdi | 138 | 06:00 | 132 | 00:00 | Sherpur | 136 | 15:00 | 127 | 13:00
Jaldhaka | 128 | 18:30 | 120 | 08:00 | Shikalbaha | 123 | 19:30 | 117 | 11:00
Jamalpur | 138 | 01:00 | 129 | 14:00 | Shikalbaha-230 | 134 | 19:30 | 129 | 09:00
Jashore | 138 | 17:00 | 122 | 00:00 | Shitalakhya | 128 | 03:00 | 124 | 10:00
Jhenaidah | 138 | 09:00 | 122 | 00:00 | Sholosohor | 131 | 19:30 | 128 | 01:00
Jhenaidah-230 | 138 | 09:00 | 129 | 00:00 | Shyampur | 128 | 05:00 | 125 | 12:00
Joydebpur | 134 | 14:00 | 124 | 11:00 | Shyampur-230 | 129 | 06:00 | 125 | 10:00
Joypurhat | 132 | 17:00 | 121 | 00:00 | Siddhirganj | 128 | 05:00 | 124 | 11:00
Juldah | 133 | 19:30 | 128 | 00:00 | Sirajganj | 132 | 07:00 | 126 | 21:00
Kabirpur | 131 | 00:00 | 120 | 11:00 | Sonargaon | 126 | 00:00 | 122 | 10:00
Kachua | 126 | 07:00 | 116 | 01:00 | Sreemongol | 132 | 08:00 | 124 | 23:00
Kaliakoir | 133 | 00:00 | 128 | 11:00 | Sreepur | 134 | 06:00 | 127 | 11:00
Kallyanpur | 131 | 01:00 | 126 | 12:00 | Srinagar | 132 | 06:00 | 126 | 12:00
Kalurghat | 131 | 08:00 | 128 | 12:00 | SSM | 132 | 01:00 | 130 | 00:00
Kamrangirchar | 132 | 05:00 | 125 | 12:00 | Sunamganj | 121 | 08:00 | 110 | 22:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 125 | 07:00 | 118 | 22:00
Kasba | 123 | 06:00 | 115 | 00:00 | Sylhet-132 | 126 | 07:00 | 118 | 23:00
Kazla | 129 | 06:00 | 124 | 11:00 | Tangail | 129 | 04:00 | 121 | 13:00
Keranigonj | 133 | 06:00 | 126 | 12:00 | Taraganj | 129 | 16:00 | 122 | 23:00
Khagrachori | 130 | 06:00 | 128 | 00:00 | Thakurgaon | 132 | 18:30 | 121 | 08:00
Khulna | 136 | 07:00 | 125 | 00:00 | TK | 131 | 19:30 | 127 | 00:00
Khulna(S) | 139 | 08:00 | 128 | 00:00 | Tongi | 134 | 04:00 | 125 | 10:00
Khulshi | 130 | 19:30 | 126 | 09:00 | Ullahpara | 134 | 05:00 | 129 | 00:00
Kishoreganj | 129 | 06:00 | 123 | 00:00 | Ullon | 136 | 06:00 | 123 | 11:00
Kodda | 135 | 00:00 | 119 | 11:00 | Uttara | 131 | 02:00 | 124 | 12:00
KSRM | 131 | 02:00 | 126 | 12:00 | UttaraNew | 131 | 02:00 | 124 | 12:00
Kulaura | 132 | 05:00 | 126 | 22:00 | Zigatola | 132 | 04:00 | 127 | 11:00
Kurigram | 128 | 16:00 | 118 | 08:00
Kushtia | 134 | 09:00 | 126 | 00:00
Laksam | 125 | 08:00 | 115 | 00:00
Lakshmipur | 119 | 14:00 | 108 | 00:00
Lalbag | 132 | 06:00 | 126 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division