## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID BANGLADESH PLC
SYSTEM OPERATION DATA
Month: June 2025
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2025-06-02 |  | 2025-05-01 |  | 2024-06-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 15691.42 | 2025-06-21 | 16603 | 2025-05-10 | 15798 | 2024-06-11 | 16603 | 2025-05-10
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 21:00 |  | 21:00 Hr.
2 | Minimum Generation (MW) | 8827.15 | 2025-06-03 | 7297.96 | 2025-05-30 | 8396 | 2024-06-20 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 16365.8 | 2025-04-24 | 16365.8 | 2025-04-24 | 16067 | 2024-05-23 | 16477 | 2024-04-30
|  |  | 05:00 Hr. |  | 19:30 Hr. |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 14156.82 | 2025-06-24 | 14834 | 2025-05-08 | 14167 | 2024-06-11 | 14594.67 | 2025-04-24
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 15720.68 | 2025-06-21 | 16999.06 | 2025-05-10 | 16700 | 2024-06-30 | 17200 | 2024-04-29
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 14578.408 |  | 14759.5487 |  | 14053.0333 |  | - | -
7 | Average Generation (MW) at Day Peak | 12594.8343 |  | 13259.9958 |  | 12257.2667 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 981 | 2025-06-20 | 941 | 2025-05-13 | 938 | 2024-06-07 | 970 | 2024-07-06
|  |  | 2:00 |  | 1:30 |  | 3:30 |  | 14:30
9 | Maximum Power Import from Tripura, India (MW) | 55 | 2025-06-15 | 62 | 2025-05-22 | 100 | 2024-06-05 | 194 | 12/06/19
|  |  | 21:15 |  | 18:30 |  | 20:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 110 | 2025-06-13 | 380 | 2025-05-27 | 1727 | 2024-06-25 | 4395 | 04/10/2022
|  |  | 21:00 |  | 21:00 |  | 19:30 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 15175.2 | 2025-06-13 | 16023.29 | 2025-05-27 | 13792 | 45468 | 14965 | 2024-05-16
|  |  | 21:00 |  | 21:00 | - | 0.8125 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2025-06-01 | 0 | 2025-05-01 | 0 | 45458 | - | -
|  |  | 21:00 |  | 20:00 |  | 21:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 13631.03 | 2025-06-01 | 11428 | 2025-05-01 | 13723 | 2024-06-15 | - | -
|  |  | 21:00 |  | 20:00 |  | 21:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 39 | 2025-06-20 | 300 | 2025-05-14 | 1808 | 45468 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 11715.34 | 2025-06-20 | 13979.15 | 2025-05-14 | 12757 | 45468 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2025-06-01 | 0 | 2025-05-01 | 0 | 45458 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 12880.09 | 2025-06-01 | 10976.06 | 2025-05-01 | 11757 | 45458 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 14 |  | 24 |  | 22 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 2 |  | 22 |  | 19 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 1336.914 |  | 1203.8725 |  | 2340.8823 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 51.8734 |  | 56.7683 |  | 125.5183 |  | - | -
22 | Net Generation of BPDB (MKWH) | 1285.0406 |  | 1147.1042 |  | 2215.364 |  | - | -
23 | Net Generation of IPP (MKWH) | 3779.248 |  | 4024.1569 |  | 3401.7047 |  | - | -
23b | Net Generation by Generation Companies | 2803.8877 |  | 2948.2899 |  | 2477.9567
24 | Net Generation of REB (MKWH) | 39.5405 |  | 37.7987 |  | 69.9332 |  | - | -
24 | Net Generation of Rental Power Plant (MKWH) | 113.4342 |  | 130.595 |  | 239.9504 |  | - | -
25 | Total Net Generation (MKHWh) (Excluding Import) | 8021.151 |  | 8287.9448 |  | 8404.909 |  | - | -
26 | Energy Generation by Gas (MKWH) | 4276.4107 |  | 4159.3337 |  | 4103.364 |  | - | -
27 | Energy Generation by Diesel (MKWH) | 0.026 |  | 11.7725 |  | 23.2046 |  | - | -
28 | Energy Generation by Furnace Oil (MKWH) | 925.4855 |  | 1104.2647 |  | 1429.8415 |  | - | -
29 | Energy Generation by Hydro (MKWH) | 119.0818 |  | 28.7773 |  | 80.8001 |  | - | -
30 | Energy Generation by Solar (MKWH) | 111.712 |  | 118.4392 |  | 72.0365 |  | - | -
30b | Energy Generation by Wind (MKWH) | 14.0246 |  | 9.2213 |  | 11.147 |  | - | -
31 | Energy Generation by Coal (MKWH) | 2626.2838 |  | 2912.9044 |  | 2809.9404 |  | - | -
32 | Enegry Import from India (MKWH) | 1378.3078 |  | 1553.6413 |  | 645.6117 |  | - | -
33 | Monthly Load Factor (%) | 83.6562 |  | 80.1315 |  | 76.6243 |  | - | -

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: June 2025
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 15691.42 | 2025-06-21 | 21:00 Hr.
Generation Period
| Dhaka | MW | 5347.14
| Chattogram | MW | 1407
| Cumilla | MW | 1424.21
| Mymensingh | MW | 1231
| Sylhet | MW | 638
a) | Total supply in East zone | MW | 10047.35
| Khulna | MW | 1894.8
| Barisal | MW | 464
| Rajshahi | MW | 1550
| Rangpur | MW | 1024
b) | Total supply in West zone | MW | 4932.8
c) | Total supply in both zone ( a+b) | MW | 14980.15
Ref: | 27.21.0000.603.16.087.20.922 | Date: 16/07/2025
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:June 2025
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 310 | 2025-06-08 | 6:00
| b) Ishurdi end | MW | 358 | 2025-06-28 | 12:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 928 | 2025-06-29 | 14:00
| b) Ishurdi end | MW | 138 | 2025-06-08 | 6:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 3.6197
| b) Ishurdi end | MKWH | 113.4327
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 110.0297
| b) Ishurdi end | MKWH | 3.5143
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 400 | 2025-06-11 | 21:00
| b)Serajganj end | MW | 720 | 2025-06-02 | 23:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 300 | 2025-06-03 | 0:00
| b)Sirajganj end | MW | 108 | 2025-06-11 | 22:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end(Sreepur) | MKWH | 267.0746
| b)Sirajganj end | MKWH | 0.568
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end(Sreepur) | MKWH | 0.5623
| b)Sirajganj end | MKWH | 276.272
30 | Transmission loss of EWI /NO-2 | % | 3.32'%
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 2952 | 2025-06-19 | 2:00
|  | MW | 1872
| b) Aminbazar end | AMPS | -
|  | MW | -
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | -
|  | MW | -
| b) Aminbazar end | AMPS | 2920 | 2025-06-19 | 2:00
|  | MW | 1871
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 22182 | 2025-06-09 | N/A
| a) Aminbazar end | MWh | -
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | - | - | N/A
| a) Aminbazar end | MWh | 22175 | 2025-06-09
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MKWH | 772.9
| b) Aminbazar end (ckt-1 ) | MWh | -
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | -
| b) Aminbazar end (ckt-2 ) | MKWH | 779.717
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 0.88%
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: June 2025
| Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bhaluka 132/33kV | Transformer-03 | 2025-06-01 11:36 | 2025-06-01 11:54 | 0.0125 | T | 33kv Beacon feeder not trip. 50/51 | 17 | 5.1 | Power interruption
Dhamrai 132/33kV | Transformer-1 | 2025-06-10 22:14 | 2025-06-10 23:38 | 0.058333 | T | PBS feeder fault O/C,SPS,86 relay | 20 | 28 | Power interruption
Dhamrai 132/33kV | Transformer-2 | 2025-06-10 22:14 | 2025-06-10 23:38 | 0.058333 | T | PBS feeder fault O/C,SPS,86 Relay | 20 | 28 | Power interruption
Dhamrai 132/33kV | Transformer-1 | 2025-06-15 16:23 | 2025-06-15 16:42 | 0.013194 | T | PBS feeder tripped O/C, 86 & SPS relay | 0 | 0 | No interruption
Satmasjid 132/33kV | 132/33 KV Transformer-1 | 2025-06-29 09:47 | 2025-06-29 10:47 | 0.041667 | T | Over Current & Earth Fault. Over Current & Earth Fault Protection Relay. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 01 | 2025-06-07 13:10 | 2025-06-07 13:30 | 0.013889 | T | Rainey weather. P132 | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 02 | 2025-06-07 13:10 | 2025-06-07 13:31 | 0.014583 | T | Rainey weather. P132 | 0 | 0 | No interruption
Aminbazar 400/230/132kV | ATR-01 | 2025-06-28 10:25 | 2025-06-28 18:37 | 0.34167 | E/O | Red Hot Maintenance work | 0 | 0 | No interruption
Bhaluka 132/33kV | Bus Section- 01 | 2025-06-02 23:07 | 2025-06-03 00:29 | 0.056944 | E/O | 33 kV feeder red hot minimize & maintenance (Feeder no 12 & 09) | 60 | 82 | Power interruption
Mirzapur 132/33kV | Transformer-01(E05) | 2025-06-03 23:22 | 2025-06-04 00:16 | 0.0375 | E/O | Red Hot Maintenance | 42 | 37.8 | Power interruption
Mymensingh 132/33kV | Transformer-2 (414T) | 2025-06-19 09:40 | 2025-06-19 12:16 | 0:37 | E/O | Red hot on 33 Y Bus DS | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 03 | 2025-06-03 12:22 | 2025-06-03 12:56 | 0.023611 | E/O | Hot Spot Maintenance Work. | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132/33 kV T-2 | 2025-06-04 15:04 | 2025-06-04 16:31 | 0.060417 | E/O | Hot Spot Maintenance Work. | 40 | 58 | Power interruption
|  |  | Total : | 0.75833 |  | Unserved Energy: |  | 238.9
Dhaka (South) Grid Circle :
Ghorashal 230kV | TARFO-2 | 2025-06-03 23:05 | 2025-06-04 21:37 | 0.93889 | T | Flashing jumper cable of Incommer:-2 Between CT & CB Y phase Siemens | 82 | 1847.7333 | Power interruption
Hasnabad 230/132kV | AUTO TR-2 | 2025-06-22 23:04 | 2025-06-23 18:32 | 0.81111 | T | OLTC PROTECT TRIP for LOR-86T ,LOR86-L No RELAY operated | 0 | 0 | No interruption
Madanganj 132/33kV | GT-1 | 2025-06-01 19:50 | 2025-06-01 20:14 | 0.016667 | T | For 33 kv Mirkadim-1 feeder trip Over current relay | 18 | 7.2 | Power interruption
Madanganj 132/33kV | GT-2 | 2025-06-01 19:50 | 2025-06-02 00:08 | 0.17917 | T | For 33 kv Mirkadim-1 feeder trip Phase inst relay | 18 | 77.4 | Power interruption
Madanganj 132/33kV | GT-2 | 2025-06-02 00:20 | 2025-06-02 18:46 | 0.76806 | T | PBS 33 kv T2 feeder fault Phase inst fault | 0 | 0 | No interruption
Madanganj 132/33kV | GT-1 | 2025-06-15 18:22 | 2025-06-16 14:55 | 0.85625 | T | PBS 33/11 kv feeder fault Over current relay | 8 | 164.4 | Power interruption
Munshiganj 132/33kV | Transformer-2 | 2025-06-09 16:46 | 2025-06-09 17:34 | 0.033333 | T | Palli biddut one phase out Backup protection relay | 52 | 41.6 | Power interruption
Munshiganj 132/33kV | Transformer-1 | 2025-06-09 16:46 | 2025-06-09 17:34 | 0.033333 | T | Backup Backup protection relay | 52 | 41.6 | Power interruption
Nawabganj 132/33kV | TR-2 | 2025-06-03 02:53 | 2025-06-03 02:57 | 0.0027778 | T | Overcurrent | 6.5 | 0.43333 | Power interruption
Nawabganj 132/33kV | TR-2 | 2025-06-10 21:37 | 2025-06-10 21:48 | 0.0076389 | T | Overcurrent protection relay | 0 | 0 | No interruption
Rampura 230/132kV | Auto Transformer - 02 | 2025-06-22 21:43 | 2025-06-23 11:37 | 0.57917 | T | T2-132kV jack BUS Insulator failure. lockout1&2 CB-638B, Siprotec 7UT86 | 0 | 0 | No interruption
Rampura 230/132kV | Auto Transformer - 04 | 2025-06-22 21:43 | 2025-06-22 22:33 | 0.034722 | T | T2-132kV jack BUS Insulator failure. Lockout Relay 1&2 CB-655B , CB-658B (SQA2) | 208 | 173.3333 | Power interruption
Rampura 230/132kV | Auto Transformer - 03 | 2025-06-22 21:43 | 2025-06-22 22:52 | 0.047917 | T | T2-132kV jack BUS Insulator failure. Lockout Relay 1&2 CB-665B, CB-668B | 0 | 0 | No interruption
Siddhirganj 230/132kV | MTR 2 | 2025-06-08 06:55 | 2025-06-08 21:17 | 0.59861 | T | OLTC OSR TRIP OLTC OSR TRIP | 0 | 0 | No interruption
Ghorashal 230kV | TARFO-2 | 2025-06-05 00:56 | 2025-06-05 02:32 | 0.066667 | E/O | Red Hot Maintenance works | 20 | 32 | Power interruption
Munshiganj 132/33kV | Transformer-1 | 2025-06-29 05:40 | 2025-06-29 08:10 | 0.10417 | E/O | 33 KV main bus & jumper connection point Red hot. | 75 | 187.5 | Power interruption
Munshiganj 132/33kV | Transformer-2 | 2025-06-29 05:40 | 2025-06-29 08:16 | 0.10833 | E/O | 33 KV main bus & jumper connection point Red hot. | 0 | 0 | No interruption
Narshingdi 132/33kV | T-1 | 2025-06-01 00:42 | 2025-06-01 02:09 | 0.060417 | E/O | Red hot at R-Phase in 33 KV T-1 Transformer Load side. Shut down has been taken from narsingdi palli biddhut-2 | 40 | 58 | Power interruption
Rampura 230/132kV | 132 kV Busbar-2 | 2025-06-22 22:30 | 2025-06-23 11:25 | 0.53819 | E/O | ART-2 Jack BUS and 132 KV BUS-2 Maintenance work. | 0 | 0 | No interruption
Shitalakhya 132/33kV | 132/33 kV GT-3 | 2025-06-17 10:46 | 2025-06-17 11:34 | 0.033333 | E/O | Gas presure low alarm found | 0 | 0 | No interruption
Shyampur 132/33kV | GT-3 | 2025-06-18 09:28 | 2025-06-18 09:45 | 0.011806 | E/O | Shutdown is given because of the red hot CT in the GT-3. | 0 | 0 | No interruption
Siddhirganj 132/33kV | T-1 | 2025-06-05 19:51 | 2025-06-06 02:59 | 0.29722 | E/O | 33 kv CB Fault DPDC side | 0 | 0 | No interruption
|  |  | Total : | 1900-01-05 03:04 |  | Unserved Energy: |  | 2631.2
Chattogram Grid Circle :
Bakulia 132/33kV | T-3 (422T) | 2025-06-30 09:02 | 2025-06-30 12:11 | 0.13125 | T | Due to 33 kv Feeder Fault Operate by BPDB. Mikro - AN112 | 8 | 25.2 | Power interruption
Coxsbazar 132/33kV | 415T-T2 | 2025-06-06 07:34 | 2025-06-06 08:24 | 0.034722 | T | Kolatoli-1 33kV feeder over current and Earth Fault. Differential Relay | 35 | 29.1667 | Power interruption
Coxsbazar 132/33kV | 415T-T2 | 2025-06-23 07:31 | 2025-06-23 08:17 | 0.031944 | T | PBS UKHIYA 33KV FEEDER FAILED TO TRIP( O/C & E/F) Differential Relay | 40 | 30.6667 | Power interruption
Halishahar 132/33kV | 405T(TR-1) | 2025-06-04 08:13 | 2025-06-04 09:12 | 0.040972 | T | Birds nest Transformer relay | 25 | 24.5833 | Power interruption
Khulshi 132/33kV | 405T (T1) | 2025-06-04 13:04 | 2025-06-04 14:21 | 0.053472 | T | Moisture show within PRD junction box. Lockout | 0 | 0 | No interruption
Khulshi 132/33kV | 405T (T1) | 2025-06-13 13:08 | 2025-06-13 14:22 | 0.051389 | T | Tripped due to PRD 1&2. Trip Relay MVAJM25 (K33) | 0 | 0 | No interruption
Madunaghat 132/33kV | TR-2(517T) | 2025-06-03 06:23 | 2025-06-03 13:07 | 0.28056 | T | OLTC PRD Trip RET-650 | 14 | 94.2667 | Power interruption
Madunaghat 132/33kV | TR-2(517T) | 2025-06-03 14:16 | 2025-06-03 18:13 | 0.16458 | T | OLTC PRD Trip RET-670,REF-615,RET-670 | 0 | 0 | No interruption
Madunaghat 132/33kV | TR-2(517T) | 2025-06-03 18:15 | 2025-06-03 19:07 | 0.036111 | T | OLTC PRD TRIP RET_650 | 0 | 0 | No interruption
Rangamati 132/33kV | Power Transformer TR1 (405T) | 2025-06-19 03:48 | 2025-06-19 12:06 | 0.34583 | T | REF 630 | 0 | 0 | No interruption
Sholosohor 132/33kV | TRAFO-01 | 2025-06-25 05:51 | 2025-06-25 06:14 | 0.015972 | T | 11kV BPDB feeder fault. (11kV sholoshahar 07no feeder) Restricted E/F, Non-Directional IDMT, Standby E/F, 86.2, 86.1 | 29 | 11.1167 | Power interruption
Baroirhat 132/33kV | Bus-B | 2025-06-28 10:10 | 2025-06-28 15:50 | 0.23611 | E/O | Maintenance work | 0 | 0 | No interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2025-06-03 22:53 | 2025-06-04 00:53 | 0.083333 | E/O | Keranihat & Bandarban feeder Redhot maintenance | 51 | 102 | Power interruption
Dohazari 132/33kV | Power Transformer -T-1 | 2025-06-30 20:24 | 2025-06-30 21:39 | 0.052083 | E/O | Patiya 33 KV BUS DS Redhot Maintenance | 26 | 32.5 | Power interruption
GPH 230/33kV | Transformer -2 (D07) | 2025-06-05 15:05 | 2025-06-05 18:49 | 0.15556 | E/O | Emergency Maintenance. | 0 | 0 | No interruption
Hathazari 230/132/33kV | MT-01 | 2025-06-19 15:52 | 2025-06-19 16:56 | 0.044444 | E/O | oil level alarm | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-01(506T) | 2025-06-03 14:35 | 2025-06-03 15:30 | 0.038194 | E/O | 33kv Bus section ds maintenance | 13 | 11.9167 | Power interruption
Kalurghat 132/33kV | TRFO-02(516T) | 2025-06-03 14:37 | 2025-06-03 15:35 | 0.040278 | E/O | 33kv bus section ds maintenance | 13 | 12.5667 | Power interruption
Khagrachori 132/33kV | TR-1 | 2025-06-01 17:02 | 2025-06-02 14:02 | 0.875 | E/O | Burning of 33 kV T-01 incomer ( R phase ) underground cable | 0 | 0 | No interruption
Khagrachori 132/33kV | TR-1 | 2025-06-03 16:43 | 2025-06-03 19:30 | 0.11597 | E/O | Maintenance of T-01 33kV underground Cable. | 0 | 0 | No interruption
Khagrachori 132/33kV | TR-1 | 2025-06-12 10:14 | 2025-06-12 15:51 | 0.23403 | E/O | 33 KV incomer-1 burn cable (R-ph) replacement. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 01:29 |  | Unserved Energy: |  | 373.9833
Cumilla Grid Circle :
Brahmanbaria 132/33kV | 403T | 2025-06-03 03:12 | 2025-06-03 06:38 | 0.14306 | T | Over Current Earth fault OCEF | 16 | 54.9333 | Power interruption
Feni 132/33kV | T-1(405T) | 2025-06-28 03:35 | 2025-06-28 04:12 | 0.025694 | T | 33kV Sultanpur Feeder Fault (R-Phase) O/C, E/F, A,B,C,N | 44 | 27.1333 | Power interruption
Shahjibazar 132/33kV | TR-02 | 2025-06-04 06:05 | 2025-06-04 06:30 | 0.017361 | T | Rain Lockout Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-06-04 11:25 | 2025-06-04 11:40 | 0.010417 | T | Rain WTI Trip ( micon ) , Lockout Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-06-14 08:03 | 2025-06-14 08:35 | 0.022222 | T | PBS BCIC Feeder Trip OC/EF | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-06-14 10:09 | 2025-06-14 10:20 | 0.0076389 | T | Bad Weather Over current Earth Fault Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-06-14 13:14 | 2025-06-14 13:51 | 0.025694 | T | Lockout Relay | 0 | 0 | No interruption
Sylhet 132/33kV | T1 | 2025-06-01 05:20 | 2025-06-01 05:32 | 0.0083333 | T | Ins O/C 51 | 23 | 4.6 | Power interruption
Sylhet 132/33kV | T1 | 2025-06-01 08:17 | 2025-06-01 08:21 | 0.0027778 | T | Ins OC 51 | 13 | 0.86667 | Power interruption
Sylhet 132/33kV | T1 | 2025-06-26 06:52 | 2025-06-26 07:01 | 0.00625 | T | 33 kv Badaghat PBS feeder C phase loop foult. OC | 2 | 0.3 | Power interruption
Brahmanbaria 132/33kV | 402T | 2025-06-06 10:44 | 2025-06-06 11:44 | 0.041667 | E/O | Emergency maint.work | 40 | 40 | Power interruption
Chandpur 132/33kV | 402T | 2025-06-20 12:47 | 2025-06-20 12:47 | 0 | E/O | No load condition | 0 | 0 | No interruption
Chandpur 132/33kV | 200KVA Aux. T-1 | 2025-06-20 12:49 | 2025-06-27 23:30 | 1900-01-06 10:41 | E/O | Emergency maint.work | 0 | 0 | No interruption
Chandpur 132/33kV | 200KVA Aux. T-2 | 2025-06-30 02:00 | 2025-06-30 02:00 | 0 | E/O | Auxiliary load shift | 0 | 0 | No interruption
Chhatak 132/33kV | T-2 | 2025-06-19 16:49 | 2025-06-19 17:27 | 0.026389 | E/O | Transformer-02 DS status cheack. | 0 | 0 | No interruption
Chhatak 132/33kV | T-3 | 2025-06-22 15:03 | 2025-06-22 16:59 | 0.080556 | E/O | Oil Leakage Problem of 132KV T-3 GCB Hydraulic Oil System. | 0 | 0 | No interruption
Chowmuhani 132/33kV | TR2-425T | 2025-06-05 21:02 | 2025-06-05 23:58 | 0.12222 | E/O | 132/33 KV Tr-02 X-former & associate 33 KV BUS R-phase Isulator Nut Red-Hot Maintn. | 40 | 117.3333 | Power interruption
Chowmuhani 132/33kV | TR2-425T | 2025-06-07 21:42 | 2025-06-08 02:16 | 0.19028 | E/O | tr-02 VCB red hot | 30 | 137 | Power interruption
Chowmuhani 132/33kV | TR2-425T | 2025-06-13 09:01 | 2025-06-13 11:45 | 0.11389 | E/O | 33kv Incoming DS to BUSBAR R Phase (red hot) Loop Maintenance. | 30 | 82 | Power interruption
Fenchuganj 230/132/33kV | TR-02 | 2025-06-21 08:16 | 2025-06-21 18:05 | 0.40903 | E/O | LT side Underground Cable Fault | 0 | 0 | No interruption
Kachua 132/33kV | TR-1 | 2025-06-17 15:05 | 2025-06-17 16:37 | 0.063889 | E/O | 33 kv main bus coupler maintenance | 15 | 23 | Power interruption
Kachua 132/33kV | TR-2 | 2025-06-17 15:07 | 2025-06-17 16:31 | 0.058333 | E/O | 33 kv main bus coupler maintenance | 18 | 25.2 | Power interruption
Muradnagar 132/33kV | 132KV Transformar-01 | 2025-06-01 18:50 | 2025-06-01 18:50 | 0 | E/O | Red Hot | 0 | 0 | No interruption
Muradnagar 132/33kV | 132KV Transformar-01 | 2025-06-23 16:00 | 2025-06-23 16:30 | 0.020833 | E/O | due to kite obstruction on 33 kv side | 14 | 7 | Power interruption
Shahjibazar 132/33kV | TR-02 | 2025-06-04 20:17 | 2025-06-05 13:02 | 0.69792 | E/O | HT Bushing oil leakage | 0 | 0 | No interruption
|  |  | Total : | 1900-01-08 12:57 |  | Unserved Energy: |  | 519.3667
Khulna Grid Circle :
Faridpur 132/33kV | Transformer-1 | 2025-06-01 14:15 | 2025-06-01 14:58 | 0.029861 | T | 33kV Modhukhali wz & 33kV Goalondo wz feeder fault. 33kV O/C & 33kV E/F | 63 | 45.15 | Power interruption
Faridpur 132/33kV | Transformer-2 | 2025-06-01 14:15 | 2025-06-01 14:59 | 0.030556 | T | 33kV Modhukhali wz & 33kV Goalondo wz feeder fault 33kV O/C & 33kV E/F | 63 | 46.2 | Power interruption
Gopalganj 132/33kV | T2 | 2025-06-15 12:43 | 2025-06-15 13:03 | 0.013889 | T | Over current instt. by REB-8 Gopalganj pbs Over current instt. | 47 | 15.6667 | Power interruption
Gopalganj 132/33kV | T1 | 2025-06-16 11:07 | 2025-06-16 11:23 | 0.011111 | T | Modumoti feeder fault Restricted Earth Fault | 45 | 12 | Power interruption
Gopalganj 132/33kV | T2 | 2025-06-20 04:15 | 2025-06-20 04:34 | 0.013194 | T | REB-5 trip Siprotec 7sj82 | 50 | 15.8333 | Power interruption
Kasba 132/33kV | TR-1 | 2025-06-10 19:55 | 2025-06-10 20:11 | 0.011111 | T | Kasba-1 PBS OC/EF due to bad weather OC/EF | 10 | 2.6667 | Power interruption
Madaripur 132/33kV | T3-426T | 2025-06-30 16:13 | 2025-06-30 16:53 | 0.027778 | T | E/F (Due to Pbs Takerhat-2 feeder E/F) Over Current Relay | 0 | 0 | No interruption
Mongla 132/33kV | T-1 | 2025-06-08 21:33 | 2025-06-08 22:47 | 0.051389 | T | Sort circuit by bird and Auxiliary tx-02 fault Over current and lockout 1&2 | 22 | 27.1333 | Power interruption
Noapara 132/33kV | T-2 | 2025-06-03 02:20 | 2025-06-03 02:47 | 0.01875 | T | REB-1 33kV FEEDER FAULT SIEMENS 7SJ81 | 0 | 0 | No interruption
Noapara 132/33kV | T-1 | 2025-06-03 02:20 | 2025-06-03 02:47 | 0.01875 | T | REB-1 33kV FEEDER FAULT SIEMENS 7SJ81 | 0.5 | 0.225 | Power interruption
Noapara 132/33kV | T-1 | 2025-06-03 09:59 | 2025-06-03 10:03 | 0.0027778 | T | REB-1 33kV FEEDER FAULT SIEMENS 7SJ81 | 25 | 1.6667 | Power interruption
Noapara 132/33kV | T-2 | 2025-06-03 09:59 | 2025-06-03 10:03 | 0.0027778 | T | REB-1 33kV FEEDER FAULT SIEMENS 7SJ81 | 12.5 | 0.83333 | Power interruption
Noapara 132/33kV | T-1 | 2025-06-11 02:26 | 2025-06-11 02:57 | 0.021528 | T | 33kV REB-1 FEEDER FAULT 7SJ81 SIEMENS | 23 | 11.8833 | Power interruption
Rajbari 132/33kV | Transformer-3 | 2025-06-23 06:27 | 2025-06-23 06:59 | 0.022222 | T | E/F 86.1&86.2 | 17 | 9.0667 | Power interruption
Satkhira 132/33kV | Transformer-2 (T-2) | 2025-06-01 13:13 | 2025-06-01 13:51 | 0.026389 | T | Winding temperature trip. Lock out relay | 64 | 40.5333 | Power interruption
Barishal 230/132kV | T-4 | 2025-06-03 17:50 | 2025-06-03 18:43 | 0.036806 | E/O | T-5 breaker fault | 30 | 26.5 | Power interruption
Gopalganj 132/33kV | T2 | 2025-06-04 07:46 | 2025-06-04 10:13 | 0.10208 | E/O | Hot spot maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | ATR-01 | 2025-06-28 23:34 | 2025-07-02 17:23 | 1900-01-02 17:49 | E/O | OLTC pressure relay Alarm | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2025-06-24 11:21 | 2025-06-24 14:30 | 0.13125 | E/O | Due to Khulna PBS work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-03 07:33 |  | Unserved Energy: |  | 255.3583
HVDC Grid Circle :
Bhangura 132/33kV | Tr-1(403T) | 2025-06-14 17:57 | 2025-06-14 18:30 | 0.022917 | T | O/C and E/F Relay P14D | 15 | 8.25 | Power interruption
Bhangura 132/33kV | Tr-2(413T) | 2025-06-14 17:57 | 2025-06-14 18:32 | 0.024306 | T | O/C and E/F Relay P14D | 0 | 0 | No interruption
Ishurdi 230/132kV | 230/132 kV T-01 | 2025-06-22 05:36 | 2025-06-22 10:07 | 0.18819 | T | bbc | 0 | 0 | No interruption
BIPTC | 20DF21 | 2025-06-10 15:57 | 2025-06-11 11:24 | 0.81042 | T | Tripped by C1 unbalance 60/61 stage-3 instant L2 | 0 | 0 | No interruption
BIPTC | 10CF21 | 2025-06-13 07:38 | 2025-06-13 17:27 | 0.40903 | T | Tripped by impedance 21R | 0 | 0 | No interruption
BIPTC | 10CF15 | 2025-06-13 19:05 | 2025-06-15 12:41 | 1899-12-31 17:36 | T | C1 Unbalance 60/61 CPR04 | 0 | 0 | No interruption
BIPTC | 10CF15 | 2025-06-22 13:07 | 2025-06-22 16:08 | 0.12569 | T | C1 unbalance 60/61 instant L1 Trip | 0 | 0 | No interruption
BIPTC | 10CF25 | 2025-06-05 09:06 | 2025-06-05 12:20 | 0.13472 | E/O | Shutdown is taken for emergency maintenance work. | 0 | 0 | No interruption
BIPTC | 20DF21 | 2025-06-11 08:42 | 2025-06-11 11:24 | 0.1125 | E/O | maintenance | 0 | 0 | No interruption
BIPTC | 10CF21 | 2025-06-13 15:28 | 2025-06-13 17:27 | 0.082639 | E/O | 10CF21 is tripped by impedance 21R | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-2(413T) | 2025-06-01 22:20 | 2025-06-01 23:17 | 0.039583 | E/O | redhot 33kv CB | 18 | 17.1 | Power interruption
Bhangura 132/33kV | Tr-2(413T) | 2025-06-02 07:10 | 2025-06-02 07:57 | 0.032639 | E/O | 33KV feeder Sky wire maintenance(pbs) | 12 | 9.4 | Power interruption
Bhangura 132/33kV | Tr-2(413T) | 2025-06-04 22:57 | 2025-06-04 23:54 | 0.039583 | E/O | Red hot | 0 | 0 | No interruption
Chuadanga 132/33kV | 132kV Tr. T1(416T) | 2025-06-14 20:36 | 2025-06-14 23:04 | 0.10278 | E/O | For red-hot maintenance | 50 | 123.3333 | Power interruption
Ishurdi 132/33kV | 132/33 kV T-2 | 2025-06-29 13:24 | 2025-06-29 13:46 | 0.015278 | E/O | short ckt at AC MCB | 30 | 11 | Power interruption
Ishurdi 132/33kV | 132/33 kV T-1 | 2025-06-29 13:24 | 2025-06-29 13:54 | 0.020833 | E/O | short ckt at AC MCB | 45 | 22.5 | Power interruption
Jashore 132/33kV | Aux (West) | 2025-06-27 10:32 | 2025-06-27 11:16 | 0.030556 | E/O | Y phase fuse change | 0 | 0 | No interruption
Jashore 132/33kV | T-3 | 2025-06-27 10:32 | 2025-06-27 11:16 | 0.030556 | E/O | Emergency maintenance work | 25 | 18.3333 | Power interruption
Kushtia 132/33kV | T-1 | 2025-06-21 21:04 | 2025-06-21 22:56 | 0.077778 | E/O | T-01 R-phase 33kv bushing red hot maintenance. | 0 | 0 | No interruption
Pabna 132/33kV | T-2 | 2025-06-22 15:20 | 2025-06-22 15:53 | 0.022917 | E/O | Red hot maintenance work. | 35 | 19.25 | Power interruption
Shahjadpur 132/33kV | T-2(415T) | 2025-06-10 22:02 | 2025-06-10 22:40 | 0.026389 | E/O | Emergency maintenance work | 24 | 15.2 | Power interruption
|  |  | Total : | 1900-01-03 01:59 |  | Unserved Energy: |  | 244.3667
Bogura Grid Circle:
Barapukuria 230/132/33kV | 230/132 KV T-01, 703T | 2025-06-02 23:49 | 2025-06-03 00:07 | 0.0125 | T | Thunderstorm SIPROTECH 7UT86 | 44 | 13.2 | Power interruption
Barapukuria 230/132/33kV | 132/33 KV T-4, 444T | 2025-06-24 02:39 | 2025-06-24 02:54 | 0.010417 | T | Thunderstorm SIPROTECH 7UT86 | 20 | 5 | Power interruption
Barapukuria 230/132/33kV | 230/132 KV T-01, 703T | 2025-06-26 16:43 | 2025-06-26 20:06 | 0.14097 | T | Mechanical Trip ABB REB500 | 50 | 169.1667 | Power interruption
Bogura 230/132kV | T-01 | 2025-06-20 09:38 | 2025-06-20 15:22 | 0.23889 | T | Auxilary Transformer Brust No Relay show | 0 | 0 | No interruption
Naogaon 132/33kV | T-1 | 2025-06-03 03:44 | 2025-06-03 15:22 | 0.48472 | T | 33KV T-1 (Y-phase) bus PT burst MCGG (O/C, Y-phase & E/F) | 0 | 0 | No interruption
Naogaon 132/33kV | T-2 | 2025-06-03 03:44 | 2025-06-03 05:38 | 0.079167 | T | 33KV T-1 (Y-phase) bus PT burst MCGG ( E/F) | 0 | 0 | No interruption
Naogaon 132/33kV | T-3 | 2025-06-20 16:58 | 2025-06-20 19:51 | 0.12014 | T | Atrai 33KV PBS feeder BKR Y-phase Bus DS loop open. MCGG OC/EF (50). Inst. (t) | 0 | 0 | No interruption
Naogaon 132/33kV | T-3 | 2025-06-22 14:01 | 2025-06-22 14:17 | 0.011111 | T | Atrai 33KV PBS feeder BKR ,CT to BKR Connecting loop flashing and burn out. MCGG, Over current A,B (t) | 0 | 0 | No interruption
Niamatpur 132/33kV | Transformer-1(407T) | 2025-06-03 00:00 | 2025-06-03 00:14 | 0.0097222 | T | Shapahar feeder fault O/C & E/F Relay | 3 | 0.7 | Power interruption
Niamatpur 132/33kV | Transformer-3(426T) | 2025-06-28 00:12 | 2025-06-28 00:44 | 0.022222 | T | Rajshahi 33kv feeder fault OC/EF and 33 kv lockout OPTD | 15 | 8 | Power interruption
Purbasadipur 132/33kV | T-1 Transformer (403T) | 2025-06-21 17:20 | 2025-06-21 17:41 | 0.014583 | T | 33Kv Feeder Fault no | 23 | 8.05 | Power interruption
Saidpur 132/33kV | TR-2 (404T) | 2025-06-03 01:10 | 2025-06-03 01:13 | 0.0020833 | T | Fault for 33kv EPZ Feeder. MCGG | 16 | 0.8 | Power interruption
Sirajganj 132/33kV | T3-(435) | 2025-06-02 23:52 | 2025-06-03 00:47 | 0.038194 | T | 33 kV Economic Zone Feeder fault Over Current Earth Fault | 0 | 0 | No interruption
Sirajganj 132/33kV | T4-(445) | 2025-06-02 23:52 | 2025-06-03 00:48 | 0.038889 | T | 33kV Economic Zone Feeder faulty Overcurrent Relay | 0 | 0 | No interruption
Thakurgaon 132/33kV | T-3(432T) | 2025-06-27 05:02 | 2025-06-27 05:10 | 0.0055556 | T | Pirganj ও Ranisankail 33kV feeder trip by E/F and O/C একই সাথে T-3 incoming O/C এ Trip করে যায়। O/C | 5 | 0.66667 | Power interruption
Barapukuria 230/132/33kV | 132/33 KV T-3, 404T | 2025-06-09 23:02 | 2025-06-10 15:25 | 0.68264 | E/O | TR-3. Mk box cable burning problem.. | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 230/132 KV T-02, 713T | 2025-06-27 06:24 | 2025-06-27 09:45 | 0.13958 | E/O | T-02 aux supply CB Replace. | 70 | 234.5 | Power interruption
Bogura 400/230kV | ATR-02 | 2025-06-21 00:27 | 2025-06-21 11:45 | 0.47083 | E/O | ATR-02 400 kV side CT( B Phase) Problem | 0 | 0 | No interruption
Jaldhaka 132/33kV | 416T-2 | 2025-06-04 08:45 | 2025-06-04 10:30 | 0.072917 | E/O | 33KV Bus Clamp of Jaldhaka NESCO Red Hot | 30 | 52.5 | Power interruption
Jaldhaka 132/33kV | 406T-1 | 2025-06-05 09:11 | 2025-06-05 11:19 | 0.088889 | E/O | ৫০/৭৫ এমভিএ ট্রান্সফরমার-০১ এর ৩৩ কেভি সিটি’র Y-ফেজে তাপমাত্রা বেশি রাইজ করায় (১৬৫ ডিগ্রি সে.) সংরক্ষণ কাজ | 7 | 14.9333 | Power interruption
Kurigram 132/33kV | Transformer T-2 (Tr-413T) | 2025-06-25 11:22 | 2025-06-25 12:09 | 0.032639 | E/O |  | 0 | 0 | No interruption
Mithapukur 132/33kV | BUS SECTION-1 (33KV) | 2025-06-12 11:25 | 2025-06-12 12:17 | 0.036111 | E/O | 33Kv Sundorganj feeder Bus DS Red-hot. | 24 | 20.8 | Power interruption
Mithapukur 132/33kV | BUS SECTION-2 (33KV) | 2025-06-12 12:27 | 2025-06-12 14:23 | 0.080556 | E/O | Due to Request for Red hot maintenance work 33kv Bus DS of Vendabari Feeder. | 24 | 46.4 | Power interruption
Mithapukur 132/33kV | TR-2 (414T) | 2025-06-21 09:15 | 2025-06-21 11:03 | 0.075 | E/O | Red hot maintenance. | 20 | 36 | Power interruption
Naogaon 132/33kV | T-1 | 2025-06-03 06:20 | 2025-06-03 15:21 | 0.37569 | E/O | CB & CT maintenance work. | 0 | 0 | No interruption
Naogaon 132/33kV | T-3 | 2025-06-06 22:18 | 2025-06-06 23:08 | 0.034722 | E/O | Baludanga 33 kv feeder(NESCO) B phase Bus side isolator red hot maintenance which is connected to T-3 33kV bus in Naogaon Grid Substation. | 0 | 0 | No interruption
Naogaon 132/33kV | T-3 | 2025-06-20 18:40 | 2025-06-20 19:49 | 0.047917 | E/O | Atrai 33KV PBS feeder BKR Y-phase Bus DS loop maintenance | 0 | 0 | No interruption
Niamatpur 132/33kV | Transformer-2 (417T) | 2025-06-10 06:58 | 2025-06-10 08:12 | 0.051389 | E/O | PBS 33kV Deluabari Feeder Source DS- R Phase Red hot Maintenance | 0 | 0 | No interruption
Palashbari 132/33kV | TR1-414T | 2025-06-01 17:03 | 2025-06-01 18:22 | 0.054861 | E/O | T-1 33kv bus s/d | 11 | 14.4833 | Power interruption
Palashbari 132/33kV | TR1-414T | 2025-06-11 16:56 | 2025-06-11 17:48 | 0.036111 | E/O | Red hot | 5 | 4.3333 | Power interruption
Panchagarh 132/33kV | T-1(407T) | 2025-06-05 09:20 | 2025-06-05 09:35 | 0.010417 | E/O | 33 kv capacitor bank-02 Bus DS Open due to no working of CB tripping signal | 6 | 1.5 | Power interruption
Saidpur 132/33kV | TR-3 (424T) | 2025-06-14 10:41 | 2025-06-14 11:13 | 0.022222 | E/O | Due to Red hot of 33kv Capacitor Bus DS | 20 | 10.6667 | Power interruption
Sirajganj 132/33kV | T4-(445) | 2025-06-03 15:43 | 2025-06-03 17:15 | 0.063889 | E/O | Emergency Red hot of Riser Conductor of 33 kv Economic Zoon. | 5 | 7.6667 | Power interruption
|  |  | Total : | 1900-01-02 14:32 |  | Unserved Energy: |  | 649.3667
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 1900-01-30 11:46 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: June 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | Gopalganj-1 | 2025-06-04 03:34 | 2025-06-04 09:46 | 0.25833 | T | Tripped | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Kaliakoir-02 | 2025-06-06 13:44 | 2025-06-06 15:34 | 0.076389 | T | Unknown | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Kaliakoir-02 | 2025-06-13 19:27 | 2025-06-13 20:04 | 0.025694 | T | Main 2 Distance R,T trip A/R block | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Kaliakoir-02 | 2025-06-13 20:20 | 2025-06-13 20:41 | 0.014583 | T | Main -2 Distance R,T trip | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Aminbazar -2 | 2025-06-06 13:43 | 2025-06-06 15:32 | 0.075694 | T | Fault. | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Old | 2025-06-14 14:16 | 2025-06-14 14:24 | 0.0055556 | T | Tripped due to fault. Relay shows overcurrent signal. | 80 | 10.6667 | Power interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2025-06-03 02:07 | 2025-06-03 02:38 | 0.021528 | T | Heavy rain and thunderstorm | 0 | 0 | No interruption
Ghatail 132/33kV | Tangail -2 | 2025-06-01 12:30 | 2025-06-01 13:16 | 0.031944 | E/O | Emergency maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Capacitor Bank-2 | 2025-06-19 09:10 | 2025-06-19 12:20 | 0.13194 | E/O | Red hot on 33 Y Bus DS | 0 | 0 | No interruption
Sherpur 132/33kV | UMPL-Sherpur Ckt-01 | 2025-06-03 09:11 | 2025-06-03 10:37 | 0.059722 | E/O | GCB nut bolt hot point maintenance. | 0 | 0 | No interruption
|  |  | Total : | 0.70139 |  | Unserved Energy: |  | 10.6667
Dhaka (South) Grid Circle :
Haripur 230/132kV | Madanganj-1 | 2025-06-02 07:33 | 2025-06-02 08:03 | 0.020833 | T | Tripped | 0 | 0 | No interruption
Haripur 230/132kV | Sonargaon 2 | 2025-06-05 16:05 | 2025-06-06 14:12 | 0.92153 | T | Thunderstorm | 0 | 0 | No interruption
Haripur 230/132kV | Ullon (Maniknagar-2) | 2025-06-10 20:55 | 2025-06-10 21:34 | 0.027083 | T | Tripped | 0 | 0 | No interruption
Rampura 230/132kV | Basundhara-01 | 2025-06-02 17:10 | 2025-06-02 17:24 | 0.0097222 | T | Unknown | 0 | 0 | No interruption
Rampura 230/132kV | Basundhara-02 | 2025-06-13 14:33 | 2025-06-13 14:41 | 0.0055556 | T | Distance Z1 | 89 | 11.8667 | Power interruption
Siddhirganj 132/33kV | 132kV MTR 2 | 2025-06-07 14:14 | 2025-06-07 21:09 | 0.28819 | T | Remote trip from 230 kv | 0 | 0 | No interruption
Siddhirganj 132/33kV | 132kV MTR 2 | 2025-06-08 06:55 | 2025-06-08 21:17 | 0.59861 | T | Remote trip from 230 kV | 0 | 0 | No interruption
Siddhirganj 132/33kV | Ullon 1 | 2025-06-29 10:53 | 2025-06-29 13:16 | 0.099306 | T | Transmission Line Faulty | 0 | 0 | No interruption
Siddhirganj 230/132kV | 335MW EGCB 1 | 2025-06-08 06:58 | 2025-06-08 12:36 | 0.23472 | T | no | 0 | 0 | No interruption
Sonargaon 132/33kV | Haripur-2 | 2025-06-05 16:05 | 2025-06-07 02:34 | 1899-12-31 10:29 | T | Bed weather and thunderstorm. | 0 | 0 | No interruption
Sonargaon 132/33kV | Daudkandi-2 | 2025-06-06 23:40 | 2025-06-10 20:23 | 1900-01-02 20:43 | T | line tripped | 0 | 0 | No interruption
Rampura 230/132kV | Moghbazar-02 | 2025-06-02 16:57 | 2025-06-21 10:38 | 1900-01-17 17:41 | E/O | Emergency maint.work | 0 | 0 | No interruption
Siddhirganj 132/33kV | 120MW EGCB GT1 | 2025-06-29 10:32 | 2025-06-29 13:25 | 0.12014 | E/O | Oil Leakage Chek | 0 | 0 | No interruption
Sonargaon 132/33kV | Daudkandi-2 | 2025-06-04 07:11 | 2025-06-04 12:38 | 0.22708 | E/O | Instruction by NLDC | 0 | 0 | No interruption
Sonargaon 132/33kV | Daudkandi-2 | 2025-06-15 10:31 | 2025-06-15 13:17 | 0.11528 | E/O | By the instructions of NLDC | 0 | 0 | No interruption
Sonargaon 132/33kV | OPML(IEL-1) | 2025-06-15 10:38 | 2025-06-15 14:34 | 0.16389 | E/O | For working at bus A | 0 | 0 | No interruption
Sonargaon 132/33kV | Haripur-2 | 2025-06-15 10:49 | 2025-06-15 14:29 | 0.15278 | E/O | Due to CB maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-26 00:31 |  | Unserved Energy: |  | 11.8667
Chattogram Grid Circle :
Bakulia 132/33kV | Bakalia-Sikalbaha Ckt-01 | 2025-06-01 14:16 | 2025-06-01 14:50 | 0.023611 | T | Emergency maint.work | 0 | 0 | No interruption
Bakulia 132/33kV | Bakalia-Sikalbaha Ckt-02 | 2025-06-01 14:24 | 2025-06-01 14:41 | 0.011806 | T | Tripped | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Sikalbaha ckt-2 | 2025-06-03 06:43 | 2025-06-03 18:14 | 0.47986 | T | Due to Heavy storm, A big tree fell on Conductor. | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2025-06-01 08:52 | 2025-06-01 09:18 | 0.018056 | T | Tripped | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2025-06-03 06:10 | 2025-06-03 06:40 | 0.020833 | T | Tripped | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-Halishahar CKT-3 | 2025-06-03 06:10 | 2025-06-03 06:43 | 0.022917 | T | Thunderstorm and heavy rainfall | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Hathazari-2 | 2025-06-01 08:27 | 2025-06-01 09:46 | 0.054861 | T | general trip,zone-1,zcom,R-Phase | 0 | 0 | No interruption
Shikalbaha 230/132kV | Intermediate-2 | 2025-06-01 12:40 | 2025-06-01 17:37 | 0.20625 | T | Tripped | 0 | 0 | No interruption
Shikalbaha 230/132kV | Bakulia-1 | 2025-06-01 14:16 | 2025-06-01 14:49 | 0.022917 | T | Tripped | 0 | 0 | No interruption
Shikalbaha 230/132kV | Bakulia-2 | 2025-06-01 14:23 | 2025-06-01 14:43 | 0.013889 | T | None | 0 | 0 | No interruption
Shikalbaha 230/132kV | Dohazari Ckt-2 | 2025-06-03 06:43 | 2025-06-03 18:13 | 0.47917 | T | Tripped | 0 | 0 | No interruption
Shikalbaha 230/132kV | Interconnection-1 | 2025-06-11 10:18 | 2025-06-11 10:52 | 0.023611 | T | O/C Fault. | 18 | 10.2 | Power interruption
Baroirhat 132/33kV | Feni-1 | 2025-06-04 09:34 | 2025-06-04 10:30 | 0.038889 | E/O | Feni ss taken s/d | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2025-06-26 14:32 | 2025-06-26 17:09 | 0.10903 | E/O | Maintenance Work of Khulsi End. | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2025-06-28 09:42 | 2025-06-28 12:12 | 0.10417 | E/O | Halishahar Forced Shutdown | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 15:07 |  | Unserved Energy: |  | 10.2
Cumilla Grid Circle :
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-1 | 2025-06-01 03:41 | 2025-06-01 04:38 | 0.039583 | T | Heavy Rain | 9 | 8.55 | Power interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-2 | 2025-06-01 03:41 | 2025-06-01 04:38 | 0.039583 | T | Heavy Rain | 9 | 8.55 | Power interruption
Daudkandi 132/33kV | Sonargaon-2 | 2025-06-06 22:36 | 2025-06-10 20:24 | 1900-01-02 21:48 | T | sonargaon-2 line conductor breakdown | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sylhet-2 | 2025-06-01 03:41 | 2025-06-01 04:40 | 0.040972 | T | Bad Weather | 17 | 16.7167 | Power interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-02 | 2025-06-09 03:27 | 2025-06-09 03:40 | 0.0090278 | T | Tripped | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-02 | 2025-06-15 12:00 | 2025-06-15 12:05 | 0.0034722 | T | N/A | 0 | 0 | No interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-1 | 2025-06-01 03:41 | 2025-06-01 04:40 | 0.040972 | T | Extreamly bad weather. | 0 | 0 | No interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-2 | 2025-06-01 03:41 | 2025-06-01 04:40 | 0.040972 | T | extreamly Bad Weather. | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-2 | 2025-06-04 16:05 | 2025-06-04 16:51 | 0.031944 | E/O | Emergency maint.work | 70 | 53.6667 | Power interruption
Chhatak 132/33kV | Sylhet 01 | 2025-06-18 12:42 | 2025-06-18 15:07 | 0.10069 | E/O | Sylhet-Chhatak Circuit-01 CT Red Hot problem. | 0 | 0 | No interruption
Cumilla(S) 132/33kV | 53.2MW Lakthanavi | 2025-06-04 15:39 | 2025-06-04 17:55 | 0.094444 | E/O | work for lakdhanavi end | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sreemongal-1 | 2025-06-09 15:37 | 2025-06-14 00:55 | 1900-01-03 09:18 | E/O | According to direction of NLDC SDE for AT-2 overload. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sreemongal-2 | 2025-06-09 15:37 | 2025-06-14 00:55 | 1900-01-03 09:18 | E/O | According to direction of NLDC SDE for AT-2 overload. | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shajibazar-Sreemongal Ckt-01 | 2025-06-06 01:07 | 2025-06-06 03:00 | 0.078472 | E/O | Sreemongol circuit 1 bus loop B phase maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV | Chhatak-Sunamgonj CKT-2 | 2025-06-26 11:34 | 2025-06-26 16:50 | 0.21944 | E/O | Eor chatak side tower maintenance CKT-2 shutdown . NLDC AE inform us at 11.32 AM then we follow the NLDC AE instructions and shutdown the CKT-2 . | 0 | 0 | No interruption
|  |  | Total : | 1900-01-12 10:09 |  | Unserved Energy: |  | 87.4833
Khulna Grid Circle :
Bagerhat 132/33kV | Bagerhat-Orion P/S Line | 2025-06-04 02:39 | 2025-06-04 02:39 | 0 | T | Tripped | 0 | 0 | No interruption
Gopalganj 132/33kV | Gopalganj 100 MW PS | 2025-06-25 17:32 | 2025-06-25 18:10 | 0.026389 | T | L/A blast BPDB substation | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Aminbazar Ckt-1 | 2025-06-04 03:34 | 2025-06-04 09:45 | 0.25764 | T | Earth fault Phase(A) Fault Current 6640 Amp. | 0 | 0 | No interruption
Madaripur 132/33kV | Gopaganj North CKT-03 | 2025-06-03 15:38 | 2025-06-03 16:15 | 0.025694 | T | Tripped | 0 | 0 | No interruption
Noapara 132/33kV | Jashore-1 | 2025-06-16 17:48 | 2025-06-16 18:36 | 0.033333 | T | Noapara-Jashore CKT-1 Distance Relay Trip. | 0 | 0 | No interruption
Satkhira 132/33kV | Khulna South-1 (L-1) | 2025-06-20 10:55 | 2025-06-20 11:15 | 0.013889 | T | Tripped | 17.5 | 5.8333 | Power interruption
Satkhira 132/33kV | Khulna South-2 (L-2) | 2025-06-20 10:55 | 2025-06-20 11:17 | 0.015278 | T | Tripped | 17.5 | 6.4167 | Power interruption
Gopalganj 132/33kV | Gopalganj North-2 | 2025-06-19 11:26 | 2025-06-19 13:38 | 0.091667 | E/O | Cable change | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rampal Ckt-1 | 2025-06-03 02:51 | 2025-06-03 13:35 | 0.44722 | E/O | Emergency maint. | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2025-06-17 12:17 | 2025-06-17 15:42 | 0.14236 | E/O | Emergency maint. | 0 | 0 | No interruption
Patuakhali 132/33kV | Barishal-Pautakhali 132kV Line | 2025-06-11 06:45 | 2025-06-11 07:57 | 0.05 | E/O | Barguna ss red hot maintenence | 13 | 15.6 | Power interruption
|  |  | Total : | 1899-12-31 02:29 |  | Unserved Energy: |  | 27.85
HVDC Grid Circle :
Bheramara 230/132kV | STG (NW) | 2025-06-04 10:37 | 2025-06-04 18:34 | 0.33125 | T | Tripped | 0 | 0 | No interruption
Jashore 132/33kV | NOA-1(L3) | 2025-06-16 17:47 | 2025-06-16 18:38 | 0.035417 | T | Tripped | 0 | 0 | No interruption
Jashore 132/33kV | Cap. Bank-1 | 2025-06-27 11:14 | 2025-06-27 11:44 | 0.020833 | T | Tripped | 0 | 0 | No interruption
Jhenaidah 132/33kV | Jhenaidah-Magura, 132kV Circuit-1(L7) | 2025-06-26 05:22 | 2025-07-01 16:34 | 1900-01-04 11:12 | T | Y- phase, PT brust , magura sub- Station. | 0 | 0 | No interruption
Magura 132/33kV | Jhenaidah Ckt. - 2 | 2025-06-26 05:22 | 2025-06-26 06:03 | 0.028472 | T | Over current | 102 | 69.7 | Power interruption
Magura 132/33kV | Jhenaidah Ckt. -1 | 2025-06-26 05:29 | 2025-06-26 18:46 | 0.55347 | E/O | PT Blast | 0 | 0 | No interruption
|  |  | Total : | 1900-01-05 10:28 |  | Unserved Energy: |  | 69.7
Bogura Grid Circle:
Bogura 132/33kV | Natore-1 | 2025-06-16 20:03 | 2025-06-16 20:47 | 0.030556 | T | Stormy Weather | 0 | 0 | No interruption
Bogura 230/132kV | Confidance UN-1 | 2025-06-02 23:25 | 2025-06-03 00:42 | 0.053472 | T | Rain & Storming | 0 | 0 | No interruption
Bogura 230/132kV | Confidance UN-2 | 2025-06-02 23:55 | 2025-06-03 00:50 | 0.038194 | T | Rain & Stroming | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2025-06-02 23:25 | 2025-06-03 15:09 | 0.65556 | T | Lockout Relay KT86.1 Operated Lockout Relay KT86.2 Operated Drirectional Earth Fault DMT (87N) Trip Distance =M1 28.0 km /M2 87.4 km Current = (R-Phase = 14.67 A, Y-Phase = 82.57 A, B-Phase = 15.31 A) | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Lalmonirhat | 2025-06-02 23:45 | 2025-06-03 00:18 | 0.022917 | T | A-phase ,Distance Relay | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Sherpur-Sirajgonj Ckt-1 | 2025-06-10 22:01 | 2025-06-11 07:34 | 0.39792 | E/O | As per the instructions of ALDC. | 0 | 0 | No interruption
Bogura 400/230kV | 400 KV Reactor (125 MVAR) | 2025-06-02 13:04 | 2025-06-17 18:48 | 1900-01-14 05:44 | E/O | ALDC Bogura Instruction. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2025-06-08 18:32 | 2025-06-08 18:32 | 0 | E/O | Abnormal sound at VT(Y) phase. | 0 | 0 | No interruption
Bogura 400/230kV | 400 KV Reactor (125 MVAR) | 2025-06-17 20:49 | 2025-06-17 20:49 | 0 | E/O | Voltage low and Instruction by ALDC Bogura. | 0 | 0 | No interruption
Kurigram 132/33kV | Capacitor Bank | 2025-06-24 21:10 | 2025-06-25 18:17 | 0.87986 | E/O | red hot at R phase cell. | 0 | 0 | No interruption
Natore 132/33kV | Rajshahi-1 | 2025-06-24 15:51 | 2025-06-24 17:11 | 0.055556 | E/O | Emergency maint.work | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Teesta Solar-1 | 2025-06-07 18:30 | 2025-06-08 19:30 | 1899-12-31 01:00 | E/O | Relay Faulty. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-17 09:57 |  | Unserved Energy: |  | 0
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 1900-03-08 17:31 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
| Ashuganj-2 | 2024-11-13 12:06 | 2024-11-13 12:18

## QF-LDC-25
QF-LDC-25
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: June 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV | 230kV Transformer-2 ( 715T2) | 2025-06-16 17:50 | 2025-06-16 17:58 | 0:08 | S/O | The rope fell on the transformer. | 0 | 0 | No interruption
Bhaluka 132/33kV | Transformer- 01 | 2025-06-02 08:22 | 2025-06-02 09:42 | 1:20 | S/O | High temperature minimize. | 0 | 0 | No interruption
Bhaluka 132/33kV | Bus A | 2025-06-02 11:13 | 2025-06-02 12:21 | 1:08 | S/O | Temperature minimize at Mymensingh circuit1 (Bus DS) | 0 | 0 | No interruption
Bhaluka 132/33kV | Transformer- 01 | 2025-06-05 05:19 | 2025-06-05 09:54 | 4:35 | S/O | 33 kv bushing clamp change | 0 | 0 | No interruption
Bhaluka 132/33kV | Transformer- 02 | 2025-06-05 09:59 | 2025-06-05 13:04 | 3:05 | S/O | Maintenance work | 0 | 0 | No interruption
Bhaluka 132/33kV | Transformer- 02 | 2025-06-27 07:05 | 2025-06-27 07:47 | 0:42 | S/O | Red hot minimize at 33 kV side | 15 | 10.5 | Power interruption
Dhamrai 132/33kV | Transformer-2 | 2025-06-15 17:25 | 2025-06-15 20:18 | 2:53 | S/O | 33 kV MAH feeder bus jumper maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV | Transformer-1 | 2025-06-18 07:49 | 2025-06-18 11:06 | 3:17 | S/O | Work by PBS. | 0 | 0 | No interruption
Jamalpur 132/33kV | T-2 | 2025-06-04 08:10 | 2025-06-04 09:28 | 1:18 | S/O | 33kv bus sections isolalor temperature rediuse | 25 | 32.5 | Power interruption
Jamalpur 132/33kV | T-4 | 2025-06-04 09:50 | 2025-06-04 10:26 | 0:36 | S/O | 33kv incomming breaker R -phase temperature rediuse | 0 | 0 | No interruption
Jamalpur 132/33kV | T-3 | 2025-06-19 08:25 | 2025-06-19 09:23 | 0:58 | S/O | Red hot remove work of 33kv Shahapur feeder incoming D.S. | 12 | 11.6 | Power interruption
Kishoreganj 132/33kV | Tr-3 (424T) | 2025-06-03 16:25 | 2025-06-03 17:51 | 1:26 | S/O | 33 kv bus hotspot maintenance | 30 | 43 | Power interruption
Kishoreganj 132/33kV | Tr-3 (424T) | 2025-06-05 06:58 | 2025-06-05 12:18 | 5:20 | S/O | T -3 33 kv bus Section. 33 kv feeder hotspot maintenance work by PBS | 40 | 213.3333 | Power interruption
Kishoreganj 132/33kV | 33 kV T1 Bus | 2025-06-08 07:30 | 2025-06-08 09:35 | 2:05 | S/O | For hotspot Maintenance | 0 | 0 | Power interruption
Kishoreganj 132/33kV | Tr-1 (404T) | 2025-06-08 07:31 | 2025-06-08 09:34 | 2:03 | S/O | For Hotspot Maintenance | 65 | 133.25 | Power interruption
Kodda 132/33kV | Tr-1 (406T) | 2025-06-26 06:16 | 2025-06-26 07:52 | 1:36 | S/O | Red hot maintenance | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-3 (50/75 MVA) | 2025-06-03 12:02 | 2025-06-03 14:38 | 2:36 | S/O | Red hot maintanence | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-4 (50/75 MVA) | 2025-06-03 15:50 | 2025-06-03 17:02 | 1:12 | S/O | Red hot Mainteance | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-2(35/50 MVA) | 2025-06-04 09:56 | 2025-06-04 12:17 | 2:21 | S/O | Red hot Maintanence | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-4 (50/75 MVA) | 2025-06-14 11:03 | 2025-06-14 17:14 | 6:11 | S/O | Redhot Maintenance. | 6 | 37.1 | Power interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-3 (50/75 MVA) | 2025-06-14 21:40 | 2025-06-14 23:29 | 1:49 | S/O | Red hot mainteance in pbs section. | 50 | 90.8333 | Power interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-3 (50/75 MVA) | 2025-06-15 10:32 | 2025-06-15 11:19 | 0:47 | S/O | Red hot mainteance | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-3 (50/75 MVA) | 2025-06-20 10:44 | 2025-06-20 12:12 | 1:28 | S/O | Oil felling | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-3 (50/75 MVA) | 2025-06-26 09:46 | 2025-06-26 13:24 | 3:38 | S/O | Oil filling | 0 | 0 | No interruption
Mirpur 132/33kV | Main Bus | 2025-06-20 10:06 | 2025-06-20 14:55 | 4:49 | S/O | Earthing Boring for T3 Bay by G2G project | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-1 (404T) | 2025-06-01 10:40 | 2025-06-01 12:52 | 2:12 | S/O | High temperature maintenance. | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-3 (424T) | 2025-06-01 12:55 | 2025-06-01 16:10 | 3:15 | S/O | High temperature maintenance | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-3 (424T) | 2025-06-02 06:25 | 2025-06-02 10:16 | 3:51 | S/O | Due to High temperature maintenance work in 33kV Capacitor bank-3 bus DS Y ph clamp of Tr-3 Transformer. | 20 | 77 | Power interruption
Mymensingh 132/33kV | Transformer-2 (414T) | 2025-06-02 13:04 | 2025-06-02 14:47 | 1:43 | S/O |  | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-2 (414T) | 2025-06-19 06:32 | 2025-06-19 08:49 | 2:17 | S/O | Red hot of 33 Batirkal Feeder T- Clamp(R&Y Ph) of TR-2:Transformer 33kV Bus.Shutdown taken by PDB. | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-1 (404T) | 2025-06-26 06:09 | 2025-06-26 07:46 | 1:37 | S/O | 33kV bus loup connection with Bus -T (R Ph) of 33kV Bhaluka-2 Feedet | 0 | 0 | No interruption
New Tongi | Tr-1 (4061 | 2025-06-27 09:44 | 2025-06-30 16:24 | 78:40 | S/O | T1 Incomer cable shifting by DESCO | 0 | 0 | No interruption
Savar 132/33kV | T-1 | 2025-06-18 09:10 | 2025-06-18 11:04 | 1:54 | S/O | Remove nest | 0 | 0 | No interruption
Savar 132/33kV | Main Bus-I | 2025-06-18 09:54 | 2025-06-18 13:45 | 3:51 | S/O | Remove Redhot | 0 | 0 | No interruption
Savar 132/33kV | T-2 | 2025-06-18 11:10 | 2025-06-18 13:45 | 2:35 | S/O | Aafter remove redhot | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 01 | 2025-06-03 10:47 | 2025-06-03 11:22 | 0:35 | S/O |  | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132/33 kV T-1 | 2025-06-01 15:48 | 2025-06-01 21:06 | 5:18 | S/O | Jack Bus repair | 35 | 185.5 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-2 | 2025-06-14 08:51 | 2025-06-14 20:53 | 12:02 | S/O | Replacement of Jack BUS (PTR-02) | 0 | 0 | No interruption
|  |  | Total : | 1900-01-06 09:11 |  | Unserved Energy: |  | 834.6167
Dhaka (South) Grid Circle :
Bhulta 132/33kV | GT1 | 2025-06-11 21:05 | 2025-06-11 22:57 | 1:52 | S/O | red hot maintenance | 0 | 0 | No interruption
Haripur 230/132kV | Bus-2 | 2025-06-16 08:21 | 2025-06-16 17:15 | 8:54 | S/O | 210MW POWER STATION BAY ISOLATOR MAINTENANCE. | 0 | 0 | No interruption
Haripur 230/132kV | Bus-1 | 2025-06-27 11:15 | 2025-06-28 20:25 | 33:10 | S/O | Bus DS change | 0 | 0 | No interruption
Keranigonj 230/132/33kV | TR-2 | 2025-06-17 09:54 | 2025-06-17 11:21 | 1:27 | S/O | Energy Meter replacement work. | 0 | 0 | No interruption
Madanganj 132/33kV | GT-2 | 2025-06-18 10:52 | 2025-06-18 14:35 | 3:43 | S/O |  | 0 | 0 | No interruption
Madanganj 132/33kV | BUS Coupler | 2025-06-26 12:45 | 2025-06-29 09:12 | 68:27 | S/O |  | 0 | 0 | No interruption
Maniknagar 132/33kV | Transformer GT-1 | 2025-06-10 09:11 | 2025-06-10 12:50 | 3:39 | S/O | Maintenance work at 33KV side. Shut down taken by Mr. Rokonul Islam, SDE, DPDC. | 0 | 0 | No interruption
Maniknagar 132/33kV | Transformer GT-2 | 2025-06-11 09:27 | 2025-06-11 14:53 | 5:26 | S/O | 33kv control room bus-2 insulation development work (DPDC) | 0 | 0 | No interruption
Meghnaghat 400/230kV | ATR-1 | 2025-06-27 05:36 | 2025-06-27 09:27 | 3:51 | S/O | For maintenance work | 0 | 0 | No interruption
Meghnaghat 400/230kV | ATR - 2 | 2025-06-27 09:37 | 2025-06-27 12:13 | 2:36 | S/O | For maintenance purpose | 0 | 0 | No interruption
Narshingdi 132/33kV | T-3 | 2025-06-27 07:23 | 2025-06-27 09:06 | 1:43 | S/O | T-3 transformer oil leakage repair work on the buchholz relay. | 0 | 0 | No interruption
Shyampur 132/33kV | GT-1 | 2025-06-16 09:09 | 2025-06-16 12:43 | 3:34 | S/O | Sparking in LT Site | 0 | 0 | No interruption
Siddhirganj 132/33kV | T-1 | 2025-06-18 09:27 | 2025-06-18 17:52 | 8:25 | S/O | Bus transfer work done by DPDC | 0 | 0 | No interruption
|  |  | Total : | 1900-01-05 02:47 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Baroaulia 132/33kV | T-1(405T) | 2025-06-27 10:54 | 2025-06-27 11:24 | 0:30 | S/O | Transformer-1 132kv circuit Breaker Change | 0 | 0 | No interruption
Chandraghona 132/33kV | TR-01(406T) | 2025-06-20 09:04 | 2025-06-20 10:05 | 1:01 | S/O | maintenance and installation of Rajastali feeder bus isolator by PDB | 20 | 20.3333 | Power interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2025-06-25 10:32 | 2025-06-25 11:02 | 0:30 | S/O | Replacing the fuse of station supply transformer. | 27 | 13.5 | Power interruption
GPH 230/33kV | Transformer-01(D05) | 2025-06-05 09:26 | 2025-06-05 14:27 | 5:01 | S/O | General maintenance | 0 | 0 | No interruption
Hathazari 230/132/33kV | MT-03 | 2025-06-04 11:48 | 2025-06-04 20:39 | 8:51 | S/O | Maintenance work | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-01 | 2025-06-13 07:08 | 2025-06-13 17:14 | 10:06 | S/O | 33 Bus Maintenance | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-01 | 2025-06-29 08:00 | 2025-06-29 15:51 | 7:51 | S/O | 33 KV Bus Maintenance | 0 | 0 | No interruption
Madunaghat 132/33kV | ATR-1(705T) | 2025-06-22 09:24 | 2025-06-26 17:57 | 104:33 | S/O | Fire protection maintenance work by CNTIC. | 0 | 0 | No interruption
Madunaghat 132/33kV | ATR-2(715T) | 2025-06-27 10:13 | 2025-06-27 10:13 | 0:00 | S/O | Fire Protection Maintenance Work by CNTIC. | 0 | 0 | No interruption
Madunaghat 400/230kV | ATR-2 7106T | 2025-06-06 09:16 | 2025-06-15 10:01 | 216:45 | S/O | Fire system installation, testing & commissioning. | 0 | 0 | No interruption
Madunaghat 400/230kV | ATR-1 7006T | 2025-06-15 12:13 | 2025-06-23 20:01 | 199:48 | S/O | Fire system install,testing & commissioning purpose. | 0 | 0 | No interruption
Sholosohor 132/33kV | TRAFO-02 | 2025-06-13 12:54 | 2025-06-13 13:58 | 1:04 | S/O | Energy Meter replacement. | 0 | 0 | No interruption
Sholosohor 132/33kV | TRAFO-01 | 2025-06-13 14:04 | 2025-06-13 15:57 | 1:53 | S/O | Energy Meter replacement. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-22 05:53 |  |  |  | 33.8333
Cumilla Grid Circle :
Chandpur 132/33kV | 422T | 2025-06-03 07:39 | 2025-06-03 10:59 | 3:20 | S/O | Maintenance | 21 | 70 | No interruption
Chandpur 132/33kV | 412T | 2025-06-06 21:10 | 2025-06-20 12:45 | 327:35 | S/O | Load alternate to T-1 Power Transformer | 0 | 0 | No interruption
Chandpur 132/33kV | 412T | 2025-06-20 08:40 | 2025-06-20 12:45 | 4:05 | S/O | Maintenance work | 12.5 | 51.0417 | Power interruption
Chauddagram 132/33kV | 132 kv T-1 | 2025-06-16 08:00 | 2025-06-16 10:37 | 2:37 | S/O | 33kv Bus Shutdown for maintenance (PBS) | 28 | 73.2667 | Power interruption
Chhatak 132/33kV | T-2 | 2025-06-03 12:30 | 2025-06-03 13:45 | 1:15 | S/O | T-2 D/S status check from control panel | 0 | 0 | Power interruption
Chowmuhani 132/33kV | TR1-415T | 2025-06-03 18:03 | 2025-06-03 20:08 | 2:05 | S/O | TR-01, 33KV Incoming DS B-Phase Loop Maintenance. | 30 | 62.5 | Power interruption
Chowmuhani 132/33kV | TR2-425T | 2025-06-05 08:54 | 2025-06-05 09:39 | 0:45 | S/O | 33KV Incoming CB to DS R Phase Loop Maintenance. | 20 | 15 | No interruption
Chowmuhani 132/33kV | TR2-425T | 2025-06-10 11:07 | 2025-06-10 12:57 | 1:50 | S/O | Tr-02 X-former & associate 33 KV BUS Section Emergency shutdown taken for 33KV Incoming DS to BUSBAR R Phase (red hot) Loop Maintenance. | 30 | 55 | No interruption
Cumilla(S) 132/33kV | TR-1 | 2025-06-04 05:12 | 2025-06-04 10:10 | 4:58 | S/O |  | 30 | 149 | No interruption
Cumilla(S) 132/33kV | TR-2 | 2025-06-15 08:36 | 2025-06-15 09:32 | 0:56 | S/O | Do | 34 | 31.7333 | No interruption
Daudkandi 132/33kV | Transformer-2 | 2025-06-22 07:13 | 2025-06-22 10:28 | 3:15 | S/O | Red Hot Removing Work | 30 | 97.5 | Power interruption
Daudkandi 132/33kV | Transformer-3 | 2025-06-27 06:54 | 2025-06-27 11:28 | 4:34 | S/O | Shutdown for Redhot Maintenance work | 30 | 137 | No interruption
Daudkandi 132/33kV | Transformer-2 | 2025-06-29 17:43 | 2025-06-29 20:55 | 3:12 | S/O | Bus Maintenance Work By PBS-3 Team | 30 | 96 | No interruption
Fenchuganj 230/132/33kV | AT-02 | 2025-06-05 09:28 | 2025-06-05 13:00 | 3:32 | S/O | Hot spot problem | 0 | 0 | No interruption
Feni 132/33kV | T-1(405T) | 2025-06-03 07:33 | 2025-06-03 10:55 | 3:22 | S/O | Shutdown taken by REB for 33kV Bus T-1 Maintenance Work | 0 | 0 | No interruption
Feni 132/33kV | T-1(405T) | 2025-06-29 07:29 | 2025-06-29 08:33 | 1:04 | S/O | Shutdown taken by BPDB, for Replace 33KV feeder incoming loop. | 31 | 33.0667 | No interruption
Kulaura 132/33kV | TR-1 AB | 2025-06-21 05:23 | 2025-06-21 07:43 | 2:20 | S/O | Auxillary Transformer-1 maintenance | 29 | 67.6667 | Power interruption
Kulaura 132/33kV | TR-2 | 2025-06-21 08:00 | 2025-06-21 16:36 | 8:36 | S/O | PDB Bay Extension Project Work | 13 | 111.8 | Power interruption
Kulaura 132/33kV | TR-1 AB | 2025-06-23 08:09 | 2025-06-23 08:46 | 0:37 | S/O | For red hot removed on TR1AB 33kv side DS | 25 | 15.4167 | No interruption
Kulaura 132/33kV | TR-2 | 2025-06-27 06:17 | 2025-06-27 09:56 | 3:39 | S/O | PDB Project Work | 12 | 43.8 | Power interruption
Ramganj 132/33kV | Transformer-01 | 2025-06-04 08:16 | 2025-06-04 10:04 | 1:48 | S/O | Temperature Bay Junction Point measurement | 10 | 18 | No interruption
Ramganj 132/33kV | Transformer -02 | 2025-06-22 07:07 | 2025-06-22 08:41 | 1:34 | S/O | Red Hot Maintenance work at 33 kv PBS feeder | 30 | 47 | Power interruption
Ramganj 132/33kV | Transformer-01 | 2025-06-23 06:46 | 2025-06-23 08:57 | 2:11 | S/O | Red hot maintenance | 10 | 21.8333 | No interruption
Shahjibazar 132/33kV | TR-06 | 2025-06-16 07:08 | 2025-06-16 09:36 | 2:28 | S/O | Shutdown taken by pbs for red hot maintenance | 72 | 177.6 | No interruption
Shahjibazar 132/33kV | TR-04 | 2025-06-16 07:09 | 2025-06-16 09:30 | 2:21 | S/O | Shutdown taken by pbs for red hot maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2025-06-16 07:17 | 2025-06-16 11:49 | 4:32 | S/O | Shutdown taken by pbs for red hot maintenance | 0 | 0 | No interruption
Sunamganj 132/33kV | Tr-1 | 2025-06-23 10:27 | 2025-06-23 11:02 | 0:35 | S/O | Tr-1 Shutdown due t incoming CB closing coil change. | 15 | 8.75 | Power interruption
Sylhet (South) | Trafo-2 | 2025-06-28 07:19 | 2025-06-28 18:35 | 11:16 | S/O | 33 kV Bay Extension work. | 4 | 45.0667 | No interruption
Sylhet 132/33kV | T4 | 2025-06-27 07:33 | 2025-06-27 09:11 | 1:38 | S/O | 33 KV ST.Aux-2 replacement work by BPDB S&D-4. | 22 | 35.9333 | Power interruption
|  |  | Total : | 1900-01-16 04:00 |  |  |  | 1463.975
Khulna Grid Circle :
Bagerhat 132/33kV | Transformer-1 (403T) | 2025-06-04 07:24 | 2025-06-04 08:54 | 1:30 | S/O | Maint.work | 0 | 0 | No interruption
Bagerhat 132/33kV | Transformer-2 (413 T) | 2025-06-04 09:31 | 2025-06-04 10:28 | 0:57 | S/O | 33 kv CT overheat maintenance work | 0 | 0 | No interruption
Barguna 132/33kV | Transformer-1 | 2025-06-06 10:40 | 2025-06-06 11:35 | 0:55 | S/O | WZPDCL-2 ফিডারে ৩৩ কেভি Bus Section-1 Y-phase এর লুপে Redhot maintenance | 0 | 0 | No interruption
Barishal 132/33kV | T-2 (415T) | 2025-06-12 07:15 | 2025-06-12 08:37 | 1:22 | S/O | 33 kv Muladi feeder red hot maintenance work. | 30 | 41 | Power interruption
Barishal 230/132kV | T-4 | 2025-06-02 11:35 | 2025-06-02 13:24 | 1:49 | S/O | Korapur 33 kV Feeder maintenance | 10 | 18.1667 | Power interruption
Barishal 230/132kV | T-5 | 2025-06-03 17:48 | 2025-06-04 14:29 | 20:41 | S/O | Hizla 33 kV feeder Bus DS loop maintenance | 20 | 19 | Power interruption 17:48 to 18:45 | 14:29
Barishal 230/132kV | T-4 | 2025-06-06 10:07 | 2025-06-06 11:56 | 1:49 | S/O | Emergency maintenance | 8 | 14.5333 | Power interruption
Barishal 230/132kV | T-5 | 2025-06-06 11:09 | 2025-06-06 11:59 | 0:50 | S/O | Maintenance work. | 24 | 20 | Power interruption
Barishal 230/132kV | T-4 | 2025-06-08 10:52 | 2025-06-08 10:58 | 0:06 | S/O | Babugonj 33kv feeder bus DS maintenance by pbs-2 | 7 | 0.7 | Power interruption
Barishal 230/132kV | T-5 | 2025-06-20 15:15 | 2025-06-20 16:57 | 1:42 | S/O | Due to mehendigonj 33 kv feeder Bus DS repair maintenance. | 20 | 34 | Power interruption
Borhanuddin 230/33kV | Tr-Load | 2025-06-14 06:31 | 2025-06-14 08:58 | 2:27 | S/O | Redhot Maintenance Work. | 90 | 220.5 | Power interruption
Faridpur 132/33kV | Transformer-2 | 2025-06-01 17:02 | 2025-06-01 18:40 | 1:38 | S/O | Red hot | 40 | 65.3333 | Power interruption
Faridpur 132/33kV | Transformer-3 | 2025-06-02 07:54 | 2025-06-02 09:38 | 1:44 | S/O | Red hot | 6 | 10.4 | Power interruption
Faridpur 132/33kV | Transformer-1 | 2025-06-02 07:59 | 2025-06-02 09:34 | 1:35 | S/O | Red hot | 20 | 31.6667 | Power interruption
Faridpur 132/33kV | ATR-2 | 2025-06-17 12:02 | 2025-06-17 18:07 | 6:05 | S/O | 230 Breaker maintenance | 0 | 0 | No interruption
Faridpur 132/33kV | ATR-1 | 2025-06-17 20:03 | 2025-06-17 20:58 | 0:55 | S/O | Project Work | 0 | 0 | No interruption
Faridpur 132/33kV | Transformer-2 | 2025-06-28 06:20 | 2025-06-28 12:24 | 6:04 | S/O | Clamp Change & Hot Spot Maintenance | 0 | 0 | No interruption
Faridpur 132/33kV | Transformer-2 | 2025-06-29 13:34 | 2025-06-29 15:48 | 2:14 | S/O | Red hot maintenance | 10 | 22.3333 | Power interruption
Goalpara 132/33kV | T-5 | 2025-06-04 07:05 | 2025-06-04 08:55 | 1:50 | S/O | 3rd transformer installation | 0 | 0 | Power interruption
Goalpara 132/33kV | T-6 | 2025-06-04 07:07 | 2025-06-04 08:45 | 1:38 | S/O | 3rd transformer installation | 3 | 4.9 | Power interruption
Goalpara 132/33kV | Bus 1 | 2025-06-04 09:45 | 2025-06-04 11:01 | 1:16 | S/O | Third transformer instelation Works. | 0 | 0 | No interruption
Goalpara 132/33kV | Bus 2 | 2025-06-04 11:17 | 2025-06-04 11:59 | 0:42 | S/O | Third Transformer Instaletion Works. | 0 | 0 | No interruption
Goalpara 132/33kV | Bus 1 | 2025-06-16 12:39 | 2025-06-17 15:39 | 27:00 | S/O | CVT PROBLEM (Y PHASE) | 0 | 0 | No interruption
Goalpara 132/33kV | T-6 | 2025-06-18 07:04 | 2025-06-18 09:15 | 2:11 | S/O |  | 0 | 0 | No interruption
Goalpara 132/33kV | Bus 2 | 2025-06-19 13:30 | 2025-06-19 20:49 | 7:19 | S/O | protechtion test by SPMD WITH T-7 | 0 | 0 | No interruption
Goalpara 132/33kV | T-5 | 2025-06-23 07:03 | 2025-06-23 09:50 | 2:47 | S/O | 3rd transformer Installation. | 3 | 8.35 | Power interruption
Goalpara 132/33kV | T-6 | 2025-06-23 07:05 | 2025-06-23 09:44 | 2:39 | S/O | 3rd transformer Installation. | 3 | 7.95 | Power interruption
Goalpara 132/33kV | T1 | 2025-06-24 06:40 | 2025-06-24 13:25 | 6:45 | S/O | Earth wire installation | 0 | 0 | No interruption
Goalpara 132/33kV | T-5 | 2025-06-24 06:42 | 2025-06-24 08:48 | 2:06 | S/O | Earth wire installation work | 0 | 0 | No interruption
Goalpara 132/33kV | T-6 | 2025-06-24 06:51 | 2025-06-24 08:52 | 2:01 | S/O | Earth wire installation | 6 | 12.1 | Power interruption
Gollamari 132/33kV | Tr-2 | 2025-06-28 07:19 | 2025-06-28 08:18 | 0:59 | S/O | Overheat Maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV | T1 | 2025-06-04 10:46 | 2025-06-04 13:20 | 2:34 | S/O | Hot spot maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Bus-01 | 2025-06-06 10:24 | 2025-06-06 11:44 | 1:20 | S/O | Hotpot maintenance | 0 | 0 | No interruption
Kasba 132/33kV | TR-1 | 2025-06-10 21:56 | 2025-06-11 00:24 | 2:28 | S/O | 33kV kasba-1 feeder PT Jumper Maintenance by PBS | 0 | 0 | No interruption
Kasba 132/33kV | TR-1 | 2025-06-11 14:20 | 2025-06-11 16:54 | 2:34 | S/O | Kasba 1 feeder Y phase PT replace work | 0 | 0 | No interruption
Madaripur 132/33kV | T3-426T | 2025-06-02 07:06 | 2025-06-02 08:49 | 1:43 | S/O | Hot Spot maintenance | 0 | 0 | No interruption
Mongla 132/33kV | T-1 | 2025-06-03 18:15 | 2025-06-03 20:10 | 1:55 | S/O | Energy meter change. | 0 | 0 | No interruption
Mongla 132/33kV | T-2 | 2025-06-04 10:25 | 2025-07-02 14:20 | 675:55 | S/O | DS Alignment Problem. | 0 | 0 | No interruption
Narail 132/33kV | TR2 (413-T) | 2025-06-12 07:03 | 2025-06-12 10:23 | 3:20 | S/O | Red Hot Maintenance | 0 | 0 | No interruption
Noapara 132/33kV | T-1 | 2025-06-06 16:47 | 2025-06-06 18:19 | 1:32 | S/O | None | 20 | 30.6667 | Power interruption
Noapara 132/33kV | T-2 | 2025-06-11 03:25 | 2025-06-11 05:23 | 1:58 | S/O | None | 14.5 | 28.5167 | Power interruption
Noapara 132/33kV | T-2 | 2025-06-13 08:37 | 2025-06-13 12:04 | 3:27 | S/O | Repair of B-phase conductor of REB-1 feeder. | 0 | 0 | No interruption
Noapara 132/33kV | T-2 | 2025-06-22 07:56 | 2025-06-22 09:24 | 1:28 | S/O |  | 0 | 0 | No interruption
Noapara 132/33kV | Bus Section-2 | 2025-06-22 08:02 | 2025-06-22 09:17 | 1:15 | S/O |  | 16 | 20 | Power interruption
Patuakhali 132/33kV | 425T (T-3) | 2025-06-05 14:32 | 2025-06-05 16:11 | 1:39 | S/O | Hot spot maintenance | 0 | 0 | No interruption
Payra 400/132/33kV | 400/132/33 kV Auto Transformer-02 | 2025-06-03 12:26 | 2025-06-03 14:03 | 1:37 | S/O | Maintenance. | 0 | 0 | No interruption
Payra 400/132/33kV | 400/132/33 kV Auto Transformer-01 | 2025-06-22 15:52 | 2025-06-22 19:19 | 3:27 | S/O | PRD Checking and Fire Detection alarm Checking and reset. | 0 | 0 | No interruption
Satkhira 132/33kV | Transformer-1 (T-1) | 2025-06-20 08:27 | 2025-06-20 12:45 | 4:18 | S/O | Change T clamp | 0 | 0 | No interruption
Shariatpur 132/33kV | T1-406T | 2025-06-21 08:23 | 2025-06-21 11:53 | 3:30 | S/O | Red Hot Maintenance by WZPDCL. | 30 | 105 | Power interruption
|  |  | Total : | 1900-02-02 13:36 |  | Unserved Energy : |  | 715.1167
HVDC Grid Circle
Bhangura 132/33kV | Tr-1(403T) | 2025-06-27 12:19 | 2025-06-27 12:40 | 0:21 | S/O | Energy meter change | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-2(413T) | 2025-06-27 12:48 | 2025-06-27 13:27 | 0:39 | S/O | Energy meter change | 0 | 0 | No interruption
Bheramara(GK) 132/33kV | TR-1 | 2025-06-07 10:05 | 2025-06-07 10:15 | 0:10 | S/O | red hot maintenance. | 17 | 2.8333 | Power interruption
Bheramara(GK) 132/33kV | TR-2 | 2025-06-07 10:06 | 2025-06-07 11:16 | 1:10 | S/O | red hot maintenance. | 17 | 19.8333 | Power interruption
BIPTC | Block-01, Trafo-02 | 2025-06-27 09:56 | 2025-06-27 21:34 | 11:38 | S/O | MOG Alarm Raised, Oil level checking, Refilling Oil. | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Bus-2 | 2025-06-22 10:29 | 2025-06-22 11:55 | 1:26 | S/O | For DSEPL work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Bus-1 | 2025-06-24 09:22 | 2025-06-24 16:07 | 6:45 | S/O |  | 2 | 13.5 | Power interruption
Ishurdi 230/132kV | 230/132 kV T-03 | 2025-06-23 09:05 | 2025-06-23 13:35 | 4:30 | S/O | DC Cable Replacement issue | 0 | 0 | No interruption
Ishurdi 230/132kV | 230/132 kV T-02 | 2025-06-24 09:22 | 2025-06-24 16:07 | 6:45 | S/O | for bus -1 Shut down | 0 | 0 | No interruption
Jhenaidah 230/132kV | Transformer- 2 | 2025-06-20 05:44 | 2025-06-20 10:04 | 4:20 | S/O | Maintenance Work | 0 | 0 | No interruption
Jhenaidah 230/132kV | Transformer- 1 | 2025-06-27 06:44 | 2025-06-27 09:26 | 2:42 | S/O | CT clamp Change | 0 | 0 | No interruption
Magura 132/33kV | T-2 (415T) | 2025-06-02 06:40 | 2025-06-02 09:28 | 2:48 | S/O | 33kV CB of Rawtara feeder replace | 17 | 47.6 | Power interruption
Magura 132/33kV | T-1 (405T) | 2025-06-16 21:40 | 2025-06-16 22:38 | 0:58 | S/O | Red Hot Maintenance by WZPDCL-Magura. | 15 | 14.5 | Power interruption
Magura 132/33kV | T-3 (425T) | 2025-06-20 09:34 | 2025-06-20 12:46 | 3:12 | S/O | 33kV Bay extension | 20 | 64 | Power interruption
|  |  | Total : | 1899-12-31 23:24 |  | Unserved Energy : |  | 162.2667
Bogura Grid Circle:
Barapukuria 230/132/33kV | 230/132 KV T-01, 703T | 2025-06-04 09:31 | 2025-06-04 16:35 | 7:04 | S/O | T-01 main-1 relay testing | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132/33 KV T-4, 444T | 2025-06-24 16:19 | 2025-06-24 17:41 | 1:22 | S/O | Emergency maintenance of 33 KV Bus | 35 | 47.8333 | Power interruption
Bog-Sherpur 132/33kV | Transformer-2 (414T) | 2025-06-24 16:21 | 2025-06-24 18:09 | 1:48 | S/O |  | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Main Bus-1 | 2025-06-30 10:10 | 2025-07-01 17:20 | 31:10 | S/O | TR-3 Project work | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-3 | 2025-06-03 07:20 | 2025-06-03 10:02 | 2:42 | S/O | maintenance work | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-1 | 2025-06-05 08:26 | 2025-06-05 10:05 | 1:39 | S/O | Puran bogura-1 (NESCO) Isolator work. | 25 | 41.25 | Power interruption
Bogura 132/33kV | Transformer-2 | 2025-06-27 08:24 | 2025-06-27 09:56 | 1:32 | S/O | 33-KV Talora Feeder Red hot Maintanance. (33-KV Bus side). | 20 | 30.6667 | Power interruption
Bogura 400/230kV | ATR-03 | 2025-06-02 09:34 | 2025-06-02 17:34 | 8:00 | S/O | DS operating Box Chance | 0 | 0 | No interruption
Bogura 400/230kV | ATR-01 | 2025-06-23 11:03 | 2025-06-23 17:42 | 6:39 | S/O | ATR-01 Paint Work | 0 | 0 | No interruption
Natore 132/33kV | TR-1 (405 T) | 2025-06-05 07:13 | 2025-06-05 09:40 | 2:27 | S/O |  | 31 | 75.95 | Power interruption
Natore 132/33kV | TR-2 (415 T) | 2025-06-05 07:13 | 2025-06-05 09:37 | 2:24 | S/O |  | 31 | 74.4 | Power interruption
Natore 132/33kV | TR-4 (435 T) | 2025-06-28 11:05 | 2025-06-28 12:52 | 1:47 | S/O | T-4 33 KV Bus Red Hot Maintenance work by pbs-1 | 25 | 44.5833 | Power interruption
Rajshahi 132/33kV | Transformer T-3 (425T) | 2025-06-03 07:52 | 2025-06-03 09:17 | 1:25 | S/O | Maintenance Work | 15 | 21.25 | Power interruption
Saidpur 132/33kV | TR-3 (424T) | 2025-06-30 06:48 | 2025-06-30 08:11 | 1:23 | S/O |  | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 23:22 |  | Unserved Energy : |  | 335.9333
Others :Nil
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 2242:13 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:June 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bajitpur 132/33kV | Ashuganj Ckt-1 | 2025-06-14 00:37 | 2025-06-14 02:04 | 1:27 | S/O | Maint.work | 0 | 0 | No interruption
Bajitpur 132/33kV | Ashuganj Ckt-1 | 2025-06-15 09:29 | 2025-06-15 11:10 | 1:41 | S/O | Maint.work | 0 | 0 | No interruption
Bhaluka 132/33kV | Mymensingh Ckt- 01 | 2025-06-02 10:25 | 2025-06-02 12:49 | 2:24 | S/O | Work at Mymensingh end(High temperature minimize). | 0 | 0 | No interruption
Bhaluka 132/33kV | BR Powergen Ckt- 01 | 2025-06-23 12:33 | 2025-06-23 16:01 | 3:28 | S/O | NLDC list End to End test | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-01 | 2025-06-03 08:48 | 2025-06-03 16:25 | 7:37 | S/O | Disk insulator replace work of Tower no.403 | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-2 | 2025-06-09 09:07 | 2025-06-09 16:19 | 7:12 | S/O | Hotspot Maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Aminbazar Ckt-01 | 2025-06-02 11:10 | 2025-06-02 13:58 | 2:48 | S/O | CT Ten delta Test | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Aminbazar Ckt-01 | 2025-06-21 12:36 | 2025-06-21 14:18 | 1:42 | S/O | Maint.work | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Aminbazar Ckt-01 | 2025-06-26 06:43 | 2025-06-26 21:08 | 14:25 | S/O | CT Changing Work | 0 | 0 | No interruption
Kodda 132/33kV | Summit 149 MW PS | 2025-06-10 07:30 | 2025-06-10 12:48 | 5:18 | S/O | Red hot maintenance | 0 | 0 | No interruption
Manikganj 132/33kV | Manikganj- Kabirpur CKT-1 | 2025-06-02 13:07 | 2025-06-03 14:31 | 25:24 | S/O | Circuit -1 B-phase top "T" connector Redhot removal | 0 | 0 | No interruption
Mirpur 132/33kV | Aminbazar-1 | 2025-06-10 07:10 | 2025-06-10 15:47 | 8:37 | S/O | Maint.work | 0 | 0 | No interruption
Mirpur 132/33kV | Aminbazar-2 | 2025-06-11 07:30 | 2025-06-11 19:45 | 12:15 | S/O | Loop Conductor(CT to CB) Change work on Mirpur S/S. | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Sector-18 | 2025-06-12 07:35 | 2025-06-12 22:18 | 14:43 | S/O | CT replacement work of all phases | 0 | 0 | No interruption
Mirpur 132/33kV | Aminbazar-2 | 2025-06-13 08:20 | 2025-06-13 09:50 | 1:30 | S/O | Maint.work | 0 | 0 | No interruption
Mirpur 132/33kV | Aminbazar-2 | 2025-06-14 11:05 | 2025-06-14 13:33 | 2:28 | S/O | Maint.work | 0 | 0 | No interruption
Mirpur 132/33kV | Aminbazar-1 | 2025-06-27 06:09 | 2025-06-27 09:56 | 3:47 | S/O | Main Bus Red hot maintenance work. | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Bhaluka Ckt-1 | 2025-06-02 10:24 | 2025-06-02 12:51 | 2:27 | S/O | Due to High temperature maintenance work in Gas Circuit Breaker Y-Ph upper clamp and Line DS Y - Ph Breaker side . | 0 | 0 | No interruption
|  |  | Total : | 1900-01-03 23:13 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Haripur 230/132kV | Sonargaon 2 | 2025-06-15 10:47 | 2025-06-15 14:29 | 3:42 | S/O | Maintenance on the other end | 0 | 0 | No interruption
Haripur 230/132kV | Meghnaghat-1 | 2025-06-26 06:14 | 2025-06-28 22:52 | 64:38 | S/O | Isolator Replacement Work. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 2 | 2025-06-17 11:26 | 2025-06-17 12:21 | 0:55 | S/O | Main Energymeter replacement work. | 0 | 0 | No interruption
Haripur 230/132kV | 132KV Bhulta-2 | 2025-06-25 11:03 | 2025-06-25 16:51 | 5:48 | S/O | Red Hot Maintenance by other end. | 0 | 0 | No interruption
Meghnaghat 230/132kV | Meghnaghat-GT-02(MPL) | 2025-06-26 13:24 | 2025-06-26 13:24 | 0:00 | S/O | DS maintenance | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Summit PP 400KV Ckt-1 | 2025-06-04 13:35 | 2025-06-04 16:32 | 2:57 | S/O | Summit Bay Line DS Maintenance | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-1 | 2025-06-26 10:42 | 2025-06-26 13:59 | 3:17 | S/O | For maintenance purpose | 0 | 0 | No interruption
Rampura 230/132kV | Moghbazar-01 | 2025-06-25 06:57 | 2025-06-25 09:18 | 2:21 | S/O | Shutdown from NLDC. | 0 | 0 | No interruption
Sonargaon 132/33kV | Daudkandi-01 | 2025-06-05 16:30 | 2025-06-06 23:40 | 31:10 | S/O | NLDC instruction for Haripur-1 ckt over loaded. Haripur-2 ckt trip condition(B-ph CB drive box mechanism problem). | 0 | 0 | No interruption
|  |  | Total : | 1900-01-03 18:48 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
AKS 132/33kV | Bar Aulia | 2025-06-15 15:26 | 2025-06-15 15:50 | 0:24 | S/O | Demand to Baraulia ss Maintenance | 0 | 0 | No interruption
Baroaulia 132/33kV | AKSPL | 2025-06-26 00:19 | 2025-06-26 11:00 | 10:41 | S/O | Akspl Berkar change | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Rampur Ckt-1 | 2025-06-14 11:36 | 2025-06-14 12:01 | 0:25 | S/O | For maintenance purpose | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-Madunaghat CKT-2 | 2025-06-04 15:58 | 2025-06-04 16:47 | 0:49 | S/O | Emergency S/D for nut bolt change at Y -phase at Khulshi S/S end. | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-Halishahar CKT-3 | 2025-06-26 14:26 | 2025-06-26 17:10 | 2:44 | S/O | To replace Damaged loop in between CB and Bus isolator at Khulshi Side | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-Halishahar CKT-3 | 2025-06-28 09:39 | 2025-06-28 12:13 | 2:34 | S/O | Project work at Halishahar Grid Sub-station. | 0 | 0 | No interruption
Rampur 230/132/33 | Halishahar-1 | 2025-06-14 11:37 | 2025-06-14 12:00 | 0:23 | S/O | Energy meter change | 0 | 0 | No interruption
Sholosohor 132/33kV | Sholoshahar-Madunaghat Ckt-1 | 2025-06-13 09:53 | 2025-06-13 10:30 | 0:37 | S/O | Energy Meter Replacement. | 0 | 0 | No interruption
Sholosohor 132/33kV | Sholoshahar-Madunaghat Ckt-1 | 2025-06-13 10:31 | 2025-06-13 10:56 | 0:25 | S/O | Energy Meter Replacement.Sholoshahar-Madunaghat Ckt-02. | 0 | 0 | No interruption
Sholosohor 132/33kV | Sholoshahar-Khulshi Ckt-1 | 2025-06-13 11:00 | 2025-06-13 11:30 | 0:30 | S/O | Energy Meter Replacement. | 0 | 0 | No interruption
Sholosohor 132/33kV | Sholoshahar-Khulshi Ckt-2 | 2025-06-13 11:41 | 2025-06-13 12:23 | 0:42 | S/O | Energy Meter Replacement. | 0 | 0 | No interruption
|  |  | Total : | 20:14 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-2 | 2025-06-19 09:16 | 2025-06-19 12:13 | 2:57 | S/O | CB maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-1 | 2025-06-29 14:20 | 2025-06-29 16:10 | 1:50 | S/O | Project-1 | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-1 | 2025-06-29 16:31 | 2025-06-29 17:47 | 1:16 | S/O | Project-1 | 0 | 0 | No interruption
Chandpur 132/33kV | 33 kV T-1 Section | 2025-06-10 06:38 | 2025-06-10 09:00 | 2:22 | S/O | For maintenance purpose | 12 | 28.4 | Power interruption
Chandpur 132/33kV | 33 kV T-2 section | 2025-06-10 06:38 | 2025-06-10 08:26 | 1:48 | S/O | For maintenance purpose | 0 | 0 | No interruption
Chowmuhani 132/33kV | Feni line-01 | 2025-06-28 11:15 | 2025-06-28 18:06 | 6:51 | S/O | commissioning of Dhagonbhuian 132/33 KV GIS S/S. | 0 | 0 | No interruption
Chowmuhani 132/33kV | Feni line-02 | 2025-06-28 11:15 | 2025-06-28 14:31 | 3:16 | S/O | commissioning of Dhagonbhuian 132/33 KV GIS S/S. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Meghnagat Ckt 1 | 2025-06-17 11:14 | 2025-06-17 13:18 | 2:04 | S/O | Over temperature remove. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-BSRM Ckt-1 | 2025-06-21 07:33 | 2025-06-25 21:46 | 110:13 | S/O | For maintenance purpose | 0 | 0 | No interruption
Daudkandi 132/33kV | Sonargaon-2 | 2025-06-04 07:34 | 2025-06-04 12:39 | 5:05 | S/O | shutdown for Redhot maintenance work | 0 | 0 | No interruption
Feni 132/33kV | Chowddagram Ckt-1 | 2025-06-28 18:20 | 2025-06-28 20:42 | 2:22 | S/O | S/D Taken by AE-Feni For Transfer DS Finger shift to Bus coupler DS | 0 | 0 | No interruption
Ramganj 132/33kV | Ramgonj- Desh Energy Ckt-01 | 2025-06-30 06:51 | 2025-06-30 10:36 | 3:45 | S/O | Temperature raising point maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV | SPCL 86 MW | 2025-06-24 08:50 | 2025-06-24 16:55 | 8:05 | S/O | 86 mw maintenance work | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal - Shahjibazar circuit-1 | 2025-06-06 01:13 | 2025-06-06 02:59 | 1:46 | S/O | Redhot removing work at Shahjibazar SS. | 0 | 0 | No interruption
Sunamganj 132/33kV | Chhatak-Sunamgonj CKT-2 | 2025-06-20 09:36 | 2025-06-20 14:57 | 5:21 | S/O | For maintenance purpose | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-1 | 2025-06-18 12:41 | 2025-06-18 15:06 | 2:25 | S/O | SD by Chatak Grid SS Operation Request by NLDC | 0 | 0 | No interruption
|  |  | Total : | 1900-01-05 17:26 |  | Unserved Energy: |  | 28.4
Khulna Grid Circle :
Barguna 132/33kV | Barguna-Bakergonj 132kv line | 2025-06-11 06:44 | 2025-06-11 07:57 | 1:13 | S/O | R phase CT connector flashing | 14 | 17.0333 | Power interruption
Barishal 230/132kV | Gopalgonj CKT-2 | 2025-06-18 12:05 | 2025-06-18 15:01 | 2:56 | S/O | Due to line ES repair maintenance at barishal end. (GIS) | 0 | 0 | No interruption
Faridpur 132/33kV | 132 KV Gopalganj (400kv) ckt-1 | 2025-06-11 09:48 | 2025-06-11 12:25 | 2:37 | S/O | Red Hot Maintenance at Gopalgonj SS end. | 0 | 0 | No interruption
Faridpur 132/33kV | 230kV Faridpur-Gopalganj CKT-1 | 2025-06-17 18:28 | 2025-06-17 18:50 | 0:22 | S/O | Project Work. | 0 | 0 | No interruption
Faridpur 132/33kV | 230kV Faridpur-Gopalganj CKT-2 | 2025-06-17 19:09 | 2025-06-17 19:54 | 0:45 | S/O | Project work. | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-NWPGCL | 2025-06-22 10:52 | 2025-06-22 18:05 | 7:13 | S/O | Busbar protection testing | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-1 | 2025-06-04 07:27 | 2025-06-04 10:15 | 2:48 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-3 | 2025-06-04 10:23 | 2025-06-04 13:54 | 3:31 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-2 | 2025-06-05 08:48 | 2025-06-05 14:15 | 5:27 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2025-06-05 12:06 | 2025-06-05 22:49 | 10:43 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Gopalganj Ckt-2 | 2025-06-06 10:30 | 2025-06-06 12:39 | 2:09 | S/O | Hotspot maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Faridpur Ckt-1 | 2025-06-11 08:49 | 2025-06-11 12:26 | 3:37 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2025-06-16 09:06 | 2025-06-16 16:14 | 7:08 | S/O | PT Installation for Rooppur Power Plant | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Gopalganj Ckt-2 | 2025-06-19 11:27 | 2025-06-19 13:38 | 2:11 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2025-06-25 16:33 | 2025-06-29 19:00 | 98:27 | S/O | Maint.work | 0 | 0 | No interruption
Madaripur 132/33kV | Gopaganj North CKT-01 | 2025-06-04 07:26 | 2025-06-04 10:16 | 2:50 | S/O | Hot spot maintenance | 0 | 0 | No interruption
Madaripur 132/33kV | Gopaganj North CKT-03 | 2025-06-04 10:22 | 2025-06-04 13:55 | 3:33 | S/O | Red hot maintaining | 0 | 0 | No interruption
Madaripur 132/33kV | Gopaganj North CKT-02 | 2025-06-05 07:54 | 2025-06-05 14:16 | 6:22 | S/O | Hot spot maintenance work | 0 | 0 | No interruption
Patuakhali 132/33kV | PAYRA-PATUAKHALI CKT-1 | 2025-06-03 14:28 | 2025-06-03 15:30 | 1:02 | S/O | Payra end red hot maintenance | 0 | 0 | No interruption
Payra 400/132/33kV | Payra Patuakhali Line-01 | 2025-06-03 14:30 | 2025-06-03 15:29 | 0:59 | S/O | CT R,Y,B phase point maintenance. | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Monakasha 400KV Line ckt-01 | 2025-06-09 09:01 | 2025-06-09 19:20 | 10:19 | S/O | Maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-06 08:12 |  | Unserved Energy: |  | 17.0333
HVDC Grid Circle :
BIPTC | 10CF14 | 2025-06-06 08:37 | 2025-06-06 08:58 | 0:21 | S/O | Maintenance Work | 0 | 0 | No interruption
BIPTC | 10CF15 | 2025-06-15 10:10 | 2025-06-15 12:41 | 2:31 | S/O | Tripped by C1 unbalance 60/61 CPR04 | 0 | 0 | No interruption
BIPTC | 20DF11 | 2025-06-29 11:11 | 2025-06-29 11:55 | 0:44 | S/O | Maintenance Work | 0 | 0 | No interruption
BIPTC | 10CF13 | 2025-06-29 12:06 | 2025-06-29 12:47 | 0:41 | S/O | Maintenance Work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kv Natore-1 | 2025-06-25 08:52 | 2025-06-27 17:22 | 56:30 | S/O | Maintenance Work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 12:47 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Bogura 230/132kV | Naogaon 132 KV Line-1 | 2025-06-16 08:38 | 2025-06-16 12:04 | 3:26 | S/O | Naogaon Substation issue. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Rooppur 400 KV Line-1 | 2025-06-25 16:39 | 2025-06-29 19:06 | 98:27 | S/O | CT, PT and Energy Meter testing work at Rooppur 400kV GIS Substation. | 0 | 0 | No interruption
Naogaon 132/33kV | Nao-Bog Ckt-1 | 2025-06-16 08:34 | 2025-06-16 12:05 | 3:31 | S/O | Line DS Y-phase Maintenance | 0 | 0 | No interruption
Natore 132/33kV | Ishurdi-1 | 2025-06-25 08:52 | 2025-06-27 17:28 | 56:36 | S/O | CT Change | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Lalmonirhat | 2025-06-04 09:05 | 2025-06-04 18:38 | 9:33 | S/O | REMOVE RED HOT | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Saidpur-1 | 2025-06-22 07:15 | 2025-06-24 13:29 | 54:14 | S/O | Project work | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Rangpur CKT-02 | 2025-06-02 21:41 | 2025-06-03 07:52 | 10:11 | S/O | QF- GMD-39 and as the instruction of NLDC (299727) 132 KV Saidpur - Rangpur ckt.-2 (Y phase) Red hot) | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Rangpur CKT-01 | 2025-06-22 07:27 | 2025-06-24 13:46 | 54:19 | S/O | 132 Kv Taraging S/S lilo connection. | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Rangpur CKT-01 | 2025-06-22 07:27 | 2025-06-24 13:46 | 54:19 | S/O | 132 Kv Taragong S/S lilo connection. | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Rangpur CKT-02 | 2025-06-25 05:49 | 2025-06-25 21:47 | 15:58 | S/O | LILO work on Taragong grid. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-14 00:34 |  | Unserved Energy: |  | 0
Others :Nil
No interruption
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1900-02-10 05:14 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:June 2025
| Area | Previous Month (May' 2025) |  |  |  | Current Month (June '2025)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 29 | 22 | 108 | 159 | 14 | 9 | 56 | 79
2 | Dhaka (South) Grid Circle. | 50 | 11 | 41 | 102 | 25 | 14 | 22 | 61
3 | Chattogram Grid Circle. | 43 | 15 | 34 | 92 | 23 | 13 | 24 | 60
4 | Cumilla Grid Circle. | 41 | 16 | 54 | 111 | 18 | 22 | 45 | 85
5 | Khulna Grid Circle. | 42 | 12 | 94 | 148 | 22 | 8 | 70 | 100
6 | HVDC Grid Circle | 16 | 27 | 54 | 97 | 12 | 15 | 19 | 46
7 | Bogura Grid Circle. | 36 | 40 | 33 | 109 | 20 | 25 | 24 | 69
8 | Others
9 | Total | 257 | 143 | 418 | 818 | 134 | 106 | 260 | 500
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:June 2025
| Area | Previous Month (May' 2025) |  |  |  | Current Month (June '2025)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 240.98 | 746.53 | 3096.75 | 4084.26 | 71.77 | 177.8 | 834.61 | 1084.18
2 | Dhaka (South) Grid Circle. | 491.35 | 269.17 | 254.42 | 1014.93 | 2365.57 | 277.5 | - | 2643.07
3 | Chattogram Grid Circle. | 354.18 | 218.73 | 29 | 601.91 | 225.2 | 158.98 | 33.83 | 418.01
4 | Cumilla Grid Circle. | 225.3 | 715.08 | 1416.22 | 2356.6 | 121.66 | 485.2 | 1492.38 | 2099.24
5 | Khulna Grid Circle. | 998.32 | 258 | 1861.79 | 3118.11 | 241.11 | 42.1 | 732.15 | 1015.36
6 | HVDC Grid Circle | 765.88 | 935.08 | 917.03 | 2617.99 | 77.95 | 236.12 | 162.27 | 476.34
7 | Bogura Grid Circle. | 428.52 | 1217.52 | 190.83 | 1836.87 | 205.58 | 443.78 | 335.93 | 985.29
8 | Others
9 | Total | 3504.53 | 4360.11 | 7766.04 | 15630.66 | 3308.84 | 1821.48 | 3591.17 | 8721.49
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-29
QF-LDC-29
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:June 2025
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 6 | 10 | 16 | 1 | 2 | 13 | 1073.51
2 | Dhaka (South) | 5031.6 | 11 | - | 11 | 2 | 3 | 6 | 2631.2
3 | Chattogram | 2042 | 10 | 2 | 12 | 2 | 5 | 5 | 407.816
4 | Khulna | 2434 | 14 | 20 | 34 | 8 | 8 | 18 | 970.48
5 | HVDC | 5954.3 | 9 | 6 | 15 | 3 | 7 | 5 | 406.63
6 | Bogura | 3145.6 | 19 | 7 | 26 | 7 | 5 | 14 | 985.3
7 | Cumilla | 2981 | 12 | 23 | 35 | 4 | 6 | 25 | 1983.34
8 | Others | - | - | - | - | - | - | - | -
| Total | 30390.1 | [6 empty] | 8458.276
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.98%
4 | Khulna | 99.98%
5 | HVDC | 99.99%
6 | Bogura | 99.98%
7 | Cumilla | 99.99% | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:June 2025
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 1 | - | 1 | 1 | - | - | 10.67
2 | Dhaka (South) | 990.29 | - | 1 | - | 1 | 1 | - | - | 11.8667
3 | Chattogram | 917 | - | 1 | - | 1 | - | 1 | - | 10.2
4 | Khulna | 1238.4 | - | 3 | 1 | 4 | 2 |  | 2 | 44.88
5 | HVDC | 1325 | - | 1 | - | 1 | - | - | 1 | 69.7
6 | Bogura | 1803.3 | - | - | - | - | - | - | - | 0
7 | Cumilla | 1648.16 | - | 4 | 1 | 5 | - | 4 | 1 | 115.88
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 263.1967
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.99%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 100%
6 | Bogura | 100%
7 | Cumilla | 99.99% | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:June 2025
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2025-06-01 | 12 | - | 15 | 21hr 40 min | 2 | 1hr 58 min | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-32
QF-LDC-32
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:June 2025
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Bhaluka 132/33kV | 1 | 0:18 | 5.1
Dhamrai 132/33kV | 2 | 2:48 | 56
Bhaluka 132/33kV | 1 | 1:22 | 82
Mirzapur 132/33kV | 1 | 0:54 | 37.8
Sreepur 230/132/33kV | 1 | 1:27 | 58
Mirpur 132/33kV | 1 | 0:08 | 10.6667
Bhaluka 132/33kV | 1 | 0:42 | 10.5
Jamalpur 132/33kV | 3 | 2:16 | 44.1
Kishoreganj 132/33kV | 3 | 8:49 | 389.58
Manikganj 132/33kV | 3 | 8:00 | 127.93
Mymensingh 132/33kV | 1 | 3:51 | 77
Sreepur 230/132/33kV | 1 | 5:18 | 185.5
Ghorashal 230kV | 1 | 22:32 | 1847.7333
Madanganj 132/33kV | 3 | 25:15 | 249
Munshiganj 132/33kV | 1 | 1:36 | 83.2
Nawabganj 132/33kV | 1 | 0:04 | 0.43333
Rampura 230/132kV | 1 | 0:50 | 173.3333
Ghorashal 230kV | 1 | 1:36 | 32
Munshiganj 132/33kV | 1 | 2:30 | 187.5
Narshingdi 132/33kV | 1 | 1:27 | 58
Rampura 230/132kV | 1 | 0:08 | 11.8667
Bakulia 132/33kV | 1 | 3:09 | 25.2
Coxsbazar 132/33kV | 1 | 1:36 | 59.83
Halishahar 132/33kV | 1 | 0:59 | 24.5833
Madunaghat 132/33kV | 1 | 6:44 | 94.2667
Sholosohor 132/33kV | 1 | 0:23 | 11.1167
Dohazari 132/33kV | 2 | 3:15 | 134.5
Kalurghat 132/33kV | 2 | 1:53 | 24.48
Shikalbaha 230/132kV | 1 | 0:34 | 10.2
Chandraghona 132/33kV | 1 | 1:01 | 20.3333
Dohazari 132/33kV | 1 | 0:30 | 13.5
Brahmanbaria 132/33kV | 1 | 3:26 | 54.9333
Feni 132/33kV | 1 | 0:37 | 27.1333
Sylhet 132/33kV | 4 | 0:46 | 5.77
Brahmanbaria 132/33kV | 1 | 1:00 | 40
Chowmuhani 132/33kV | 3 | 10:14 | 336.33
Kachua 132/33kV | 2 | 2:56 | 48.2
Muradnagar 132/33kV | 1 | 0:30 | 7
Beanibazar 132/33kV | 1 | 1:54 | 17.1
Fenchuganj 230/132/33kV | 1 | 0:59 | 16.7167
Brahmanbaria 132/33kV | 1 | 0:46 | 53.6667
Chandpur 132/33kV | 2 | 7:25 | 121.04
Chauddagram 132/33kV | 1 | 2:37 | 73.2667
Chowmuhani 132/33kV | 3 | 4:40 | 132.5
Cumilla(S) 132/33kV | 2 | 5:54 | 180.73
Daudkandi 132/33kV | 3 | 11:01 | 330.5
Feni 132/33kV | 1 | 1:04 | 33.0667
Kulaura 132/33kV | 4 | 2:20 | 67.6667
Kulaura 132/33kV | 1 | 15:12 | 171.02
Ramganj 132/33kV | 2 | 1:48 | 18
Ramganj 132/33kV | 1 | 3:22 | 68.83
Shahjibazar 132/33kV | 1 | 2:28 | 177.6
Sunamganj 132/33kV | 1 | 0:35 | 8.75
Sylhet (South) | 1 | 11:16 | 45.0667
Sylhet 132/33kV | 1 | 1:38 | 35.9333
Chandpur 132/33kV | 1 | 2:22 | 28.4
Faridpur 132/33kV | 2 | 1:27 | 91.35
Gopalganj 132/33kV | 3 | 0:55 | 43.5
Kasba 132/33kV | 1 | 0:16 | 2.6667
Mongla 132/33kV | 1 | 1:14 | 27.1333
Noapara 132/33kV | 4 | 1:06 | 14.61
Rajbari 132/33kV | 1 | 0:32 | 9.0667
Satkhira 132/33kV | 1 | 0:38 | 40.5333
Barishal 230/132kV | 1 | 0:53 | 26.5
Satkhira 132/33kV | 2 | 0:42 | 12.25
Patuakhali 132/33kV | 1 | 1:12 | 15.6
Barishal 132/33kV | 1 | 1:22 | 41
Barishal 230/132kV | 6 | 1:49 | 18.1667
Barishal 230/132kV | 5 | 25:08 | 88.23
Borhanuddin 230/33kV | 1 | 2:27 | 220.5
Faridpur 132/33kV | 5 | 13:16 | 129.73
Goalpara 132/33kV | 4 | 2:47 | 33.3
Noapara 132/33kV | 3 | 4:45 | 79.18
Shariatpur 132/33kV | 1 | 3:30 | 105
Barguna 132/33kV | 4 | 3:30 | 51.78
Chuadanga 132/33kV | 1 | 2:28 | 123.3333
Ishurdi 132/33kV | 2 | 0:52 | 33.5
Jashore 132/33kV | 1 | 0:44 | 18.3333
Pabna 132/33kV | 1 | 0:33 | 19.25
Shahjadpur 132/33kV | 1 | 0:38 | 15.2
Magura 132/33kV | 1 | 0:41 | 69.7
Bheramara(GK) 132/33kV | 2 | 1:20 | 22.67
Ishurdi 132/33kV | 1 | 6:45 | 13.5
Magura 132/33kV | 3 | 6:58 | 126.1
Barapukuria 230/132/33kV | 3 | 3:56 | 187.37
Niamatpur 132/33kV | 2 | 0:46 | 8.7
Purbasadipur 132/33kV | 1 | 0:21 | 8.05
Saidpur 132/33kV | 1 | 0:03 | 0.8
Thakurgaon 132/33kV | 1 | 0:08 | 0.66667
Barapukuria 230/132/33kV | 1 | 3:21 | 234.5
Jaldhaka 132/33kV | 2 | 3:53 | 67.43
Mithapukur 132/33kV | 3 | 4:36 | 103.2
Palashbari 132/33kV | 1 | 1:19 | 14.4833
Palashbari 132/33kV | 2 | 0:52 | 4.3333
Panchagarh 132/33kV | 2 | 0:15 | 1.5
Saidpur 132/33kV | 2 | 0:32 | 10.6667
Sirajganj 132/33kV | 1 | 1:32 | 7.6667
Barapukuria 230/132/33kV | 1 | 1:22 | 47.8333
Bogura 132/33kV | 2 | 3:11 | 71.92
Natore 132/33kV | 3 | 6:38 | 194.93
Rajshahi 132/33kV | 1 | 1:25 | 21.25
| 172 | 331:23 | 8721.4567
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: June 2025
Sl No. | Sub-station | Load (MW) | Date & Time
1 | AKS | 24 | 2025-06-01 18:30
2 | AKSML | 152 | 2025-06-05 03:00
3 | Aftabnagar | 42 | 2025-06-22 13:00
4 | Agargaon | 144 | 2025-06-25 13:00
5 | Agrabad | 100 | 2025-06-24 19:00
6 | Amnura | 48 | 2025-06-05 15:00
7 | Ashuganj | 112.5 | 2025-06-13 02:00
8 | BSRM | 211 | 2025-06-19 09:00
9 | Bagerhat | 92 | 2025-06-08 23:00
10 | Bajitpur | 64 | 2025-06-21 21:00
11 | Bakulia | 103 | 2025-06-19 13:00
12 | Banani | 42.8 | 2025-06-30 13:00
13 | Bangabhaban | 21 | 2025-06-15 11:00
14 | Barapukuria | 79 | 2025-06-13 23:00
15 | Barguna | 28 | 2025-06-08 01:00
16 | Barishal | 126 | 2025-06-02 13:00
17 | Barishal-230 | 122 | 2025-06-14 23:00
18 | Baroaulia | 75 | 2025-06-25 13:00
19 | Baroirhat | 71 | 2025-06-07 22:00
20 | Bashundhara | 204 | 2025-06-30 13:00
21 | BashundharaCement | 17 | 2025-06-28 18:00
22 | Beanibazar | 98 | 2025-06-07 23:00
23 | Benapole | 83 | 2025-06-12 21:00
24 | Bhaluka | 163 | 2025-06-03 20:00
25 | Bhandaria | 67 | 2025-06-10 22:00
26 | Bhangura | 66 | 2025-06-16 05:00
27 | Bheramara(GK) | 76 | 2025-06-11 00:00
28 | Bhulta | 272 | 2025-06-24 01:00
29 | Bog-Sherpur | 72 | 2025-06-12 04:00
30 | Bogura | 187 | 2025-06-13 01:00
31 | Borhanuddin | 95 | 2025-06-30 00:00
32 | Brahmanbaria | 155 | 2025-06-07 22:00
33 | Cantonment | 170 | 2025-06-23 13:00
34 | Chandina | 26.66 | 2025-06-05 19:30
35 | Chandpur | 94 | 2025-06-07 23:00
36 | Chandraghona | 41 | 2025-06-07 23:00
37 | Chapai | 84 | 2025-06-14 23:00
38 | Charsaidpur | 50 | 2025-06-22 12:00
39 | Chauddagram | 87 | 2025-06-08 21:00
40 | Chhatak | 45 | 2025-06-30 00:00
41 | Chowmuhani | 250 | 2025-06-10 19:00
42 | Chuadanga | 131 | 2025-06-15 01:00
43 | Coxsbazar | 143 | 2025-06-26 19:00
44 | Cumilla(N) | 171 | 2025-06-21 23:00
45 | Cumilla(S) | 187 | 2025-06-29 13:00
46 | Daganbhuiyan | N/A | N/A
47 | Daudkandi | 162 | 2025-06-30 21:00
48 | Dhaka | 84 | 2025-06-30 13:00
49 | Dhamrai | 138 | 2025-06-02 14:00
50 | Dhanmondi | 168 | 2025-06-25 13:00
51 | Dohazari | 120 | 2025-06-13 21:00
52 | Faridpur | 180 | 2025-06-14 21:00
53 | Fatullah | 104 | 2025-06-24 16:00
54 | Fenchuganj | 51 | 2025-06-12 23:00
55 | Feni | 138 | 2025-06-07 23:00
56 | GPH | 90 | 2025-06-20 15:00
57 | Ghatail | 90 | 2025-06-09 21:00
58 | Ghorashal | 20 | 2025-06-04 11:00
59 | Ghorashal-230 | 103 | 2025-06-24 21:00
60 | Goalpara | 46 | 2025-06-14 00:00
61 | Gollamari | 112 | 2025-06-03 00:00
62 | Gopalganj | 125 | 2025-06-12 22:00
63 | Gulshan | 162 | 2025-06-24 14:00
64 | Halishahar | 107 | 2025-06-19 11:00
65 | HaripurSBU | 186 | 2025-06-02 16:00
66 | Hasnabad | 79 | 2025-06-23 23:00
67 | Hathazari | 90 | 2025-06-07 19:00
68 | Ishurdi | 92 | 2025-06-16 19:30
69 | Jaldhaka | 104 | 2025-06-11 00:00
70 | Jamalpur | 165 | 2025-06-10 22:00
71 | Jashore | 163 | 2025-06-14 21:00
72 | Jhenaidah | 150 | 2025-06-11 00:00
73 | Joydebpur | 154 | 2025-06-23 18:30
74 | Joypurhat | 80 | 2025-06-14 01:00
75 | Juldah | 18 | 2025-06-25 15:00
76 | KSRM | 30 | 2025-06-26 08:00
77 | Kabirpur | 266 | 2025-06-25 10:00
78 | Kachua | 115 | 2025-06-09 00:00
79 | Kallyanpur | 120 | 2025-06-16 18:00
80 | Kalurghat | 64 | 2025-06-21 13:00
81 | Kamrangirchar | 69 | 2025-06-29 13:00
82 | Kaptai | N/A | N/A
83 | Kasba | 44 | 2025-06-07 23:00
84 | Kazla | 107 | 2025-06-30 00:00
85 | Keranigonj | 96 | 2025-06-15 00:00
86 | Khagrachori | 36 | 2025-06-06 19:00
87 | Khulna | 85 | 2025-06-03 13:00
88 | Khulshi | 184 | 2025-06-19 12:00
89 | Kishoreganj | 162 | 2025-06-15 23:00
90 | Kodda | 317 | 2025-06-19 15:00
91 | Kulaura | 61 | 2025-06-29 19:00
92 | Kurigram | 90 | 2025-06-25 12:00
93 | Kushtia | 178 | 2025-06-02 20:00
94 | Lakshmipur | N/A | N/A
95 | Lalbag | 66 | 2025-06-23 00:00
96 | Lalmonirhat | 73 | 2025-06-15 20:00
97 | MI_Cement | 18.1 | 2025-06-03 17:00
98 | Madanganj | 48 | 2025-06-01 00:00
99 | Madaripur | 135 | 2025-06-10 00:00
100 | Madartek | 98 | 2025-06-26 00:00
101 | Madunaghat | 63 | 2025-06-09 23:00
102 | Magura | 75 | 2025-06-10 23:00
103 | Mahasthangarh | 106 | 2025-06-13 00:00
104 | Maijdee | N/A | N/A
105 | Manikganj | 154 | 2025-06-14 14:00
106 | Maniknagar | 90 | 2025-06-24 13:00
107 | Matarbari | 59 | 2025-06-24 23:00
108 | Matuail | 67 | 2025-06-24 15:00
109 | Millgate | 128 | 2025-06-28 12:00
110 | Mirpur | 129.5 | 2025-06-24 15:00
111 | Mirsorai | 16 | 2025-06-02 14:00
112 | Mirzapur | 47 | 2025-06-30 22:00
113 | Mithapukur | 80 | 2025-06-11 20:00
114 | Modern | N/A | N/A
115 | Mogbazar | 167.9 | 2025-06-25 15:00
116 | Mongla | 47 | 2025-06-19 16:00
117 | Motijheel | 45 | 2025-06-30 19:00
118 | Muktagacha | 46 | 2025-06-10 22:00
119 | Munshiganj | 128 | 2025-06-10 00:00
120 | Muradnagar | 37 | 2025-06-07 22:00
121 | Mymensingh | 226 | 2025-06-13 22:00
122 | Naogaon | 169 | 2025-06-14 00:00
123 | Narail | 68 | 2025-06-10 21:00
124 | Narinda | 98 | 2025-06-23 16:00
125 | Narshingdi | 200 | 2025-06-25 23:00
126 | Natore | 183 | 2025-06-10 23:00
127 | Nawabganj | 81.4 | 2025-06-02 00:00
128 | Netrakona | 162 | 2025-06-10 21:00
129 | New | 92.2 | 2025-06-26 12:00
130 | Niamatpur | 92 | 2025-06-13 00:00
131 | Noapara | 52 | 2025-06-02 20:00
132 | PHP | 10 | 2025-06-14 13:00
133 | Pabna | 135 | 2025-06-23 21:00
134 | Palashbari | 136 | 2025-06-17 01:00
135 | Panchagarh | 69 | 2025-06-13 20:00
136 | Patuakhali | 97.2 | 2025-06-14 00:00
137 | Payra | 42 | 2025-06-10 23:00
138 | Postogola | 63 | 2025-06-24 13:00
139 | Purbachal | 23 | 2025-06-24 21:00
140 | Purbasadipur | 152 | 2025-06-23 21:00
141 | Rahanpur | 39 | 2025-06-09 23:00
142 | Rahim | 53 | 2025-06-19 16:00
143 | Rajbari | 92 | 2025-06-10 22:00
144 | Rajendrapur | 143 | 2025-06-01 09:00
145 | Rajshahi | 128 | 2025-06-14 01:00
146 | Rajshahi-230 | 114 | 2025-06-14 21:00
147 | Ramganj | 126 | 2025-06-10 19:30
148 | Rampur | 55 | 2025-06-25 14:00
149 | Rangamati | 20 | 2025-06-12 19:00
150 | Rangpur | 171 | 2025-06-15 19:30
151 | Ruppur | 9.4 | 2025-06-30 06:00
152 | SSM | 16 | 2025-06-04 04:00
153 | Saidpur | 124 | 2025-06-26 21:00
154 | Satkhira | 160 | 2025-06-11 00:00
155 | Satmasjid | 106 | 2025-06-23 16:00
156 | Savar | 242 | 2025-06-26 16:00
157 | SevenRings | 35.38 | 2025-06-25 19:00
158 | ShahCement | 39 | 2025-06-19 03:00
159 | Shahjadpur | 94 | 2025-06-02 19:30
160 | Shahjibazar | 138 | 2025-06-22 23:00
161 | Shahmirpur | 67 | 2025-06-16 00:00
162 | Shariatpur | 108 | 2025-06-09 22:00
163 | Sherpur | 186 | 2025-06-10 23:00
164 | Shikalbaha | 28 | 2025-06-01 00:00
165 | Shitalakhya | 89.9 | 2025-06-01 11:00
166 | Sholosohor | 49 | 2025-06-24 19:00
167 | Shyampur | 182 | 2025-06-01 10:00
168 | Siddhirganj | 137 | 2025-06-24 13:00
169 | Sirajganj | 122 | 2025-06-02 21:00
170 | Sonargaon | 169 | 2025-06-04 03:00
171 | Sreemongol | 94 | 2025-06-25 23:00
172 | Sreepur | 109 | 2025-06-02 19:30
173 | Srinagar | 58.71 | 2025-06-29 22:00
174 | Sunamganj | 66 | 2025-06-14 19:30
175 | Sylhet | 56 | 2025-06-28 00:00
176 | Sylhet-132 | 161 | 2025-06-28 15:00
177 | TK | 59 | 2025-06-05 04:00
178 | Tangail | 198 | 2025-06-29 19:30
179 | Taraganj | N/A | N/A
180 | Thakurgaon | 127 | 2025-06-13 20:00
181 | Tongi | 173 | 2025-06-28 12:00
182 | Ullahpara | 44 | 2025-06-02 19:30
183 | Ullon | 57 | 2025-06-14 00:00
184 | Uttara | 105 | 2025-06-16 13:00
185 | UttaraNew | 76 | 2025-06-08 09:00
186 | Zigatola | 96 | 2025-06-23 01:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID BANGLADESH PLC. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: June 2025
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 5761.81 | 2025-06-24 | 15:00
Chattogram | 1538 | 2025-06-25 | 0:00
Cumilla | 1563.22 | 2025-06-14 | 23:00
Mymensingh | 1346 | 2025-06-13 | 21:00
Sylhet | 704 | 2025-06-14 | 23:00
Khulna | 2021 | 2025-06-14 | 0:00
Barishal | 553.2 | 2025-06-14 | 0:00
Rajshahi | 1752 | 2025-06-14 | 1:00
Rangpur | 1065 | 2025-06-15 | 21:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: June 2025
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar | 400 | 408 | 2025-06-07 13:00 | 282 | 2025-06-21 19:30
2 | Ashuganj | 400 | N/A | N/A | N/A | N/A
3 | Bhulta | 400 | 416 | 2025-06-07 05:00 | 359 | 2025-06-26 10:00
4 | Bibiana | 400 | 396 | 2025-06-03 04:00 | 378 | 2025-06-19 02:00
5 | BIPTC | 400 | 408 | 2025-06-08 08:00 | 385 | 2025-06-08 23:00
6 | Bogura | 400 | 408 | 2025-06-07 09:00 | 366 | 2025-06-17 21:00
7 | Gopalganj | 400 | 409 | 2025-06-04 05:00 | 375 | 2025-06-25 23:00
8 | Kaliakoir | 400 | 392 | 2025-06-10 22:00 | 355 | 2025-06-26 11:00
9 | Madunaghat | 400 | 405 | 2025-06-07 08:00 | 384 | 2025-06-19 02:00
10 | Meghnaghat | 400 | 405 | 2025-06-07 10:00 | 357 | 2025-06-26 01:00
11 | Payra | 400 | 421 | 2025-06-04 05:00 | 404 | 2025-06-02 00:00
12 | Rahanpur | 400 | 417 | 2025-06-07 08:00 | 382 | 2025-06-02 13:00
13 | Rampal | 400 | 411 | 2025-06-04 05:00 | 383 | 2025-06-25 23:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon | 230 | 266 | 2025-06-08 09:00 | 210 | 2025-06-26 11:00
2 | AKSML | 230 | 236 | 2025-06-25 19:30 | 221 | 2025-06-21 12:00
3 | Aminbazar | 230 | 238 | 2025-06-07 08:00 | 221 | 2025-06-01
4 | Ashuganj | 230 | 241 | 2025-06-08 08:00 | 218 | 2025-06-20 12:00
5 | Ashuganj-400 | 230 | N/A | N/A | N/A | N/A
6 | Baghabari | 230 | 236 | 2025-06-06 09:00 | 222 | 2025-06-15
7 | Barapukuria | 230 | 233 | 2025-06-03 00:00 | 212 | 2025-06-11 23:00
8 | Barapukuria-230 | 230 | N/A | N/A | N/A | N/A
9 | Barishal | 230 | 244 | 2025-06-04 05:00 | 215 | 2025-06-15
10 | Bheramara | 230 | 235 | 2025-06-03 01:00 | 220 | 2025-06-15 00:00
11 | Bhulta | 230 | 243 | 2025-06-07 05:00 | 204 | 2025-06-26 11:00
12 | Bibiana | 230 | 234 | 2025-06-06 07:00 | 219 | 2025-06-19
13 | BIPTC | 230 | 237 | 2025-06-09 08:00 | 213 | 2025-06-26 23:00
14 | Bogura | 230 | 238 | 2025-06-07 08:00 | 218 | 2025-06-02 13:00
15 | Bogura-400 | 230 | 238 | 2025-06-07 09:00 | 217 | 2025-06-02 13:00
16 | Borhanuddin | 230 | 248 | 2025-06-03 04:00 | 218 | 2025-06-15 00:00
17 | BSRM | 230 | 235 | 2025-06-07 08:00 | 217 | 2025-06-19 09:00
18 | Cumilla(N) | 230 | 237 | 2025-06-11 05:00 | 212 | 2025-06-26 10:00
19 | Faridpur | 230 | 240 | 2025-06-04 05:00 | 213 | 2025-06-26
20 | Fenchuganj | 230 | 238 | 2025-06-04 04:00 | 217 | 2025-06-20 01:00
21 | Ghorashal | 230 | 244 | 2025-06-11 01:00 | 220 | 2025-06-16 15:00
22 | Ghorashal-230 | 230 | 257 | 2025-06-08 04:00 | 220 | 2025-06-16 15:00
23 | Gopalganj | 230 | 243 | 2025-06-04 05:00 | 216 | 2025-06-26
24 | GPH | 230 | 235 | 2025-06-07 08:00 | 221 | 2025-06-19 08:00
25 | Haripur | 230 | 234 | 2025-06-07 08:00 | 211 | 2025-06-24 12:00
26 | Hasnabad | 230 | 235 | 2025-06-06 18:00 | 211 | 2025-06-24 12:00
27 | Hathazari | 230 | 237 | 2025-06-03 08:00 | 222 | 2025-06-19 08:00
28 | Ishurdi | 230 | 237 | 2025-06-09 08:00 | 220 | 2025-06-25 00:00
29 | Jhenaidah | 230 | 234 | 2025-06-03 06:00 | 208 | 2025-06-15 00:00
30 | Kaliakoir | 230 | 246 | 2025-06-10 22:00 | 215 | 2025-06-26 11:00
31 | Keranigonj | 230 | 235 | 2025-06-07 08:00 | 209 | 2025-06-26 11:00
32 | Khulna(S) | 230 | 235 | 2025-06-03 04:00 | 212 | 2025-06-11 23:00
33 | Madunaghat | 230 | 238 | 2025-06-03 07:00 | 224 | 2025-06-19 08:00
34 | Madunaghat-400 | 230 | 238 | 2025-06-03 07:00 | 224 | 2025-06-19 08:00
35 | Maniknagar | 230 | 234 | 2025-06-07 08:00 | 208 | 2025-06-26 11:00
36 | Meghnaghat | 230 | 241 | 2025-06-07 08:00 | 220 | 2025-06-24 11:00
37 | Meghnaghat-400 | 230 | 235 | 2025-06-07 08:00 | 214 | 2025-06-25 23:00
38 | Mirsorai | 230 | 236 | 2025-06-07 08:00 | 218 | 2025-06-19 09:00
39 | Rajshahi | 230 | 236 | 2025-06-01 18:30 | 218 | 2025-06-11 23:00
40 | Rampal | 230 | 235 | 2025-06-04 05:00 | 213 | 2025-06-15 00:00
41 | Rampur | 230 | N/A | N/A | N/A | N/A
42 | Rampura | 230 | 242 | 2025-06-07 05:00 | 202 | 2025-06-26 10:00
43 | Shikalbaha | 230 | 236 | 2025-06-03 06:00 | 220 | 2025-06-09 07:00
44 | Shyampur | 230 | 235 | 2025-06-07 08:00 | 211 | 2025-06-26 11:00
45 | Siddhirganj | 230 | 234 | 2025-06-06 15:00 | 211 | 2025-06-26 11:00
46 | Sirajgonj | 230 | 269 | 2025-06-29 06:00 | 230 | 2025-06-01 00:00
47 | Sreepur | 230 | 237 | 2025-06-21 19:00 | 214 | 2025-06-28 19:30
48 | Tongi | 230 | 241 | 2025-06-08 18:00 | 210 | 2025-06-28 15:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar | 132 | 141 | 2025-06-30 06:00 | 119 | 2025-06-19 11:00
2 | Agargaon | 132 | 140 | 2025-06-03 06:00 | 121 | 2025-06-26 11:00
3 | Agrabad | 132 | 137 | 2025-06-03 07:00 | 124 | 2025-06-29 15:00
4 | AKS | 132 | 134 | 2025-06-03 07:00 | 125 | 2025-06-17 15:00
5 | Aminbazar | 132 | 139 | 2025-06-06 05:00 | 122 | 2025-06-15 15:00
6 | Amnura | 132 | 140 | 2025-06-01 18:30 | 120 | 2025-06-02 20:00
7 | Ashuganj | 132 | 143 | 2025-06-10 21:00 | 130 | 2025-06-26 10:00
8 | Bagerhat | 132 | 139 | 2025-06-04 03:00 | 115 | 2025-06-09 23:00
9 | Bajitpur | 132 | 135 | 2025-06-02 08:00 | 122 | 2025-06-12 23:00
10 | Bakulia | 132 | 138 | 2025-06-03 06:00 | 126 | 2025-06-29 15:00
11 | Banani | 132 | 141 | 2025-06-30 06:00 | 119 | 2025-06-19 11:00
12 | Bangabhaban | 132 | 139 | 2025-06-05 17:00 | 119 | 2025-06-19 09:00
13 | Barapukuria | 132 | 140 | 2025-06-02 23:00 | 122 | 2025-06-15 23:00
14 | Barguna | 132 | 138 | 2025-06-01 00:00 | 127 | 2025-06-01 23:00
0 | Barishal | 132 | 138 | 2025-06-03 03:00 | 121 | 2025-06-14 21:00
16 | Barishal-230 | 132 | 138 | 2025-06-18 06:00 | 121 | 2025-06-14 21:00
17 | Baroaulia | 132 | 136 | 2025-06-03 06:00 | 126 | 2025-06-29 13:00
18 | Baroirhat | 132 | 134 | 2025-06-10 19:30 | 116 | 2025-06-26 02:00
19 | Bashundhara | 132 | 141 | 2025-06-03 04:00 | 117 | 2025-06-28 14:00
20 | BashundharaCement | 132 | 138 | 2025-06-07 09:00 | 115 | 2025-06-18 13:00
21 | Beanibazar | 132 | 135 | 2025-06-01 05:00 | 118 | 2025-06-12 01:00
22 | Benapole | 132 | 138 | 2025-06-03 02:00 | 112 | 2025-06-11 23:00
23 | Bhaluka | 132 | 135 | 2025-06-02 07:00 | 119 | 2025-06-28 19:30
24 | Bhandaria | 132 | 136 | 2025-06-03 04:00 | 110 | 2025-06-14 21:00
25 | Bhangura | 132 | 136 | 2025-06-03 06:00 | 125 | 2025-06-11 23:00
26 | Bheramara | 132 | 139 | 2025-06-07 08:00 | 124 | 2025-06-15 00:00
27 | Bheramara(GK) | 132 | 163 | 2025-06-02 01:00 | 124 | 2025-06-15 00:00
28 | Bhulta | 132 | 132 | 2025-06-07 09:00 | 113 | 2025-06-26 11:00
29 | Bog-Sherpur | 132 | 139 | 2025-06-02 05:00 | 123 | 2025-06-15 00:00
30 | Bogura | 132 | 142 | 2025-06-03 00:00 | 126 | 2025-06-12 01:00
31 | Bogura-230 | 132 | 141 | 2025-06-02 05:00 | 126 | 2025-06-12 00:00
32 | Brahmanbaria | 132 | 139 | 2025-06-10 21:00 | 119 | 2025-06-26 11:00
33 | Cantonment | 132 | 139 | 2025-06-03 03:00 | 120 | 2025-06-26 11:00
34 | Chandina | 132 | 136 | 2025-06-10 21:00 | 120 | 2025-06-25 23:00
35 | Chandpur | 132 | 140 | 2025-06-10 20:00 | 140 | 2025-06-10 20:00
36 | Chandraghona | 132 | 136 | 2025-06-03 07:00 | 128 | 2025-06-13 13:00
37 | Chapai | 132 | 138 | 2025-06-30 17:00 | 120 | 2025-06-25 00:00
39 | Charsaidpur | 132 | 139 | 2025-06-07 10:00 | 121 | 2025-06-24 10:00
40 | Chauddagram | 132 | 134 | 2025-06-10 20:00 | 115 | 2025-06-12 22:00
41 | Chhatak | 132 | 132 | 2025-06-01 04:00 | 115 | 2025-06-11 19:00
42 | Chowmuhani | 132 | 130 | 2025-06-10 20:00 | 104 | 2025-06-28 13:00
43 | Chuadanga | 132 | 137 | 2025-06-19 05:00 | 115 | 2025-06-12 22:00
44 | Coxsbazar | 132 | 135 | 2025-06-03 09:00 | 109 | 2025-06-08 23:00
45 | Cumilla(N) | 132 | 137 | 2025-06-10 20:00 | 120 | 2025-06-23 23:00
46 | Cumilla(S) | 132 | 139 | 2025-06-10 15:00 | 118 | 2025-06-29 15:00
47 | Daganbhuiyan | 132 | N/A | N/A | N/A | N/A
48 | Daudkandi | 132 | 137 | 2025-06-10 21:00 | 114 | 2025-06-29 15:00
49 | Dhaka | 132 | 138 | 2025-06-06 06:00 | 120 | 2025-06-19 11:00
50 | Dhamrai | 132 | 142 | 2025-06-10 23:00 | 120 | 2025-06-26 11:00
51 | Dhanmondi | 132 | 141 | 2025-06-30 05:00 | 119.5 | 2025-06-19 11:00
52 | Dohazari | 132 | 136 | 2025-06-03 08:00 | 119 | 2025-06-13 13:00
53 | Faridpur | 132 | 140 | 2025-06-04 05:00 | 125 | 2025-06-15
54 | Fatullah | 132 | 139 | 2025-06-07 08:00 | 121 | 2025-06-24 11:00
55 | Fenchuganj | 132 | 139 | 2025-06-03 06:00 | 128 | 2025-06-12 01:00
56 | Feni | 132 | 132 | 2025-06-10 20:00 | 114 | 2025-06-26 00:00
57 | Ghatail | 132 | 140 | 2025-06-03 01:00 | 114 | 2025-06-15 00:00
58 | Ghorashal | 132 | 143 | 2025-06-08 18:00 | 125 | 2025-06-26 11:00
59 | Goalpara | 132 | 142 | 2025-06-03 03:00 | 120 | 2025-06-09 23:00
60 | Gollamari | 132 | 140 | 2025-06-03 03:00 | 123 | 2025-06-15 00:00
61 | Gopalganj | 132 | 139 | 2025-06-03 03:00 | 123 | 2025-06-15 00:00
62 | Gopalganj-400 | 132 | 163 | 2025-06-03 09:00 | 128 | 2025-06-26 00:00
63 | Gulshan | 132 | 139 | 2025-06-15 06:00 | 120 | 2025-06-19 11:00
64 | Halishahar | 132 | 137 | 2025-06-03 07:00 | 120 | 2025-06-30 16:00
65 | Haripur | 132 | 138 | 2025-06-07 08:00 | 122 | 2025-06-24 10:00
66 | HaripurSBU | 132 | 138 | 2025-06-07 08:00 | 114 | 2025-06-22 22:00
67 | Hasnabad | 132 | 140 | 2025-06-07 10:00 | 123 | 2025-06-24 13:00
68 | Hathazari | 132 | 138 | 2025-06-03 09:00 | 138 | 2025-06-03 09:00
69 | Ishurdi | 132 | 139 | 2025-06-02 05:00 | 127 | 2025-06-15 00:00
70 | Jaldhaka | 132 | 138 | 2025-06-02 23:00 | 111 | 2025-06-05 23:00
71 | Jamalpur | 132 | 142 | 2025-06-03 01:00 | 113 | 2025-06-06 22:00
72 | Jashore | 132 | 140 | 2025-06-19 05:00 | 115 | 2025-06-02 19:30
73 | Jhenaidah | 132 | 139 | 2025-06-03 05:00 | 110 | 2025-06-15 00:00
74 | Jhenaidah-230 | 132 | 140 | 2025-06-19 05:00 | 119 | 2025-06-15 00:00
75 | Joydebpur | 132 | 144 | 2025-06-08 18:30 | 121 | 2025-06-28 00:00
76 | Joypurhat | 132 | 137 | 2025-06-07 08:00 | 113 | 2025-06-12 00:00
77 | Juldah | 132 | 138 | 2025-06-19 21:00 | 127 | 2025-06-17 12:00
78 | Kabirpur | 132 | 142 | 2025-06-10 23:00 | 117 | 2025-06-26 11:00
79 | Kachua | 132 | 136 | 2025-06-10 21:00 | 115 | 2025-06-20 10:00
80 | Kaliakoir | 132 | 143 | 2025-06-06 14:00 | 123 | 2025-06-26 10:00
81 | Kallyanpur | 132 | 139 | 2025-06-06 03:00 | 122 | 2025-06-15 13:00
82 | Kalurghat | 132 | 134 | 2025-06-22 01:00 | 126 | 2025-06-26 11:00
83 | Kamrangirchar | 132 | 139 | 2025-06-05 16:00 | 120 | 2025-06-23 11:00
84 | Kaptai | 132 | N/A | N/A | N/A | N/A
85 | Kasba | 132 | 136 | 2025-06-10 21:00 | 116 | 2025-06-29 15:00
86 | Kazla | 132 | 139 | 2025-06-05 18:00 | 119 | 2025-06-18 13:00
87 | Keranigonj | 132 | 139 | 2025-06-05 16:00 | 122 | 2025-06-21 12:00
88 | Khagrachori | 132 | 136 | 2025-06-03 07:00 | 126 | 2025-06-13 13:00
89 | Khulna | 132 | 139 | 2025-06-03 03:00 | 121 | 2025-06-23 23:00
90 | Khulna(S) | 132 | 142 | 2025-06-09 06:00 | 123 | 2025-06-13 00:00
91 | Khulshi | 132 | 136 | 2025-06-03 07:00 | 124 | 2025-06-29 15:00
92 | Kishoreganj | 132 | 135 | 2025-06-02 07:00 | 115 | 2025-06-13 19:30
93 | Kodda | 132 | 145 | 2025-06-10 22:00 | 119 | 2025-06-16 15:00
94 | KSRM | 132 | 137 | 2025-06-03 05:00 | 127 | 2025-06-17 14:00
95 | Kulaura | 132 | 139 | 2025-06-03 04:00 | 127 | 2025-06-24 22:00
96 | Kurigram | 132 | 140 | 2025-06-03 01:00 | 111 | 2025-06-12 01:00
97 | Kushtia | 132 | 136 | 2025-06-19 04:00 | 116 | 2025-06-15
98 | Lakshmipur | 132 | N/A | N/A | N/A | N/A
99 | Lalbag | 132 | 140 | 2025-06-07 08:00 | 122 | 2025-06-21 12:00
100 | Lalmonirhat | 132 | 137 | 2025-06-03 01:00 | 114 | 2025-06-12 00:00
101 | Madanganj | 132 | 138 | 2025-06-07 09:00 | 120 | 2025-06-24 11:00
102 | Madaripur | 132 | 138 | 2025-06-03 07:00 | 127 | 2025-06-01 00:00
103 | Madartek | 132 | 140 | 2025-06-30 06:00 | 140 | 2025-06-30 06:00
104 | Madunaghat | 132 | 137 | 2025-06-03 08:00 | 126 | 2025-06-19 07:00
105 | Magura | 132 | 137 | 2025-06-03 04:00 | 117 | 2025-06-15 00:00
106 | Mahasthangarh | 132 | 140 | 2025-06-03 00:00 | 120 | 2025-06-12 01:00
107 | Maijdee | 132 | N/A | N/A | N/A | N/A
108 | Manikganj | 132 | 137 | 2025-06-06 14:00 | 118 | 2025-06-13 19:30
109 | Maniknagar | 132 | 139 | 2025-06-05 17:00 | 119 | 2025-06-19 09:00
110 | Matarbari | 132 | 135 | 2025-06-03 09:00 | 107 | 2025-06-13 13:00
111 | Matuail | 132 | 138 | 2025-06-07 08:00 | 121 | 2025-06-24 12:00
112 | Millgate | 132 | 141 | 2025-06-03 03:00 | 118 | 2025-06-26 11:00
113 | Mirpur | 132 | 138 | 2025-06-06 07:00 | 119 | 2025-06-16 10:00
114 | Mirzapur | 132 | 140 | 2025-06-10 23:00 | 122 | 2025-06-15 00:00
115 | Mithapukur | 132 | 139 | 2025-06-03 01:00 | 115 | 2025-06-28 23:00
116 | MI_Cement | 132 | 138 | 2025-06-07 07:00 | 121 | 2025-06-24 10:00
117 | Modern | 132 | N/A | N/A | N/A | N/A
118 | Mogbazar | 132 | 152 | 2025-06-23 13:00 | 120 | 2025-06-26 11:00
119 | Mongla | 132 | 140 | 2025-06-03 03:00 | 116 | 2025-06-04 23:00
120 | Motijheel | 132 | 139 | 2025-06-05 17:00 | 119 | 2025-06-19 09:00
121 | Muktagacha | 132 | 160 | 2025-06-19 04:00 | 115 | 2025-06-15 00:00
122 | Munshiganj | 132 | 137 | 2025-06-07 07:00 | 120 | 2025-06-24 11:00
123 | Muradnagar | 132 | 137 | 2025-06-10 21:00 | 117 | 2025-06-29 15:00
124 | Mymensingh | 132 | 147 | 2025-06-03 20:00 | 115 | 2025-06-15
125 | Naogaon | 132 | 140 | 2025-06-02 05:00 | 117 | 2025-06-11 23:00
126 | Narail | 132 | 150 | 2025-06-13 21:00 | 115 | 2025-06-15 00:00
127 | Narinda | 132 | 10 | 2025-06-20 09:00 | 0 | 2025-06-01
128 | Narshingdi | 132 | 145 | 2025-06-10 22:00 | 112 | 2025-06-26 10:00
129 | Natore | 132 | 137 | 2025-06-03 01:00 | 122 | 2025-06-15
130 | Nawabganj | 132 | 139 | 2025-06-03 03:00 | 120 | 2025-06-21 12:00
131 | Netrakona | 132 | 133 | 2025-06-02 07:00 | 107 | 2025-06-13 00:00
132 | New | 132 | 142 | 2025-06-03 03:00 | 119 | 2025-06-26 11:00
133 | Niamatpur | 132 | 138 | 2025-06-07 08:00 | 125 | 2025-06-03 14:00
134 | Noapara | 132 | 140 | 2025-06-03 03:00 | 118 | 2025-06-11 23:00
135 | Pabna | 132 | 137 | 2025-06-07 08:00 | 122 | 2025-06-15 00:00
136 | Palashbari | 132 | 138 | 2025-06-03 00:00 | 115 | 2025-06-12 00:00
137 | Panchagarh | 132 | 140 | 2025-06-02 22:00 | 114 | 2025-06-13
139 | Patuakhali | 132 | 138 | 2025-06-01 00:00 | 127 | 2025-06-11 23:00
140 | Payra | 132 | 138 | 2025-06-03 04:00 | 131 | 2025-06-10 00:00
141 | PHP | 132 | 134 | 2025-06-10 20:00 | 115 | 2025-06-24 23:00
142 | Postogola | 132 | 140 | 2025-06-07 09:00 | 123 | 2025-06-24 11:00
143 | Purbachal | 132 | 141 | 2025-06-30 06:00 | 118 | 2025-06-26 11:00
144 | Purbasadipur | 132 | 136 | 2025-06-02 23:00 | 113 | 2025-06-13 00:00
145 | Rahanpur | 132 | 139 | 2025-06-07 08:00 | 126 | 2025-06-03 15:00
146 | Rahanpur-400 | 132 | 139 | 2025-06-07 08:00 | 126 | 2025-06-02 13:00
147 | Rahim | 132 | 138 | 2025-06-07 08:00 | 122 | 2025-06-24 12:00
148 | Rajbari | 132 | 140 | 2025-06-04 05:00 | 123 | 2025-06-15 00:00
149 | Rajendrapur | 132 | 146 | 2025-06-10 23:00 | 118 | 2025-06-28 19:30
150 | Rajshahi | 132 | 137 | 2025-06-07 08:00 | 120 | 2025-06-16 15:00
151 | Rajshahi-230 | 132 | 137 | 2025-06-02 05:00 | 112 | 2025-06-02 13:00
152 | Ramganj | 132 | 133 | 2025-06-19 02:00 | 106 | 2025-06-30 10:00
153 | Rampur | 132 | 136 | 2025-06-03 07:00 | 125 | 2025-06-29 15:00
154 | Rampura | 132 | 140 | 2025-06-30 06:00 | 120 | 2025-06-26 10:00
155 | Rangamati | 132 | 136 | 2025-06-03 01:00 | 127 | 2025-06-13 13:00
156 | Rangpur | 132 | 140 | 2025-06-03 00:00 | 115 | 2025-06-12 00:00
157 | Ruppur | 132 | 139 | 2025-06-05 09:00 | 126 | 2025-06-14 00:00
158 | Saidpur | 132 | 139 | 2025-06-03 00:00 | 114 | 2025-06-12 23:00
159 | Satkhira | 132 | 139 | 2025-06-04 05:00 | 113 | 2025-06-09 23:00
160 | Satmasjid | 132 | 139 | 2025-06-03 05:00 | 121 | 2025-06-26 11:00
161 | Savar | 132 | 138 | 2025-06-06 07:00 | 119 | 2025-06-16 11:00
162 | SevenRings | 132 | 144 | 2025-06-07 05:00 | 124 | 2025-06-28 19:30
163 | ShahCement | 132 | 139 | 2025-06-07 10:00 | 121 | 2025-06-24 10:00
164 | Shahjadpur | 132 | 140 | 2025-06-11 00:00 | 130 | 2025-06-11 20:00
165 | Shahjibazar | 132 | 140 | 2025-06-10 21:00 | 120 | 2025-06-13 03:00
166 | Shahmirpur | 132 | 137 | 2025-06-03 07:00 | 127 | 2025-06-09 14:00
167 | Shariatpur | 132 | 138 | 2025-06-03 04:00 | 123 | 2025-06-14 21:00
168 | Sherpur | 132 | 142 | 2025-06-03 01:00 | 108 | 2025-06-07 17:00
169 | Shikalbaha | 132 | 127 | 2025-06-03 07:00 | 116 | 2025-06-13 13:00
170 | Shikalbaha-230 | 132 | 138 | 2025-06-03 07:00 | 128 | 2025-06-17 11:00
171 | Shitalakhya | 132 | 138 | 2025-06-07 07:00 | 121 | 2025-06-24 10:00
172 | Sholosohor | 132 | 136 | 2025-06-19 21:00 | 125 | 2025-06-29 15:00
173 | Shyampur | 132 | 138 | 2025-06-17 07:00 | 119 | 2025-06-24 12:00
174 | Shyampur-230 | 132 | 138 | 2025-06-06 18:00 | 120 | 2025-06-24 12:00
175 | Siddhirganj | 132 | 138 | 2025-06-07 05:00 | 122 | 2025-06-24 11:00
176 | Sirajganj | 132 | 137 | 2025-06-03 00:00 | 122 | 2025-06-11 22:00
177 | Sonargaon | 132 | 139 | 2025-06-10 21:00 | 119 | 2025-06-24 10:00
178 | Sreemongol | 132 | 139 | 2025-06-10 21:00 | 117 | 2025-06-13 19:00
179 | Sreepur | 132 | 137 | 2025-06-02 07:00 | 122 | 2025-06-28 19:30
180 | Srinagar | 132 | 160 | 2025-06-03 00:00 | 121 | 2025-06-21 12:00
181 | SSM | 132 | 140 | 2025-06-05 06:00 | 128 | 2025-06-03 11:00
182 | Sunamganj | 132 | 132 | 2025-06-03 04:00 | 111 | 2025-06-12 01:00
183 | Sylhet | 132 | 135 | 2025-06-03 06:00 | 118 | 2025-06-12 01:00
184 | Sylhet-132 | 132 | 133 | 2025-06-01 07:00 | 120 | 2025-06-12 00:00
185 | Tangail | 132 | 139 | 2025-06-03 01:00 | 118 | 2025-06-11 19:00
186 | Taraganj | 132 | N/A | N/A | N/A | N/A
187 | Thakurgaon | 132 | 139 | 2025-06-26 18:00 | 112 | 2025-06-22 12:00
188 | TK | 132 | 135 | 2025-06-03 07:00 | 127 | 2025-06-09 13:00
189 | Tongi | 132 | 142 | 2025-06-03 03:00 | 124 | 2025-06-16 15:00
190 | Ullahpara | 132 | 138 | 2025-06-21 01:00 | 126 | 2025-06-26 22:00
191 | Ullon | 132 | 140 | 2025-06-30 06:00 | 119 | 2025-06-26 11:00
192 | Uttara | 132 | 138 | 2025-06-06 06:00 | 119 | 2025-06-15 15:00
193 | UttaraNew | 132 | 137 | 2025-06-06 06:00 | 119 | 2025-06-28 15:00
194 | Zigatola | 132 | 140 | 2025-06-07 08:00 | 124 | 2025-06-11 23:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-36
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month: June 2025
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Aminbazar 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 28-06-2025 | 16:00 | 401 | 189 | 85.2515
Aminbazar 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 28-06-2025 | 16:00 | 401 | 189 | 85.2515
Aminbazar 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 520 | 28-06-2025 | 16:00 | 401 | 189 | 85.2515
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 325 | 01-06-2025 | 00:00 | 0 | 0 | 0
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 26-06-2025 | 16:00 | 211 | 89 | 44.0389
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 26-06-2025 | 16:00 | 211 | 89 | 44.0389
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | 520 | 12-06-2025 | 01:00 | 266 | 95 | 54.3183
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | 520 | 14-06-2025 | 23:00 | 265 | 60 | 52.2515
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 750 | 21-06-2025 | 01:00 | 579 | 66 | 77.6999
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 750 | 23-06-2025 | 16:00 | 481 | 123 | 66.197
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 750 | 21-06-2025 | 01:00 | 578 | 66 | 77.5675
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | 325 | 14-06-2025 | 22:00 | 213 | 48 | 67.182
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | 325 | 14-06-2025 | 22:00 | 213 | 48 | 67.182
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | 325 | 14-06-2025 | 22:00 | 213 | 48 | 67.182
Gopalganj 400/230kV Grid Sub-Station | ATR-04 | 400/230 | 750 | 14-06-2025 | 22:00 | 367 | 94 | 50.5129
Gopalganj 400/230kV Grid Sub-Station | ATR-05 | 400/230 | 750 | --- | --- | --- | --- | ---
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 520 | 13-06-2025 | 19:30 | 458 | 104 | 90.3191
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 520 | 13-06-2025 | 19:30 | 458 | 104 | 90.3191
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 325 | 21-06-2025 | 19:30 | 299 | 44 | 92.9908
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 325 | 21-06-2025 | 19:30 | 299 | 44 | 92.9908
Madunaghat 400/230kV Grid Sub-Station | ATR-1 7006T | 400/230 | 750 | 15-06-2025 | 10:00 | 500 | 198 | 71.7036
Madunaghat 400/230kV Grid Sub-Station | ATR-2 7106T | 400/230 | 750 | 15-06-2025 | 14:00 | 498 | 197 | 71.4066
Madunaghat 400/230kV Grid Sub-Station | ATR-3 7206T | 400/230 | 750 | 15-06-2025 | 10:00 | 500 | 198 | 71.7036
Meghnaghat 400/230kV Grid Sub-Station | ATR-1 | 400/230 | 750 | 13-06-2025 | 23:00 | 495 | 143 | 68.6989
Meghnaghat 400/230kV Grid Sub-Station | ATR-2 | 400/230 | 750 | 13-06-2025 | 23:00 | 493 | 142 | 68.4057
Meghnaghat 400/230kV Grid Sub-Station | ATR-3 | 400/230 | 750 | --- | --- | --- | --- | ---
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | 520 | 13-06-2025 | 23:00 | 476 | 97 | 93.4198
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | 520 | 13-06-2025 | 23:00 | 472 | 96 | 92.6277
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | 325 | 12-06-2025 | 00:00 | 75 | 30 | 24.8546
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | 325 | 22-06-2025 | 19:00 | 101 | 30 | 32.4189
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 520 | 15-06-2025 | 00:00 | 190 | 62 | 38.4346
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 520 | 15-06-2025 | 00:00 | 190 | 62 | 38.4346
Amtali 400/132kV Grid Sub-Station | --- | --- | --- | --- | --- | --- | --- | ---
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 300 | 23-06-2025 | 16:00 | 204 | 85 | 73.6667
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 300 | 23-06-2025 | 16:00 | 204 | 85 | 73.6667
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 225 | 24-06-2025 | 23:00 | 182 | 46 | 83.4325
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 225 | 24-06-2025 | 23:00 | 182 | 46 | 83.4325
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 225 | 24-06-2025 | 09:00 | 185 | 50 | 85.1723
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 300 | 03-06-2025 | 19:30 | 228 | 105 | 83.672
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 300 | 27-06-2025 | 01:00 | 200 | 4 | 66.68
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 300 | 10-06-2025 | 21:00 | 205 | 60 | 71.2
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 225 | 10-06-2025 | 21:00 | 154 | 45 | 71.3067
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 225 | 21-06-2025 | 19:30 | 225 | 32 | 101.0063
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 225 | 26-06-2025 | 20:00 | 216 | 62 | 99.8765
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 300 | 22-06-2025 | 23:00 | 275 | 48 | 93.0526
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 29-06-2025 | 23:00 | 147 | 49 | 51.6505
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 29-06-2025 | 23:00 | 147 | 49 | 51.6505
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | 225 | 15-06-2025 | 03:00 | 143 | 41 | 66.1162
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | 225 | 14-06-2025 | 22:00 | 144 | 45 | 67.0522
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 225 | 04-06-2025 | 00:00 | 178 | 49 | 82.0539
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 225 | 04-06-2025 | 00:00 | 178 | 49 | 82.0539
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 300 | 04-06-2025 | 00:00 | 239 | 69 | 82.9203
Bogura 230/132kV Grid Sub-Station | T-04 | 230/132 | 300 | 04-06-2025 | 00:00 | 239 | 69 | 82.9203
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-01 | 230/132 | 225 | 06-06-2025 | 19:00 | 177 | 69 | 84.4327
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-02 | 230/132 | 225 | 06-06-2025 | 19:00 | 175 | 67 | 83.2832
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-03 | 230/132 | 225 | 06-06-2025 | 22:00 | 188 | 72 | 89.4736
Fenchuganj 230/132/33kV Grid Sub-Station | AT-01 | 230/132 | 300 | 26-06-2025 | 23:00 | 201 | 74 | 71.3964
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 300 | 26-06-2025 | 23:00 | 251 | 94 | 89.3414
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 125 | 16-06-2025 | 06:00 | 100 | 0 | 80
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 125 | 16-06-2025 | 06:00 | 100 | 0 | 80
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 225 | 23-06-2025 | 00:00 | 93 | 78 | 53.9465
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 225 | 23-06-2025 | 00:00 | 102 | 77 | 56.8003
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 225 | 23-06-2025 | 00:00 | 97 | 82 | 56.4514
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 225 | 04-06-2025 | 12:00 | 218 | 218 | 137.0216
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 225 | 01-06-2025 | 09:00 | 89 | 74 | 51.4424
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 225 | 23-06-2025 | 00:00 | 90 | 65 | 49.3413
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 150 | 04-06-2025 | 19:00 | 117 | 57 | 86.764
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 150 | 04-06-2025 | 19:00 | 117 | 57 | 86.764
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 150 | 27-06-2025 | 19:30 | 105 | 49 | 77.2471
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 150 | 04-06-2025 | 19:00 | 117 | 57 | 86.764
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 225 | 15-06-2025 | 03:00 | 130 | 75 | 66.7037
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 225 | 15-06-2025 | 03:00 | 130 | 74 | 66.4827
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 225 | 14-06-2025 | 01:00 | 129 | 62 | 63.6115
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | 300 | 20-06-2025 | 09:00 | 225 | 33 | 75.8024
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | 300 | 14-06-2025 | 01:00 | 214 | 60 | 74.084
Kaliakoir 230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 300 | 22-06-2025 | 07:00 | 164 | 54 | 57.5538
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 23-06-2025 | 00:00 | 206 | 64 | 71.9043
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 23-06-2025 | 00:00 | 206 | 64 | 71.9043
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 300 | 01-06-2025 | 00:00 | 0 | 0 | 0
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | 225 | 03-06-2025 | 00:00 | 167 | 59 | 78.7181
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | 225 | 03-06-2025 | 00:00 | 167 | 59 | 78.7181
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | 300 | 02-06-2025 | 00:00 | 194 | 70 | 68.7475
Madunaghat 230/132/33kV Grid Sub-Station | ATR-1(705T) | 230/132 | 300 | 29-06-2025 | 15:00 | 114 | 12 | 38.2099
Madunaghat 230/132/33kV Grid Sub-Station | ATR-2(715T) | 230/132 | 300 | 26-06-2025 | 10:00 | 111 | 6 | 37.054
Madunaghat 230/132/33kV Grid Sub-Station | ATR-3(725T) | 230/132 | 300 | 29-06-2025 | 15:00 | 114 | 12 | 38.2099
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 300 | 24-06-2025 | 13:00 | 168 | 75 | 61.327
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 300 | 24-06-2025 | 13:00 | 168 | 75 | 61.327
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | 300 | 12-06-2025 | 01:00 | 102 | 11 | 34.1971
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | 300 | 12-06-2025 | 01:00 | 102 | 11 | 34.1971
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 300 | 01-06-2025 | 00:00 | 1 | 0 | 0.33333
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 300 | 01-06-2025 | 00:00 | 1 | 0 | 0.33333
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 230/132 | 450 | 28-06-2025 | 11:00 | 280 | 27 | 62.5108
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 LT | 230/132 | 450 | 23-06-2025 | 11:00 | 316 | 73 | 72.0716
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 LT | 230/132 | 450 | 23-06-2025 | 11:00 | 316 | 73 | 72.0716
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 300 | 26-06-2025 | 10:00 | 202 | 129 | 79.8923
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 300 | 26-06-2025 | 10:00 | 202 | 129 | 79.8923
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 300 | 01-06-2025 | 10:00 | 148 | 38 | 50.9335
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 300 | 01-06-2025 | 10:00 | 148 | 38 | 50.9335
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 300 | 23-06-2025 | 00:00 | 106 | 16 | 35.7336
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 300 | 23-06-2025 | 00:00 | 106 | 19 | 35.8965
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 300 | 22-06-2025 | 19:00 | 252 | 95 | 89.7707
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 300 | 09-06-2025 | 01:00 | 288 | 73 | 99.0359
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 225 | 13-06-2025 | 00:00 | 200 | 35 | 90.2397
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 225 | 13-06-2025 | 00:00 | 185 | 40 | 84.1222
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 225 | 28-06-2025 | 15:00 | 74 | 0 | 32.8889
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF_LDC_37
|  |  |  | POWER GRID BANGLADESH PLC. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID BANGLADESH PLC. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[5 empty] | Report on load shedding | [12 empty] | Report on load shedding
Month: June 2025 |  |  |  | (For Evening Peak) | [10 empty] | Month: June 2025 |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur
2025-06-01 | 13631.03 | 13631.03 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-06-01 | 12880.09 | 12880.09 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-02 | 15051 | 15100 | 47 | 19:30 Hr. | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | - | 2025-06-02 | 12801.37 | 12801.37 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-03 | 14306 | 14306 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-06-03 | 12043.2 | 12043.2 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-04 | 14121 | 14121 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-06-04 | 12191.8 | 12191.8 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-05 | 13231.55 | 13231.55 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-06-05 | 11487.61 | 11487.61 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-06 | 12427.27 | 12427.27 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-06-06 | 10434.97 | 10434.97 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-07 | 13105.7 | 13105.7 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-06-07 | 9699.51 | 9699.51 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-08 | 13223.2 | 13223.2 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-06-08 | 10847.71 | 10847.71 | 0 | 10:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-09 | 13849.75 | 13921.75 | 69 | 21:00 Hr. | 0 | 0 | 25 | 0 | 28 | 0 | 0 | 0 | 16 | - | 2025-06-09 | 11389.04 | 11389.04 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-10 | 13265.5 | 13340.5 | 72 | 20:00 Hr | 0 | 0 | 15 | 0 | 22 | 0 | 0 | 0 | 35 | - | 2025-06-10 | 11765.5 | 11765.5 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0
2025-06-11 | 14031.3 | 14055.34 | 23 | 21:00 Hr. | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 13 | - | 2025-06-11 | 11683.28 | 11683.28 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-12 | 14695.11 | 14771.11 | 73 | 21:00 Hr. | 0 | 0 | 15 | 0 | 8 | 0 | 0 | 0 | 50 | - | 2025-06-12 | 12281.96 | 12281.96 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-13 | 15175.2 | 15290.2 | 110 | 21:00 Hr. | 0 | 0 | 15 | 10 | 15 | 15 | 0 | 0 | 55 | - | 2025-06-13 | 12525.98 | 12525.98 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-14 | 15487.83 | 15487.83 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-06-14 | 13304.81 | 13304.81 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-15 | 15599.57 | 15641.57 | 40 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | - | 2025-06-15 | 14146.38 | 14146.38 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-16 | 15034.64 | 15055.64 | 0 | 20:00 Hr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | - | 2025-06-16 | 13818.7 | 13818.7 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-17 | 14530 | 14530 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-06-17 | 12828.16 | 12828.16 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-18 | 14183.1 | 14183.1 | 0 | 20:00 Hr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-06-18 | 12670.57 | 12670.57 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-19 | 14304.2 | 14304.2 | 0 | 20:00 Hr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-06-19 | 12725.85 | 12725.85 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-20 | 13873.78 | 13873.78 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-06-20 | 11715.34 | 11756.1 | 39 | 12:00 Hr. | 0 | 0 | 7 | 0 | 0 | 32 | 0 | 0 | 0 | -
2025-06-21 | 15691.42 | 15720.68 | 28 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | - | 2025-06-21 | 12855.02 | 12855.02 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-22 | 15637.7 | 15637.7 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-06-22 | 13850.4 | 13850.4 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-23 | 15680.65 | 15680.65 | 0 | 20:00 Hr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-06-23 | 13843.01 | 13843.01 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-24 | 15661.2 | 15690.46 | 28 | 19:30 Hr. | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | - | 2025-06-24 | 14156.82 | 14193.82 | 35 | 12:00 Hr. | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-25 | 15501.74 | 15570.74 | 66 | 19:30 Hr. | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 36 | - | 2025-06-25 | 13738.74 | 13738.74 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-26 | 15378.76 | 15400.76 | 21 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | - | 2025-06-26 | 14005.18 | 14005.18 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-27 | 14363.76 | 14363.76 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-06-27 | 12226.52 | 12226.52 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-28 | 15476.72 | 15520.72 | 42 | 20:00 Hr | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 7 | 20 | - | 2025-06-28 | 12351.12 | 12351.12 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-29 | 15414.24 | 15469.24 | 53 | 19:30 Hr. | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 |  | 2025-06-29 | 13912.03 | 13912.03 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-06-30 | 15419.32 | 15499.32 | 77 | 19:30 Hr. | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 37 |  | 2025-06-30 | 13664.36 | 13664.36 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
[16 empty] | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: June 2025
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 15691.42 | 2025-06-21 | 21:00 Hr.
2 | Maximum Day Peak Genaration | MW | 14156.82 | 2025-06-24 | 12:00 Hr.
3 | Maximum Evening Peak Demand | MW | 15720.68 | 2025-06-21 | 21:00 Hr.
4 | Minimum Generation | MW | 8827.15 | 2025-06-03 | 05:00 Hr.
5 | Average of the daily evening peak Genaration | MW | 14578.408 | - | -
6 | Average of the daily day peak Genaration | MW | 12594.8343 | - | -
7 | Maximum load shed (Evening Peak) | MW | 110 | 2025-06-13 | 21:00 Hr.
8 | Minimum load shed | MW | 0 | 2025-06-01 | 21:00 Hr.
9 | Total nos. of load shed days | Day | 14 | - | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW/Day | 24.9667 | - | -
11 | Total Generation | MkWh | 9451.3322 | - | -
12 | Total Generation by BPDB | MkWh | 1336.914 | % of total Gen. | 14.15%
13 | Total Generation by IPP | MkWh | 3779.248 | '' | 39.99%
14 | A) Total Generation by Generation Companies | MkWh | 2803.8877 | '' | 29.67%
| B) Total Generation by REB | MkWh | 39.5405 | " | 0.4184%
| C) Total Generation by RENTAL | MkWh | 113.4342 | " | 1.2%
| D) Total Imported from India (BIPTC) | MkWh | 593.328 | " | 6.278%
| E) Total Imported from Tripura, India (A.C) | MkWh | 25.3805 | " | 0.2685%
| F) Total Imported from Nepal | MkWh | 14.6 | " | 0.1545%
| E) Total Imported from India (Adani Power Jharkhanda Ltd) | MkWh | 744.9994 | " | 7.882%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4276.4107 | % of total Gen. | 45.25%
| B) Oil | MkWh | 925.5115 | '' | 9.792%
| C) Hydro | MkWh | 119.0818 | '' | 1.26%
| D) Solar | MkWh | 111.712 | '' | 1.182%
| E) Coal | MkWh | 2626.2838 | '' | 27.79%
| F) BIPTC (Import from India) | MkWh | 593.328 | '' | 6.278%
| G) A.C (Import from Tripura, India) | MkWh | 25.3805 | '' | 0.2685%
| H) Total Imported from Nepal | MkWh | 14.6 | '' | 0.1545%
| I) Adani (Import from India) | MkWh | 744.9994 | '' | 7.895%
| J) Wind | MkWh | 14.0246 | '' | 0.1486%
16 | Maximun of the daily total Generation . | MkWh | 345.1582 | 2025-06-15
17 | Monthly Load factor | % | 83.6562 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 57745.3556 | - | -
| A) Gas | M.Taka | 14966.3671 | - | -
| B) Coal | M.Taka | 16845.4156 | - | -
| C) HFO | M.Taka | 17260.608 | - | -
| D) HSD | M.Taka | 1.3796 | - | -
| E) Hydro | M.Taka | 11.9082 | - | -
| F) Solar | M.Taka | 1827.9244 | - | -
| G) Total Import | M.Taka | 6831.7528 | - | -
| H) Wind |  | 205.3207
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 2357.2798 | 2025-06-25
| A) Gas | M.Taka | 610.395 | 2025-06-08
| B) Coal | M.Taka | 725.8184 | 2025-06-01
| C) HFO | M.Taka | 954.1606 | 2025-06-25
| D) HSD | M.Taka | 1.3796 | 2025-06-26 | -
| E) Hydro | M.Taka | 0.43618 | 2025-06-21 | -
| F) Solar | M.Taka | 81.0861 | 2025-06-13 | -
| G) Total Import |  | 284.7845 | 2025-06-15
| H) Wind | M.Taka | 16.6896 | 2025-06-25
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 6.1315
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 6.2945
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 83.73 | 30/06/2025 | 06:00
b) | Actual | FT (MSL) | 97.92 | 30/06/2025 | 06:00
22 | Peak Genaration of June 2024 | MW | 15798 | 2024-06-11 | 21:00
23 | Peak Demand of June 2024 | MW | 16700 | 2024-06-11 | 21:00
24 | Maximum peak Generation recorded upto 30/06/2025 | MW | 16477 | 2024-04-30 | 21:00
25 | Maximum peak Demand recorded upto 30/06/2025 | MW | 17200 | 29/04/2024 | 21:00
26 | Maximum load shed recorded upto 30/06/2025 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## FGMO Weekly
Power Grid Bangladesh PLC.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status | [17 empty] | SR at 50 Hz (MW)
SL | Plant Name | Owner | Installed capacity | Capability Status of Last Week | 26.06.2025 | 19.06.2025 | 12.06.2025 | 05.06.2025 | 29.05.2025 | 22.05.2025 | 15.05.2025 | 08.05.2025 | 01.05.2025 | 24.04.2025 | 17.04.2025 | 10.04.2025 | 03.04.2025 | 27.03.2025 | 20.03.2025 | 13.03.2025 | 06.03.2025 | 27.02.2025 | 20.02.2025 | 13.02.2025 | 06.02.2025 | 30.01.2025 | 23.01.2025 | 16.01.2025 | 09.01.2025 | 02.01.2025 | 28.11.2024 | 21.11.2024 | 14.11.2024 | 07.11.2024 | 31.10.2024 | 24.10.2024 | 17.10.2024 | 10.10.2024 | 03.10.2024 | 26.09.2024 | 19.09.2024 | 05.09.2024 | 12.09.2024 | 29.08.2024 | 22.08.2024 | 15.08.2024 | 08.08.2024 | 01.08.2024 | 25.07.2024 | 18.07.2024 | 11.07.2024 | 04.07.2024 | 27.06.2024 | 20.06.2024 | 13.06.2024 | 06.06.2024 | 30.05.2024 | 22.05.2024 | 16.05.2024 | 09.05.2024 | 02.05.2024 | 25.04.2024 | 18.04.2024 | 11.04.2024 | 04.04.2024 | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
(MW)
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | Capable | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | Capable | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | Capable |  |  | 20 | [41 empty] | 20 | [7 empty] | 20 | 20 | 20 | 20
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 | Capable | 20 | 20 | 20 | 20 | [40 empty] | 20 |  | 15 | 15 |  | 15 |  |  |  | 20 | 20 | 20 | 20
5 | Meghnaghat CCPP(Summit) | IPP | 305 | Capable | 35 | 35 | 35 | 35 | 35 | 10 | 10 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 15 | 30 | [7 empty] | 35 | [6 empty] | 25 | 15 | 15 | 15 | 15 | 30 | 30 | 30 |  |  |  | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
6 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | Capable | [25 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 |  |  | 30 | 30 | 30 |  |  |  | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
7 | Ashuganj 225 MW CCPP | APSCL | 221 | Capable | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | [11 empty] | 15 | 15 | 15 | 15 | [15 empty] | 16 | 16 | 16 | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
8 | Bheramara 410 MW CCPP | NWPGCL | 410 | Capable | [42 empty] | 40 | [6 empty] | 30 |  |  |  | 30 | 30 | 30 | 30 | 30
9 | Haripur 412 MW CCPP | EGCB | 412 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
10 | Fenchugonj CCPP Phase-1 | BPDB | 97 | Capable | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
11 | Chandpur 150 MW CCPP | BPDB | 163 | Capable
12 | Siddhirganj 2x120 MW GTPP | EGCB | 210 | Capable
13 | Shikalbaha 225 MW CCPP | BPDB | 225 | Capable
14 | Shikalbaha Peaking GT | BPDB | 150 | Capable
15 | Shahjibazar 330 MW CCPP | BPDB | 330 | Capable | [18 empty] | 40 | [20 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 |  |  |  | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
16 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | Capable | [15 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
17 | Fenchugonj CCPP Phase-2 | BPDB | 104 | Capable | [15 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
18 | Bhola 225 MW CCPP | BPDB | 194 | Capable | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365 | Capable
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 | Capable |  |  | 20 | 20 | [38 empty] | 20 | [6 empty] | 15 | [6 empty] | 15 | 20 | 20 | 20
21 | Siddhirganj 335 MW CCPP | EGCB | 335 | Capable |  |  |  | 30 | 30 | 30 | 30 |  | 30 | 30
22 | Bibiyana-III 400 MW CCPP | BPDB | 400 | Capable | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 |  |  |  |  | 35 | 35 | 35 | 35 | 35 | [14 empty] | 35 | 35 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
23 | Sylhet 225 MW CCPP | BPDB | 231 | Capable
24 | RPCL 210 MW CCPP | IPP | 210 | Capable but not tested recently
25 | a) Baghabari 71 MW GTPP | BPDB | 71 | Not Capable but feasible
26 | b) Baghabari 100 MW GTPP | BPDB | 100 | Not Capable but feasible
27 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40 | Capable
28 | Karnaphuli Hydro PP Unit: 3 | BPDB | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50 | Not Capable but feasible
| a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410 | Not Capable but feasible
29 | Bibiyana South 400 MW CCPP | BPDB | 400 | Capable | [23 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30
| Barapukuria 275 MW TPP Unit-3 | BPDB | 274 | Not Capable but feasible
30 | Payra 1320 MW Unit-1 & 2 | BCPCL | 1244 | Capable
31 | Kushiara 163 MW CCPP (KP) | IPP | 163 | Capable | 16 |  |  | 16 | 16 | 16 | 16 | 10 | 10 | 10 | 10 | 10
32 | Bhola Nutan Bidyut | IPP | 220 | Capable
33 | Haripur 360MW CCPP(HPL) | IPP | 360 | Not Capable but feasible
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450 | Not Capable but feasible
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | 1150 | Capable
36 | Anwara 300 MW PP (United) | IPP | 300 | Capable
37 | Chandpur 200MW (Desh energy) | IPP | 200 | Capable
38 | Meghnaghat 104 MW PP (OPCL) | IPP | 104 | Capable
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | 105 | Capable
40 | Gazipur 100 MW PP | IPP | 105 | Capable
41 | United Payra Power Ltd. | IPP | 150 | Capable
42 | Madhumati 100 MW PP | IPP | 100 | Capable
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | 105 | Capable
44 | Karnaphuli Power Ltd. | IPP | 110 | Capable
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | 300 | Capable
46 | Madanganj-55 MW PP(Summit) | IPP | 55 | Capable
47 | Kodda 149 MW PP Unit-1 (Summit) | IPP | 149 | Capable
48 | Feni Lanka Power | IPP | 114 | Capable
49 | Barisal 110 MW PP (Summit) | IPP | 110 | Capable
50 | Manikganj 162 MW (MPGL) | IPP | 162 | Capable
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | 55 | Capable
52 | Zodiac 54 MW | IPP | 54 | Capable
53 | Anlima Energy Ltd | IPP | 116 | Capable
54 | Thakurgaon 115 MW (EPV) | IPP | 115 | Capable
55 | Confidence Unit-2 Bogura | IPP | 113 | Capable
56 | Confidence Unit-1 Bogura | IPP | 113 | Capable
57 | Kamalaghat 54 MW Banco Energy | IPP | 54 | Capable
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | 55 | Capable
59 | Kodda 150 MW (BR Power) | IPP | 149 | Capable
60 | Chandpur 115 MW (Doreen) | IPP | 115 | Capable
61 | Kanchan Purbachal Power Ltd | IPP | 55 | Capable
62 | Chattogram SS Power U- 1 & 2 | Private | 1224 | Capable | 66 | 66
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | 1436 | Capable | 40 | 40
64 | Rampal 1320 MW U-1 & 2 | BIFPCL | 1234 | Capable | 50 | 50
65 | Barishal 307 MW PP (BEPCL) | Private | 307 | Capable | 30 | 30
| Payra 1320 MW Unit-1 | BCPCL | 621 | Capable | [7 empty] | 20 | 20
| Payra 1320 MW Unit-2 | BCPCL | 622 | Capable | [7 empty] | 20 | 20
| Shahjibazar GTPP Unit 8 & 9 | BPDB | 70 | Capable
| Shajibazar 100 MW PP | BPDB | 100 | Not Capable but feasible
| Khulna 225 MW CCPP | NWPGCL | 230 | Capable but not tested recently
Total Installed capacity |  |  |  |  | 19739 | 19739 | 14388 | 14388 | 14388 | 14388 | 14388 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity |  |  |  |  | 6795 | 6632 | 2862 | 3135 | 2325 | 2165 | 2165 | 2525 | 2855 | 2325 | 1595 | 1635 | 1072 | 1812 | 1432 | 1464 | 1064 | 592 | 1332 | 1282 | 1682 | 1302 | 1302 | 1685 | 1685 | 1315 | 1813 | 2027 | 1475 | 1475 | 1092 | 1124 | 744 | 712 | 712 | 1802 | 1492 | 1152 | 1492 | 2442 | 2442 | 2036 | 2956 | 2416 | 2476 | 1836 | 1696 | 1696 | 1876 | 3336 | 1196 | 1196 | 1796 | 3416 | 3436 | 3076 | 3038 | 2824 | 2996 | 2996 | 2024 | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve |  |  |  |  | 424 | 408 | 262 | 288 | 218 | 193 | 193 | 222 | 252 | 212 | 152 | 137 | 92 | 172 | 142 | 144 | 109 | 67 | 137 | 132 | 167 | 137 | 137 | 162 | 162 | 122 | 160 | 179 | 132 | 132 | 107 | 109 | 79 | 77 | 77 | 172 | 137 | 107 | 137 | 217 | 217 | 186 | 271 | 216 | 226 | 156 | 141 | 156 | 171 | 291 | 111 | 111 | 161 | 311 | 316 | 276 | 269 | 254 | 280 | 280 | 198 | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO |  |  |  |  | 14 | 13 | 11 | 12 | 9 | 9 | 9 | 10 | 11 | 9 | 7 | 7 | 5 | 7 | 6 | 7 | 6 | 3 | 5 | 5 | 6 | 5 | 5 | 6 | 6 | 5 | 6 | 8 | 5 | 5 | 4 | 5 | 4 | 3 | 3 | 6 | 5 | 4 | 5 | 8 | 8 | 8 | 11 | 9 | 10 | 7 | 7 | 7 | 7 | 12 | 5 | 5 | 7 | 12 | 12 | 11 | 11 | 10 | 11 | 11 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list |  |  |  |  | 68 | 68 | 64 | 64 | 64 | 64 | 64 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list |  |  |  |  | 74 | 74 | 70 | 70 | 70 | 70 | 70 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable |  |  |  |  | 62 | 62 | 58 | 58 | 58 | 58 | 58 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently |  |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible |  |  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD
New FGMO capable plants under BPSREIP:
Letter date: 09/06/2024
1. Anwara 300 MW Power Plant (United)
2.Chandpur 200 MW Power Plant (Desh energy)
3. Rupsha 105 MW Power Plant (Orion rupsha)
4. Gazipur 100 MW Power Ltd
5. United Payra Power Ltd
6.Sikalbaha 105 MW Power Plant (Baraka Sikalbaha)
7.Karnaphuli Power Ltd
8. Feni Lanka Power Ltd
9. Barisal 110 MW Power Plant (Summit)
10. Madanganj-55 MW Power Plant (Summit)
11. Madhumati 100 MW Power Plant
12. Nawabganj 55 MW Power Plant(Dhaka Southern Power)
13.Manikganj 55 MW Power plant ((Dhaka Southern Power)
14. Manikganj 162 MW Power Plant (MPGL)
15. Zodiac 54 MW Power Plant

## FGMO
Power Grid Bangladesh PLC.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month: June 2025
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ | √ |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | [6 empty] | √ | √ | √ | √ | √ | √ | √
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | [5 empty] | √ |  |  |  |  | √ | √ | √ | [5 empty] | √
5 | Meghnaghat CCPP(Summit) | IPP | 305 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
6 | Ashuganj 450 MW CCPP(North) | APSCL | 360
7 | Ashuganj 225 MW CCPP | APSCL | 221 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
8 | Bheramara 410 MW CCPP | NWPGCL | 410
9 | Haripur 412 MW CCPP | EGCB | 412 | √ | [8 empty] | √ |  |  |  | √ | √ | [7 empty] | √ | √
10 | Fenchugonj CCPP Phase-1 | BPDB | 97 |  | √ | √
11 | Chandpur 150 MW CCPP | BPDB | 163
12 | Siddhirganj 2x120 MW GTPP | EGCB | 210
13 | Shikalbaha 225 MW CCPP | BPDB | 225
14 | Shikalbaha Peaking GT | BPDB | 150
15 | Shahjibazar 330 MW CCPP | BPDB | 330
16 | Ashuganj 450 MW CCPP(South) | APSCL | 360
17 | Fenchugonj CCPP Phase-2 | BPDB | 104
18 | Bhola 225 MW CCPP | BPDB | 194 | [27 empty] | √ | √ | √
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
21 | Siddhirganj 335 MW CCPP | EGCB | 335
22 | Bibiyana-III 400 MW CCPP | BPDB | 400
23 | Sylhet 225 MW CCPP | BPDB | 231
24 | RPCL 210 MW CCPP | IPP | 210
25 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
26 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
27 | Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
| a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
28 | Bibiyana-III 400 MW CCPP | BPDB | 400
29 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
30 | Payra 1320 MW Unit-1 & 2 | BCPCL | 1244
31 | Kushiara 163 MW CCPP (KP) | IPP | 163 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | [5 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
32 | Bhola Nutan Bidyut | IPP | 220
33 | Haripur 360MW CCPP(HPL) | IPP | 360
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | 1150
36 | Anwara 300 MW PP (United) | IPP | 300 | [19 empty] | √ | √ | √
37 | Chandpur 200MW (Desh energy) | IPP | 200 | [19 empty] | √ | √
38 | Meghnaghat 104 MW PP (OPCL) | IPP | 104
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | 105
40 | Gazipur 100 MW PP | IPP | 105
41 | United Payra Power Ltd. | IPP | 150
42 | Madhumati 100 MW PP | IPP | 100
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | 105
44 | Karnaphuli Power Ltd. | IPP | 110 | [19 empty] | √ | √ | √
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | 300
46 | Madanganj-55 MW PP(Summit) | IPP | 55
47 | Kodda 149 MW PP Unit-1 (Summit) | IPP | 149
48 | Feni Lanka Power | IPP | 114 | [19 empty] | √ | √ | √
49 | Barisal 110 MW PP (Summit) | IPP | 110
50 | Manikganj 162 MW (MPGL) | IPP | 162
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | 55
52 | Zodiac 54 MW | IPP | 54
53 | Anlima Energy Ltd | IPP | 116
54 | Thakurgaon 115 MW (EPV) | IPP | 115
55 | Confidence Unit-2 Bogura | IPP | 113
56 | Confidence Unit-1 Bogura | IPP | 113
57 | Kamalaghat 54 MW Banco Energy | IPP | 54
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | 55
59 | Kodda 150 MW (BR Power) | IPP | 149
60 | Chandpur 115 MW (Doreen) | IPP | 115
61 | Kanchan Purbachal Power Ltd | IPP | 55
62 | Chattogram SS Power U- 1 & 2 | Private | 1224 | [9 empty] | √ |  | √ | √ |  |  |  |  | √ |  | √ | √ | √ |  | √ | √ |  | √ | √ | √ | √
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | 1436 | [29 empty] | √
64 | Rampal 1320 MW U-1 & 2 | BIFPCL | 1234 | [11 empty] | √ | √ |  | √ |  |  |  |  | √ | √ |  |  |  | √ |  | √ | √ | √ | √
65 | Barishal 307 MW PP (BEPCL) | Private | 307 | [19 empty] | √ | √ | √ |  | √ |  |  | √ | √ |  | √
| Bibiyana South 400 MW | BPDB | 383
| Ashuganj 420 MW CCPP(East) | APSCL | 400
| Ashuganj 55 MW PP (Precision) | QRPP | 55
| Bagura 113 MW PP (Confidence)-2 | IPP | 113
| Energypac Power Venture Thakurgaon Ltd. | IPP | 115
| Chandpur 150 MW CCPP | BPDB | 163
| Khulna 225 MW CCPP | NWPGCL | 230
| Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
| Shajibazar 100 MW PP | BPDB | 100
| Payra 1320 MW Unit-1 | BCPCL | 622 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √