## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 30-07-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 29-07-2025 | during | 30-07-2025 | during | 30-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 0 | 0 | 0 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 270 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 149 | 147 | 150 | 335 | 150 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 194 | 198 | 208.13 | 208.13 | 200 | 200 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 26 | 330 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 5 | 0 | 7 | 7 | 7 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 49.2 | 15.6 | 53.97 | 53.97 | 53.97 | 53.97 | FGMO
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 62 | 149.36 | 149.36 | 144 | 144 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 17 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21.5 | 26.2 | 33 | 33 | 28 | 28 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 34 | 33 | 52.19 | 52.19 | 33 | 33 | Fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 300 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 125 | 96 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 70 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 2 | 0 | 104 | 104 | 16 | 16 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 162 | 126 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 12 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 35 | 35 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 178 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 733.79 | 520 | 500 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 125 | 125 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6673.514 | 2199.7 | 2267.8 | 5238.15 | 5393.15 | 3773.47 | 3928.47
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 8 | 0 | 9 | 0 | 9 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 36 | 28 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 220 | 218 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 218 | 220 | 213 | 213 | 213 | 213 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 15 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 2 | 77 | 80 | 80 | 80 | 80 | Machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 66 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 4 | 22 | 0 | 0 | 0 | 0 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.44 | 0 | 1.44 | 0 | 1.44 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 855 | 993 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 16 | 9 | 34 | 22 | 34 | 22 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 640 | 713 | 770 | 770 | 770 | 770 | -
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 2024.44 | 2385 | 3835.16 | 3812.72 | 3835.16 | 3812.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 135 | 190 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 341 | 356 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 340 | 340 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 29 | 35 | 46.7 | 46.7 | 39 | 39 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 46 | 48 | 55 | 55 | 53 | 53 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 137 | 180 | 195 | 195 | 130 | 130 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 100 | 40 | 150 | 150 | 140 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 22 | 37 | 47 | 47 | 47 | 47 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 70 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 132 | 180 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 34 | 58 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 43 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 63 | 79 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 39 | 47 | 113 | 113 | 36 | 36 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 112 | 97 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 41 | 0 | 30 | 0 | 30 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1732 | 1844 | 2409.56 | 2379.56 | 2134.36 | 2104.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 29-07-2025 | during | 30-07-2025 | during | 30-07-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 66 | 87 | 157.5 | 157.5 | 102 | 102 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 181 | 150 | 200 | 200 | 170.2 | 170.2 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 84 | 103 | 115 | 115 | 100 | 100 | Engine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 34.43 | 0 | 35 | 0 | 35 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 12 | 17 | 54.5 | 54.5 | 35 | 35 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 390.43 | 369 | 586.1 | 549 | 456.3 | 419.2
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 50 | 70 | 70 | 70 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 144 | 153 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 81 | 83 | 83 | 82 | 82 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | Plant Shutdown as per schedule HGPI work
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 362 | 355 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 310 | 310 | 320 | 320 | 320 | 320 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1001 | 1025 | 1096 | 1096 | 1038 | 1038
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 854 | 854 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 211 | 208 | 410 | 410 | 225 | 225 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 53 | 53 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 11 | 0 | 40 | 0 | 40 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 823 | 1126 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1937 | 2226 | 3592.2 | 3552.2 | 3265.2 | 3225.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 305 | 305 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 995 | 1105 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 176 | 215 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.04 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1816.04 | 1965 | 2162 | 2161 | 2152 | 2151
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 204 | 201 | 214 | 214 | 205 | 205 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 205 | 160 | 220 | 220 | 206 | 206 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 204 | 150 | 220 | 220 | 208 | 208 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 405 | 341 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 27 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 40 | 96 | 96 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 108 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.58 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 967.41 | 1443.18 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 64.28 | 0 | 0 | 0 | 0 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 13 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3410 | 3452.96 | 2065.27 | 2583.18 | 3132.47 | 3026.87 | 3055.09 | 2949.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 46 | 0 | 0 | 0 | 47 | 47 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 111 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 8 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 115 | 114 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 13 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 212 | 0 | 152.25 | 0 | 152.25 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 505 | 227 | 445.85 | 262 | 492.85 | 309
System Total |  |  |  |  | 28565.2 | 27779.665 | 13670.88 | 14891.98 | 22497.49 | 22232.5 | 20202.43 | 19937.44
Forecast Scenario (30-07-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14800 |  | 0 |  | 14800
|  |  |  | 1:00 | 14310 |  | 0 |  | 14310
|  |  |  | 2:00 | 13820 |  | 0 |  | 13820
|  |  |  | 3:00 | 13480 |  | 0 |  | 13480
|  |  |  | 4:00 | 12970 |  | 0 |  | 12970
|  |  |  | 5:00 | 12740 |  | 0 |  | 12740
|  |  |  | 6:00 | 12270 |  | 0 |  | 12270
|  |  |  | 7:00 | 12280 |  | 0 |  | 12280
|  |  |  | 8:00 | 12170 |  | 0 |  | 12170
|  |  |  | 9:00 | 12540 |  | 0 |  | 12540
|  |  |  | 10:00 | 12730 |  | 0 |  | 12730
|  |  |  | 11:00 | 13040 |  | 0 |  | 13040
|  |  |  | 12:00 | 13440 |  | 0 |  | 13440
|  |  |  | 13:00 | 13520 |  | 0 |  | 13520
|  |  |  | 14:00 | 13190 |  | 0 |  | 13190
|  |  |  | 15:00 | 13180 |  | 0 |  | 13180
|  |  |  | 16:00 | 13080 |  | 0 |  | 13080
|  |  |  | 17:00 | 12720 |  | 0 |  | 12720
|  |  |  | 18:00 | 12610 |  | 0 |  | 12610
|  |  |  | 18:30 | 13300 |  | 0 |  | 13300
|  |  |  | 19:00 | 14120 |  | 0 |  | 14120
|  |  |  | 19:30 | 14510 |  | 0 |  | 14510
|  |  |  | 20:00 | 14570 |  | 0 |  | 14570
|  |  |  | 21:00 | 14730 |  | 0 |  | 14730
|  |  |  | 22:00 | 14550 |  | 0 |  | 14550
|  |  |  | 23:00 | 14480 |  | 0 |  | 14480
Probable Maximum Temperature: |  |  | 30.00°C
Probable Maximum Demand at Day Peak: |  |  | 13440.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14730.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14730.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 321.34 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:35 hrs on 30-07-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 29-07-2025 | [28 empty] | Date: | 29-07-2025 | [28 empty] | Date: | 29-07-2025 | [28 empty] | Date: | 29-07-2025 | [28 empty] | Date: | 29-07-2025 | [11 empty] | Date: | 29-07-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [11 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 733.790 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 87 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 46 | 35 | 65 | 0 | 0 | 0 | 55 | 116 | 0 | 450 | 151 | 0 | 0 | 0 | 335 | 198 | 0 | 0 | 125 | 21.7 | 19 | 0 | 0 | 0 | 0 | 39 | 0 | 15 | 66 | 67 | 0 | 12 | 12 | 0 | 221 | 15 | 10 | 735 | 0 | 0 | 19 | 8 | 64 | 221 | 0 | 0 | 0 | 1150 | 0 | 51 | 40 | 71 | 0 | 354 | 340 | 53 | 199 | 39 | 113 | 50 | 163 | 46 | 20 | 92 | 42 | 25 | 0 | 31 | 0 | 300 | 384 | 0 | 60 | 135 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 102 | 170 | 49 | 0 | 0 | 7 | 7503.7 | 854 | 208 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1205 | 17 | 1464 | 0 | 32 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 27 | 0 | 200 | 0 | 170 | 0 | 170 | 0 | 356 | 0 | 0 | 0 | 48 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 120 | 220 | 0 | 306 | 1120 | 0 | 7158 | 14661.7 | 105.08
01:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 39.4 | 17 | 65 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 151 | 0 | 0 | 0 | 335 | 198 | 0 | 0 | 90 | 20 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 32 | 67 | 0 | 12 | 12 | 0 | 220 | 0 | 26 | 728 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1138 | 0 | 51 | 0 | 71 | 0 | 354 | 335 | 52 | 200 | 36 | 95 | 70 | 158 | 42 | 20 | 91 | 42 | 25 | 0 | 31 | 0 | 300 | 371 | 0 | 60 | 134 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 94 | 164 | 49 | 0 | 0 | 12 | 7003.4 | 855 | 209 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1182 | 0 | 1456 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 170 | 0 | 170 | 0 | 353 | 0 | 0 | 0 | 47 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 118 | 220 | 0 | 306 | 1120 | 0 | 6981 | 13984.4 | 105.1
02:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 17 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 151 | 0 | 0 | 0 | 332 | 197 | 0 | 0 | 70 | 20 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 32 | 32 | 0 | 12 | 12 | 0 | 220 | 0 | 33 | 750 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 71 | 0 | 353 | 340 | 52 | 204 | 36 | 91 | 70 | 149 | 36 | 20 | 92 | 40 | 25 | 0 | 0 | 0 | 300 | 388 | 0 | 60 | 141 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 94 | 164 | 70 | 0 | 0 | 12 | 6846 | 855 | 209 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1125 | 0 | 1364 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 170 | 0 | 170 | 0 | 370 | 0 | 0 | 0 | 47 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 118 | 220 | 0 | 305 | 1115 | 0 | 6844 | 13690 | 105.12
03:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 17 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 151 | 0 | 0 | 0 | 332 | 198 | 0 | 0 | 70 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 32 | 0 | 0 | 12 | 12 | 0 | 219 | 0 | 33 | 733 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 71 | 0 | 354 | 340 | 52 | 200 | 36 | 91 | 50 | 150 | 35 | 20 | 92 | 40 | 0 | 0 | 0 | 0 | 295 | 386 | 0 | 60 | 142 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 94 | 125 | 101 | 0 | 0 | 12 | 6849 | 854 | 215 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 0 | 1262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 170 | 0 | 170 | 0 | 365 | 0 | 0 | 0 | 46 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 118 | 220 | 0 | 306 | 1050 | 0 | 6523 | 13372 | 105.14
04:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 17 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 151 | 0 | 0 | 0 | 333 | 198 | 0 | 0 | 35 | 21 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 16 | 0 | 0 | 12 | 12 | 0 | 218 | 0 | 33 | 739 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1005 | 0 | 51 | 0 | 71 | 0 | 354 | 340 | 52 | 203 | 36 | 91 | 50 | 145 | 36 | 20 | 92 | 38 | 0 | 0 | 0 | 0 | 295 | 388 | 0 | 60 | 138 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 94 | 85 | 101 | 0 | 0 | 12 | 6815 | 854 | 215 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 976 | 0 | 1118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 170 | 0 | 170 | 0 | 377 | 0 | 0 | 0 | 45 | 74 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 118 | 220 | 0 | 305 | 1010 | 0 | 6141 | 12956 | 105.16
05:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 17 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 151 | 0 | 0 | 0 | 334 | 196 | 0 | 0 | 40 | 21 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 0 | 0 | 12 | 12 | 0 | 217 | 0 | 33 | 738 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1004 | 0 | 51 | 0 | 71 | 0 | 354 | 340 | 52 | 205 | 36 | 91 | 50 | 152 | 36 | 20 | 94 | 36 | 0 | 0 | 0 | 0 | 295 | 388 | 0 | 60 | 150 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 94 | 85 | 101 | 0 | 0 | 12 | 6604 | 854 | 224 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 930 | 0 | 1124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 197 | 0 | 197 | 0 | 414 | 0 | 0 | 0 | 45 | 74 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 118 | 220 | 0 | 306 | 1000 | 0 | 6193 | 12797 | 105.18
06:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 17 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 154 | 0 | 0 | 0 | 335 | 200 | 0 | 1 | 125 | 21 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0.23 | 216 | 0 | 5 | 730 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 881 | 0 | 51 | 0 | 76 | 0 | 300 | 300 | 52 | 195 | 36 | 16 | 50 | 144 | 36 | 20 | 17 | 34 | 0 | 2 | 0 | 0 | 295 | 382 | 0 | 60 | 152 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 94 | 85 | 102 | 0 | 1.99 | 12 | 6276.22 | 854 | 224 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 885 | 0 | 1119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 200 | 0 | 198 | 0 | 197 | 0 | 396 | 0 | 0.03 | 0 | 46 | 35 | 1 | 34 | 0 | 0 | 0 | 19 | 0.02 | 0 | 197 | 118 | 220 | 0 | 306 | 980 | 0 | 6068.55 | 12344.77 | 105.2
07:00 | 0 | 1 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 17 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 152 | 0 | 0 | 0 | 334 | 197 | 0 | 6 | 125 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0.33 | 217 | 0 | 29 | 728 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 903 | 2 | 51 | 0 | 80 | 0 | 335 | 325 | 51 | 206 | 36 | 16 | 50 | 120 | 36 | 20 | 16 | 34 | 0 | 9 | 0 | 0 | 295 | 388 | 0 | 60 | 157 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 85 | 94 | 100 | 0 | 7.75 | 12 | 6440.08 | 854 | 224 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4 | 828 | 0 | 1027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 7.56 | 201 | 0 | 198 | 0 | 198 | 0 | 414 | 0 | 0.94 | 0 | 48 | 35 | 1 | 34 | 0 | 0 | 0.5 | 52 | 0.04 | 0 | 202 | 118 | 220 | 0 | 307 | 900 | 0 | 5915.04 | 12355.12 | 105.22
08:00 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 17 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 151 | 0 | 0 | 0 | 330 | 196 | 0 | 12 | 125 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 1.45 | 217 | 0 | 6 | 745 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 906 | 5 | 51 | 0 | 103 | 0 | 348 | 340 | 52 | 89 | 36 | 15 | 70 | 100 | 31 | 20 | 16 | 32 | 0 | 6 | 0 | 0 | 310 | 386 | 0 | 60 | 153 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 0 | 85 | 105 | 94 | 0 | 16.44 | 12 | 6374.89 | 853 | 225 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 23 | 797 | 0 | 1024.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 24.3 | 202 | 0 | 198 | 0 | 198 | 0 | 407 | 0 | 1.94 | 0 | 48 | 35 | 13 | 34 | 0 | 0 | 2.3 | 78 | 0.06 | 0 | 202 | 120 | 220 | 0 | 306 | 890 | 0 | 5946.43 | 12321.32 | 105.24
09:00 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 17 | 82 | 0 | 0 | 0 | 15 | 57 | 0 | 225 | 148 | 0 | 0 | 12 | 0 | 196 | 0 | 11 | 125 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 12 | 12 | 1.29 | 218 | 0 | 3 | 735 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 903 | 4 | 51 | 1 | 107 | 0 | 347 | 340 | 51 | 126 | 35 | 17 | 70 | 108 | 29 | 20 | 16 | 22 | 0 | 13 | 0 | 0 | 310 | 390 | 0 | 60 | 157 | 8 | 0 | 81 | 30 | 0 | 18 | 0 | 0 | 94 | 105 | 94 | 1 | 16.41 | 12 | 6207.7 | 855 | 220 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5 | 821 | 0 | 1034.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22.13 | 202 | 0 | 202 | 0 | 207 | 0 | 414 | 0 | 3.3 | 0 | 50 | 90 | 9 | 70 | 0 | 0 | 1.6 | 79 | 0.19 | 0 | 206 | 120 | 220 | 0 | 305 | 894 | 0 | 6084.45 | 12292.15 | 105.26
10:00 | 0 | 35 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 42 | 17 | 85 | 0 | 45 | 4 | 53 | 112 | 0 | 225 | 147 | 0 | 0 | 35 | 0 | 194 | 0 | 15 | 125 | 28 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 12 | 12 | 2.1 | 218 | 0 | 3 | 755 | 0 | 0 | 26 | 0 | 0 | 218 | 0 | 0 | 0 | 848 | 6 | 51 | 58 | 130 | 0 | 340 | 340 | 50 | 126 | 35 | 70 | 70 | 140 | 31 | 17 | 18 | 32 | 16 | 32 | 0 | 0 | 310 | 388 | 0 | 60 | 156 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 0 | 84 | 142 | 67 | 2 | 29.4 | 12 | 6621.5 | 854 | 218 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 17 | 822 | 0 | 922.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 6.63 | 205 | 0 | 206 | 0 | 208 | 0 | 389 | 0 | 0.93 | 0 | 45 | 115 | 29 | 100 | 0 | 0 | 4.4 | 190 | 0.28 | 0 | 200 | 120 | 220 | 0 | 307 | 915 | 0 | 6183.31 | 12804.81 | 105.28
11:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 46.5 | 17 | 114 | 0 | 210 | 40 | 55 | 162 | 0 | 225 | 149 | 0 | 0 | 35 | 0 | 196 | 0 | 24 | 125 | 27.8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 12 | 12 | 0 | 220 | 0 | 3 | 678 | 0 | 0 | 32 | 0 | 0 | 218 | 0 | 0 | 0 | 842 | 10 | 51 | 100 | 132 | 0 | 346 | 340 | 46 | 136 | 32 | 112 | 70 | 129 | 31 | 20 | 65 | 30 | 43 | 32 | 22 | 0 | 310 | 350 | 0 | 60 | 148 | 6 | 0 | 79 | 30 | 0 | 18 | 0 | 0 | 84 | 173 | 66 | 1 | 54.05 | 12 | 7120.35 | 854 | 211 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12 | 795 | 0 | 916.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 64.29 | 204 | 0 | 205 | 0 | 206 | 0 | 352 | 0 | 4.95 | 0 | 46 | 115 | 36 | 113 | 0 | 0 | 4.3 | 204 | 0.17 | 0 | 170 | 120 | 180 | 0 | 305 | 995 | 0 | 6191.56 | 13311.91 | 105.3
12:00 | 5 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 49.2 | 17 | 125 | 16 | 300 | 55 | 55 | 162 | 2 | 225 | 149 | 0 | 0 | 35 | 26 | 194 | 0 | 12 | 125 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 2 | 0 | 12 | 12 | 1.44 | 220 | 0 | 4 | 640 | 0 | 0 | 36 | 0 | 0 | 218 | 0 | 0 | 0 | 855 | 8 | 51 | 100 | 137 | 0 | 341 | 340 | 46 | 135 | 29 | 112 | 50 | 132 | 39 | 17 | 63 | 34 | 43 | 41 | 22 | 0 | 310 | 362 | 0 | 50 | 144 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 12 | 84 | 181 | 66 | 1 | 34.43 | 12 | 7347.57 | 854 | 211 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 11 | 823 | 0 | 967.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 64.28 | 204 | 0 | 205 | 0 | 204 | 0 | 405 | 0 | 2.58 | 0 | 46 | 115 | 13 | 111 | 0 | 0 | 8 | 212 | 0.04 | 0 | 176 | 120 | 220 | 0 | 305 | 995 | 0 | 6323.31 | 13670.88 | 105.32
13:00 | 7 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 48.4 | 17 | 125 | 91 | 300 | 55 | 55 | 162 | 16 | 225 | 142 | 0 | 0 | 35 | 38 | 194 | 0 | 6 | 125 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 23 | 0 | 12 | 12 | 2.57 | 220 | 0 | 10 | 589 | 53 | 0 | 39 | 0 | 0 | 218 | 0 | 0 | 0 | 810 | 10 | 51 | 100 | 152 | 0 | 351 | 340 | 45 | 45 | 30 | 99 | 50 | 132 | 44 | 20 | 80 | 36 | 52.2 | 12 | 27 | 0 | 310 | 360 | 0 | 50 | 156 | 0 | 0 | 81 | 30 | 0 | 18 | 0 | 0 | 83 | 180 | 65 | 3 | 48.34 | 12 | 7263.01 | 854 | 205 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12 | 902 | 0 | 1003.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 65.95 | 202 | 0 | 204 | 0 | 205 | 0 | 395 | 0 | 2.44 | 0 | 46 | 115 | 35 | 111 | 0 | 0 | 4.2 | 202 | 0.02 | 0 | 169 | 120 | 220 | 0 | 304 | 998 | 0 | 6434.32 | 13697.33 | 105.33
14:00 | 7 | 86 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 45.5 | 17 | 125 | 95 | 300 | 55 | 55 | 162 | 16 | 225 | 149 | 65 | 0 | 35 | 235 | 130 | 0 | 17 | 142 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 24 | 0 | 12 | 12 | 2.76 | 221 | 0 | 2 | 614 | 53 | 0 | 39 | 0 | 0 | 218 | 0 | 0 | 0 | 845 | 9 | 51 | 100 | 162 | 0 | 280 | 305 | 46 | 42 | 32 | 112 | 50 | 125 | 46 | 20 | 80 | 34 | 52.2 | 30 | 29 | 0 | 310 | 383 | 0 | 50 | 134 | 8 | 0 | 81 | 30 | 0 | 16 | 0 | 0 | 83 | 180 | 66 | 2 | 56.34 | 12 | 7516.3 | 854 | 198 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 27 | 887 | 0 | 1008 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2 | 0 | 0 | 13 | 0 | 60.77 | 202 | 0 | 160 | 0 | 180 | 0 | 351 | 0 | 5.55 | 0 | 46 | 115 | 9 | 111 | 0 | 0 | 8 | 177 | 0.02 | 0 | 171 | 100 | 180 | 0 | 307 | 800 | 0 | 6016.54 | 13532.84 | 105.34
15:00 | 7 | 35 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 49.4 | 17 | 125 | 16 | 195 | 30 | 55 | 162 | 0 | 225 | 143 | 69 | 0 | 35 | 328 | 197 | 0 | 15 | 142 | 27.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 33 | 0 | 12 | 12 | 2.79 | 218 | 0 | 2 | 650 | 17 | 0 | 39 | 0 | 0 | 218 | 0 | 0 | 0 | 845 | 4 | 51 | 10 | 163 | 0 | 339 | 340 | 46 | 63 | 31 | 68 | 50 | 137 | 44 | 20 | 64 | 12 | 8 | 5 | 28 | 0 | 315 | 375 | 0 | 70 | 146 | 8 | 0 | 78 | 30 | 0 | 16 | 0 | 0 | 73 | 150 | 69 | 1 | 13.16 | 12 | 7232.85 | 854 | 200 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 37 | 941 | 0 | 1062 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2 | 0 | 0 | 18 | 0 | 45 | 203 | 0 | 160 | 0 | 150 | 0 | 371 | 0 | 2.2 | 0 | 47 | 114 | 6 | 111 | 0 | 0 | 1.9 | 164 | 0.04 | 0 | 174 | 120 | 220 | 0 | 307 | 815 | 0 | 6169.34 | 13402.19 | 105.35
16:00 | 7 | 34 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 43 | 17 | 137 | 16 | 95 | 15 | 55 | 126 | 0 | 225 | 149 | 65 | 0 | 17 | 331 | 165 | 0 | 7 | 142 | 27.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 45 | 0 | 12 | 12 | 2.47 | 217 | 0 | 3 | 679 | 17 | 0 | 40 | 0 | 0 | 219 | 0 | 0 | 0 | 841 | 0 | 51 | 10 | 172 | 0 | 315 | 340 | 45 | 64 | 29 | 48 | 50 | 140 | 43 | 20 | 30 | 50 | 8 | 21 | 36 | 0 | 310 | 380 | 0 | 70 | 146 | 8 | 0 | 80 | 30 | 0 | 16 | 0 | 0 | 74 | 100 | 69 | 1 | 14.25 | 12 | 7110.22 | 855 | 198 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 28 | 861 | 0 | 1104 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2 | 0 | 0 | 22 | 0 | 2.21 | 175 | 0 | 160 | 0 | 150 | 0 | 344 | 0 | 0.1 | 0 | 45 | 113 | 24 | 111 | 0 | 0 | 1.6 | 110 | 0.25 | 0 | 167 | 120 | 180 | 0 | 305 | 845 | 0 | 5967.36 | 13077.58 | 105.36
17:00 | 7 | 34 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 31 | 17 | 145 | 16 | 95 | 15 | 55 | 115 | 0 | 225 | 145 | 70 | 0 | 17 | 327 | 136 | 0 | 3 | 142 | 27.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 62 | 0 | 12 | 12 | 0.28 | 217 | 0 | 12 | 692 | 17 | 0 | 40 | 0 | 0 | 220 | 0 | 0 | 0 | 844 | 2 | 51 | 10 | 175 | 0 | 300 | 340 | 46 | 61 | 31 | 46 | 50 | 146 | 46 | 20 | 30 | 48 | 8 | 20 | 36 | 0 | 310 | 375 | 0 | 70 | 135 | 8 | 0 | 79 | 30 | 0 | 16 | 0 | 0 | 83 | 100 | 70 | 0 | 8.39 | 12 | 7091.17 | 854 | 198 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 19 | 797 | 0 | 1020 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2 | 0 | 0 | 16 | 0 | 7 | 160 | 0 | 160 | 0 | 150 | 0 | 352 | 0 | 0.47 | 0 | 40 | 113 | 10 | 113 | 0 | 0 | 2.9 | 52 | 0.14 | 0 | 172 | 120 | 180 | 0 | 305 | 850 | 0 | 5737.71 | 12828.88 | 105.37
18:00 | 7 | 34 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 30.4 | 17 | 149 | 31 | 95 | 15 | 55 | 113 | 0 | 225 | 150 | 125 | 0 | 17 | 326 | 75 | 0 | 1 | 142 | 25.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 67 | 0 | 12 | 12 | 0.18 | 217 | 0 | 15 | 707 | 17 | 0 | 39 | 0 | 0 | 219 | 0 | 0 | 0 | 845 | 0 | 51 | 10 | 175 | 0 | 300 | 280 | 47 | 62 | 31 | 48 | 70 | 145 | 46 | 20 | 31 | 50 | 8 | 3 | 37 | 0 | 310 | 336 | 0 | 70 | 134 | 8 | 0 | 79 | 30 | 0 | 18 | 0 | 6 | 84 | 100 | 70 | 0 | 1.8 | 12 | 7043.88 | 854 | 198 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 795 | 0 | 1027 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2 | 0 | 0 | 4 | 0 | 3.05 | 160 | 0 | 160 | 0 | 150 | 0 | 368 | 0 | 0.28 | 0 | 38 | 113 | 2 | 112 | 0 | 0 | 0.9 | 22 | 0.05 | 0 | 173 | 120 | 180 | 0 | 306 | 780 | 0 | 5615.48 | 12659.36 | 105.38
19:00 | 14 | 86 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 33.2 | 17 | 149 | 110 | 195 | 17 | 55 | 150 | 2 | 225 | 152 | 140 | 0 | 35 | 327 | 130 | 0 | 0 | 142 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 66 | 73 | 0 | 12 | 12 | 0 | 217 | 0 | 15 | 717 | 17 | 0 | 40 | 0 | 5 | 220 | 0 | 0 | 0 | 1000 | 0 | 51 | 55 | 175 | 0 | 315 | 295 | 47 | 155 | 33 | 62 | 70 | 156 | 46 | 20 | 78 | 58 | 52.2 | 0 | 37 | 0 | 310 | 360 | 0 | 70 | 136 | 8 | 0 | 81 | 30 | 0 | 18 | 0 | 17 | 93 | 118 | 86 | 0 | 0 | 12 | 8024.9 | 854 | 208 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 812 | 13 | 1131 | 0 | 0 | 0 | 25 | 16 | 0 | 87 | 8 | 0 | 0 | 27 | 0 | 160 | 0 | 160 | 0 | 150 | 0 | 375 | 0 | 0 | 0 | 0 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 120 | 220 | 0 | 306 | 825 | 0 | 5935 | 13959.9 | 105.39
19:30 | 50 | 86 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 43.2 | 17 | 120 | 110 | 195 | 55 | 55 | 140 | 16 | 225 | 146 | 145 | 0 | 35 | 330 | 199 | 0 | 0 | 125 | 26.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 66 | 77 | 0 | 12 | 12 | 0 | 217 | 0 | 17 | 711 | 0 | 0 | 40 | 0 | 9 | 220 | 0 | 0 | 0 | 975 | 0 | 51 | 130 | 175 | 0 | 353 | 335 | 47 | 212 | 33 | 94 | 70 | 180 | 46 | 20 | 81 | 56 | 52.2 | 0 | 37 | 0 | 310 | 356 | 0 | 70 | 142 | 8 | 0 | 81 | 30 | 0 | 18 | 0 | 17 | 93 | 150 | 86 | 0 | 0 | 12 | 8385.6 | 854 | 209 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 938 | 17 | 1173 | 0 | 0 | 0 | 70 | 72 | 0 | 87 | 10 | 0 | 0 | 27 | 0 | 160 | 0 | 160 | 0 | 150 | 0 | 337 | 0 | 0 | 0 | 0 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 120 | 220 | 0 | 305 | 1050 | 0 | 6439 | 14824.6
20:00 | 7 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 45 | 17 | 130 | 62 | 15 | 30 | 52 | 143 | 16 | 225 | 149 | 150 | 0 | 17 | 330 | 198 | 0 | 0 | 125 | 26.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 66 | 77 | 0 | 12 | 12 | 0 | 218 | 0 | 22 | 723 | 0 | 0 | 40 | 0 | 18 | 220 | 0 | 0 | 0 | 1005 | 0 | 51 | 40 | 175 | 0 | 352 | 335 | 47 | 194 | 32 | 96 | 70 | 180 | 46 | 20 | 79 | 56 | 16 | 0 | 37 | 0 | 310 | 371 | 0 | 70 | 150 | 8 | 0 | 80 | 30 | 0 | 18 | 0 | 17 | 93 | 150 | 87 | 0 | 0 | 12 | 8010.2 | 854 | 208 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1022 | 17 | 1276 | 0 | 0 | 0 | 95 | 80 | 0 | 40 | 0 | 0 | 0 | 27 | 0 | 168 | 0 | 160 | 0 | 150 | 0 | 350 | 0 | 0 | 0 | 0 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 120 | 220 | 0 | 306 | 1060 | 0 | 6636 | 14646.2 | 105.4
21:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 15.6 | 17 | 96 | 62 | 0 | 0 | 35 | 126 | 0 | 270 | 147 | 178 | 0 | 17 | 330 | 198 | 0 | 0 | 125 | 26.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 66 | 77 | 0 | 12 | 12 | 0 | 218 | 0 | 22 | 713 | 0 | 0 | 28 | 0 | 15 | 220 | 0 | 0 | 0 | 993 | 0 | 51 | 40 | 180 | 0 | 356 | 340 | 48 | 190 | 35 | 97 | 70 | 180 | 47 | 20 | 79 | 58 | 16 | 0 | 37 | 0 | 310 | 355 | 0 | 70 | 153 | 8 | 0 | 81 | 30 | 0 | 18 | 0 | 17 | 103 | 150 | 87 | 0 | 0 | 12 | 7890.8 | 854 | 208 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1126 | 0 | 1443.18 | 0 | 0 | 0 | 113 | 108 | 0 | 40 | 0 | 0 | 0 | 27 | 0 | 201 | 0 | 160 | 0 | 150 | 0 | 341 | 0 | 0 | 0 | 0 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 120 | 220 | 0 | 305 | 1105 | 0 | 7001.18 | 14891.98 | 105.41
22:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 15 | 17 | 96 | 62 | 0 | 0 | 17 | 106 | 0 | 300 | 153 | 300 | 0 | 17 | 335 | 199 | 0 | 0 | 125 | 25 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 66 | 32 | 0 | 12 | 12 | 0 | 218 | 0 | 20 | 712 | 0 | 0 | 26 | 0 | 0 | 220 | 0 | 0 | 0 | 965 | 0 | 51 | 0 | 185 | 0 | 357 | 340 | 48 | 184 | 36 | 65 | 50 | 180 | 47 | 20 | 97 | 42 | 16 | 0 | 37 | 0 | 310 | 351 | 0 | 70 | 149 | 8 | 0 | 81 | 30 | 0 | 18 | 0 | 17 | 103 | 150 | 87 | 0 | 0 | 12 | 7752 | 855 | 207 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1109 | 0 | 1449 | 0 | 0 | 0 | 113 | 113 | 0 | 40 | 0 | 0 | 0 | 27 | 0 | 202 | 0 | 160 | 0 | 150 | 0 | 333 | 0 | 0 | 0 | 0 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 213 | 120 | 220 | 0 | 306 | 1105 | 0 | 6987 | 14739 | 105.42
23:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 15 | 17 | 81 | 48 | 0 | 0 | 17 | 96 | 0 | 350 | 151 | 320 | 0 | 17 | 333 | 136 | 0 | 0 | 125 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 66 | 32 | 0 | 12 | 12 | 0 | 219 | 0 | 22 | 750 | 0 | 0 | 26 | 0 | 0 | 219 | 0 | 0 | 0 | 1005 | 0 | 51 | 0 | 127 | 0 | 349 | 340 | 48 | 177 | 36 | 61 | 50 | 155 | 46 | 20 | 65 | 40 | 16 | 0 | 38 | 0 | 310 | 389 | 0 | 70 | 136 | 8 | 0 | 82 | 30 | 0 | 18 | 0 | 17 | 103 | 150 | 86 | 0 | 0 | 12 | 7633 | 854 | 221 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 1371.57 | 0 | 0 | 0 | 113 | 113 | 0 | 40 | 0 | 0 | 0 | 27 | 0 | 202 | 0 | 160 | 0 | 150 | 0 | 380 | 0 | 0 | 0 | 0 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 222 | 120 | 220 | 0 | 304 | 1060 | 0 | 6922.57 | 14555.57 | 105.43
Total KWH | 116928 | 1032960 | 788160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9146230 | 574560 | 436320 | 2415024 | 628320 | 1984691 | 408814 | 737931 | 2125440 | 58560 | 6417500 | 3595025 | 1504027 | 0 | 410175 | 6360548 | 4521000 | 0 | 155571 | 2784000 | 565200 | 500760 | 0 | 0 | 0 | 0 | 0 | 0 | 409440 | 504046 | 691500 | 0 | 263040 | 255360 | 18406 | 5289338 | 11709 | 396000 | 17090909.09 | 185673 | 0 | 537600 | 2336.4 | 93673 | 5207582 | 0 | 0 | 0 | 22401816 | 58995 | 1147706 | 883200 | 3077818 | 0 | 8428800 | 8018000 | 1165920 | 3575000 | 814968 | 1800000 | 1376270 | 3510240 | 970200 | 463550 | 1446660 | 971520 | 449237 | 205536 | 489184 | 0 | 7326100 | 9315000 | 0 | 1454160 | 3503945 | 159216 | 0 | 1946880 | 716448 | 0 | 437000 | 0 | 267480 | 2122800 | 3242400 | 1850880 | 13600 | 270880 | 294960 | 172400725.49 | 20681454 | 5239584 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 195840 | 22443630 | 44160 | 27629960 | 0 | 78480 | 0 | 547680 | 553344 | 0 | 383168 | 13326 | 0 | 238900 | 155570 | 327000 | 4788182 | 0 | 4546127 | 0 | 4498127 | 0 | 8987563 | 0 | 28800 | 0 | 802909 | 2374318 | 201733 | 2315500 | 0 | 0 | 44744.52 | 1498320 | 1426 | 0 | 4909000 | 2838000 | 5317680 | 0 | 7351992 | 24203636.36 | 0 | 154152153.88 | 326552879.37

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 29-07-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13670.88 | MW | 12:00 Hr. | Energy Generated |  |  | 326.5529 |  | MKWHr.
| Day Peak Demand |  |  | 13670.88 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.591 |  | MKWHr.
| Evening Peak Generation |  |  | 14891.98 | MW | 21:00 Hr. | Energy Demand |  |  | 327.1439 |  | MKWHr.
| Evening Peak Demand |  |  | 15000.98 | MW | 21:00 Hr. | Maximum Temperature |  |  | 32.3 |  | °C
| Minimum Generation of the Day |  |  | 12292.15 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 989.06 |  | MMCFD
| Maximum Generation of the Day |  |  | 14891.98 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.3715 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 32.6103 | 0 | 14.5019 | 0 | 0 | 0.15557 | 0 | 0 | 47.2677 | Gas | 129.2068 | Gas | 445246558.07
| Chattogram Zone |  |  | 5.6036 | 39.4927 | 2.5449 | 0 | 5.2893 | 0.077401 | 0 | 0.40944 | 53.4174 | Coal | 99.2039 | Coal | 592915665.05
| Cumilla Zone |  |  | 28.068 | 0 | 9.5487 | 0 | 0 | 0.20554 | 0.97152 | 0 | 38.7938 | HFO | 38.9887 | HFO | 724009459.528
| Mymensingh Zone |  |  | 1.8509 | 0 | 5.9276 | 0 | 0 | 0.28448 | 0 | 0 | 8.063 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 24.8587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.8587 | Hydro | 5.2893 | Hydro | 528933.8
| Khulna Zone |  |  | 5.2396 | 22.4436 | 0.04416 | 0 | 0 | 0.19584 | 21.5935 | 0 | 49.5167 | Solar | 3.2598 | Solar | 55437602.6072
| Barishal Zone |  |  | 8.1557 | 36.4646 | 0 | 0 | 0 | 0.001426 | 0 | 0 | 44.6217 | Import | 50.1949 | Import | 256509621.34
| Rajshahi Zone |  |  | 22.82 | 0 | 1.7316 | 0 | 0 | 0.5947 | 27.63 | 0 | 52.7762 | Wind | 0.40944 | Wind | 5994201.6
| Rangpur Zone |  |  | 0 | 0.80291 | 4.6898 | 0 | 0 | 1.7448 | 0 | 0 | 7.2375
| Total |  |  | 129.2068 | 99.2039 | 38.9887 | 0 | 5.2893 | 3.2598 | 50.1949 | 0.40944 | 326.5529
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 445246558.07 |  | Hydro | 528933.8
|  |  |  | Coal | 592915665.05 |  | Solar | 55437602.6072
|  |  |  | HFO | 724009459.528 |  | Import | 256509621.34
|  |  |  | HSD | 0 |  | Wind | 5994201.6
[5 empty] | Total: | 208,06,42,041 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.6815 | Peak Hr Flow | 854.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 46849145.55 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.63 | Peak Hr Flow | 1443.18 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 650 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.97152 | Peak Hr Flow | 58.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 974 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 49.2829 | Peak Hr Flow | 2355.18 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5106
|  |  |  | Chattogram |  | 0 |  | 1424
|  |  |  | Cumilla |  | 0 |  | 1319
|  |  |  | Mymensingh |  | 0 |  | 1248
|  |  |  | Sylhet |  | 30 |  | 647
|  |  |  | Khulna |  | 0 |  | 1681
|  |  |  | Barishal |  | 0 |  | 438
|  |  |  | Rajshahi |  | 0 |  | 1518
|  |  |  | Rangpur |  | 74 |  | 1035
|  |  |  | Total |  | 104 |  | 14416
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Bibiana-II 341 MW CCPP (Summit) GT |  |  | 222 | 3 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
|  | 4 | Bibiana-II 341 MW CCPP (Summit) ST |  |  | 119 | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 641 |  |  |  | Total | 707
|  |  |  | Total Unavailable Capacity |  |  |  | 1348
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:04 |  | Ashuganj CCPP 225 MW Shutdown with remarks:- ST
| 08:05 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- GT Running
| 08:05 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- GT
|  | 08:40 | Kodda 132/33kV S/S Tr-3 (426T) HT is restored.
|  | 08:52 | Kodda 132/33kV S/S Tr-3 (426T) LT is restored.
| 09:10 | 17:14 | Barapukuria-Saidpur 132 kV Ckt-2 Scheduled S/D from Saidpur 132/33kV end Due to QF-GMD-39
and as the instruction by ALDC, Bogura
|  | 09:15 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 LT is restored.
|  | 09:15 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 HT is restored.
| 09:21 | 17:18 | Barapukuria-Saidpur 132 kV Ckt-2 Scheduled S/D from Barapukuria 230/132/33kV end Due to
Maintenance work at Saidpur Substation end.
| 09:54 | 14:26 | Daudkandi-Sonargaon 132 kV Ckt-1 Forced S/D from Sonargaon 132/33kV end Due to According
to the direction of NLDC
| 09:54 | 14:26 | Daudkandi-Sonargaon 132 kV Ckt-2 Forced S/D from Sonargaon 132/33kV end Due to According
to the direction of NLDC-299724
|  | 10:10 | Ashuganj-Kishoreganj 132kV Ckt-2 is restored.
| 10:25 | 14:56 | Ashuganj-Ghorasal 132kV Ckt-2 Scheduled S/D from Ashuganj 230/132/33kV end Due to due to
132KV busbar-1 temperature issue
|  | 11:05 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-1 is restored.
|  | 11:06 | Jashore 132/33kV S/S JH-1(L2) is restored.
| 11:24 | 13:50 | Hasnabad 132/33kV S/S Fatulla (Pre-Brahmongaon) Forced S/D Due to Red hot maintenance
| 11:30 | 13:17 | Ghorashal 230kV S/S TARFO-2 LT Scheduled S/D Due to Transfor Bushing Tightening | [7 empty] | 53.0MW load interrup.
| 11:35 | 13:12 | Ghorashal 230kV S/S TARFO-2 HT Scheduled S/D Due to Transformer Bushing clamp tightening. | [7 empty] | 53.0MW load interrup.
| 11:41 | 13:21 | Hasnabad 230/132kV S/S AUTO TR-1 LT Scheduled S/D Due to 132 kV Isolator maintenance work (DS-121)
| 11:42 | 13:21 | Hasnabad 230/132kV S/S AUTO TR-1 HT Scheduled S/D Due to 132 kV Isolator maintenance work (DS-121)
|  | 11:43 | Bibiana 400/230kV S/S Summit GTG is restored.
| 11:45 |  | Hasnabad 132/33kV S/S 132kV Main Bus Forced S/D Due to Red hot maintenance work.
| 12:00 |  | Day peak generation: 13668 MW
| 12:18 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- GT
| 12:39 |  | Meghnaghat CCPP(Summit)-2 Shutdown with remarks:- GT
| 13:35 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- GT
| 14:51 | 16:04 | Bajitpur 132/33kV S/S Tr-1(404T) HT Forced S/D Due to 33kV bus section-1 insulator broken maintenance. | [7 empty] | 40.0MW load interrup.
| 15:28 | 17:01 | Mahasthangarh 132/33kV S/S 416T MTR 2 LT Scheduled S/D Due to Kalai 33 kV Feeder Source | [7 empty] | 30.0MW load
|  |  | side DS Maintemance Work. | [7 empty] | interrup.
| 15:30 | 17:01 | Mahasthangarh 132/33kV S/S 416T MTR 2 HT Scheduled S/D Due to Kalai 33 kV Feeder Source | [7 empty] | 30.0MW load interrup.
|  |  | side DS Maintemance Work. | [7 empty] | interrup.
| 15:47 | 19:06 | Gopalganj 132/33kV S/S T2 LT Scheduled S/D Due to 33 kv bus Section-3 DS maintenance. | [7 empty] | 55.0MW load interrup.
| 15:47 | 19:05 | Gopalganj 132/33kV S/S T2 HT Scheduled S/D Due to 33 kv bus Section-3 DS maintenance. | [7 empty] | 55.0MW load interrup.
| 16:03 | 17:24 | Gollamari 132/33kV S/S Tr-2 LT Forced S/D Due to Fault of 33kv Pbs feeder.
| 16:04 | 17:23 | Gollamari 132/33kV S/S Tr-2 HT Forced S/D Due to Fault of 33kv Pbs feeder.
| 16:39 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- ST
| 16:39 |  | Summit Meghnaghat-2 589 MW CCPP ST was sync.
|  | 16:44 | Ashuganj 230/132/33kV S/S T-4 Kalabagan HT is restored.
|  | 16:50 | Ashuganj 230/132/33kV S/S T-4 Kalabagan LT is restored.
|  | 18:02 | Ashuganj 230/132/33kV S/S TR-OAT-12 LT is restored.
|  | 18:05 | Ashuganj 230/132/33kV S/S TR-OAT-12 HT is restored.
| 18:06 |  | Barapukuria PS Unit-1 tripped due to reheater leakage.
| 18:22 |  | Ashuganj 225MW ST was synchronized.
| 18:22 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- ST
| 18:33 |  | BIPTC S/S 20DF42 Tripped showing 87 ACF relays Due to Tripped by Capacitor unbalance
| 19:25 | 21:25 | Chowmuhani 132/33kV S/S TR1 Scheduled S/D Due to Emergency shutdown of TR-01 for red hot
occurs at R phase 33 KV side
| 20:45 |  | Meghnaghat 450MW CCPP GT1 was sync.
| 20:45 |  | Meghnaghat 450 MW CCPP (MPL) Synchronized with remarks:- GT-1
| 21:00 |  | Evening Peak Generation: 14891 MW.
| 22:41 | 23:48 | Chowmuhani 132/33kV S/S TR2-425T LT Forced S/D Due to 33KV REB Sadar Incoming DS Y Phase | [7 empty] | 30.0MW load
|  |  | (red hot) Loop Maintenance | [7 empty] | interrup.
| 22:42 | 00:02 | Chowmuhani 132/33kV S/S TR1-415T LT Forced S/D Due to 33KV Maijdee Incoming DS Y Phase | [7 empty] | 30.0MW load
|  |  | (red hot) Loop Maintenance | [7 empty] | interrup.
| 01:15 |  | JERA Meghnaghat Power Limited 718 MW CCPP GT-12 was shutdown.
| 06:06 |  | Hathazari 230/132/33kV S/S T-01 HT Scheduled S/D Due to 33 kv Bus maintenance | [7 empty] | 40.0MW load interrup.
| 06:06 |  | Hathazari 230/132/33kV S/S T-01 LT Scheduled S/D Due to 33 kV Bus maintenance | [7 empty] | 40.0MW load interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 29-07-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 270 | 6417500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 147 | 3595025 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 408814 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 198 | 4521000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 6360548 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 116928 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 15.6 | 574560 | FGMO
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 62 | 628320 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 737931 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 410175 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 26.2 | 565200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 500760 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 33 | 788160 | Fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 1984691 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 96 | 2415024 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1032960 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 58560 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 2125440 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 155571 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 436320 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 178 | 1504027 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 733.79 | 500 | 9146230 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 125 | 2784000 | Engine Problem
Dhaka Area Total |  |  |  |  | 6673.514 | 2267.8 | 47267744
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 2336.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 58995 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 28 | 537600 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 218 | 5289338 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 5207582 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 15 | 93673 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 77 | 691500 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 504046 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 263040 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 22 | 396000 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 18406 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 11709 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 255360 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 185673 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 993 | 22401816 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 9 | 409440 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 713 | 17090909.09 | -
Chattogram Area Total |  |  |  |  | 4895.72 | 2385 | 53417423.49
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 190 | 3575000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 356 | 8428800 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 340 | 8018000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 35 | 814968 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 48 | 1165920 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 180 | 3077818 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1147706 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 40 | 883200 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 37 | 489184 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1376270 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 180 | 3510240 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 58 | 971520 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 16 | 449237 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 463550 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 79 | 1446660 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 47 | 970200 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 97 | 1800000 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 205536 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1844 | 38793809
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 87 | 1850880 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 150 | 3242400 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 103 | 2122800 | Engine Problem
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 270880 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 294960 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 267480 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 369 | 8063000
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 70 | 1454160 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 153 | 3503945 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 716448 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1946880 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 437000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 159216 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | -
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 355 | 9315000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 310 | 7326100 | -
Sylhet Area Total |  |  |  |  | 2325 | 1025 | 24858749
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 854 | 20681454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 208 | 5239584 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 44160 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 195840 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1126 | 22443630 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2226 | 49516668
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 305 | 7351992 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2838000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1105 | 24203636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5317680 | -
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 215 | 4909000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1426 | -
Barishal Area Total |  |  |  |  | 2236 | 1965 | 44621734.36
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 78480 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 13326 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 201 | 4788182 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 160 | 4546127 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 150 | 4498127 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 341 | 8987563 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 155570 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 40 | 383168 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 108 | 553344 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 547680 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 28800 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1443.18 | 27629960 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 327000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 238900 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2583.18 | 52776227
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 802909 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 2315500 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 44744.52 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 114 | 2374318 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 201733 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1498320 | -
Rangpur Area Total |  |  |  |  | 950 | 227 | 7237524.52
Eastern Grid Total |  |  |  |  | 17401.505 | 7890.8 | 172400725.49
Western Grid Total |  |  |  |  | 10378.16 | 7001.18 | 154152153.88
National Grid Total |  |  |  |  | 27779.665 | 14891.98 | 326552879.37
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 29-07-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9714.88 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4598.6 | MW
i) Dhaka area |  |  | 5106.48 |  | MW | i) Khulna area |  |  |  | 1680.9 | MW
ii) Chattogram area |  |  | 1424 |  | MW | ii) Barishal area |  |  |  | 438.5 | MW
iii) Cumilla area |  |  | 1319.4 |  | MW | iii) Rajshahi area |  |  |  | 1518.2 | MW
iv) Mymensingh area |  |  | 1248 |  | MW | iv) Rangpur area |  |  |  | 961 | MW
v) Sylhet area |  |  | 617 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14313.48 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 8 | 02:00 | 67 | Hathazari | 95 | 18:30 | 133 | PHP | 8 | 02:00
2 | AKSML | 136 | 03:00 | 68 | Ishurdi | 82 | 19:30 | 134 | Pabna | 122 | 19:30
3 | Aftabnagar | 54 | 11:00 | 69 | Jaldhaka | 74 | 21:00 | 135 | Palashbari | 108 | 20:00
4 | Agargaon | 134 | 13:00 | 70 | Jamalpur | 138 | 21:00 | 136 | Panchagarh | 66 | 21:00
5 | Agrabad | 76 | 19:00 | 71 | Jashore | 134 | 19:30 | 137 | Patuakhali | 62 | 00:00
6 | Amnura | 36 | 01:00 | 72 | Jhenaidah | 116 | 21:00 | 138 | Payra | 32 | 00:00
7 | Ashuganj | 95 | 00:00 | 73 | Joydebpur | 148 | 15:00 | 139 | Postogola | 60 | 12:00
8 | BSRM | 209 | 20:00 | 74 | Joypurhat | 64 | 21:00 | 140 | Purbachal | 20 | 19:00
9 | Bagerhat | 77 | 00:00 | 75 | Juldah | 17 | 00:00 | 141 | Purbasadipur | 124 | 01:00
10 | Bajitpur | 78 | 17:00 | 76 | KSRM | 43 | 13:00 | 142 | Rahanpur | 40 | 23:00
11 | Bakulia | 98 | 12:00 | 77 | Kabirpur | 240 | 15:00 | 143 | Rahim | 24 | 07:00
12 | Banani | 88 | 12:00 | 78 | Kachua | 88 | 19:00 | 144 | Rajbari | 79 | 20:00
13 | Bangabhaban | 18 | 10:00 | 79 | Kallyanpur | 102 | 00:00 | 145 | Rajendrapur | 131 | 19:30
14 | Barapukuria | 72 | 19:30 | 80 | Kalurghat | 36 | 14:00 | 146 | Rajshahi | 106 | 00:00
15 | Barguna | 20 | 19:00 | 81 | Kamrangirchar | 75 | 14:00 | 147 | Rajshahi-230 | 84 | 21:00
16 | Barishal | 106 | 12:00 | 82 | Kaptai | N/A | N/A | 148 | Ramganj | 116 | 00:00
17 | Barishal-230 | 90 | 23:00 | 83 | Kasba | 36 | 21:00 | 149 | Rampur | 36 | 19:00
18 | Baroaulia | 59 | 10:00 | 84 | Kazla | 98 | 16:00 | 150 | Rangamati | 17 | 19:00
19 | Baroirhat | 71 | 19:30 | 85 | Keranigonj | 83 | 19:00 | 151 | Rangpur | 146 | 20:00
20 | Bashundhara | 196 | 13:00 | 86 | Khagrachori | 32 | 19:00 | 152 | Ruppur | 6.8 | 09:00
21 | BashundharaCement | 10 | 16:00 | 87 | Khulna | 66 | 13:00 | 153 | SSM | 0 | 00:00
22 | Beanibazar | 76 | 00:00 | 88 | Khulshi | 184 | 15:00 | 154 | Saidpur | 113 | 20:00
23 | Benapole | 64 | 20:00 | 89 | Kishoreganj | 131 | 19:30 | 155 | Satkhira | 121 | 20:00
24 | Bhaluka | 157 | 19:00 | 90 | Kodda | 319 | 11:00 | 156 | Satmasjid | 98 | 13:00
25 | Bhandaria | 52 | 00:00 | 91 | Kulaura | 53 | 22:00 | 157 | Savar | 237 | 11:00
26 | Bhangura | 36 | 20:00 | 92 | Kurigram | 66 | 21:00 | 158 | SevenRings | 20.62 | 19:00
27 | Bheramara(GK) | 63 | 00:00 | 93 | Kushtia | 147 | 19:30 | 159 | ShahCement | 35 | 17:00
28 | Bhulta | 239 | 21:00 | 94 | Laksam | 33 | 00:00 | 160 | Shahjadpur | 84 | 19:30
29 | Bog-Sherpur | 68 | 19:30 | 95 | Lakshmipur | 33 | 23:00 | 161 | Shahjibazar | 127 | 00:00
30 | Bogura | 177 | 22:00 | 96 | Lalbag | 56 | 12:00 | 162 | Shahmirpur | 60 | 00:00
31 | Borhanuddin | 92 | 21:00 | 97 | Lalmonirhat | 70 | 19:30 | 163 | Shariatpur | 86 | 00:00
32 | Brahmanbaria | 132 | 23:00 | 98 | MI_Cement | 14.2 | 09:00 | 164 | Sherpur | 156 | 21:00
33 | Cantonment | 144 | 13:00 | 99 | Madanganj | 36 | 00:00 | 165 | Shikalbaha | 19 | 19:30
34 | Chandina | 13.4 | 21:00 | 100 | Madaripur | 107 | 23:00 | 166 | Shitalakhya | 80.4 | 11:00
35 | Chandpur | 76 | 19:30 | 101 | Madartek | 90 | 00:00 | 167 | Sholosohor | 45 | 12:00
36 | Chandraghona | 34 | 19:00 | 102 | Madunaghat | 52 | 19:00 | 168 | Shyampur | 152 | 13:00
37 | Chapai | 68 | 21:00 | 103 | Magura | 66 | 19:30 | 169 | Siddhirganj | 122 | 12:00
38 | Charsaidpur | 24 | 04:00 | 104 | Mahasthangarh | 86 | 19:30 | 170 | Sirajganj | 114 | 21:00
39 | Chauddagram | 67 | 00:00 | 105 | Maijdee | 15 | 00:00 | 171 | Sonargaon | 93 | 09:00
40 | Chhatak | 42 | 22:00 | 106 | Manikganj | 126 | 21:00 | 172 | Sreemongol | 79 | 00:00
41 | Chowmuhani | 162 | 00:00 | 107 | Maniknagar | 84 | 13:00 | 173 | Sreepur | 103 | 19:00
42 | Chuadanga | 104 | 00:00 | 108 | Matarbari | 47 | 19:30 | 174 | Srinagar | 46.5 | 22:00
43 | Coxsbazar | 122 | 19:30 | 109 | Matuail | 62 | 13:00 | 175 | Sunamganj | 56 | 18:30
44 | Cumilla(N) | 133 | 00:00 | 110 | Millgate | 121 | 12:00 | 176 | Sylhet | 55 | 19:30
45 | Cumilla(S) | 157 | 19:00 | 111 | Mirpur | 127 | 13:00 | 177 | Sylhet-132 | 129 | 13:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 10 | 00:00 | 178 | TK | 32 | 21:00
47 | Daudkandi | 149 | 19:00 | 113 | Mirzapur | 47 | 22:00 | 179 | Tangail | 176 | 21:00
48 | Dhaka | 76 | 12:00 | 114 | Mithapukur | 76 | 19:30 | 180 | Taraganj | 26 | 19:00
49 | Dhamrai | 116 | 08:00 | 115 | Modern | N/A | N/A | 181 | Thakurgaon | 112 | 19:30
50 | Dhanmondi | 129 | 13:00 | 116 | Mogbazar | 149.9 | 13:00 | 182 | Tongi | 109 | 08:00
51 | Dohazari | 94 | 20:00 | 117 | Mongla | 35 | 11:00 | 183 | Ullahpara | 38 | 19:30
52 | Faridpur | 162 | 19:30 | 118 | Motijheel | 45 | 13:00 | 184 | Ullon | 40 | 19:00
53 | Fatullah | 99 | 10:00 | 119 | Muktagacha | 37 | 19:30 | 185 | Uttara | 85 | 12:00
54 | Fenchuganj | 45 | 23:00 | 120 | Munshiganj | 127 | 01:00 | 186 | UttaraNew | 60 | 12:00
55 | Feni | 99 | 20:00 | 121 | Muradnagar | 41 | 21:00 | 187 | Zigatola | 70 | 13:00
56 | GPH | 77 | 09:00 | 122 | Mymensingh | 198 | 19:30
57 | Ghatail | 82 | 19:00 | 123 | Naogaon | 132 | 19:30
58 | Ghorashal | 12 | 18:30 | 124 | Narail | 56 | 19:30
59 | Ghorashal-230 | 80 | 19:30 | 125 | Narinda | 79 | 13:00
60 | Goalpara | 30 | 00:00 | 126 | Narshingdi | 178 | 22:00
61 | Gollamari | 86 | 19:30 | 127 | Natore | 145 | 21:00
62 | Gopalganj | 116.8 | 20:00 | 128 | Nawabganj | 57.2 | 22:00
63 | Gulshan | 74 | 11:00 | 129 | Netrakona | 149 | 19:30
64 | Halishahar | 66 | 16:00 | 130 | New | 84.3 | 15:00
65 | HaripurSBU | 151 | 11:00 | 131 | Niamatpur | 70 | 00:00
66 | Hasnabad | 74 | 21:00 | 132 | Noapara | 45 | 07:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 29-07-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14661.7 | 18 |  | 14680.51
1:00 | 13984.4 | 15 |  | 14000.4
2:00 | 13690 | 10 |  | 13700
3:00 | 13372 | 0 |  | 13372
4:00 | 12956 | 0 |  | 12956
5:00 | 12797 | 0 |  | 12797
6:00 | 12344.77 | 0 |  | 12344.77
7:00 | 12355.12 | 0 |  | 12355.12
8:00 | 12321.32 | 0 |  | 12321.32
9:00 | 12292.15 | 0 |  | 12292.15
10:00 | 12804.81 | 0 |  | 12804.81
11:00 | 13311.91 | 0 |  | 13311.91
12:00 | 13670.88 | 0 |  | 13670.88
13:00 | 13697.33 | 40 |  | 13739.33
14:00 | 13532.84 | 58 |  | 13593.84
15:00 | 13402.19 | 30 |  | 13433.19
16:00 | 13077.58 | 0 |  | 13077.58
17:00 | 12828.88 | 0 |  | 12828.88
18:00 | 12659.36 | 0 |  | 12659.36
19:00 | 13959.9 | 30 |  | 13990.9
19:30 | 14824.6 | 168 |  | 15000.6
20:00 | 14646.2 | 147 |  | 14800.2
21:00 | 14891.98 | 104 |  | 15000.98
22:00 | 14739 | 77 |  | 14819
23:00 | 14555.57 | 62 |  | 14620.57
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 29-07-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7503.7 | 7158 | 14661.7 | DAILY GENERATION CURVE
00:30 | 7253.55 | 7069.5 | 14323.05
01:00 | 7003.4 | 6981 | 13984.4 | 29-07-2025
01:30 | 6924.7 | 6912.5 | 13837.2
02:00 | 6846 | 6844 | 13690
02:30 | 6847.5 | 6683.5 | 13531
03:00 | 6849 | 6523 | 13372
03:30 | 6832 | 6332 | 13164
04:00 | 6815 | 6141 | 12956
04:30 | 6709.5 | 6167 | 12876.5
05:00 | 6604 | 6193 | 12797
05:30 | 6440.11 | 6130.775 | 12570.885
06:00 | 6276.22 | 6068.55 | 12344.77
06:30 | 6358.15 | 5991.795 | 12349.945
07:00 | 6440.08 | 5915.04 | 12355.12
07:30 | 6407.485 | 5930.735 | 12338.22
08:00 | 6374.89 | 5946.43 | 12321.32
08:30 | 6291.295 | 6015.44 | 12306.735
09:00 | 6207.7 | 6084.45 | 12292.15
09:30 | 6414.6 | 6133.88 | 12548.48
10:00 | 6621.5 | 6183.31 | 12804.81
10:30 | 6870.925 | 6187.435 | 13058.36
11:00 | 7120.35 | 6191.56 | 13311.91
11:30 | 7233.96 | 6257.435 | 13491.395
12:00 | 7347.57 | 6323.31 | 13670.88
12:30 | 7305.29 | 6378.815 | 13684.105
13:00 | 7263.01 | 6434.32 | 13697.33
13:30 | 7389.655 | 6225.43 | 13615.085
14:00 | 7516.3 | 6016.54 | 13532.84
14:30 | 7374.575 | 6092.94 | 13467.515
15:00 | 7232.85 | 6169.34 | 13402.19
15:30 | 7171.535 | 6068.35 | 13239.885
16:00 | 7110.22 | 5967.36 | 13077.58
16:30 | 7100.695 | 5852.535 | 12953.23
17:00 | 7091.17 | 5737.71 | 12828.88
17:30 | 7067.525 | 5676.595 | 12744.12
18:00 | 7043.88 | 5615.48 | 12659.36
18:30 | 7534.39 | 5775.24 | 13309.63
19:00 | 8024.9 | 5935 | 13959.9
19:30 | 8385.6 | 6439 | 14824.6
20:00 | 8010.2 | 6636 | 14646.2
20:30 | 7950.5 | 6818.59 | 14769.09 |  | Executive Engineer
21:00 | 7890.8 | 7001.18 | 14891.98 |  | Network Operation Division
21:30 | 7821.4 | 6994.09 | 14815.49
22:00 | 7752 | 6987 | 14739
22:30 | 7692.5 | 6954.785 | 14647.285
23:00 | 7633 | 6922.57 | 14555.57

## En-Curve
QF-LDC-12
Date | 29-07-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3801 | 1313.7 | 854 | 38 | 42 | 1464 | 221 | 4844 | 0 | 564 | 1505 | 0 | 0 | 15 | 18 | DAILY ENERGY CURVE
00:30 | 3799 | 1329.85 | 854.5 | 38 | 42 | 1460 | 220.5 | 4821.5 | 0 | 449.5 | 1296.2 | 0 | 0 | 12 | 16.5 | 29-07-2025
01:00 | 3797 | 1346 | 855 | 38 | 42 | 1456 | 220 | 4799 | 0 | 335 | 1087.4 | 0 | 0 | 9 | 15
01:30 | 3827 | 1355.5 | 855 | 38 | 41 | 1410 | 220 | 4759.5 | 0 | 267 | 1050.2 | 0 | 0 | 14 | 12.5 | Energy Generated | 326.5529 |  | MKWHr
02:00 | 3857 | 1365 | 855 | 38 | 40 | 1364 | 220 | 4720 | 0 | 199 | 1013 | 0 | 0 | 19 | 10 | Energy not Served | 0.591 |  | MKWHr
02:30 | 3858.5 | 1482.5 | 854.5 | 38 | 40 | 1313 | 219.5 | 4568 | 0 | 167 | 973.5 | 0 | 0 | 16.5 | 5 | Total Energy Requirement | 327.1439 |  | MKWHr
03:00 | 3860 | 1600 | 854 | 38 | 40 | 1262 | 219 | 4416 | 0 | 135 | 934 | 0 | 0 | 14 | 0
03:30 | 3868.5 | 1629.5 | 854 | 38 | 39 | 1190 | 218.5 | 4349 | 0 | 101 | 860 | 0 | 0 | 16.5 | 0
04:00 | 3877 | 1659 | 854 | 38 | 38 | 1118 | 218 | 4282 | 0 | 67 | 786 | 0 | 0 | 19 | 0
04:30 | 3928 | 1552 | 854 | 38 | 37 | 1121 | 217.5 | 4253.5 | 0 | 69.5 | 790.5 | 0 | 0 | 15.5 | 0
05:00 | 3979 | 1445 | 854 | 38 | 36 | 1124 | 217 | 4225 | 0 | 72 | 795 | 0 | 0 | 12 | 0
05:30 | 3918 | 1436.5 | 854 | 38 | 35 | 1121.5 | 216.5 | 4125 | 13.385 | 106.5 | 690.5 | 0 | 0 | 16 | 0
06:00 | 3857 | 1428 | 854 | 38 | 34 | 1119 | 216 | 4025 | 26.77 | 141 | 586 | 0 | 0 | 20 | 0
06:30 | 3902.5 | 1447 | 854 | 38 | 34 | 1073 | 216.5 | 3970.5 | 60.445 | 145.5 | 589.5 | 0 | 0 | 19 | 0
07:00 | 3948 | 1466 | 854 | 38 | 34 | 1027 | 217 | 3916 | 94.12 | 150 | 593 | 0 | 0 | 18 | 0
07:30 | 3913 | 1464 | 853.5 | 38 | 33 | 1025.915 | 217 | 3905 | 141.805 | 163 | 562.5 | 0 | 0 | 21.5 | 0
08:00 | 3878 | 1462 | 853 | 38 | 32 | 1024.83 | 217 | 3894 | 189.49 | 176 | 532 | 0 | 0 | 25 | 0
08:30 | 3740 | 1465 | 854 | 38 | 27 | 1029.53 | 217.5 | 3904 | 186.205 | 176 | 640.5 | 0 | 0 | 29 | 0
09:00 | 3602 | 1468 | 855 | 38 | 22 | 1034.23 | 218 | 3914 | 182.92 | 176 | 749 | 0 | 0 | 33 | 0
09:30 | 3572 | 1474.5 | 854.5 | 38 | 27 | 978.15 | 218 | 3903 | 284.33 | 185 | 989 | 0 | 0 | 25 | 0
10:00 | 3542 | 1481 | 854 | 38 | 32 | 922.07 | 218 | 3892 | 385.74 | 194 | 1229 | 0 | 0 | 17 | 0
10:30 | 3506 | 1484.9 | 854 | 38 | 31 | 919.46 | 219 | 3861.5 | 436.25 | 212.5 | 1470.75 | 0 | 0 | 25 | 0
11:00 | 3470 | 1488.8 | 854 | 38 | 30 | 916.85 | 220 | 3831 | 486.76 | 231 | 1712.5 | 0 | 0 | 33 | 0
11:30 | 3494 | 1566.15 | 854 | 38 | 32 | 942.13 | 220 | 3835.5 | 454.265 | 240 | 1790.85 | 0 | 0 | 24.5 | 0
12:00 | 3518 | 1643.5 | 854 | 38 | 34 | 967.41 | 220 | 3840 | 421.77 | 249 | 1869.2 | 0 | 0 | 16 | 0
12:30 | 3474 | 1594.5 | 854 | 38 | 35 | 985.56 | 220 | 3829 | 423.145 | 309.5 | 1906.9 | 0 | 0 | 14.5 | 20
13:00 | 3430 | 1545.5 | 854 | 38 | 36 | 1003.71 | 220 | 3818 | 424.52 | 370 | 1944.6 | 0 | 0 | 13 | 40
13:30 | 3384 | 1556 | 854 | 38 | 35 | 1005.855 | 220.5 | 3744 | 420.98 | 394.1 | 1947.15 | 0 | 0 | 15.5 | 49
14:00 | 3338 | 1566.5 | 854 | 38 | 34 | 1008 | 221 | 3670 | 417.44 | 418.2 | 1949.7 | 0 | 0 | 18 | 58
14:30 | 3491.5 | 1593.5 | 854 | 38 | 23 | 1035 | 219.5 | 3724.5 | 366.265 | 361.7 | 1748.05 | 0 | 0 | 12.5 | 44
15:00 | 3645 | 1620.5 | 854 | 38 | 12 | 1062 | 218 | 3779 | 315.09 | 305.2 | 1546.4 | 0 | 0 | 7 | 30
15:30 | 3590 | 1657 | 854.5 | 38 | 31 | 1083 | 217.5 | 3761 | 274.485 | 314.7 | 1414.2 | 0 | 0 | 4.5 | 15
16:00 | 3535 | 1693.5 | 855 | 38 | 50 | 1104 | 217 | 3743 | 233.88 | 324.2 | 1282 | 0 | 0 | 2 | 0
16:30 | 3505.5 | 1694.5 | 854.5 | 38 | 49 | 1062 | 217 | 3721.5 | 187.53 | 337.2 | 1283.5 | 0 | 0 | 3 | 0
17:00 | 3476 | 1695.5 | 854 | 38 | 48 | 1020 | 217 | 3700 | 141.18 | 350.2 | 1285 | 0 | 0 | 4 | 0
17:30 | 3414.5 | 1726 | 854 | 38 | 49 | 1023.5 | 217 | 3672 | 91.22 | 360.7 | 1289.2 | 0 | 0 | 9 | 0
18:00 | 3353 | 1756.5 | 854 | 38 | 50 | 1027 | 217 | 3644 | 41.26 | 371.2 | 1293.4 | 0 | 0 | 14 | 0
18:30 | 3472.5 | 1785 | 854 | 38 | 54 | 1079 | 217 | 3738.5 | 20.63 | 529.6 | 1508.4 | 0 | 0 | 13 | 15
19:00 | 3592 | 1813.5 | 854 | 38 | 58 | 1131 | 217 | 3833 | 0 | 688 | 1723.4 | 0 | 0 | 12 | 30
19:30 | 3758 | 1825.2 | 854 | 38 | 56 | 1173 | 217 | 4194 | 0 | 658 | 2040.4 | 0 | 0 | 11 | 168
20:00 | 3773 | 1845.2 | 854 | 38 | 56 | 1276 | 218 | 4334 | 0 | 537 | 1702 | 0 | 0 | 13 | 147
20:30 | 3781 | 1885.7 | 854 | 38 | 57 | 1359.59 | 218 | 4395.5 | 0 | 537 | 1632.3 | 0 | 0 | 11 | 125.5
21:00 | 3789 | 1926.2 | 854 | 38 | 58 | 1443.18 | 218 | 4457 | 0 | 537 | 1562.6 | 0 | 0 | 9 | 104
21:30 | 3774 | 1964.1 | 854.5 | 38 | 50 | 1446.09 | 218 | 4433.5 | 0 | 514.5 | 1510.3 | 0 | 0 | 12.5 | 90.5
22:00 | 3759 | 2002 | 855 | 38 | 42 | 1449 | 218 | 4410 | 0 | 492 | 1458 | 0 | 0 | 16 | 77
22:30 | 3767.5 | 1979.5 | 854.5 | 38 | 41 | 1410.285 | 218.5 | 4425.5 | 0 | 481.5 | 1414.5 | 0 | 0 | 16.5 | 69.5
23:00 | 3776 | 1957 | 854 | 38 | 40 | 1371.57 | 219 | 4441 | 0 | 471 | 1371 | 0 | 0 | 17 | 62
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 29-07-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 385 | 18:30 | 370 | 10:00 | Payra | 416 | 18:00 | 410 | 00:00
Ashuganj | 403 | 18:30 | 382 | 10:00 | Rahanpur | 402 | 10:00 | 381 | 00:00
Bhulta | 399 | 18:30 | 383 | 10:00 | Rampal | 407 | 14:00 | 393 | 01:00
Bibiana | 386 | 14:00 | 377 | 01:00
BIPTC | 402 | 06:00 | 392 | 20:00
Bogura | 385 | 11:00 | 359 | 22:00
Gopalganj | 400 | 14:00 | 386 | 01:00
Kaliakoir | 377 | 18:30 | 363 | 01:00
Madunaghat | 391 | 14:00 | 384 | 02:00
Meghnaghat | 386 | 18:00 | 369 | 10:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 224 | 18:30 | 214 | 10:00 | Keranigonj | 221 | 14:00 | 212 | 09:00
AKSML | 229 | 17:00 | 223 | 01:00 | Khulna(S) | 232 | 14:00 | 219 | 22:00
Aminbazar | 224 | 14:00 | 215 | 09:00 | Madunaghat | 232 | 14:00 | 226 | 10:00
Ashuganj | 234 | 17:00 | 225 | 00:00 | Madunaghat-400 | 231 | 14:00 | 227 | 02:00
Ashuganj-400 | 234 | 18:00 | 225 | 1:00 | Maniknagar | 218 | 19:00 | 206 | 10:00
Baghabari | 235 | 10:00 | 226 | 20:00 | Meghnaghat | 227 | 19:30 | 218 | 08:00
Barapukuria | 226 | 10:00 | 196 | 23:00 | Meghnaghat-400 | 223 | 19:30 | 213 | 09:00
Barapukuria-230 | 226 | 10:00 | 200 | 23:00 | Mirsorai | 229 | 14:00 | 219 | 01:00
Barishal | 229 | 14:00 | 221 | 00:00 | Rajshahi | 232 | 06:00 | 219 | 21:00
Bheramara | 234 | 06:00 | 222 | 20:00 | Rampal | 232 | 14:00 | 221 | 21:00
Bhulta | 229 | 04:00 | 208 | 09:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 229 | 18:30 | 219 | 01:00 | Rampura | 228 | 04:00 | 212 | 10:00
BIPTC | 236 | 06:00 | 221 | 20:00 | Shikalbaha | 229 | 14:00 | 223 | 01:00
Bogura | 238 | 11:00 | 223 | 00:00 | Shyampur | 220 | 14:00 | 211 | 09:00
Bogura-400 | 238 | 11:00 | 223 | 00:00 | Siddhirganj | 221 | 19:30 | 210 | 09:00
Borhanuddin | 234 | 13:00 | 228 | 00:00 | Sirajgonj | 241 | 11:00 | 234 | 21:00
BSRM | 228 | 14:00 | 218 | 10:00 | Sreepur | 230 | 14:00 | 221 | 23:00
Cumilla(N) | 224 | 18:00 | 215 | 00:00 | Tongi | 227 | 13:00 | 219 | 08:00
Faridpur | 227 | 14:00 | 218 | 00:00
Fenchuganj | 228 | 18:00 | 219 | 00:00
Ghorashal | 230 | 03:00 | 225 | 00:00
Ghorashal-230 | 229 | 14:00 | 215 | 10:00
Gopalganj | 228 | 18:00 | 220 | 00:00
GPH | 229 | 09:00 | 220 | 23:00
Haripur | 220 | 18:30 | 209 | 09:00
Hasnabad | 221 | 14:00 | 211 | 09:00
Hathazari | 225 | 00:00 | 220 | 10:00
Ishurdi | 236 | 06:00 | 224 | 20:00
Jhenaidah | 232 | 06:00 | 216 | 20:00
Kaliakoir | 233 | 14:00 | 223 | 01:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 04:00 | 127 | 08:00 | Lalmonirhat | 131 | 10:00 | 118 | 19:00
Agargaon | 130 | 06:00 | 125 | 09:00 | Madanganj | 129 | 19:30 | 121 | 09:00
Agrabad | 130 | 13:00 | 126 | 10:00 | Madaripur | 135 | 14:00 | 129 | 00:00
AKS | 128 | 13:00 | 125 | 03:00 | Madartek | 137 | 18:30 | 132 | 09:00
Aminbazar | 132 | 18:30 | 126 | 09:00 | Madunaghat | 131 | 13:00 | 128 | 02:00
Amnura | 136 | 10:00 | 128 | 00:00 | Magura | 135 | 05:00 | 122 | 21:00
Ashuganj | 141 | 18:30 | 135 | 00:00 | Mahasthangarh | 136 | 10:00 | 126 | 00:00
Bagerhat | 133 | 10:00 | 122 | 21:00 | Maijdee | 123 | 13:00 | 111 | 00:00
Bajitpur | 132 | 05:00 | 125 | 00:00 | Manikganj | 127 | 13:00 | 121 | 10:00
Bakulia | 132 | 14:00 | 127 | 01:00 | Maniknagar | 129 | 04:00 | 122 | 10:00
Banani | 138 | 04:00 | 125 | 10:00 | Matarbari | 122 | 14:00 | 112 | 01:00
Bangabhaban | 129 | 19:30 | 121 | 10:00 | Matuail | 129 | 19:00 | 122 | 09:00
Barapukuria | 139 | 10:00 | 118 | 23:00 | Millgate | 132 | 04:00 | 126 | 10:00
Barguna | 135 | 08:00 | 131 | 00:00 | Mirpur | 131 | 18:30 | 124 | 09:00
Barishal | 134 | 18:30 | 128 | 00:00 | Mirzapur | 131 | 14:00 | 126 | 00:00
Barishal-230 | 134 | 14:00 | 128 | 00:00 | Mithapukur | 127 | 08:00 | 114 | 00:00
Baroaulia | 130 | 18:00 | 127 | 06:00 | MI_Cement | 131 | 19:30 | 122 | 09:00
Baroirhat | 126 | 14:00 | 118 | 00:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 137 | 04:00 | 126 | 10:00 | Mogbazar | 139 | 03:00 | 127 | 10:00
BashundharaCement | 129 | 19:30 | 121 | 09:00 | Mongla | 133 | 10:00 | 123 | 23:00
Beanibazar | 127 | 07:00 | 117 | 00:00 | Motijheel | 129 | 19:30 | 121 | 10:00
Benapole | 133 | 18:30 | 121 | 23:00 | Muktagacha | 134 | 13:00 | 130 | 19:00
Bhaluka | 133 | 14:00 | 124 | 21:00 | Munshiganj | 129 | 19:00 | 123 | 12:00
Bhandaria | 130 | 18:00 | 120 | 00:00 | Muradnagar | 126 | 18:30 | 117 | 10:00
Bhangura | 134 | 06:00 | 128 | 20:00 | Mymensingh | 135 | 10:00 | 116 | 21:00
Bheramara | 137 | 06:00 | 132 | 22:00 | Naogaon | 135 | 18:30 | 125 | 00:00
Bheramara(GK) | 137 | 06:00 | 131 | 22:00 | Narail | 134 | 07:00 | 121 | 19:30
Bhulta | 124 | 18:00 | 117 | 09:00 | Narinda | 129 | 4:00 | 122 | 10:00
Bog-Sherpur | 137 | 11:00 | 129 | 01:00 | Narshingdi | 139 | 18:00 | 118 | 08:00
Bogura | 139 | 11:00 | 130 | 00:00 | Natore | 135 | 18:30 | 127 | 21:00
Bogura-230 | 140 | 11:00 | 131 | 00:00 | Nawabganj | 132 | 18:30 | 126 | 00:00
Brahmanbaria | 137 | 18:00 | 128 | 00:00 | Netrakona | 126 | 06:00 | 113 | 21:00
Cantonment | 130 | 18:00 | 125 | 09:00 | New | 135 | 14:00 | 128 | 00:00
Chandina | 129 | 18:30 | 121 | 10:00 | Niamatpur | 136 | 06:00 | 128 | 21:00
Chandpur | 130 | 15:00 | 120 | 07:00 | Noapara | 136 | 14:00 | 125 | 21:00
Chandraghona | 132 | 14:00 | 129 | 10:00 | Pabna | 135 | 06:00 | 128 | 20:00
Chapai | 136 | 09:00 | 127 | 22:00 | Palashbari | 126 | 09:00 | 112 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 19:00 | 122 | 09:00 | Panchagarh | 135 | 09:00 | 117 | 23:00
Chauddagram | 125 | 13:00 | 117 | 00:00 | Patuakhali | 135 | 15:00 | 132 | 00:00
Chhatak | 126 | 07:00 | 113 | 00:00 | Payra | 137 | 18:00 | 133 | 00:00
Chowmuhani | 124 | 14:00 | 111 | 00:00 | PHP | 125 | 14:00 | 117 | 00:00
Chuadanga | 135 | 07:00 | 120 | 21:00 | Postogola | 131 | 19:00 | 125 | 09:00
Coxsbazar | 120 | 12:00 | 115 | 00:00 | Purbachal | 138 | 03:00 | 124 | 10:00
Cumilla(N) | 129 | 18:30 | 122 | 00:00 | Purbasadipur | 133 | 10:00 | 114 | 23:00
Cumilla(S) | 133 | 05:00 | 120 | 00:00 | Rahanpur | 138 | 10:00 | 130 | 21:00
Daganbhuiyan | 125 | 14:00 | 114 | 00:00 | Rahanpur-400 | 138 | 10:00 | 131 | 21:00
Daudkandi | 124 | 18:00 | 113 | 10:00 | Rahim | 129 | 18:30 | 122 | 09:00
Dhaka | 140 | 06:00 | 130 | 09:00 | Rajbari | 134 | 14:00 | 127 | 00:00
Dhamrai | 131 | 14:00 | 125 | 10:00 | Rajendrapur | 136 | 07:00 | 123 | 11:00
Dhanmondi | 138 | 05:00 | 126 | 10:00 | Rajshahi | 133 | 06:00 | 127 | 20:00
Dohazari | 128 | 15:00 | 124 | 04:00 | Rajshahi-230 | 134 | 06:00 | 126 | 21:00
Faridpur | 135 | 14:00 | 128 | 00:00 | Ramganj | 125 | 14:00 | 116 | 02:00
Fatullah | 131 | 19:30 | 123 | 09:00 | Rampur | 130 | 14:00 | 126 | 01:00
Fenchuganj | 134 | 18:00 | 127 | 00:00 | Rampura | 138 | 04:00 | 126 | 10:00
Feni | 125 | 14:00 | 118 | 10:00 | Rangamati | 131 | 13:00 | 128 | 02:00
Ghatail | 130 | 14:00 | 125 | 20:00 | Rangpur | 135 | 09:00 | 116 | 20:00
Ghorashal | 139 | 14:00 | 132 | 00:00 | Ruppur | 138 | 06:00 | 131 | 19:30
Goalpara | 138 | 14:00 | 126 | 19:30 | Saidpur | 132 | 10:00 | 113 | 23:00
Gollamari | 137 | 08:00 | 129 | 21:00 | Satkhira | 135 | 17:00 | 123 | 21:00
Gopalganj | 137 | 18:00 | 129 | 01:00 | Satmasjid | 130 | 18:30 | 125 | 09:00
Gopalganj-400 | 137 | 18:00 | 131 | 00:00 | Savar | 133 | 13:00 | 124 | 01:00
Gulshan | 137 | 18:30 | 126 | 10:00 | SevenRings | 139 | 14:00 | 131 | 00:00
Halishahar | 131 | 14:00 | 127 | 01:00 | ShahCement | 130 | 19:00 | 122 | 09:00
Haripur | 129 | 18:00 | 121 | 09:00 | Shahjadpur | 138 | 04:00 | 133 | 00:00
HaripurSBU | 129 | 19:00 | 121 | 09:00 | Shahjibazar | 135 | 18:30 | 126 | 00:00
Hasnabad | 131 | 18:30 | 125 | 09:00 | Shahmirpur | 132 | 01:00 | 128 | 05:00
Hathazari | 133 | 18:00 | 128 | 09:00 | Shariatpur | 134 | 14:00 | 127 | 00:00
Ishurdi | 138 | 06:00 | 132 | 20:00 | Sherpur | 137 | 10:00 | 130 | 20:00
Jaldhaka | 132 | 09:00 | 109 | 23:00 | Shikalbaha | 121 | 13:00 | 117 | 01:00
Jamalpur | 140 | 10:00 | 132 | 19:00 | Shikalbaha-230 | 132 | 14:00 | 128 | 01:00
Jashore | 138 | 10:00 | 120 | 19:30 | Shitalakhya | 131 | 19:30 | 122 | 09:00
Jhenaidah | 138 | 10:00 | 123 | 21:00 | Sholosohor | 131 | 14:00 | 128 | 01:00
Jhenaidah-230 | 138 | 10:00 | 125 | 21:00 | Shyampur | 130 | 19:30 | 125 | 09:00
Joydebpur | 139 | 18:00 | 124 | 10:00 | Shyampur-230 | 130 | 18:00 | 120 | 19:30
Joypurhat | 133 | 10:00 | 122 | 00:00 | Siddhirganj | 129 | 18:30 | 122 | 09:00
Juldah | 131 | 14:00 | 128 | 00:00 | Sirajganj | 135 | 14:00 | 127 | 21:00
Kabirpur | 133 | 13:00 | 122 | 10:00 | Sonargaon | 128 | 19:00 | 119 | 10:00
Kachua | 127 | 13:00 | 119 | 00:00 | Sreemongol | 133 | 18:00 | 124 | 00:00
Kaliakoir | 135 | 14:00 | 128 | 08:00 | Sreepur | 134 | 06:00 | 127 | 21:00
Kallyanpur | 133 | 14:00 | 126 | 01:00 | Srinagar | 132 | 18:30 | 126 | 10:00
Kalurghat | 131 | 14:00 | 128 | 01:00 | SSM | 132 | 01:00 | 130 | 12:00
Kamrangirchar | 132 | 18:30 | 126 | 10:00 | Sunamganj | 123 | 18:00 | 110 | 01:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 127 | 08:00 | 115 | 09:00
Kasba | 126 | 18:30 | 118 | 09:00 | Sylhet-132 | 128 | 05:00 | 119 | 00:00
Kazla | 128 | 04:00 | 122 | 10:00 | Tangail | 129 | 18:30 | 123 | 21:00
Keranigonj | 132 | 18:30 | 126 | 10:00 | Taraganj | 133 | 10:00 | 119 | 22:00
Khagrachori | 131 | 18:00 | 127 | 01:00 | Thakurgaon | 134 | 09:00 | 116 | 23:00
Khulna | 136 | 10:00 | 126 | 21:00 | TK | 130 | 13:00 | 128 | 00:00
Khulna(S) | 138 | 14:00 | 129 | 19:30 | Tongi | 133 | 05:00 | 129 | 00:00
Khulshi | 130 | 14:00 | 126 | 01:00 | Ullahpara | 135 | 07:00 | 128 | 22:00
Kishoreganj | 131 | 05:00 | 121 | 21:00 | Ullon | 138 | 04:00 | 125 | 10:00
Kodda | 139 | 17:00 | 122 | 08:00 | Uttara | 131 | 14:00 | 124 | 08:00
KSRM | 132 | 18:30 | 126 | 10:00 | UttaraNew | 130 | 14:00 | 124 | 08:00
Kulaura | 134 | 18:00 | 125 | 00:00 | Zigatola | 132 | 18:00 | 127 | 10:00
Kurigram | 132 | 09:00 | 114 | 22:00
Kushtia | 134 | 17:00 | 127 | 20:00
Laksam | 128 | 14:00 | 117 | 01:00
Lakshmipur | 124 | 14:00 | 112 | 00:00
Lalbag | 132 | 18:30 | 126 | 10:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division