## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 01-08-2025 | [28 empty] | Date: | 01-08-2025 | [28 empty] | Date: | 01-08-2025 | [28 empty] | Date: | 01-08-2025 | [28 empty] | Date: | 01-08-2025 | [12 empty] | Date: | 01-08-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [12 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 733.790 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 35 | 100 | 15 | 45 | 0 | 45 | 146 | 0 | 450 | 142 | 500 | 0 | 35 | 333 | 137 | 0 | 0 | 90 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 65 | 32 | 0 | 12 | 12 | 0 | 219 | 0 | 27 | 464 | 0 | 0 | 19 | 0 | 28 | 220 | 0 | 0 | 0 | 1095 | 0 | 51 | 56 | 43 | 0 | 356 | 340 | 48 | 194 | 31 | 113 | 50 | 159 | 62 | 20 | 97 | 46 | 0 | 0 | 43 | 70 | 285 | 302 | 0 | 60 | 133 | 7 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 104 | 120 | 80 | 0 | 0 | 12 | 7475 | 430 | 196 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1142 | 0 | 1439.28 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 198 | 0 | 198 | 0 | 343 | 0 | 0 | 166 | 0 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 120 | 220 | 0 | 305 | 1120 | 0 | 6645.28 | 14120.28 | 105.92
01:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 35 | 100 | 0 | 45 | 0 | 55 | 140 | 0 | 450 | 140 | 378 | 0 | 35 | 335 | 137 | 0 | 0 | 52 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 65 | 32 | 0 | 12 | 12 | 0 | 220 | 0 | 30 | 429 | 0 | 0 | 19 | 0 | 46 | 221 | 0 | 0 | 0 | 1040 | 0 | 51 | 100 | 45 | 0 | 356 | 340 | 48 | 187 | 31 | 96 | 50 | 162 | 62 | 20 | 97 | 44 | 0 | 0 | 43 | 65 | 286 | 291 | 0 | 60 | 129 | 7 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 104 | 120 | 80 | 0 | 0 | 10 | 7188 | 430 | 196 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1109 | 0 | 1446.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 198 | 0 | 198 | 0 | 333 | 0 | 0 | 167 | 0 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 269 | 120 | 220 | 0 | 305 | 1120 | 0 | 6578.3 | 13766.3 | 105.93
02:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.5 | 35 | 82 | 0 | 0 | 0 | 0 | 144 | 0 | 450 | 50 | 390 | 0 | 0 | 333 | 135 | 0 | 0 | 52 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 33 | 32 | 0 | 12 | 12 | 0 | 220 | 0 | 30 | 416 | 0 | 0 | 19 | 0 | 46 | 221 | 0 | 0 | 0 | 1090 | 0 | 51 | 40 | 45 | 0 | 359 | 340 | 48 | 193 | 31 | 93 | 50 | 162 | 57 | 20 | 71 | 42 | 0 | 0 | 44 | 75 | 286 | 302 | 0 | 60 | 133 | 7 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 104 | 120 | 98 | 0 | 0 | 11 | 6878.5 | 430 | 198 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1037 | 0 | 1437.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 198 | 0 | 198 | 0 | 341 | 0 | 0 | 165 | 0 | 114 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 120 | 220 | 0 | 306 | 1120 | 0 | 6452.07 | 13330.57 | 105.94
03:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.4 | 35 | 66 | 0 | 0 | 0 | 0 | 72 | 0 | 450 | 0 | 440 | 0 | 0 | 333 | 135 | 0 | 0 | 52 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 33 | 0 | 0 | 12 | 12 | 0 | 220 | 0 | 33 | 416 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1090 | 0 | 51 | 0 | 45 | 0 | 356 | 340 | 48 | 195 | 31 | 90 | 50 | 161 | 58 | 20 | 46 | 38 | 0 | 0 | 44 | 0 | 286 | 328 | 0 | 60 | 135 | 7 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 104 | 75 | 98 | 0 | 0 | 12 | 6511.4 | 430 | 199 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1032 | 0 | 1452.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 198 | 0 | 198 | 0 | 398 | 0 | 0 | 166 | 0 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 120 | 220 | 0 | 304 | 1120 | 0 | 6475.95 | 12987.35 | 105.95
04:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 450 | 0 | 0 | 333 | 136 | 0 | 0 | 52 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 0 | 0 | 12 | 12 | 0 | 220 | 0 | 33 | 466 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 45 | 0 | 354 | 340 | 47 | 197 | 31 | 91 | 50 | 162 | 57 | 8 | 30 | 40 | 0 | 0 | 44 | 0 | 286 | 383 | 0 | 60 | 131 | 7 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 104 | 75 | 98 | 0 | 0 | 12 | 6475 | 430 | 203 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 942 | 0 | 1359.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 198 | 0 | 198 | 0 | 402 | 0 | 0 | 169 | 0 | 50 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 120 | 220 | 0 | 305 | 1119 | 0 | 6217.2 | 12692.2 | 105.96
05:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 450 | 0 | 0 | 333 | 136 | 0 | 0 | 52 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 12 | 12 | 0 | 220 | 0 | 33 | 492 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 925 | 0 | 51 | 0 | 45 | 0 | 353 | 340 | 48 | 202 | 31 | 90 | 50 | 161 | 60 | 8 | 31 | 38 | 0 | 0 | 44 | 0 | 286 | 388 | 0 | 60 | 136 | 7 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 104 | 75 | 99 | 0 | 0 | 12 | 6321 | 431 | 203 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 862 | 0 | 1214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 198 | 0 | 198 | 0 | 414 | 0 | 0 | 166 | 0 | 50 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 120 | 220 | 0 | 306 | 1122 | 0 | 6009 | 12330 | 105.97
06:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 450 | 0 | 0 | 280 | 136 | 0 | 0 | 35 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0.05 | 220 | 0 | 3 | 492 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 45 | 0 | 300 | 340 | 48 | 197 | 31 | 93 | 50 | 162 | 62 | 8 | 31 | 36 | 0 | 3 | 44 | 0 | 286 | 325 | 0 | 60 | 135 | 7 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 104 | 55 | 101 | 0 | 0.6 | 12 | 5961.65 | 430 | 204 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 821 | 0 | 1043.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55 | 203 | 0 | 198 | 0 | 198 | 0 | 351 | 0 | 0.05 | 168 | 0 | 50 | 1 | 90 | 0 | 0 | 0 | 0 | 0.01 | 0 | 172 | 120 | 220 | 0 | 305 | 1050 | 0 | 5663.8 | 11625.45 | 105.98
07:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 32 | 0 | 350 | 0 | 450 | 0 | 0 | 280 | 136 | 0 | 1 | 35 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0.58 | 218 | 0 | 37 | 515 | 0 | 0 | 2 | 0 | 0 | 221 | 0 | 0 | 0 | 855 | 0 | 51 | 0 | 45 | 0 | 300 | 340 | 48 | 196 | 31 | 89 | 50 | 162 | 62 | 8 | 62 | 36 | 0 | 15 | 44 | 0 | 286 | 325 | 0 | 60 | 133 | 7 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 96 | 55 | 101 | 0 | 3.68 | 12 | 6038.26 | 431 | 209 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7 | 820 | 0 | 878.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 6 | 0 | 4.31 | 203 | 0 | 198 | 0 | 180 | 0 | 350 | 0 | 0.54 | 168 | 0 | 50 | 3 | 90 | 0 | 0 | 0.6 | 3 | 0.04 | 0 | 172 | 120 | 220 | 0 | 283 | 800 | 0 | 5235.41 | 11273.67 | 105.99
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 46 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 0 | 440 | 0 | 0 | 280 | 136 | 0 | 2 | 0 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 1.59 | 218 | 0 | 42 | 537 | 0 | 0 | 8 | 0 | 0 | 221 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 45 | 0 | 300 | 340 | 48 | 196 | 31 | 90 | 30 | 161 | 57 | 11 | 77 | 34 | 0 | 11 | 44 | 0 | 286 | 316 | 0 | 60 | 133 | 7 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 95 | 45 | 100 | 1 | 8.97 | 12 | 5958.56 | 430 | 212 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 48 | 793 | 0 | 855.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8.91 | 203 | 0 | 199 | 0 | 150 | 0 | 347 | 0 | 0.64 | 171 | 0 | 50 | 2 | 70 | 0 | 0 | 3.8 | 15 | 0.1 | 0 | 170 | 120 | 220 | 0 | 285 | 790 | 0 | 5199.88 | 11158.44 | 106
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 13 | 0 | 350 | 0 | 447 | 0 | 0 | 280 | 136 | 0 | 8 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.02 | 219 | 0 | 32 | 484 | 0 | 0 | 4 | 0 | 0 | 219 | 0 | 0 | 0 | 831 | 0 | 51 | 0 | 45 | 0 | 300 | 340 | 48 | 198 | 31 | 90 | 30 | 161 | 58 | 20 | 15 | 34 | 0 | 16 | 0 | 0 | 280 | 305 | 0 | 60 | 132 | 7 | 0 | 79 | 0 | 0 | 18 | 0 | 17 | 75 | 45 | 100 | 1 | 14.55 | 0 | 5685.57 | 433 | 212 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 49 | 782 | 0 | 861 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 0 | 13 | 0 | 11.28 | 203 | 0 | 201 | 0 | 150 | 0 | 349 | 0 | 1.18 | 174 | 0 | 88 | 2 | 108 | 0 | 0 | 1.6 | 65 | 0.11 | 0 | 171 | 120 | 180 | 0 | 304 | 740 | 0 | 5265.67 | 10951.24 | 106.01
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 14 | 0 | 350 | 0 | 400 | 0 | 0 | 280 | 76 | 0 | 16 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.69 | 220 | 0 | 29 | 420 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 844 | 0 | 51 | 0 | 45 | 0 | 300 | 340 | 48 | 196 | 31 | 90 | 30 | 161 | 55 | 20 | 14 | 34 | 0 | 31 | 0 | 0 | 280 | 320 | 0 | 60 | 135 | 7 | 0 | 78 | 0 | 0 | 18 | 0 | 17 | 75 | 45 | 98 | 1 | 19.54 | 0 | 5561.23 | 433 | 230 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 68 | 795 | 0 | 859 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 5.34 | 11 | 0 | 33.14 | 205 | 0 | 202 | 0 | 150 | 0 | 351 | 0 | 5.26 | 175 | 0 | 95 | 2 | 113 | 0 | 0 | 5.4 | 106 | 0.34 | 0 | 171 | 120 | 180 | 0 | 306 | 705 | 0 | 5372.98 | 10934.21 | 106.02
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 15 | 0 | 350 | 0 | 350 | 0 | 0 | 280 | 74 | 0 | 20 | 0 | 17 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.99 | 221 | 0 | 38 | 406 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 45 | 0 | 300 | 280 | 48 | 199 | 31 | 90 | 30 | 153 | 52 | 14 | 15 | 34 | 0 | 34 | 0 | 0 | 286 | 335 | 0 | 60 | 136 | 6 | 0 | 80 | 0 | 0 | 18 | 0 | 17 | 75 | 45 | 111 | 1 | 2.21 | 0 | 5438.2 | 433 | 238 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 83 | 801 | 0 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 38.34 | 82 | 0 | 36.7 | 203 | 0 | 201 | 0 | 150 | 0 | 359 | 0 | 4.7 | 175 | 0 | 95 | 13 | 113 | 0 | 0 | 5.6 | 178 | 0.61 | 0 | 174 | 120 | 180 | 0 | 308 | 700 | 0 | 5606.45 | 11044.65 | 106.03
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 420 | 0 | 410 | 0 | 0 | 330 | 135 | 0 | 35 | 0 | 17 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 221 | 0 | 26 | 400 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 860 | 0 | 51 | 0 | 45 | 0 | 339 | 280 | 47 | 209 | 30 | 94 | 30 | 146 | 53 | 14 | 16 | 38 | 0 | 5 | 0 | 0 | 290 | 389 | 0 | 60 | 149 | 6 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 75 | 45 | 134 | 1 | 8.67 | 0 | 5806.17 | 433 | 247 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 104 | 822 | 0 | 882 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 47.34 | 111 | 0 | 21.2 | 204 | 0 | 201 | 0 | 150 | 0 | 386 | 0 | 3.42 | 175 | 0 | 95 | 40 | 113 | 0 | 0 | 5.1 | 212 | 0.73 | 0 | 174 | 120 | 220 | 0 | 307 | 740 | 0 | 5860.29 | 11666.46 | 106.04
13:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 15 | 0 | 420 | 0 | 550 | 0 | 0 | 335 | 199 | 0 | 21 | 35 | 17 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.28 | 221 | 0 | 31 | 405 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 950 | 0 | 51 | 0 | 45 | 0 | 346 | 340 | 47 | 198 | 31 | 91 | 30 | 161 | 52 | 14 | 17 | 42 | 0 | 24 | 0 | 0 | 300 | 395 | 0 | 60 | 156 | 6 | 0 | 81 | 0 | 0 | 18 | 0 | 17 | 86 | 75 | 154 | 1 | 26.63 | 1 | 6345.91 | 434 | 256 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 42 | 901 | 0 | 960 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 17.3 | 54 | 0 | 28.66 | 205 | 0 | 201 | 0 | 200 | 0 | 397 | 0 | 1.86 | 175 | 0 | 95 | 27 | 113 | 0 | 0 | 8 | 33 | 0.18 | 0 | 220 | 120 | 220 | 0 | 305 | 890 | 0 | 5950.5 | 12296.41 | 106.04
14:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 440 | 0 | 0 | 270 | 134 | 0 | 9 | 35 | 17 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.16 | 221 | 0 | 30 | 411 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 950 | 0 | 51 | 0 | 45 | 0 | 300 | 280 | 47 | 192 | 28 | 92 | 30 | 160 | 53 | 20 | 14 | 40 | 0 | 34 | 0 | 10 | 300 | 366 | 0 | 60 | 143 | 6 | 0 | 79 | 0 | 0 | 18 | 0 | 17 | 94 | 75 | 141 | 1 | 15.65 | 11 | 5850.81 | 433 | 263 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14 | 966 | 0 | 969 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 31.3 | 68 | 0 | 41.26 | 170 | 0 | 201 | 0 | 203 | 0 | 342 | 0 | 4.77 | 175 | 0 | 70 | 32 | 70 | 0 | 0 | 8 | 55 | 0.31 | 0 | 217 | 120 | 180 | 0 | 305 | 980 | 0 | 5965.14 | 11815.95 | 106.05
15:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 450 | 0 | 0 | 270 | 133 | 0 | 3 | 0 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.34 | 221 | 0 | 23 | 412 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 950 | 0 | 51 | 0 | 45 | 0 | 300 | 280 | 46 | 198 | 28 | 50 | 30 | 120 | 53 | 20 | 0 | 40 | 0 | 33 | 0 | 30 | 300 | 381 | 0 | 60 | 132 | 6 | 0 | 80 | 0 | 0 | 18 | 0 | 17 | 45 | 16 | 150 | 1 | 42.87 | 12 | 5652.71 | 433 | 274 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 974 | 0 | 973 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 6.7 | 28 | 0 | 47.08 | 169 | 0 | 188 | 0 | 189 | 0 | 353 | 0 | 4.55 | 170 | 0 | 35 | 11 | 34 | 0 | 0 | 6 | 89 | 0.08 | 0 | 218 | 120 | 180 | 0 | 306 | 990 | 0 | 5862.91 | 11515.62 | 106.05
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 450 | 0 | 0 | 270 | 133 | 0 | 1 | 0 | 17.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0.85 | 221 | 0 | 23 | 553 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 893 | 5 | 51 | 0 | 45 | 0 | 300 | 280 | 47 | 200 | 30 | 16 | 30 | 100 | 49 | 20 | 0 | 34 | 0 | 24 | 0 | 38 | 300 | 365 | 0 | 60 | 138 | 6 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 45 | 16 | 150 | 1 | 11.87 | 0 | 5635.22 | 433 | 285 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 931 | 0 | 979 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 4.08 | 0 | 0 | 29.97 | 173 | 0 | 195 | 0 | 194 | 0 | 363 | 0 | 3.22 | 165 | 0 | 35 | 19 | 34 | 0 | 0 | 4.5 | 64 | 0.06 | 0 | 172 | 120 | 180 | 0 | 306 | 900 | 0 | 5654.33 | 11289.55 | 106.06
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 445 | 0 | 0 | 270 | 133 | 0 | 3 | 0 | 17.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0.75 | 221 | 0 | 24 | 540 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 843 | 3 | 51 | 0 | 45 | 0 | 300 | 280 | 48 | 198 | 30 | 15 | 30 | 93 | 47 | 20 | 0 | 34 | 0 | 5 | 0 | 65 | 300 | 377 | 0 | 60 | 133 | 6 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 45 | 16 | 150 | 0 | 7.25 | 0 | 5565.5 | 433 | 301 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 11 | 837 | 0 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 5.9 | 3 | 0 | 14.56 | 170 | 0 | 190 | 0 | 189 | 0 | 352 | 0 | 0.91 | 164 | 0 | 35 | 7 | 34 | 0 | 0 | 2.9 | 42 | 0.07 | 0 | 172 | 120 | 180 | 0 | 304 | 822 | 0 | 5355.84 | 10921.34 | 106.06
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 450 | 0 | 0 | 270 | 133 | 0 | 1 | 0 | 17.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0.07 | 219 | 0 | 24 | 610 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 854 | 1 | 51 | 0 | 45 | 0 | 300 | 280 | 47 | 199 | 30 | 15 | 30 | 95 | 54 | 20 | 0 | 32 | 0 | 3 | 0 | 110 | 300 | 392 | 0 | 60 | 136 | 6 | 0 | 83 | 0 | 0 | 18 | 0 | 17 | 45 | 16 | 150 | 0 | 3.02 | 0 | 5717.59 | 433 | 325 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4 | 793 | 0 | 856 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 2.04 | 0 | 0 | 2.81 | 172 | 0 | 193 | 0 | 191 | 0 | 358 | 0 | 0.24 | 164 | 0 | 35 | 1 | 38 | 0 | 0 | 0.8 | 19 | 0.01 | 0 | 172 | 120 | 180 | 0 | 306 | 705 | 0 | 5117.4 | 10834.99 | 106.07
19:00 | 0 | 17 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 7 | 0 | 32 | 0 | 0 | 8 | 60 | 0 | 450 | 0 | 550 | 0 | 0 | 335 | 200 | 0 | 0 | 60 | 17.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 33 | 7 | 0 | 0 | 0 | 0 | 219 | 0 | 29 | 730 | 0 | 0 | 5 | 0 | 0 | 218 | 0 | 0 | 0 | 1045 | 0 | 51 | 15 | 70 | 0 | 349 | 340 | 48 | 201 | 30 | 21 | 30 | 110 | 54 | 20 | 35 | 40 | 6 | 0 | 0 | 120 | 300 | 387 | 0 | 60 | 146 | 6 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 64 | 55 | 151 | 0 | 0 | 2 | 6902.5 | 433 | 333 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 972 | 0 | 1075 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 12 | 0 | 180 | 0 | 201 | 0 | 200 | 0 | 362 | 0 | 0 | 167 | 0 | 90 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 226 | 120 | 220 | 0 | 306 | 750 | 0 | 5850 | 12752.5 | 106.07
19:30 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 35 | 32 | 32 | 0 | 0 | 35 | 66 | 0 | 450 | 0 | 542 | 0 | 0 | 335 | 198 | 0 | 0 | 90 | 17.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 33 | 16 | 0 | 6 | 12 | 0 | 219 | 0 | 29 | 731 | 0 | 0 | 19 | 0 | 0 | 218 | 0 | 0 | 0 | 1080 | 0 | 51 | 80 | 80 | 0 | 353 | 340 | 48 | 196 | 30 | 60 | 30 | 180 | 54 | 20 | 45 | 38 | 16 | 0 | 0 | 175 | 300 | 365 | 0 | 60 | 135 | 6 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 105 | 65 | 151 | 0 | 0 | 12 | 7420.5 | 433 | 341 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1084 | 0 | 1154 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 23 | 0 | 170 | 0 | 192 | 0 | 189 | 0 | 349 | 0 | 0 | 166 | 0 | 100 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 120 | 220 | 0 | 306 | 870 | 0 | 6158 | 13578.5
20:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.8 | 0 | 29 | 32 | 0 | 0 | 0 | 35 | 12 | 450 | 0 | 555 | 0 | 0 | 335 | 195 | 0 | 0 | 90 | 17.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 33 | 16 | 0 | 12 | 12 | 0 | 218 | 0 | 29 | 730 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1100 | 0 | 51 | 30 | 80 | 0 | 349 | 340 | 49 | 204 | 30 | 60 | 30 | 179 | 54 | 20 | 16 | 38 | 0 | 0 | 0 | 160 | 300 | 360 | 0 | 60 | 133 | 6 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 113 | 91 | 151 | 0 | 0 | 12 | 7245.3 | 433 | 355 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1077 | 0 | 1166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 190 | 0 | 189 | 0 | 373 | 0 | 0 | 170 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 120 | 220 | 0 | 306 | 884 | 0 | 6150 | 13395.3 | 106.08
21:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 555 | 0 | 0 | 335 | 197 | 0 | 0 | 90 | 18.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 33 | 0 | 0 | 12 | 25 | 0 | 218 | 0 | 29 | 730 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1165 | 0 | 51 | 0 | 162 | 0 | 348 | 340 | 49 | 204 | 30 | 67 | 30 | 180 | 54 | 20 | 15 | 40 | 0 | 0 | 0 | 150 | 300 | 359 | 0 | 60 | 156 | 6 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 103 | 90 | 151 | 0 | 0 | 12 | 7306.5 | 433 | 362 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1044 | 0 | 1206.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 201 | 0 | 199 | 0 | 414 | 0 | 0 | 174 | 0 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 120 | 220 | 0 | 305 | 950 | 0 | 6313.72 | 13620.22 | 106.08
22:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 31 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 555 | 0 | 0 | 335 | 196 | 0 | 0 | 90 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 33 | 0 | 0 | 12 | 25 | 0 | 219 | 0 | 36 | 728 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1165 | 0 | 51 | 0 | 172 | 0 | 348 | 340 | 49 | 207 | 30 | 68 | 30 | 176 | 53 | 20 | 16 | 42 | 0 | 0 | 0 | 40 | 300 | 373 | 0 | 60 | 159 | 6 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 104 | 90 | 151 | 0 | 0 | 12 | 7232 | 433 | 365 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1010 | 0 | 1214.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 198 | 0 | 198 | 0 | 414 | 0 | 0 | 175 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 120 | 220 | 0 | 306 | 1110 | 0 | 6454.57 | 13686.57 | 106.09
23:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 31 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 570 | 0 | 0 | 334 | 196 | 0 | 0 | 90 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 33 | 0 | 0 | 12 | 25 | 0 | 220 | 0 | 36 | 726 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1175 | 0 | 51 | 0 | 172 | 0 | 347 | 340 | 49 | 209 | 30 | 67 | 30 | 176 | 53 | 20 | 16 | 42 | 0 | 0 | 0 | 30 | 300 | 393 | 0 | 60 | 159 | 6 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 103 | 90 | 152 | 0 | 0 | 12 | 7280 | 431 | 370 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1022 | 0 | 1228.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 200 | 0 | 199 | 0 | 414 | 0 | 0 | 175 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 120 | 220 | 0 | 305 | 1105 | 0 | 6484.75 | 13764.75 | 106.09
Total KWH | 0 | 421834 | 31253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165564 | 470520 | 788112 | 167520 | 56455 | 0 | 126312 | 643680 | 18240 | 9535000 | 239535 | 11050145 | 0 | 45240 | 7429631 | 3786000 | 0 | 119344 | 928800 | 469200 | 441360 | 0 | 0 | 0 | 0 | 0 | 0 | 183840 | 351051 | 115776 | 0 | 166080 | 203520 | 19199 | 5294636 | 0 | 776640 | 12734545.46 | 0 | 0 | 95520 | 0 | 128799 | 5203214 | 0 | 0 | 0 | 23438179 | 12690 | 1204196 | 286036 | 1572364 | 0 | 8226600 | 7860000 | 1146720 | 4879000 | 736632 | 1777920 | 842260 | 3675360 | 1333920 | 386450 | 687420 | 912000 | 27946 | 258227 | 402032 | 950520 | 7000000 | 8910000 | 0 | 1385780 | 3375981 | 165600 | 0 | 1976640 | 0 | 0 | 449000 | 0 | 429480 | 2108400 | 1615200 | 2896320 | 9850 | 194690 | 192960 | 153532938.46 | 10468363 | 6480000 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 440640 | 22130910 | 0 | 26082909 | 0 | 0 | 0 | 0 | 19296 | 0 | 155840 | 0 | 0 | 81218 | 400829 | 16240 | 302248 | 4738000 | 0 | 4990291 | 0 | 4747418 | 0 | 9010981 | 0 | 28080 | 4141000 | 0 | 1911052 | 151929 | 2256000 | 0 | 0 | 47966.88 | 889920 | 2469 | 0 | 4822000 | 2880000 | 5234468 | 0 | 7279272 | 23234909.09 | 0 | 143856248.97 | 297389187.43

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 02-08-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-08-2025 | during | 02-08-2025 | during | 02-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 0 | 0 | 0 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 135 | 197 | 208.13 | 208.13 | 208.13 | 208.13 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 7 | 7 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 32 | 149.36 | 149.36 | 144 | 144 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 17 | 18.5 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 25 | 25 | Fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 16 | 32 | 149 | 149 | 114 | 114 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 34 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 16 | 16 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 16 | 0 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 35 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 0 | 55 | 55 | 35 | 35 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 410 | 555 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 733.79 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 90 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6673.514 | 1410 | 1765.5 | 5409.95 | 5377.95 | 3816.6 | 3784.6
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 5 | 0 | 5 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 221 | 218 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 219 | 0 | 0 | 0 | 0 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 72 | 98 | 98 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 33 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 100 | 100 | 12 | 36 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 26 | 29 | 2 | 25 | 2 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.5 | 0 | 4.37 | 0 | 4.37 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 25 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 860 | 1165 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 14 | 28 | 28 | 28 | 28 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 400 | 730 | 770 | 770 | 770 | 770 | -
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 1724.5 | 2445 | 3585.09 | 3622.72 | 3459.09 | 3496.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 209 | 204 | 220 | 220 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 339 | 348 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 280 | 340 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 30 | 30 | 46.7 | 46.7 | 35 | 35 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 47 | 49 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 45 | 162 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 140 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 30 | 30 | 163 | 163 | 30 | 30 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 146 | 180 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 38 | 40 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 20 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 16 | 15 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 53 | 54 | 113 | 113 | 46 | 46 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 94 | 67 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 5 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1397 | 1590 | 2428.56 | 2378.56 | 2191.86 | 2141.86
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-08-2025 | during | 02-08-2025 | during | 02-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 134 | 151 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 45 | 90 | 200 | 200 | 170.2 | 170.2 | Engine Problem
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 75 | 103 | 115 | 115 | 100 | 100 | Engine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 8.67 | 0 | 44.15 | 0 | 44.15 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 35 | 35 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 280.67 | 373 | 595.05 | 549 | 520.75 | 474.7
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 60 | 60 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 149 | 156 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 84 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 6 | 6 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 150 | 341 | 341 | 150 | 150 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 389 | 359 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 290 | 300 | 300 | 300 | 300 | 300 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 994 | 1133 | 1375 | 1375 | 1123 | 1123
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 433 | 433 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 247 | 362 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 53 | 53 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 104 | 0 | 62 | 0 | 62 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 822 | 1044 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1644 | 1877 | 3614.2 | 3552.2 | 3472 | 3410
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 307 | 305 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 740 | 950 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 174 | 231 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.73 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1561.73 | 1826 | 2162 | 2161 | 2152 | 2151
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 47.34 | 0 | 0 | 0 | 47.34 | 0 | -
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 42 | 42 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 204 | 194 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 201 | 201 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 199 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 386 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 | 27 | 27 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 8.5 | 0 | 96 | 96 | 87 | 87 | Engine Problem
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.42 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 882 | 1206.72 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 21.2 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 111 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3474 | 3516.96 | 2014.46 | 2214.72 | 3193.47 | 3026.87 | 3182.43 | 2968.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 175 | 174 | 160 | 160 | 160 | 160 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 113 | 107 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.1 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 95 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 40 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 212 | 0 | 157.63 | 0 | 157.63 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 640.1 | 396 | 611.23 | 422 | 611.23 | 422
System Total |  |  |  |  | 28671.2 | 27843.665 | 11666.46 | 13620.22 | 22974.55 | 22465.3 | 20528.96 | 19972.37
Forecast Scenario (02-08-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13700 |  | 0 |  | 13700
|  |  |  | 1:00 | 13440 |  | 0 |  | 13440
|  |  |  | 2:00 | 13020 |  | 0 |  | 13020
|  |  |  | 3:00 | 12660 |  | 0 |  | 12660
|  |  |  | 4:00 | 12410 |  | 0 |  | 12410
|  |  |  | 5:00 | 12210 |  | 0 |  | 12210
|  |  |  | 6:00 | 11580 |  | 0 |  | 11580
|  |  |  | 7:00 | 11590 |  | 0 |  | 11590
|  |  |  | 8:00 | 11600 |  | 0 |  | 11600
|  |  |  | 9:00 | 11580 |  | 0 |  | 11580
|  |  |  | 10:00 | 12000 |  | 0 |  | 12000
|  |  |  | 11:00 | 12870 |  | 0 |  | 12870
|  |  |  | 12:00 | 13510 |  | 0 |  | 13510
|  |  |  | 13:00 | 13870 |  | 0 |  | 13870
|  |  |  | 14:00 | 13910 |  | 0 |  | 13910
|  |  |  | 15:00 | 14220 |  | 0 |  | 14220
|  |  |  | 16:00 | 14130 |  | 0 |  | 14130
|  |  |  | 17:00 | 13670 |  | 0 |  | 13670
|  |  |  | 18:00 | 13330 |  | 0 |  | 13330
|  |  |  | 18:30 | 13900 |  | 0 |  | 13900
|  |  |  | 19:00 | 14720 |  | 0 |  | 14720
|  |  |  | 19:30 | 15640 |  | 0 |  | 15640
|  |  |  | 20:00 | 15740 |  | 0 |  | 15740
|  |  |  | 21:00 | 15850 |  | 0 |  | 15850
|  |  |  | 22:00 | 15720 |  | 0 |  | 15720
|  |  |  | 23:00 | 15740 |  | 0 |  | 15740
Probable Maximum Temperature: |  |  | 31.00°C
Probable Maximum Demand at Day Peak: |  |  | 13510.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15850.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15050.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 312.67 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:51 hrs on 02-08-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 01-08-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11666.46 | MW | 12:00 Hr. | Energy Generated |  |  | 297.3892 |  | MKWHr.
| Day Peak Demand |  |  | 11666.46 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.111 |  | MKWHr.
| Evening Peak Generation |  |  | 13620.22 | MW | 21:00 Hr. | Energy Demand |  |  | 297.5002 |  | MKWHr.
| Evening Peak Demand |  |  | 13620.22 | MW | 21:00 Hr. | Maximum Temperature |  |  | 30 |  | °C
| Minimum Generation of the Day |  |  | 10921.34 | MW | 17:00 Hr. | Total Gas Supplied |  |  | 981.49 |  | MMCFD
| Maximum Generation of the Day |  |  | 14120.28 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.8107 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 32.9509 | 0 | 3.8635 | 0 | 0 | 0.11934 | 0 | 0 | 36.9337 | Gas | 130.9759 | Gas | 477868140.65
| Chattogram Zone |  |  | 5.9799 | 36.1727 | 1.0607 | 0 | 5.2946 | 0.031889 | 0 | 0.18384 | 48.7237 | Coal | 97.7808 | Coal | 585255266.9025
| Cumilla Zone |  |  | 26.8542 | 0 | 8.1906 | 0 | 0 | 0.25823 | 0.912 | 0 | 36.2151 | HFO | 21.8194 | HFO | 397571416.9
| Mymensingh Zone |  |  | 2.8963 | 0 | 4.346 | 0 | 0 | 0.20454 | 0 | 0 | 7.4469 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 24.2135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.2135 | Hydro | 5.2946 | Hydro | 529463.6
| Khulna Zone |  |  | 6.48 | 22.1309 | 0 | 0 | 0 | 0.44064 | 11.3804 | 0 | 40.4319 | Solar | 2.9593 | Solar | 47060751.0968
| Barishal Zone |  |  | 8.1145 | 35.3362 | 0 | 0 | 0 | 0.002469 | 0 | 0 | 43.4531 | Import | 38.3753 | Import | 217052710.34
| Rajshahi Zone |  |  | 23.4867 | 0 | 0.19138 | 0 | 0 | 0.81237 | 26.0829 | 0 | 50.5733 | Wind | 0.18384 | Wind | 2691417.6
| Rangpur Zone |  |  | 0 | 4.141 | 4.1671 | 0 | 0 | 1.0898 | 0 | 0 | 9.3979
| Total |  |  | 130.9759 | 97.7808 | 21.8194 | 0 | 5.2946 | 2.9593 | 38.3753 | 0.18384 | 297.3892
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 477868140.65 |  | Hydro | 529463.6
|  |  |  | Coal | 585255266.9025 |  | Solar | 47060751.0968
|  |  |  | HFO | 397571416.9 |  | Import | 217052710.34
|  |  |  | HSD | 0 |  | Wind | 2691417.6
[5 empty] | Total: | 172,80,29,167 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 10.4684 | Peak Hr Flow | 433.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 9590381.88 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.0829 | Peak Hr Flow | 1206.72 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 506 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.912 | Peak Hr Flow | 40.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 924 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 37.4633 | Peak Hr Flow | 1679.72 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4330
|  |  |  | Chattogram |  | 0 |  | 1316
|  |  |  | Cumilla |  | 0 |  | 1291
|  |  |  | Mymensingh |  | 0 |  | 1189
|  |  |  | Sylhet |  | 0 |  | 540
|  |  |  | Khulna |  | 0 |  | 1516
|  |  |  | Barishal |  | 0 |  | 438
|  |  |  | Rajshahi |  | 0 |  | 1442
|  |  |  | Rangpur |  | 0 |  | 992
|  |  |  | Total |  | 0 |  | 13054
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[7 empty] | 4 | Sylhet 225 MW CCPP GT |  |  | 142
[7 empty] | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 707
|  |  |  | Total Unavailable Capacity |  |  |  | 1007
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:45 | Shahjibazar 132/33kV S/S TR-06 HT is restored.
|  | 08:50 | Shahjibazar 132/33kV S/S TR-06 LT is restored.
| 08:51 | 10:17 | Madaripur 132/33kV S/S T1-405T HT Forced S/D Due to Hot spot maintenance
| 08:51 | 10:17 | Madaripur 132/33kV S/S T1-405T LT Forced S/D Due to Hot spot maintenance
| 08:58 | 17:44 | Gopalganj 400/132kV S/S 400kV Rooppur Project Work S/D
| 09:01 | 13:14 | Barapukuria-Saidpur 132 kV Ckt-2 Scheduled S/D from Saidpur 132/33kV end Due to Braker | [7 empty] | 7.0MW load
|  |  | replacement work. | [7 empty] | interrup. Saidpur
132/33kV end
| 09:11 | 13:18 | Barapukuria-Saidpur 132 kV Ckt-2 Scheduled S/D from Barapukuria 230/132/33kV end Due to
Due to Maintenance work at Saidpur Substation end.
| 09:37 | 10:30 | Kasba 132/33kV S/S TR-1 HT Scheduled S/D Due to Shutdown taken by PBS for Isolator red
hot maintenace
| 09:37 | 10:31 | Kasba 132/33kV S/S TR-1 LT Scheduled S/D Due to Shutdown taken by PBS for red hot
maintenace
|  | 10:11 | Meghnaghat 230/132kV S/S Bus2 is restored.
| 10:34 |  | New Tongi S/S T2(413T) LT Scheduled S/D Due to DESCO AIS to GIS work.
|  | 10:46 | Meghnaghat-Shyampur 230kV Ckt-2 is restored.
| 11:00 | 11:52 | Kasba 132/33kV S/S TR-2 LT Scheduled S/D Due to Kasba-2 feeder Isolator Jumper red hot
maintenance by PBS.
| 11:00 | 11:52 | Kasba 132/33kV S/S TR-2 HT Scheduled S/D Due to Kasba-2 feeder Isolator Jumper red hot
maintenance by PBS.
|  | 11:10 | Feni 132/33kV S/S Bus-2 is restored.
|  | 11:15 | Keranigonj 230/132/33kV S/S ATR-2 LT is restored.
|  | 11:15 | Keranigonj 230/132/33kV S/S ATR-2 HT is restored.
|  | 11:31 | Madunaghat-TKCL 132kV Ckt-1 is restored.
|  | 11:34 | Madunaghat-Sikalbaha 132kV Ckt-2 is restored.
|  | 11:36 | Feni-PHP 132kV Ckt-1 is restored.
|  | 11:36 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) HT is restored.
|  | 11:38 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) LT is restored.
|  | 11:40 | Baroirhat-Feni 132 kV Ckt-2 is restored.
|  | 11:48 | Chowmuhani-Feni 132 kV Ckt-2 is restored.
|  | 11:50 | Chowmuhani-Feni 132 kV Ckt-1 is restored.
|  | 12:23 | Dohazari-Sikalbaha 132 kV Ckt-1 is restored.
| 12:23 | 12:50 | Bagerhat 132/33kV S/S Transformer-1 (403T) LT Scheduled S/D Due to Hotspot maintenance
| 12:24 | 12:49 | Bagerhat 132/33kV S/S Transformer-1 (403T) HT Scheduled S/D Due to Same as LT
| 12:25 |  | Sikalbaha-Patiya ckt-1 was switched on for the first time.
| 12:37 |  | Patiya-Dohazari ckt-1 was switched on for the first time.
|  | 13:00 | Coxsbazar 132/33kV S/S Main Bus is restored.
| 13:10 |  | Summit Bibiana-2 CCPP GT sync.
| 13:17 | 15:00 | Cox'sbazar-Dohazari 132 kV Ckt-2 Tripped from Coxsbazar 132/33kV end showing MCGG relays
Due to 33 kv Incoming C.B flashing
| 14:21 |  | Sikalbaha-Patiya ckt-2 was switched on for the first time
| 14:48 |  | Patiya-Dohazari ckt-2 was switched on for the first time
| 16:26 |  | Summit Bibiana-2 CCPP ST was sync.
| 17:45 |  | Sathia 132/33kV T1&T2 transformers were shutdown at 17:45 hr. and Sathia-Pabna solar park
ckt-1 was shutdown at 18:30hr due to DC supply fail.
| 17:45 | 18:10 | Shahjibazar 132/33kV S/S TR-06 LT Scheduled S/D Due to S/D taken By PDB
| 18:08 |  | Patiya 132/33kV T2 & T1 transformer were switched on (no load condition) for the first
time at 18:08hr & 18:14 hr respectively.
| 21:00 |  | Evening peak Generation is 13619 MW
| 21:11 |  | Summit Bibiana-2 CCPP ST was shutdown at 21:11 hr due to main steam valve leakag
| 23:33 |  | Summit Bibiana-2 CCPP GT was forced shutdown due to unavailability of ST.
|  | 00:06 | Shahjibazar 132/33kV S/S TR-02 HT is restored.
|  | 00:08 | Shahjibazar 132/33kV S/S TR-02 LT is restored.
| 02:13 |  | Meghnaghat CCPP(Summit) GT-1 Synchronized with remarks:- None
| 02:13 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- GT1
| 05:43 |  | Meghnaghat CCPP(Summit) ST Synchronized with remarks:- None
| 05:43 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- ST
| 06:00 |  | Minimum generation: 11937 MW
| 06:04 |  | Madunaghat-Sikalbaha 132kV Ckt-2 Scheduled S/D from Madunaghat 132/33kV end Due to For
the Chattogram waterlogging mitigation project by the Bangladesh Army.
| 06:10 |  | Madunaghat-TKCL 132kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end Due to For the
Chattogram waterlogging mitigation project by the Bangladesh Army.
| 07:02 |  | Chauddagram-Feni 132 kV Ckt-1 Scheduled S/D from Feni 132/33kV end Due to Chauddagram ckt
-1 S/D taken by EEGBPS Project for Feni 230 kV LILO Stringing Work
| 07:21 |  | Chauddagram-Feni 132 kV Ckt-1 Scheduled S/D from Chauddagram 132/33kV end Due to Feni - 1
gone under shutdown for there schedule maintenance.
| 07:32 |  | Bogura 132/33kV S/S Transformer-1 HT Scheduled S/D Due to T-1 33kv PT change work
| 07:32 |  | Bogura 132/33kV S/S Transformer-1 LT Scheduled S/D Due to T-1 33kv PT change work | [7 empty] | 20.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 01-08-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9535000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 239535 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 197 | 3786000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7429631 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 165564 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 32 | 167520 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 126312 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 45240 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18.5 | 469200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 441360 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 31253 | Fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 56455 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 32 | 788112 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 421834 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 18240 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 643680 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 119344 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 470520 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 555 | 11050145 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 733.79 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 90 | 928800 | Engine Problem
Dhaka Area Total |  |  |  |  | 6673.514 | 1765.5 | 36933745
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 12690 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 95520 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 218 | 5294636 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 219 | 5203214 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 128799 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 115776 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 33 | 351051 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 166080 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 29 | 776640 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 19199 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 203520 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1165 | 23438179 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 14 | 183840 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 730 | 12734545.46 | -
Chattogram Area Total |  |  |  |  | 4895.72 | 2445 | 48723689.46
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 204 | 4879000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 348 | 8226600 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 340 | 7860000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 30 | 736632 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 49 | 1146720 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 162 | 1572364 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1204196 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 286036 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 402032 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 30 | 842260 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 180 | 3675360 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 40 | 912000 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 27946 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 386450 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 15 | 687420 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 54 | 1333920 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 67 | 1777920 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 258227 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1590 | 36215083
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 151 | 2896320 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9850 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 90 | 1615200 | Engine Problem
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 103 | 2108400 | Engine Problem
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 194690 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 192960 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 429480 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 373 | 7446900
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1385780 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 156 | 3375981 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1976640 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 449000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 6 | 165600 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 150 | 950520 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 359 | 8910000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 300 | 7000000 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1133 | 24213521
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 433 | 10468363 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 362 | 6480000 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 440640 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1044 | 22130910 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1877 | 40431913
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 305 | 7279272 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2880000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 950 | 23234909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5234468 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 231 | 4822000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2469 | -
Barishal Area Total |  |  |  |  | 2236 | 1826 | 43453118.09
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 81218 | -
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 194 | 4738000 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 201 | 4990291 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 199 | 4747418 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9010981 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 16240 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 155840 | Engine Problem
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 19296 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 28080 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1206.72 | 26082909 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 302248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 400829 | -
Rajshahi Area Total |  |  |  |  | 3516.96 | 2214.72 | 50573350
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 174 | 4141000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 2256000 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 47966.88 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1911052 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 151929 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 889920 | -
Rangpur Area Total |  |  |  |  | 950 | 396 | 9397867.88
Eastern Grid Total |  |  |  |  | 17401.505 | 7306.5 | 153532938.46
Western Grid Total |  |  |  |  | 10442.16 | 6313.72 | 143856248.97
National Grid Total |  |  |  |  | 27843.665 | 13620.22 | 297389187.43
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 01-08-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8665.62 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4387.2 | MW
i) Dhaka area |  |  | 4330.14 |  | MW | i) Khulna area |  |  |  | 1515.5 | MW
ii) Chattogram area |  |  | 1315.7 |  | MW | ii) Barishal area |  |  |  | 437.5 | MW
iii) Cumilla area |  |  | 1290.78 |  | MW | iii) Rajshahi area |  |  |  | 1442.2 | MW
iv) Mymensingh area |  |  | 1189 |  | MW | iv) Rangpur area |  |  |  | 992 | MW
v) Sylhet area |  |  | 540 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13052.82 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 5 | 03:00 | 67 | Hathazari | 77 | 00:00 | 133 | PHP | 8 | 04:00
2 | AKSML | 173.3 | 09:00 | 68 | Ishurdi | 71 | 19:30 | 134 | Pabna | 112 | 19:30
3 | Aftabnagar | 44 | 11:00 | 69 | Jaldhaka | 90 | 23:00 | 135 | Palashbari | 102 | 22:00
4 | Agargaon | 110 | 13:00 | 70 | Jamalpur | 130 | 19:30 | 136 | Panchagarh | 61 | 02:00
5 | Agrabad | 70 | 13:00 | 71 | Jashore | 128 | 19:30 | 137 | Patuakhali | 66 | 23:00
6 | Amnura | 28 | 23:00 | 72 | Jhenaidah | 126 | 19:00 | 138 | Payra | 32 | 00:00
7 | Ashuganj | 101 | 00:00 | 73 | Joydebpur | 127 | 00:00 | 139 | Postogola | 53 | 00:00
8 | BSRM | 204 | 23:00 | 74 | Joypurhat | 61 | 22:00 | 140 | Purbachal | 20 | 00:00
9 | Bagerhat | 83 | 23:00 | 75 | Juldah | 14.5 | 00:00 | 141 | Purbasadipur | 132 | 00:00
10 | Bajitpur | 72 | 23:00 | 76 | KSRM | 55 | 06:00 | 142 | Rahanpur | 42 | 22:00
11 | Bakulia | 77 | 21:00 | 77 | Kabirpur | 179 | 12:00 | 143 | Rahim | 22 | 02:00
12 | Banani | 54.4 | 19:00 | 78 | Kachua | 86 | 20:00 | 144 | Rajbari | 78 | 20:00
13 | Bangabhaban | 4 | 10:00 | 79 | Kallyanpur | 96 | 00:00 | 145 | Rajendrapur | 128 | 00:00
14 | Barapukuria | 63 | 01:00 | 80 | Kalurghat | 28 | 01:00 | 146 | Rajshahi | 107 | 21:00
15 | Barguna | 22 | 22:00 | 81 | Kamrangirchar | 66 | 00:00 | 147 | Rajshahi-230 | 84 | 13:00
16 | Barishal | 107 | 13:00 | 82 | Kaptai | N/A | N/A | 148 | Ramganj | 116 | 01:00
17 | Barishal-230 | 92 | 19:30 | 83 | Kasba | 35 | 22:00 | 149 | Rampur | 36 | 00:00
18 | Baroaulia | 53 | 01:00 | 84 | Kazla | 86 | 00:00 | 150 | Rangamati | 17 | 19:00
19 | Baroirhat | 67 | 00:00 | 85 | Keranigonj | 85 | 00:00 | 151 | Rangpur | 140 | 13:00
20 | Bashundhara | 161 | 13:00 | 86 | Khagrachori | 32 | 20:00 | 152 | Ruppur | 6 | 11:00
21 | BashundharaCement | 10 | 06:00 | 87 | Khulna | 64 | 13:00 | 153 | SSM | 15 | 00:00
22 | Beanibazar | 78 | 22:00 | 88 | Khulshi | 168 | 13:00 | 154 | Saidpur | 104 | 00:00
23 | Benapole | 64 | 19:30 | 89 | Kishoreganj | 131 | 23:00 | 155 | Satkhira | 122 | 19:30
24 | Bhaluka | 138 | 00:00 | 90 | Kodda | 251 | 00:00 | 156 | Satmasjid | 83 | 13:00
25 | Bhandaria | 65 | 22:00 | 91 | Kulaura | 53 | 23:00 | 157 | Savar | 175 | 00:00
26 | Bhangura | 36 | 19:00 | 92 | Kurigram | 64 | 02:00 | 158 | SevenRings | 17.68 | 03:00
27 | Bheramara(GK) | 64 | 21:00 | 93 | Kushtia | 133 | 19:30 | 159 | ShahCement | 22 | 01:00
28 | Bhulta | 217 | 00:00 | 94 | Laksam | 34 | 00:00 | 160 | Shahjadpur | 78 | 21:00
29 | Bog-Sherpur | 62 | 00:00 | 95 | Lakshmipur | 21 | 00:00 | 161 | Shahjibazar | 34 | 13:00
30 | Bogura | 165 | 01:00 | 96 | Lalbag | 51 | 00:00 | 162 | Shahmirpur | 49.5 | 00:00
31 | Borhanuddin | 93 | 22:00 | 97 | Lalmonirhat | 66 | 01:00 | 163 | Shariatpur | 83 | 00:00
32 | Brahmanbaria | 132 | 00:00 | 98 | MI_Cement | 12.1 | 01:00 | 164 | Sherpur | 150 | 22:00
33 | Cantonment | 120 | 13:00 | 99 | Madanganj | 40 | 00:00 | 165 | Shikalbaha | 17 | 18:00
34 | Chandina | 18 | 06:00 | 100 | Madaripur | 99 | 23:00 | 166 | Shitalakhya | 56.3 | 01:00
35 | Chandpur | 69 | 20:00 | 101 | Madartek | 84 | 00:00 | 167 | Sholosohor | 36 | 23:00
36 | Chandraghona | 35 | 12:00 | 102 | Madunaghat | 49 | 10:00 | 168 | Shyampur | 154 | 00:00
37 | Chapai | 67 | 21:00 | 103 | Magura | 63 | 19:30 | 169 | Siddhirganj | 96 | 00:00
38 | Charsaidpur | 40 | 08:00 | 104 | Mahasthangarh | 86 | 00:00 | 170 | Sirajganj | 98 | 21:00
39 | Chauddagram | 67 | 00:00 | 105 | Maijdee | 14 | 00:00 | 171 | Sonargaon | 114 | 00:00
40 | Chhatak | 41 | 00:00 | 106 | Manikganj | 116 | 22:00 | 172 | Sreemongol | 92 | 23:00
41 | Chowmuhani | 180 | 00:00 | 107 | Maniknagar | 64 | 00:00 | 173 | Sreepur | 85 | 00:00
42 | Chuadanga | 109 | 21:00 | 108 | Matarbari | 52 | 19:30 | 174 | Srinagar | 44.77 | 22:00
43 | Coxsbazar | 135 | 21:00 | 109 | Matuail | 60 | 00:00 | 175 | Sunamganj | 60 | 21:00
44 | Cumilla(N) | 138 | 00:00 | 110 | Millgate | 103 | 00:00 | 176 | Sylhet | 52 | 21:00
45 | Cumilla(S) | 128 | 01:00 | 111 | Mirpur | 107 | 12:00 | 177 | Sylhet-132 | 111 | 23:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 10 | 00:00 | 178 | TK | 36.5 | 13:00
47 | Daudkandi | 146 | 00:00 | 113 | Mirzapur | 42 | 00:00 | 179 | Tangail | 169 | 20:00
48 | Dhaka | 34 | 00:00 | 114 | Mithapukur | 68 | 19:30 | 180 | Taraganj | 24 | 00:00
49 | Dhamrai | 104 | 00:00 | 115 | Modern | N/A | N/A | 181 | Thakurgaon | 112 | 20:00
50 | Dhanmondi | 107.6 | 19:00 | 116 | Mogbazar | 111.8 | 12:00 | 182 | Tongi | 80 | 00:00
51 | Dohazari | 103 | 19:00 | 117 | Mongla | 37 | 00:00 | 183 | Ullahpara | 38 | 20:00
52 | Faridpur | 153 | 22:00 | 118 | Motijheel | 35 | 13:00 | 184 | Ullon | 41 | 00:00
53 | Fatullah | 80 | 00:00 | 119 | Muktagacha | 36 | 21:00 | 185 | Uttara | 70 | 19:30
54 | Fenchuganj | 43 | 00:00 | 120 | Munshiganj | 102 | 23:00 | 186 | UttaraNew | 54 | 00:00
55 | Feni | 103 | 21:00 | 121 | Muradnagar | 40 | 22:00 | 187 | Zigatola | 66 | 13:00
56 | GPH | 92 | 01:00 | 122 | Mymensingh | 196 | 20:00
57 | Ghatail | 86 | 19:00 | 123 | Naogaon | 125 | 21:00
58 | Ghorashal | 12 | 00:00 | 124 | Narail | 54.5 | 19:30
59 | Ghorashal-230 | 72 | 00:00 | 125 | Narinda | 52 | 13:00
60 | Goalpara | 33 | 13:00 | 126 | Narshingdi | 164 | 22:00
61 | Gollamari | 76 | 13:00 | 127 | Natore | 140 | 19:30
62 | Gopalganj | 104 | 19:30 | 128 | Nawabganj | 55.4 | 22:00
63 | Gulshan | 48 | 13:00 | 129 | Netrakona | 145 | 19:30
64 | Halishahar | 36 | 23:00 | 130 | New | 56.3 | 00:00
65 | HaripurSBU | 139 | 00:00 | 131 | Niamatpur | 78 | 22:00
66 | Hasnabad | 72 | 00:00 | 132 | Noapara | 38 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 01-08-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14120.28 | 57 |  | 14179.85
1:00 | 13766.3 | 0 |  | 13766.3
2:00 | 13330.57 | 0 |  | 13330.57
3:00 | 12987.35 | 0 |  | 12987.35
4:00 | 12692.2 | 0 |  | 12692.2
5:00 | 12330 | 0 |  | 12330
6:00 | 11625.45 | 0 |  | 11625.45
7:00 | 11273.67 | 29 |  | 11303.98
8:00 | 11158.44 | 25 |  | 11184.44
9:00 | 10951.24 | 0 |  | 10951.24
10:00 | 10934.21 | 0 |  | 10934.21
11:00 | 11044.65 | 0 |  | 11044.65
12:00 | 11666.46 | 0 |  | 11666.46
13:00 | 12296.41 | 0 |  | 12296.41
14:00 | 11815.95 | 0 |  | 11815.95
15:00 | 11515.62 | 0 |  | 11515.62
16:00 | 11289.55 | 0 |  | 11289.55
17:00 | 10921.34 | 0 |  | 10921.34
18:00 | 10834.99 | 0 |  | 10834.99
19:00 | 12752.5 | 0 |  | 12752.5
19:30 | 13578.5 | 0 |  | 13578.5
20:00 | 13395.3 | 0 |  | 13395.3
21:00 | 13620.22 | 0 |  | 13620.22
22:00 | 13686.57 | 0 |  | 13686.57
23:00 | 13764.75 | 0 |  | 13764.75
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 01-08-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7475 | 6645.28 | 14120.28 | DAILY GENERATION CURVE
00:30 | 7331.5 | 6611.79 | 13943.29
01:00 | 7188 | 6578.3 | 13766.3 | 01-08-2025
01:30 | 7033.25 | 6515.185 | 13548.435
02:00 | 6878.5 | 6452.07 | 13330.57
02:30 | 6694.95 | 6464.01 | 13158.96
03:00 | 6511.4 | 6475.95 | 12987.35
03:30 | 6493.2 | 6346.575 | 12839.775
04:00 | 6475 | 6217.2 | 12692.2
04:30 | 6398 | 6113.1 | 12511.1
05:00 | 6321 | 6009 | 12330
05:30 | 6141.325 | 5836.4 | 11977.725
06:00 | 5961.65 | 5663.8 | 11625.45
06:30 | 5999.955 | 5449.605 | 11449.56
07:00 | 6038.26 | 5235.41 | 11273.67
07:30 | 5998.41 | 5217.645 | 11216.055
08:00 | 5958.56 | 5199.88 | 11158.44
08:30 | 5822.065 | 5232.775 | 11054.84
09:00 | 5685.57 | 5265.67 | 10951.24
09:30 | 5623.4 | 5319.325 | 10942.725
10:00 | 5561.23 | 5372.98 | 10934.21
10:30 | 5499.715 | 5489.715 | 10989.43
11:00 | 5438.2 | 5606.45 | 11044.65
11:30 | 5622.185 | 5733.37 | 11355.555
12:00 | 5806.17 | 5860.29 | 11666.46
12:30 | 6076.04 | 5905.395 | 11981.435
13:00 | 6345.91 | 5950.5 | 12296.41
13:30 | 6098.36 | 5957.82 | 12056.18
14:00 | 5850.81 | 5965.14 | 11815.95
14:30 | 5751.76 | 5914.025 | 11665.785
15:00 | 5652.71 | 5862.91 | 11515.62
15:30 | 5643.965 | 5758.62 | 11402.585
16:00 | 5635.22 | 5654.33 | 11289.55
16:30 | 5600.36 | 5505.085 | 11105.445
17:00 | 5565.5 | 5355.84 | 10921.34
17:30 | 5641.545 | 5236.62 | 10878.165
18:00 | 5717.59 | 5117.4 | 10834.99
18:30 | 6310.045 | 5483.7 | 11793.745
19:00 | 6902.5 | 5850 | 12752.5
19:30 | 7420.5 | 6158 | 13578.5
20:00 | 7245.3 | 6150 | 13395.3
20:30 | 7275.9 | 6231.86 | 13507.76 |  | Executive Engineer
21:00 | 7306.5 | 6313.72 | 13620.22 |  | Network Operation Division
21:30 | 7269.25 | 6384.145 | 13653.395
22:00 | 7232 | 6454.57 | 13686.57
22:30 | 7256 | 6469.66 | 13725.66
23:00 | 7280 | 6484.75 | 13764.75

## En-Curve
QF-LDC-12
Date | 01-08-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3664 | 1838 | 430 | 38 | 46 | 1439.28 | 219 | 4566 | 0 | 357 | 1507 | 0 | 0 | 16 | 57 | DAILY ENERGY CURVE
00:30 | 3651.5 | 1774 | 430 | 38 | 45 | 1442.79 | 219.5 | 4502.5 | 0 | 303.5 | 1522 | 0 | 0 | 14.5 | 28.5 | 01-08-2025
01:00 | 3639 | 1710 | 430 | 38 | 44 | 1446.3 | 220 | 4439 | 0 | 250 | 1537 | 0 | 0 | 13 | 0
01:30 | 3661.5 | 1678 | 430 | 38 | 43 | 1441.685 | 220 | 4393.5 | 0 | 214 | 1417.25 | 0 | 0 | 11.5 | 0 | Energy Generated | 297.3892 |  | MKWHr
02:00 | 3684 | 1646 | 430 | 38 | 42 | 1437.07 | 220 | 4348 | 0 | 178 | 1297.5 | 0 | 0 | 10 | 0 | Energy not Served | 0.111 |  | MKWHr
02:30 | 3725 | 1611 | 430 | 38 | 40 | 1445.01 | 220 | 4345.5 | 0 | 162 | 1135.95 | 0 | 0 | 6.5 | 0 | Total Energy Requirement | 297.5002 |  | MKWHr
03:00 | 3766 | 1576 | 430 | 38 | 38 | 1452.95 | 220 | 4343 | 0 | 146 | 974.4 | 0 | 0 | 3 | 0
03:30 | 3798.5 | 1572.5 | 430 | 38 | 39 | 1406.075 | 220 | 4307.5 | 0 | 138 | 885.7 | 0 | 0 | 4.5 | 0
04:00 | 3831 | 1569 | 430 | 38 | 40 | 1359.2 | 220 | 4272 | 0 | 130 | 797 | 0 | 0 | 6 | 0
04:30 | 3842 | 1572 | 430.5 | 38 | 39 | 1286.6 | 220 | 4159.5 | 0 | 121.5 | 798 | 0 | 0 | 4 | 0
05:00 | 3853 | 1575 | 431 | 38 | 38 | 1214 | 220 | 4047 | 0 | 113 | 799 | 0 | 0 | 2 | 0
05:30 | 3736 | 1509.5 | 430.5 | 38 | 37 | 1128.595 | 220 | 3977.5 | 3.13 | 104.5 | 792 | 0 | 0 | 1 | 0
06:00 | 3619 | 1444 | 430 | 38 | 36 | 1043.19 | 220 | 3908 | 6.26 | 96 | 785 | 0 | 0 | 0 | 0
06:30 | 3611.5 | 1460 | 430.5 | 38 | 36 | 961 | 219 | 3760.5 | 25.56 | 96 | 811.5 | 0 | 0 | 0 | 14.5
07:00 | 3604 | 1476 | 431 | 38 | 36 | 878.81 | 218 | 3613 | 44.86 | 96 | 838 | 0 | 0 | 0 | 29
07:30 | 3574.5 | 1474.5 | 430.5 | 38 | 35 | 867.12 | 218 | 3604.5 | 82.935 | 70 | 821 | 0 | 0 | 0 | 27
08:00 | 3545 | 1473 | 430 | 38 | 34 | 855.43 | 218 | 3596 | 121.01 | 44 | 804 | 0 | 0 | 0 | 25
08:30 | 3538.5 | 1451.5 | 431.5 | 38 | 34 | 858.215 | 218.5 | 3541 | 152.875 | 26.25 | 764.5 | 0 | 0 | 0 | 12.5
09:00 | 3532 | 1430 | 433 | 38 | 34 | 861 | 219 | 3486 | 184.74 | 8.5 | 725 | 0 | 0 | 0 | 0
09:30 | 3519 | 1406 | 433 | 38 | 34 | 860 | 219.5 | 3451 | 246.225 | 8.5 | 727.5 | 0 | 0 | 0 | 0
10:00 | 3506 | 1382 | 433 | 38 | 34 | 859 | 220 | 3416 | 307.71 | 8.5 | 730 | 0 | 0 | 0 | 0
10:30 | 3499.5 | 1355.5 | 433 | 38 | 34 | 863.5 | 220.5 | 3415 | 405.43 | 8.5 | 716.5 | 0 | 0 | 0 | 0
11:00 | 3493 | 1329 | 433 | 38 | 34 | 868 | 221 | 3414 | 503.15 | 8.5 | 703 | 0 | 0 | 0 | 0
11:30 | 3630 | 1415 | 433 | 38 | 36 | 875 | 221 | 3446 | 550.055 | 8.5 | 703 | 0 | 0 | 0 | 0
12:00 | 3767 | 1501 | 433 | 38 | 38 | 882 | 221 | 3478 | 596.96 | 8.5 | 703 | 0 | 0 | 0 | 0
12:30 | 3884.5 | 1576.5 | 433.5 | 38 | 40 | 921 | 221 | 3662 | 441.435 | 34.5 | 729 | 0 | 0 | 0 | 0
13:00 | 4002 | 1652 | 434 | 38 | 42 | 960 | 221 | 3846 | 285.91 | 60.5 | 755 | 0 | 0 | 0 | 0
13:30 | 3819.5 | 1538.5 | 433.5 | 38 | 41 | 964.5 | 221 | 3925 | 301.18 | 60.5 | 713.5 | 0 | 0 | 0 | 0
14:00 | 3637 | 1425 | 433 | 38 | 40 | 969 | 221 | 4004 | 316.45 | 60.5 | 672 | 0 | 0 | 0 | 0
14:30 | 3649 | 1427.75 | 433 | 38 | 40 | 971 | 221 | 4012 | 304.035 | 43 | 527 | 0 | 0 | 0 | 0
15:00 | 3661 | 1430.5 | 433 | 38 | 40 | 973 | 221 | 4020 | 291.62 | 25.5 | 382 | 0 | 0 | 0 | 0
15:30 | 3672 | 1447 | 433 | 38 | 37 | 976 | 221 | 3970 | 239.085 | 17 | 347 | 0 | 0 | 5.5 | 0
16:00 | 3683 | 1463.5 | 433 | 38 | 34 | 979 | 221 | 3920 | 186.55 | 8.5 | 312 | 0 | 0 | 11 | 0
16:30 | 3684 | 1473.5 | 433 | 38 | 34 | 949 | 221 | 3801 | 146.445 | 8.5 | 307 | 0 | 0 | 10 | 0
17:00 | 3685 | 1483.5 | 433 | 38 | 34 | 919 | 221 | 3682 | 106.34 | 8.5 | 302 | 0 | 0 | 9 | 0
17:30 | 3712 | 1508.5 | 433 | 38 | 33 | 887.5 | 220 | 3643 | 72.165 | 8.5 | 308.5 | 0 | 0 | 14 | 0
18:00 | 3739 | 1533.5 | 433 | 38 | 32 | 856 | 219 | 3604 | 37.99 | 8.5 | 315 | 0 | 0 | 19 | 0
18:30 | 3877 | 1680 | 433 | 38 | 36 | 965.5 | 219 | 3900 | 18.995 | 115.75 | 493 | 0 | 0 | 17.5 | 0
19:00 | 4015 | 1826.5 | 433 | 38 | 40 | 1075 | 219 | 4196 | 0 | 223 | 671 | 0 | 0 | 16 | 0
19:30 | 3955 | 1879.5 | 433 | 38 | 38 | 1154 | 219 | 4467 | 0 | 296 | 1084 | 0 | 0 | 15 | 0
20:00 | 3987 | 1876.5 | 433 | 38 | 38 | 1166 | 218 | 4498 | 0 | 205 | 926.8 | 0 | 0 | 9 | 0
20:30 | 4034 | 1924.5 | 433 | 38 | 39 | 1186.36 | 218 | 4548.5 | 0 | 197 | 877.9 | 0 | 0 | 11.5 | 0
21:00 | 4081 | 1972.5 | 433 | 38 | 40 | 1206.72 | 218 | 4599 | 0 | 189 | 829 | 0 | 0 | 14 | 0
21:30 | 4088 | 1927.25 | 433 | 38 | 41 | 1210.645 | 218.5 | 4662 | 0 | 188.5 | 831 | 0 | 0 | 15.5 | 0
22:00 | 4095 | 1882 | 433 | 38 | 42 | 1214.57 | 219 | 4725 | 0 | 188 | 833 | 0 | 0 | 17 | 0
22:30 | 4111.5 | 1884.5 | 432 | 38 | 42 | 1221.66 | 219.5 | 4733 | 0 | 188 | 832 | 0 | 0 | 23.5 | 0
23:00 | 4128 | 1887 | 431 | 38 | 42 | 1228.75 | 220 | 4741 | 0 | 188 | 831 | 0 | 0 | 30 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 01-08-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 389 | 08:00 | 378 | 21:00 | Payra | 417 | 08:00 | 411 | 01:00
Ashuganj | 407 | 7:00 | 391 | 23:00 | Rahanpur | 405 | 10:00 | 385 | 01:00
Bhulta | 403 | 07:00 | 387 | 23:00 | Rampal | 409 | 18:00 | 396 | 23:00
Bibiana | 388 | 08:00 | 380 | 03:00
BIPTC | 409 | 04:00 | 401 | 19:30
Bogura | 388 | 10:00 | 364 | 01:00
Gopalganj | 403 | 09:00 | 390 | 23:00
Kaliakoir | 380 | 08:00 | 370 | 21:00
Madunaghat | 396 | 08:00 | 389 | 00:00
Meghnaghat | 391 | 07:00 | 379 | 23:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 227 | 18:00 | 219 | 23:00 | Keranigonj | 225 | 18:00 | 216 | 23:00
AKSML | 235 | 07:00 | 221 | 22:00 | Khulna(S) | 233 | 18:00 | 220 | 23:00
Aminbazar | 228 | 16:00 | 220 | 22:00 | Madunaghat | 235 | 07:00 | 226 | 22:00
Ashuganj | 235 | 08:00 | 227 | 13:00 | Madunaghat-400 | 236 | 08:00 | 229 | 00:00
Ashuganj-400 | 235 | 08:00 | 227 | 13:00 | Maniknagar | 222 | 18:00 | 215 | 22:00
Baghabari | 237 | 10:00 | 227 | 22:00 | Meghnaghat | 229 | 07:00 | 221 | 23:00
Barapukuria | 229 | 09:00 | 215 | 01:00 | Meghnaghat-400 | 225 | 08:00 | 218 | 23:00
Barapukuria-230 | 229 | 09:00 | 215 | 01:00 | Mirsorai | 228 | 08:00 | 217 | 23:00
Barishal | 232 | 09:00 | 222 | 22:00 | Rajshahi | 233 | 09:00 | 220 | 00:00
Bheramara | 234 | 09:00 | 223 | 23:00 | Rampal | 233 | 08:00 | 222 | 00:00
Bhulta | 232 | 07:00 | 213 | 23:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 231 | 18:00 | 221 | 23:00 | Rampura | 231 | 07:00 | 220 | 23:00
BIPTC | 235 | 07:00 | 222 | 23:00 | Shikalbaha | 233 | 08:00 | 223 | 22:00
Bogura | 240 | 10:00 | 226 | 01:00 | Shyampur | 224 | 18:30 | 216 | 23:00
Bogura-400 | 240 | 10:00 | 226 | 01:00 | Siddhirganj | 223 | 06:00 | 217 | 22:00
Borhanuddin | 239 | 09:00 | 229 | 00:00 | Sirajgonj | 242 | 10:00 | 235 | 23:00
BSRM | 228 | 07:00 | 217 | 23:00 | Sreepur | 232 | 07:00 | 225 | 03:00
Cumilla(N) | 225 | 07:00 | 215 | 23:00 | Tongi | 228 | 05:00 | 222 | 00:00
Faridpur | 235 | 18:30 | 219 | 23:00
Fenchuganj | 230 | 18:00 | 222 | 23:00
Ghorashal | 230 | 01:00 | 225 | 00:00
Ghorashal-230 | 230 | 07:00 | 222 | 21:00
Gopalganj | 230 | 08:00 | 221 | 23:00
GPH | 232 | 08:00 | 221 | 23:00
Haripur | 223 | 18:00 | 216 | 23:00
Hasnabad | 224 | 07:00 | 217 | 23:00
Hathazari | 231 | 04:00 | 220 | 23:00
Ishurdi | 236 | 07:00 | 226 | 21:00
Jhenaidah | 232 | 10:00 | 218 | 19:30
Kaliakoir | 234 | 07:00 | 227 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 00:00 | 132 | 13:00 | Lalmonirhat | 134 | 09:00 | 121 | 19:30
Agargaon | 133 | 07:00 | 128 | 23:00 | Madanganj | 131 | 18:30 | 125 | 23:00
Agrabad | 136 | 08:00 | 126 | 22:00 | Madaripur | 136 | 09:00 | 130 | 00:00
AKS | 132 | 08:00 | 124 | 23:00 | Madartek | 138 | 07:00 | 131 | 13:00
Aminbazar | 134 | 16:00 | 128 | 21:00 | Madunaghat | 134 | 07:00 | 127 | 22:00
Amnura | 137 | 09:00 | 126 | 22:00 | Magura | 133 | 08:00 | 122 | 23:00
Ashuganj | 144 | 08:00 | 139 | 23:00 | Mahasthangarh | 137 | 09:00 | 127 | 23:00
Bagerhat | 134 | 09:00 | 121 | 23:00 | Maijdee | 123 | 11:00 | 107 | 23:00
Bajitpur | 132 | 07:00 | 126 | 22:00 | Manikganj | 131 | 07:00 | 125 | 22:00
Bakulia | 137 | 08:00 | 127 | 23:00 | Maniknagar | 134 | 18:00 | 130 | 22:00
Banani | 138 | 00:00 | 130 | 13:00 | Matarbari | 130 | 14:00 | 109 | 21:00
Bangabhaban | 134 | 18:00 | 130 | 01:00 | Matuail | 131 | 18:00 | 126 | 23:00
Barapukuria | 140 | 09:00 | 128 | 19:30 | Millgate | 135 | 08:00 | 129 | 22:00
Barguna | 135 | 08:00 | 131 | 00:00 | Mirpur | 133 | 18:00 | 128 | 22:00
Barishal | 136 | 18:00 | 127 | 23:00 | Mirzapur | 131 | 09:00 | 126 | 13:00
Barishal-230 | 136 | 08:00 | 128 | 23:00 | Mithapukur | 129 | 18:00 | 116 | 00:00
Baroaulia | 134 | 08:00 | 129 | 00:00 | MI_Cement | 131 | 18:00 | 126 | 23:00
Baroirhat | 132 | 08:00 | 114 | 23:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 139 | 00:00 | 129 | 01:00 | Mogbazar | 140 | 08:00 | 133 | 23:00
BashundharaCement | 131 | 18:30 | 125 | 23:00 | Mongla | 135 | 09:00 | 123 | 23:00
Beanibazar | 129 | 18:00 | 118 | 23:00 | Motijheel | 134 | 18:00 | 130 | 01:00
Benapole | 134 | 07:00 | 122 | 23:00 | Muktagacha | 135 | 11:00 | 128 | 18:00
Bhaluka | 133 | 07:00 | 125 | 23:00 | Munshiganj | 131 | 18:00 | 125 | 23:00
Bhandaria | 134 | 17:00 | 117 | 23:00 | Muradnagar | 128 | 08:00 | 118 | 23:00
Bhangura | 136 | 09:00 | 129 | 23:00 | Mymensingh | 136 | 06:00 | 118 | 23:00
Bheramara | 138 | 06:00 | 133 | 00:00 | Naogaon | 136 | 09:00 | 125 | 23:00
Bheramara(GK) | 138 | 08:00 | 132 | 00:00 | Narail | 133 | 09:00 | 121 | 20:00
Bhulta | 126 | 18:00 | 118 | 23:00 | Narinda | 134 | 18:00 | 130 | 22:00
Bog-Sherpur | 139 | 09:00 | 129 | 22:00 | Narshingdi | 137 | 06:00 | 120 | 23:00
Bogura | 141 | 10:00 | 132 | 00:00 | Natore | 136 | 09:00 | 128 | 21:00
Bogura-230 | 141 | 09:00 | 132 | 00:00 | Nawabganj | 135 | 18:00 | 128 | 23:00
Brahmanbaria | 140 | 07:00 | 131 | 23:00 | Netrakona | 127 | 07:00 | 116 | 23:00
Cantonment | 133 | 07:00 | 128 | 23:00 | New | 135 | 05:00 | 129 | 23:00
Chandina | 130 | 08:00 | 121 | 23:00 | Niamatpur | 138 | 09:00 | 129 | 00:00
Chandpur | 130 | 08:00 | 118 | 22:00 | Noapara | 136 | 09:00 | 125 | 23:00
Chandraghona | 134 | 07:00 | 128 | 22:00 | Pabna | 136 | 06:00 | 129 | 22:00
Chapai | 137 | 10:00 | 128 | 00:00 | Palashbari | 128 | 10:00 | 114 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 131 | 18:00 | 126 | 23:00 | Panchagarh | 135 | 09:00 | 120 | 19:30
Chauddagram | 126 | 07:00 | 112 | 23:00 | Patuakhali | 136 | 18:00 | 132 | 00:00
Chhatak | 126 | 17:00 | 114 | 23:00 | Payra | 137 | 07:00 | 133 | 23:00
Chowmuhani | 123 | 11:00 | 108 | 23:00 | PHP | 130 | 10:00 | 112 | 23:00
Chuadanga | 134 | 09:00 | 121 | 23:00 | Postogola | 133 | 18:00 | 129 | 03:00
Coxsbazar | 120 | 05:00 | 111 | 20:00 | Purbachal | 139 | 07:00 | 128 | 23:00
Cumilla(N) | 130 | 08:00 | 120 | 23:00 | Purbasadipur | 134 | 09:00 | 121 | 19:30
Cumilla(S) | 132 | 01:00 | 118 | 23:00 | Rahanpur | 139 | 10:00 | 134 | 23:00
Daganbhuiyan | 124 | 07:00 | 110 | 22:00 | Rahanpur-400 | 139 | 09:00 | 132 | 01:00
Daudkandi | 126 | 08:00 | 117 | 23:00 | Rahim | 130 | 09:00 | 126 | 02:00
Dhaka | 139 | 07:00 | 133 | 23:00 | Rajbari | 135 | 08:00 | 128 | 23:00
Dhamrai | 134 | 07:00 | 128 | 00:00 | Rajendrapur | 132 | 07:00 | 123 | 13:00
Dhanmondi | 139 | 00:00 | 132 | 23:00 | Rajshahi | 135 | 09:00 | 127 | 20:00
Dohazari | 128 | 14:00 | 121 | 21:00 | Rajshahi-230 | 134 | 09:00 | 127 | 00:00
Faridpur | 136 | 08:00 | 130 | 22:00 | Ramganj | 126 | 07:00 | 109 | 23:00
Fatullah | 132 | 18:00 | 127 | 23:00 | Rampur | 135 | 08:00 | 126 | 21:00
Fenchuganj | 136 | 07:00 | 129 | 23:00 | Rampura | 138 | 00:00 | 132 | 12:00
Feni | 126 | 08:00 | 114 | 22:00 | Rangamati | 133 | 07:00 | 127 | 21:00
Ghatail | 130 | 00:00 | 125 | 23:00 | Rangpur | 135 | 09:00 | 123 | 19:30
Ghorashal | 136 | 04:00 | 132 | 22:00 | Ruppur | 138 | 09:00 | 132 | 00:00
Goalpara | 138 | 10:00 | 128 | 23:00 | Saidpur | 133 | 09:00 | 122 | 19:30
Gollamari | 138 | 08:00 | 129 | 23:00 | Satkhira | 136 | 09:00 | 123 | 23:00
Gopalganj | 136 | 07:00 | 128 | 23:00 | Satmasjid | 133 | 08:00 | 128 | 23:00
Gopalganj-400 | 138 | 09:00 | 132 | 23:00 | Savar | 134 | 19:00 | 126 | 23:00
Gulshan | 139 | 07:00 | 132 | 12:00 | SevenRings | 138 | 07:00 | 131 | 23:00
Halishahar | 137 | 08:00 | 127 | 23:00 | ShahCement | 131 | 18:00 | 126 | 23:00
Haripur | 131 | 18:00 | 126 | 22:00 | Shahjadpur | 139 | 08:00 | 133 | 21:00
HaripurSBU | 131 | 18:00 | 126 | 22:00 | Shahjibazar | 139 | 17:00 | 132 | 23:00
Hasnabad | 133 | 18:00 | 128 | 23:00 | Shahmirpur | 137 | 08:00 | 127 | 23:00
Hathazari | 135 | 08:00 | 128 | 22:00 | Shariatpur | 135 | 09:00 | 127 | 23:00
Ishurdi | 139 | 09:00 | 133 | 00:00 | Sherpur | 136 | 00:00 | 122 | 18:00
Jaldhaka | 132 | 09:00 | 120 | 19:30 | Shikalbaha | 127 | 08:00 | 117 | 21:00
Jamalpur | 138 | 00:00 | 125 | 18:00 | Shikalbaha-230 | 138 | 08:00 | 128 | 22:00
Jashore | 132 | 07:00 | 121 | 19:30 | Shitalakhya | 131 | 18:00 | 126 | 23:00
Jhenaidah | 136 | 07:00 | 124 | 20:00 | Sholosohor | 133 | 07:00 | 127 | 23:00
Jhenaidah-230 | 136 | 08:00 | 126 | 23:00 | Shyampur | 132 | 18:00 | 127 | 04:00
Joydebpur | 139 | 00:00 | 130 | 15:00 | Shyampur-230 | 134 | 18:30 | 126 | 04:00
Joypurhat | 135 | 09:00 | 123 | 22:00 | Siddhirganj | 131 | 18:00 | 126 | 23:00
Juldah | 136 | 08:00 | 128 | 00:00 | Sirajganj | 137 | 10:00 | 129 | 00:00
Kabirpur | 132 | 04:00 | 128 | 12:00 | Sonargaon | 130 | 18:00 | 123 | 23:00
Kachua | 128 | 07:00 | 116 | 23:00 | Sreemongol | 136 | 07:00 | 128 | 23:00
Kaliakoir | 136 | 07:00 | 130 | 12:00 | Sreepur | 135 | 07:00 | 129 | 22:00
Kallyanpur | 134 | 18:00 | 128 | 22:00 | Srinagar | 135 | 18:00 | 130 | 22:00
Kalurghat | 134 | 07:00 | 127 | 23:00 | SSM | 139 | 08:00 | 131 | 02:00
Kamrangirchar | 136 | 18:00 | 129 | 04:00 | Sunamganj | 124 | 08:00 | 111 | 23:00
Kaptai | 136 | 9:00 | 131 | 00:00 | Sylhet | 129 | 18:00 | 119 | 23:00
Kasba | 127 | 08:00 | 117 | 23:00 | Sylhet-132 | 129 | 08:00 | 120 | 23:00
Kazla | 134 | 19:00 | 130 | 00:00 | Tangail | 129 | 07:00 | 123 | 22:00
Keranigonj | 136 | 18:00 | 129 | 23:00 | Taraganj | 133 | 09:00 | 124 | 19:00
Khagrachori | 133 | 08:00 | 126 | 21:00 | Thakurgaon | 134 | 09:00 | 120 | 15:00
Khulna | 137 | 09:00 | 126 | 23:00 | TK | 132 | 05:00 | 127 | 21:00
Khulna(S) | 138 | 08:00 | 129 | 23:00 | Tongi | 135 | 08:00 | 131 | 23:00
Khulshi | 134 | 08:00 | 125 | 21:00 | Ullahpara | 138 | 10:00 | 130 | 00:00
Kishoreganj | 130 | 07:00 | 121 | 23:00 | Ullon | 138 | 00:00 | 132 | 13:00
Kodda | 134 | 01:00 | 124 | 12:00 | Uttara | 133 | 18:00 | 128 | 21:00
KSRM | 135 | 08:00 | 127 | 03:00 | UttaraNew | 133 | 08:00 | 127 | 23:00
Kulaura | 135 | 18:00 | 127 | 23:00 | Zigatola | 135 | 18:00 | 129 | 04:00
Kurigram | 132 | 09:00 | 120 | 19:30
Kushtia | 136 | 09:00 | 128 | 00:00
Laksam | 127 | 08:00 | 115 | 23:00
Lakshmipur | 125 | 07:00 | 108 | 23:00
Lalbag | 135 | 18:30 | 130 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division