## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 03-08-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 02-08-2025 | during | 03-08-2025 | during | 03-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 0 | 0 | 0 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 302 | 298 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 189 | 132 | 208.13 | 208.13 | 208.13 | 208.13 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 322 | 330 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 50 | 7 | 50 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 49 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 16 | 149.36 | 149.36 | 144 | 144 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 28 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | Fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 45 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 50 | 33 | 149 | 149 | 114 | 114 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 85 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 16 | 16 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 154 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 9 | 0 | 24 | 0 | 24 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 414 | 415 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 733.79 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 90 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6673.514 | 1955 | 2278 | 5417.15 | 5436.15 | 3716.8 | 3735.8
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 100 | 120 | 120 | 120 | 120 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 1 | 0 | 5 | 0 | 5 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 26 | 33 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 221 | 219 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 36 | 48 | 72 | 98 | 98 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 31 | 65 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 50 | 100 | 100 | 12 | 36 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 12 | 31 | 2 | 20 | 2 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0.28 | 0 | 3.65 | 0 | 3.65 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 31 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1004 | 1145 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 7 | 14 | 12 | 3 | 12 | 3 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 757 | 765 | 770 | 770 | 770 | 770 | -
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2096.28 | 2489 | 3688.37 | 3712.72 | 3562.37 | 3586.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 208 | 203 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 332 | 345 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 340 | 340 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 33 | 33 | 46.7 | 46.7 | 35 | 35 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 43 | 47 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 86 | 86 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 10 | 150 | 150 | 140 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 37 | 47 | 47 | 47 | 47 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 70 | 163 | 163 | 70 | 70 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 140 | 161 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 54 | 46 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 16 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 106 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 54 | 60 | 113 | 113 | 46 | 46 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 75 | 93 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 53 | 0 | 40 | 0 | 40 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1552 | 1760.2 | 2419.56 | 2379.56 | 2217.36 | 2177.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 02-08-2025 | during | 03-08-2025 | during | 03-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 149 | 146 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 65 | 120 | 200 | 200 | 170.2 | 170.2 | Engine Problem
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 65 | 87 | 115 | 115 | 100 | 100 | Engine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 10.12 | 0 | 35 | 0 | 35 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 35 | 35 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 301.12 | 382 | 585.9 | 549 | 511.6 | 474.7
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 142 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 84 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 6 | 7 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 385 | 333 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 295 | 280 | 300 | 300 | 300 | 300 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 996 | 924 | 1005 | 1005 | 944 | 944
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 433 | 886 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 42 | 42 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 389 | 365 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 11 | 105 | 105 | 53 | 53 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 50 | 0 | 55 | 0 | 55 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 920 | 1111 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1830 | 2411 | 3609.2 | 3554.2 | 3465 | 3410
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 305 | 305 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 955 | 1120 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 173 | 251 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.07 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1773.07 | 2016 | 2162 | 2161 | 2152 | 2151
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 45.74 | 0 | 0 | 0 | 0 | 0 | -
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 36 | 47 | 47 | 42 | 42 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 197 | 177 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 178 | 177 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 184 | 176 | 220 | 220 | 220 | 220 | Plant is running as per NLDC demand
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 384 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 14 | 30 | 30 | 27 | 27 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 42 | 96 | 96 | 87 | 87 | Engine Problem
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.17 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1028.72 | 1446 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 34.02 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 39 | 0 | 90 | 0 | 90 | 0 | -
Rajshahi Area Total |  |  |  |  | 3474 | 3516.96 | 2123.65 | 2488 | 3183.47 | 3026.87 | 3081.69 | 2925.09
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 176 | 180 | 160 | 160 | 160 | 160 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.7 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 95 | 95 | 115 | 115 | Schedule Maintenance
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 28 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 101 | 0 | 92.24 | 0 | 92.24 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 377.7 | 408 | 525.84 | 402 | 545.84 | 422
System Total |  |  |  |  | 28671.2 | 27843.665 | 13004.82 | 15156.2 | 22596.49 | 22226.5 | 20196.66 | 19826.67
Forecast Scenario (03-08-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15070 |  | 0 |  | 15070
|  |  |  | 1:00 | 14520 |  | 0 |  | 14520
|  |  |  | 2:00 | 13970 |  | 0 |  | 13970
|  |  |  | 3:00 | 13670 |  | 0 |  | 13670
|  |  |  | 4:00 | 13290 |  | 0 |  | 13290
|  |  |  | 5:00 | 13110 |  | 0 |  | 13110
|  |  |  | 6:00 | 12620 |  | 0 |  | 12620
|  |  |  | 7:00 | 12510 |  | 0 |  | 12510
|  |  |  | 8:00 | 12510 |  | 0 |  | 12510
|  |  |  | 9:00 | 12880 |  | 0 |  | 12880
|  |  |  | 10:00 | 13020 |  | 0 |  | 13020
|  |  |  | 11:00 | 13240 |  | 0 |  | 13240
|  |  |  | 12:00 | 13850 |  | 0 |  | 13850
|  |  |  | 13:00 | 14100 |  | 0 |  | 14100
|  |  |  | 14:00 | 13920 |  | 0 |  | 13920
|  |  |  | 15:00 | 14090 |  | 0 |  | 14090
|  |  |  | 16:00 | 13990 |  | 0 |  | 13990
|  |  |  | 17:00 | 13540 |  | 0 |  | 13540
|  |  |  | 18:00 | 13130 |  | 0 |  | 13130
|  |  |  | 18:30 | 13800 |  | 0 |  | 13800
|  |  |  | 19:00 | 14400 |  | 0 |  | 14400
|  |  |  | 19:30 | 14820 |  | 0 |  | 14820
|  |  |  | 20:00 | 14800 |  | 0 |  | 14800
|  |  |  | 21:00 | 14820 |  | 0 |  | 14820
|  |  |  | 22:00 | 14420 |  | 0 |  | 14420
|  |  |  | 23:00 | 14500 |  | 0 |  | 14500
Probable Maximum Temperature: |  |  | 31.10°C
Probable Maximum Demand at Day Peak: |  |  | 13850.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14820.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14820.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 329.97 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:15 hrs on 03-08-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 02-08-2025 | [28 empty] | Date: | 02-08-2025 | [28 empty] | Date: | 02-08-2025 | [28 empty] | Date: | 02-08-2025 | [28 empty] | Date: | 02-08-2025 | [12 empty] | Date: | 02-08-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [12 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 733.790 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 31 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 547 | 0 | 0 | 332 | 198 | 0 | 0 | 90 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 33 | 0 | 0 | 12 | 25 | 0 | 220 | 0 | 36 | 727 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1170 | 0 | 51 | 0 | 172 | 0 | 347 | 340 | 50 | 208 | 30 | 77 | 30 | 162 | 53 | 20 | 34 | 40 | 0 | 0 | 0 | 0 | 290 | 382 | 0 | 60 | 159 | 6 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 102 | 90 | 154 | 0 | 0 | 12 | 7221 | 431 | 375 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1016 | 0 | 1213.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 202 | 0 | 203 | 0 | 414 | 0 | 0 | 178 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 120 | 220 | 0 | 305 | 1110 | 0 | 6483.86 | 13704.86 | 106.1
01:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 540 | 0 | 0 | 333 | 198 | 0 | 0 | 70 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 33 | 0 | 0 | 12 | 25 | 0 | 221 | 0 | 34 | 727 | 0 | 0 | 0 | 0 | 15 | 124 | 0 | 0 | 0 | 1140 | 0 | 51 | 0 | 172 | 0 | 352 | 340 | 50 | 194 | 30 | 94 | 30 | 147 | 48 | 20 | 30 | 40 | 0 | 0 | 0 | 0 | 290 | 351 | 0 | 60 | 157 | 6 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 93 | 90 | 154 | 0 | 0 | 12 | 7000 | 433 | 379 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 0 | 1198.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 195 | 0 | 196 | 0 | 406 | 0 | 0 | 173 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 120 | 220 | 0 | 306 | 1105 | 0 | 6419.17 | 13419.17 | 106.11
02:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 560 | 0 | 0 | 330 | 196 | 0 | 0 | 70 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 0 | 0 | 12 | 25 | 0 | 221 | 0 | 37 | 728 | 0 | 0 | 0 | 0 | 17 | 32 | 0 | 0 | 0 | 1045 | 0 | 51 | 0 | 178 | 0 | 350 | 340 | 50 | 203 | 30 | 93 | 30 | 141 | 49 | 20 | 30 | 38 | 0 | 0 | 0 | 0 | 290 | 371 | 0 | 60 | 138 | 6 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 93 | 90 | 154 | 0 | 0 | 12 | 6806 | 434 | 388 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 894 | 0 | 1135.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 195 | 0 | 193 | 0 | 368 | 0 | 0 | 172 | 0 | 90 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 120 | 220 | 0 | 306 | 1100 | 0 | 6162.48 | 12968.48 | 106.12
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 11 | 555 | 0 | 0 | 330 | 194 | 0 | 0 | 35 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 33 | 0 | 0 | 12 | 25 | 0 | 221 | 0 | 38 | 728 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 1050 | 0 | 51 | 0 | 180 | 0 | 344 | 340 | 50 | 205 | 30 | 93 | 30 | 141 | 55 | 20 | 31 | 38 | 0 | 0 | 0 | 0 | 290 | 373 | 0 | 60 | 140 | 6 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 93 | 90 | 154 | 0 | 0 | 12 | 6734 | 434 | 388 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 847 | 0 | 1109.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 198 | 0 | 196 | 0 | 382 | 0 | 0 | 172 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 120 | 220 | 0 | 305 | 1100 | 0 | 6013.96 | 12747.96 | 106.13
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 20 | 555 | 0 | 0 | 331 | 195 | 0 | 0 | 35 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 33 | 0 | 0 | 12 | 25 | 0 | 221 | 0 | 37 | 728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 945 | 0 | 51 | 0 | 180 | 0 | 346 | 340 | 49 | 207 | 30 | 94 | 30 | 140 | 56 | 20 | 17 | 38 | 0 | 0 | 0 | 0 | 290 | 389 | 0 | 60 | 139 | 6 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 93 | 35 | 154 | 0 | 0 | 12 | 6557 | 433 | 388 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 806 | 0 | 1018.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 197 | 0 | 196 | 0 | 384 | 0 | 0 | 171 | 0 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 120 | 220 | 0 | 305 | 1100 | 0 | 5840.25 | 12397.25 | 106.14
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 40 | 540 | 0 | 0 | 334 | 196 | 0 | 0 | 35 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 33 | 0 | 0 | 12 | 25 | 0 | 220 | 0 | 37 | 728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 940 | 0 | 51 | 0 | 180 | 0 | 352 | 340 | 49 | 197 | 30 | 93 | 30 | 140 | 56 | 20 | 17 | 36 | 0 | 0 | 0 | 0 | 290 | 374 | 0 | 60 | 135 | 6 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 93 | 35 | 154 | 0 | 0 | 12 | 6526 | 433 | 407 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 786 | 0 | 916.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 195 | 0 | 193 | 0 | 351 | 0 | 0 | 174 | 0 | 50 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 120 | 220 | 0 | 305 | 1100 | 0 | 5698.88 | 12224.88 | 106.15
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 83 | 545 | 0 | 0 | 333 | 136 | 0 | 1 | 35 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 33 | 0 | 0 | 12 | 25 | 0.06 | 219 | 0 | 38 | 734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 930 | 0 | 51 | 0 | 180 | 0 | 353 | 340 | 49 | 196 | 30 | 93 | 50 | 140 | 56 | 20 | 17 | 36 | 0 | 1 | 0 | 0 | 290 | 364 | 0 | 60 | 131 | 6 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 94 | 35 | 154 | 0 | 1.02 | 12 | 6516.08 | 433 | 407 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1.67 | 770 | 0 | 916.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0.67 | 188 | 0 | 190 | 0 | 188 | 0 | 350 | 0 | 0.04 | 172 | 0 | 50 | 0 | 48 | 0 | 0 | 0 | 2 | 0.02 | 0 | 171 | 120 | 220 | 0 | 305 | 852 | 0 | 5423.06 | 11939.14 | 106.16
07:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 108 | 545 | 0 | 0 | 332 | 134 | 0 | 7 | 35 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 33 | 0 | 0 | 12 | 25 | 0 | 219 | 0 | 38 | 728 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 1 | 51 | 0 | 182 | 0 | 349 | 340 | 50 | 195 | 30 | 83 | 50 | 140 | 52 | 20 | 17 | 32 | 0 | 7 | 0 | 0 | 290 | 372 | 0 | 60 | 133 | 6 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 93 | 45 | 154 | 0 | 4.17 | 12 | 6580.17 | 433 | 365 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14.96 | 796 | 0 | 920.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.15 | 14 | 0 | 3.9 | 191 | 0 | 193 | 0 | 192 | 0 | 349 | 0 | 0.28 | 172 | 0 | 35 | 1 | 34 | 0 | 0 | 0.2 | 13 | 0.01 | 0 | 169 | 120 | 220 | 0 | 305 | 850 | 0 | 5439.52 | 12019.69 | 106.17
08:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 150 | 565 | 0 | 0 | 328 | 133 | 0 | 9 | 35 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 33 | 0 | 0 | 12 | 25 | 0.36 | 218 | 0 | 10 | 727 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 865 | 2 | 51 | 0 | 182 | 0 | 315 | 340 | 50 | 207 | 30 | 84 | 50 | 140 | 54 | 20 | 17 | 32 | 0 | 14 | 0 | 0 | 290 | 346 | 0 | 60 | 133 | 6 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 94 | 85 | 152 | 0 | 4.45 | 12 | 6563.81 | 433 | 374 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12.45 | 781 | 0 | 935.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.83 | 22 | 0 | 11.59 | 185 | 0 | 188 | 0 | 187 | 0 | 384 | 0 | 0.86 | 174 | 0 | 35 | 7 | 34 | 0 | 0 | 0.5 | 28 | 0.02 | 0 | 173 | 120 | 220 | 0 | 306 | 840 | 0 | 5506.71 | 12070.52 | 106.18
09:00 | 0 | 22 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 154 | 557 | 0 | 0 | 329 | 133 | 0 | 14 | 70 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 33 | 0 | 0 | 12 | 25 | 1.01 | 218 | 0 | 12 | 731 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 862 | 0 | 51 | 0 | 182 | 0 | 342 | 340 | 49 | 202 | 30 | 86 | 50 | 140 | 55 | 20 | 17 | 52 | 0 | 18 | 0 | 0 | 290 | 385 | 0 | 60 | 153 | 6 | 0 | 80 | 0 | 0 | 18 | 0 | 17 | 94 | 85 | 153 | 1 | 11.45 | 12 | 6781.46 | 433 | 381 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 51 | 825 | 0 | 920.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.31 | 78 | 0 | 27.11 | 177 | 0 | 185 | 0 | 184 | 0 | 367 | 0 | 3.08 | 176 | 0 | 35 | 18 | 34 | 0 | 0 | 1.1 | 28 | 0.02 | 0 | 173 | 120 | 220 | 0 | 305 | 850 | 0 | 5647.55 | 12429.01 | 106.19
10:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 33 | 0 | 0 | 0 | 20 | 0 | 0 | 450 | 168 | 540 | 0 | 0 | 328 | 133 | 0 | 26 | 70 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 33 | 0 | 0 | 12 | 25 | 1.42 | 219 | 0 | 12 | 730 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 182 | 0 | 342 | 340 | 46 | 195 | 33 | 92 | 50 | 140 | 55 | 12 | 17 | 50 | 0 | 24 | 0 | 0 | 290 | 366 | 0 | 60 | 159 | 6 | 0 | 78 | 0 | 0 | 18 | 0 | 17 | 65 | 65 | 152 | 1 | 12.84 | 12 | 6730.26 | 433 | 385 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 64.6 | 770 | 0 | 903.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.61 | 41 | 0 | 23.65 | 166 | 0 | 174 | 0 | 173 | 0 | 350 | 0 | 2.24 | 176 | 0 | 35 | 28 | 34 | 0 | 0 | 0.9 | 46 | 0.04 | 0 | 168 | 120 | 220 | 0 | 305 | 840 | 0 | 5531.73 | 12261.99 | 106.2
11:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 450 | 310 | 554 | 0 | 0 | 326 | 132 | 0 | 6 | 70 | 2 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 32 | 0 | 0 | 12 | 25 | 0.55 | 220 | 0 | 5 | 735 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 86 | 0 | 337 | 340 | 44 | 199 | 33 | 89 | 50 | 140 | 55 | 12 | 17 | 54 | 0 | 13 | 0 | 0 | 290 | 390 | 0 | 60 | 156 | 6 | 0 | 77 | 0 | 0 | 18 | 0 | 17 | 65 | 65 | 151 | 0 | 18.42 | 12 | 6827.97 | 433 | 389 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 23.71 | 808 | 0 | 924.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.86 | 67 | 0 | 29.16 | 177 | 0 | 179 | 0 | 182 | 0 | 414 | 0 | 2.41 | 175 | 0 | 35 | 30 | 34 | 0 | 0 | 2.9 | 133 | 0.02 | 0 | 172 | 120 | 220 | 0 | 303 | 855 | 0 | 5804.14 | 12632.11 | 106.21
12:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 35 | 0 | 0 | 450 | 302 | 414 | 0 | 0 | 322 | 189 | 0 | 9 | 70 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 31 | 0 | 0 | 12 | 25 | 0.28 | 221 | 0 | 12 | 757 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 1 | 51 | 0 | 86 | 0 | 332 | 340 | 43 | 208 | 33 | 75 | 50 | 140 | 54 | 16 | 17 | 54 | 0 | 53 | 0 | 0 | 295 | 385 | 0 | 60 | 156 | 6 | 0 | 76 | 0 | 0 | 18 | 0 | 0 | 65 | 65 | 149 | 0 | 10.12 | 12 | 6900.4 | 433 | 389 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 50 | 920 | 0 | 1028.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.74 | 39 | 0 | 34.02 | 197 | 0 | 178 | 0 | 184 | 0 | 414 | 0 | 3.17 | 176 | 0 | 35 | 28 | 34 | 0 | 0 | 3.7 | 101 | 0.07 | 0 | 173 | 120 | 220 | 0 | 305 | 955 | 0 | 6104.42 | 13004.82 | 106.23
13:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 68 | 0 | 0 | 0 | 35 | 25 | 0 | 450 | 298 | 417 | 0 | 0 | 326 | 193 | 0 | 3 | 70 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 30 | 0 | 0 | 12 | 25 | 0.17 | 221 | 0 | 12 | 756 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 2 | 51 | 0 | 85 | 0 | 334 | 340 | 41 | 205 | 29 | 73 | 70 | 155 | 55 | 17 | 17 | 56 | 0 | 16 | 0 | 0 | 295 | 385 | 0 | 60 | 155 | 6 | 0 | 78 | 0 | 0 | 18 | 0 | 3 | 65 | 65 | 150 | 1 | 11.88 | 12 | 7045.05 | 433 | 385 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 23 | 1085 | 0 | 1023.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.79 | 60 | 0 | 14 | 200 | 0 | 196 | 0 | 199 | 0 | 414 | 0 | 1.11 | 174 | 0 | 35 | 0 | 34 | 0 | 0 | 2.6 | 178 | 0.36 | 0 | 221 | 120 | 220 | 0 | 305 | 1040 | 0 | 6444.29 | 13489.34 | 106.25
14:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 68 | 0 | 0 | 0 | 35 | 34 | 0 | 450 | 302 | 406 | 0 | 0 | 326 | 192 | 0 | 3 | 70 | 27 | 21 | 0 | 0 | 0 | 0 | 17 | 0 | 3 | 28 | 0 | 0 | 12 | 25 | 0.88 | 221 | 0 | 8 | 756 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 1148 | 8 | 51 | 0 | 86 | 0 | 336 | 340 | 42 | 200 | 29 | 73 | 70 | 157 | 54 | 20 | 47 | 60 | 0 | 8 | 0 | 0 | 295 | 384 | 0 | 60 | 156 | 6 | 0 | 79 | 0 | 0 | 18 | 0 | 17 | 65 | 65 | 150 | 1 | 7.18 | 12 | 7179.06 | 433 | 384 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1.63 | 1150 | 0 | 1128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.93 | 14 | 0 | 5.75 | 198 | 0 | 196 | 0 | 195 | 0 | 402 | 0 | 0.46 | 174 | 0 | 35 | 27 | 34 | 0 | 0 | 4.1 | 88 | 0.23 | 0 | 220 | 120 | 220 | 0 | 305 | 1045 | 0 | 6421.1 | 13600.16 | 106.27
15:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 65 | 0 | 0 | 0 | 35 | 32 | 16 | 450 | 295 | 398 | 0 | 0 | 330 | 193 | 0 | 3 | 35 | 27 | 21 | 0 | 0 | 0 | 0 | 78 | 0 | 8 | 28 | 0 | 0 | 12 | 25 | 1.03 | 221 | 0 | 5 | 758 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 8 | 51 | 0 | 86 | 0 | 336 | 340 | 42 | 200 | 29 | 74 | 70 | 159 | 54 | 20 | 46 | 44 | 0 | 5 | 0 | 0 | 295 | 365 | 0 | 60 | 156 | 0 | 0 | 80 | 0 | 0 | 18 | 0 | 17 | 65 | 65 | 152 | 0 | 1.43 | 12 | 7170.46 | 434 | 382 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 15 | 1132 | 0 | 1124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.26 | 6 | 0 | 1.48 | 192 | 0 | 191 | 0 | 193 | 0 | 406 | 0 | 0.17 | 175 | 0 | 35 | 23 | 34 | 0 | 0 | 2.8 | 102 | 0.07 | 0 | 219 | 120 | 220 | 0 | 305 | 1048 | 0 | 6401.78 | 13572.24 | 106.3
16:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 32 | 0 | 0 | 0 | 35 | 31 | 16 | 450 | 300 | 397 | 0 | 0 | 328 | 193 | 0 | 3 | 35 | 28 | 21 | 0 | 0 | 0 | 0 | 74 | 0 | 17 | 33 | 0 | 0 | 36 | 25 | 0.66 | 220 | 0 | 5 | 758 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 1010 | 5 | 51 | 0 | 86 | 0 | 342 | 340 | 42 | 196 | 32 | 72 | 70 | 170 | 53 | 20 | 45 | 42 | 0 | 11 | 0 | 0 | 290 | 366 | 0 | 60 | 153 | 2 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 65 | 65 | 154 | 0 | 1.87 | 12 | 7034.53 | 503 | 376 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 1081 | 0 | 1116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.48 | 12 | 0 | 2.48 | 188 | 0 | 187 | 0 | 191 | 0 | 403 | 0 | 0.22 | 179 | 0 | 35 | 20 | 34 | 0 | 0 | 1.4 | 40 | 0.13 | 0 | 171 | 120 | 220 | 0 | 303 | 1040 | 0 | 6268.71 | 13303.24 | 106.33
17:00 | 0 | 33 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 16 | 0 | 0 | 0 | 35 | 32 | 18 | 450 | 296 | 387 | 0 | 0 | 328 | 193 | 0 | 2 | 17 | 28 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | 17 | 33 | 0 | 0 | 50 | 25 | 0.54 | 220 | 0 | 22 | 756 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 920 | 1 | 51 | 0 | 86 | 0 | 342 | 340 | 42 | 192 | 32 | 72 | 70 | 163 | 55 | 20 | 46 | 38 | 0 | 7 | 0 | 0 | 290 | 361 | 0 | 60 | 152 | 6 | 0 | 83 | 0 | 0 | 18 | 0 | 17 | 65 | 55 | 154 | 0 | 0.25 | 12 | 6822.79 | 561 | 375 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5 | 960 | 0 | 963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.01 | 7 | 0 | 2.26 | 188 | 0 | 186 | 0 | 189 | 0 | 395 | 0 | 0.19 | 178 | 0 | 35 | 7 | 34 | 0 | 0 | 1.1 | 71 | 0.07 | 0 | 166 | 120 | 220 | 0 | 304 | 960 | 0 | 5968.63 | 12791.42 | 106.36
18:00 | 0 | 33 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 16 | 5 | 0 | 0 | 35 | 31 | 0 | 350 | 305 | 405 | 0 | 0 | 328 | 193 | 0 | 0 | 26 | 28 | 21 | 0 | 0 | 0 | 0 | 12 | 40 | 11 | 33 | 0 | 0 | 50 | 30 | 0.13 | 220 | 0 | 13 | 762 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 909 | 0 | 51 | 0 | 86 | 0 | 300 | 340 | 43 | 198 | 32 | 72 | 50 | 160 | 61 | 20 | 49 | 38 | 0 | 1 | 0 | 0 | 290 | 387 | 0 | 60 | 156 | 6 | 0 | 83 | 0 | 0 | 18 | 0 | 17 | 72 | 55 | 142 | 0 | 0.07 | 12 | 6734.2 | 562 | 373 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 950 | 0 | 973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61 | 192 | 0 | 175 | 0 | 172 | 0 | 409 | 0 | 0.05 | 179 | 0 | 56 | 0 | 52 | 0 | 0 | 0.3 | 10 | 0.01 | 0 | 171 | 120 | 180 | 0 | 305 | 951 | 0 | 5871.97 | 12606.17 | 106.39
19:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 35 | 43 | 16 | 30 | 0 | 40 | 118 | 0 | 450 | 300 | 434 | 0 | 20 | 324 | 191 | 0 | 0 | 125 | 28 | 21 | 0 | 0 | 0 | 0 | 12 | 70 | 12 | 66 | 12 | 0 | 50 | 27 | 0 | 219 | 0 | 22 | 732 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 0 | 51 | 25 | 95 | 0 | 338 | 340 | 43 | 210 | 33 | 91 | 50 | 159 | 63 | 20 | 114 | 46 | 30 | 0 | 20 | 0 | 285 | 391 | 0 | 60 | 158 | 6 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 96 | 120 | 146 | 0 | 0 | 12 | 7744 | 592 | 366 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 0 | 1154 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 12 | 0 | 0 | 0 | 12 | 0 | 196 | 0 | 178 | 0 | 177 | 0 | 410 | 0 | 0 | 204 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 120 | 220 | 0 | 305 | 970 | 0 | 6405 | 14149 | 106.42
19:30 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 35 | 68 | 16 | 70 | 21 | 55 | 140 | 0 | 450 | 289 | 378 | 0 | 35 | 333 | 133 | 0 | 0 | 108 | 28 | 21 | 0 | 0 | 0 | 0 | 12 | 70 | 16 | 66 | 31 | 0 | 50 | 30 | 0 | 218 | 0 | 17 | 717 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 1075 | 0 | 51 | 100 | 95 | 0 | 346 | 340 | 45 | 180 | 33 | 93 | 70 | 160 | 63 | 16 | 94 | 46 | 52.2 | 0 | 25 | 0 | 280 | 346 | 0 | 60 | 152 | 7 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 96 | 120 | 147 | 0 | 0 | 12 | 7811.2 | 707 | 368 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1138 | 0 | 1398 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 12 | 0 | 0 | 0 | 14 | 0 | 189 | 0 | 171 | 0 | 169 | 0 | 332 | 0 | 0 | 179 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 120 | 220 | 0 | 305 | 1140 | 0 | 7057 | 14868.2
20:00 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.1 | 35 | 45 | 16 | 45 | 0 | 55 | 144 | 0 | 450 | 294 | 394 | 0 | 35 | 331 | 133 | 0 | 0 | 90 | 28 | 21 | 0 | 0 | 0 | 0 | 0 | 100 | 22 | 66 | 35 | 0 | 50 | 30 | 0 | 218 | 0 | 28 | 750 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 1140 | 0 | 51 | 60 | 95 | 0 | 300 | 340 | 45 | 193 | 33 | 93 | 70 | 161 | 61 | 20 | 99 | 46 | 52.2 | 0 | 37 | 0 | 280 | 329 | 0 | 60 | 139 | 7 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 97 | 120 | 146 | 0 | 0 | 12 | 7801.3 | 832 | 369 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1127 | 0 | 1451 | 0 | 16 | 0 | 0 | 0 | 0 | 95 | 30 | 0 | 0 | 0 | 14 | 0 | 179 | 0 | 169 | 0 | 167 | 0 | 352 | 0 | 0 | 177 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 120 | 220 | 0 | 305 | 1130 | 0 | 7268 | 15069.3 | 106.45
21:00 | 0 | 85 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 35 | 33 | 16 | 45 | 0 | 55 | 154 | 0 | 450 | 298 | 415 | 0 | 17 | 330 | 132 | 0 | 0 | 90 | 28 | 21 | 0 | 0 | 0 | 0 | 0 | 100 | 14 | 65 | 36 | 0 | 50 | 31 | 0 | 219 | 0 | 31 | 765 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 1145 | 0 | 51 | 10 | 86 | 0 | 345 | 340 | 47 | 203 | 33 | 93 | 70 | 161 | 60 | 20 | 106 | 46 | 52.2 | 0 | 37 | 0 | 280 | 333 | 0 | 60 | 142 | 7 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 87 | 120 | 146 | 0 | 0 | 12 | 7833.2 | 886 | 365 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1111 | 11 | 1446 | 0 | 36 | 0 | 0 | 0 | 0 | 42 | 36 | 0 | 0 | 0 | 14 | 0 | 177 | 0 | 177 | 0 | 176 | 0 | 384 | 0 | 0 | 180 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 251 | 120 | 220 | 0 | 305 | 1120 | 0 | 7323 | 15156.2 | 106.48
22:00 | 0 | 85 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.8 | 35 | 33 | 16 | 0 | 0 | 55 | 153 | 0 | 450 | 294 | 400 | 0 | 17 | 333 | 134 | 0 | 0 | 90 | 28 | 21 | 0 | 0 | 0 | 0 | 0 | 100 | 15 | 65 | 36 | 0 | 50 | 32 | 0 | 218 | 0 | 33 | 771 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 1135 | 0 | 51 | 10 | 86 | 0 | 350 | 340 | 48 | 195 | 33 | 93 | 70 | 162 | 63 | 20 | 106 | 48 | 52.2 | 0 | 37 | 0 | 280 | 320 | 0 | 60 | 138 | 7 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 87 | 120 | 143 | 0 | 0 | 12 | 7756 | 886 | 362 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1103 | 11 | 1449 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 174 | 0 | 173 | 0 | 353 | 0 | 0 | 180 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 120 | 220 | 0 | 303 | 1120 | 0 | 7184 | 14940 | 106.51
23:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 35 | 32 | 16 | 0 | 0 | 44 | 150 | 0 | 450 | 298 | 410 | 0 | 0 | 331 | 197 | 0 | 0 | 52 | 26 | 22 | 0 | 0 | 0 | 0 | 0 | 110 | 19 | 33 | 7 | 0 | 50 | 25 | 0 | 218 | 0 | 2 | 765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1145 | 0 | 51 | 0 | 110 | 0 | 353 | 340 | 49 | 199 | 33 | 93 | 50 | 161 | 63 | 12 | 105 | 46 | 52.2 | 0 | 37 | 0 | 285 | 380 | 0 | 60 | 143 | 7 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 87 | 120 | 143 | 0 | 0 | 6 | 7631.2 | 882 | 362 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1103 | 0 | 1449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 180 | 0 | 178 | 0 | 408 | 0 | 0 | 180 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 120 | 220 | 0 | 304 | 1110 | 0 | 7221 | 14852.2 | 106.54
Total KWH | 0 | 793920 | 402240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231912 | 575280 | 880416 | 118560 | 133735 | 11074 | 577815 | 982080 | 53760 | 10176500 | 4670255 | 11287355 | 0 | 83089 | 7928522 | 4360000 | 0 | 88751 | 1426800 | 473400 | 469800 | 0 | 0 | 0 | 0 | 220728 | 650000 | 331680 | 906561 | 139967 | 0 | 570240 | 607680 | 7320 | 5307949 | 0 | 516000 | 17949090.91 | 0 | 0 | 471840 | 0 | 62727 | 336153 | 0 | 0 | 0 | 24692725 | 30375 | 1169773 | 158909 | 3178182 | 0 | 8497500 | 8232000 | 1111680 | 4869000 | 755928 | 2068800 | 1241280 | 3624960 | 1348200 | 420200 | 1077300 | 1056960 | 264427 | 186927 | 178400 | 0 | 6919500 | 9184000 | 0 | 1401120 | 3549109.1 | 147480 | 0 | 1957440 | 0 | 0 | 448000 | 0 | 410040 | 1987200 | 1939200 | 3525120 | 5350 | 90690 | 288720 | 169819695.01 | 13010909 | 9254592 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 343440 | 22960000 | 40220 | 26612727 | 0 | 60612 | 0 | 0 | 0 | 0 | 193456 | 61717 | 0 | 192956 | 419490 | 29739 | 160504 | 4577000 | 0 | 4702091 | 0 | 4723509 | 0 | 9203345 | 0 | 13980 | 4313000 | 0 | 1620380 | 172676 | 1529001 | 0 | 0 | 22584 | 802080 | 3033 | 0 | 4865000 | 2878000 | 5364020 | 0 | 7330176 | 25086545.45 | 0 | 151458782.45 | 321278477.46

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 02-08-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13004.82 | MW | 12:00 Hr. | Energy Generated |  |  | 321.2785 |  | MKWHr.
| Day Peak Demand |  |  | 13004.82 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.044 |  | MKWHr.
| Evening Peak Generation |  |  | 15156.2 | MW | 21:00 Hr. | Energy Demand |  |  | 321.3225 |  | MKWHr.
| Evening Peak Demand |  |  | 15156.2 | MW | 21:00 Hr. | Maximum Temperature |  |  | 34.2 |  | °C
| Minimum Generation of the Day |  |  | 11939.14 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1030.86 |  | MMCFD
| Maximum Generation of the Day |  |  | 15156.2 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 5.9125 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.3658 | 0 | 6.2707 | 0 | 0 | 0.088751 | 0 | 0 | 45.7253 | Gas | 138.1779 | Gas | 507626632.741
| Chattogram Zone |  |  | 1.5022 | 42.6418 | 2.9797 | 0 | 5.3079 | 0.037695 | 0 | 0.33168 | 52.801 | Coal | 107.1965 | Coal | 640643019.1841
| Cumilla Zone |  |  | 29.4755 | 0 | 8.721 | 0 | 0 | 0.18693 | 1.057 | 0 | 39.4404 | HFO | 26.1317 | HFO | 478167631.37
| Mymensingh Zone |  |  | 3.5251 | 0 | 4.6252 | 0 | 0 | 0.09604 | 0 | 0 | 8.2463 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 23.6066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.6066 | Hydro | 5.3079 | Hydro | 530794.9
| Khulna Zone |  |  | 9.2546 | 22.96 | 0.04022 | 0 | 0 | 0.34344 | 13.9229 | 0 | 46.5212 | Solar | 2.5402 | Solar | 38681171.55
| Barishal Zone |  |  | 8.242 | 37.2817 | 0 | 0 | 0 | 0.003033 | 0 | 0 | 45.5268 | Import | 41.5926 | Import | 229060086.82
| Rajshahi Zone |  |  | 23.2059 | 0 | 0.34552 | 0 | 0 | 0.78693 | 26.6127 | 0 | 50.9511 | Wind | 0.33168 | Wind | 4855795.2
| Rangpur Zone |  |  | 0 | 4.313 | 3.1494 | 0 | 0 | 0.99734 | 0 | 0 | 8.4597
| Total |  |  | 138.1779 | 107.1965 | 26.1317 | 0 | 5.3079 | 2.5402 | 41.5926 | 0.33168 | 321.2785
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 507626632.741 |  | Hydro | 530794.9
|  |  |  | Coal | 640643019.1841 |  | Solar | 38681171.55
|  |  |  | HFO | 478167631.37 |  | Import | 229060086.82
|  |  |  | HSD | 0 |  | Wind | 4855795.2
[5 empty] | Total: | 189,95,65,131 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 13.0109 | Peak Hr Flow | 886.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 44053747.71 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.6127 | Peak Hr Flow | 1446.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 726 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.057 | Peak Hr Flow | 46.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 924 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 40.6806 | Peak Hr Flow | 2378.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5176
|  |  |  | Chattogram |  | 0 |  | 1408
|  |  |  | Cumilla |  | 0 |  | 1446
|  |  |  | Mymensingh |  | 0 |  | 1131
|  |  |  | Sylhet |  | 0 |  | 600
|  |  |  | Khulna |  | 0 |  | 1808
|  |  |  | Barishal |  | 0 |  | 482
|  |  |  | Rajshahi |  | 0 |  | 1486
|  |  |  | Rangpur |  | 0 |  | 999
|  |  |  | Total |  | 0 |  | 14536
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[7 empty] | 4 | Sylhet 225 MW CCPP GT |  |  | 142
[7 empty] | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 707
|  |  |  | Total Unavailable Capacity |  |  |  | 1007
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:15 | 11:12 | Siddhirganj 132/33kV S/S T-1 LT Scheduled S/D Due to Replacement of multifunctional meter
| 08:16 | 11:11 | Siddhirganj 132/33kV S/S T-1 HT Scheduled S/D Due to Replacement of multifunctional meter
| 08:20 | 11:27 | Dhamrai 132/33kV S/S Transformer-2 LT Scheduled S/D Due to PBS Work
| 08:21 | 11:27 | Dhamrai 132/33kV S/S Transformer-2 HT Scheduled S/D Due to PBS work
| 08:43 | 15:23 | Ishurdi 132/33kV S/S 132/33 kV T-1 HT Scheduled S/D | [7 empty] | 30.0MW load
interrup.
| 08:43 | 15:23 | Ishurdi 132/33kV S/S 132/33 kV T-1 LT Scheduled S/D | [7 empty] | 25.0MW load
interrup.
| 08:54 |  | Summit Meghnaghat-2 589 MW CCPP GT2 was sync.
| 08:54 |  | Meghnaghat CCPP(Summit) GT-2 Synchronized with remarks:- As per NLDC demand
| 08:54 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- GT2
| 08:55 | 08:55 | Cumilla(N) 230/132/33kV S/S 132KV T-05 LT Scheduled S/D Due to 33kv Underground to Over
head line replaced.
| 08:55 | 01:14 | Cumilla(N) 230/132/33kV S/S 132KV T-03 HT Scheduled S/D
| 08:55 | 01:38 | Cumilla(N) 230/132/33kV S/S 132KV T-03 LT Scheduled S/D Due to 33kv Underground to OHL
Replaced
| 09:42 | 18:45 | Gopalganj 400/132kV S/S 400kV Rooppur Project Work S/D
| 10:20 | 14:18 | Madunaghat 132/33kV S/S ATR-3(725T) LT Project Work S/D Due to SCADA Integration by CNTIC
project
| 10:20 | 14:09 | Madunaghat 132/33kV S/S ATR-3(725T) HT Project Work S/D Due to SCADA Integration by CNTIC
project
| 10:50 | 16:38 | Rajbari 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Oltc oil leakage observation
| 10:51 | 16:37 | Rajbari 132/33kV S/S Transformer-1 HT Scheduled S/D Due to oil leakaOltcge observation
| 11:23 | 13:30 | Siddhirganj 132/33kV S/S T-2 LT Scheduled S/D Due to Replacement of multifunctional
meter.
| 11:25 | 13:23 | Siddhirganj 132/33kV S/S T-2 HT Scheduled S/D Due to Replacement of multifunctional
meter.
|  | 11:40 | Bogura 132/33kV S/S 132KV Bus-B is restored.
|  | 11:55 | Bogura 132/33kV S/S Transformer-1 HT is restored.
|  | 11:56 | Bogura 132/33kV S/S Transformer-1 LT is restored.
| 12:00 |  | Day Peak Generation 13002 MW.
| 13:09 | 14:30 | Bajitpur 132/33kV S/S 132 kV Bus Coupler Scheduled S/D
| 14:08 |  | Bagabari-Shatiya 132 CB open Bagabari S/S end. ( Protection work)
| 14:37 | 16:54 | Madunaghat 132/33kV S/S ATR-1(705T) HT Project Work S/D
| 14:37 | 16:54 | Madunaghat 132/33kV S/S ATR-1(705T) LT Project Work S/D
|  | 15:16 | Madunaghat-TKCL 132kV Ckt-1 is restored.
| 15:28 | 18:36 | Bhandaria 132/33kV S/S Transformer-1 LT Forced S/D Due to Bamna PBS 33 KV feeder Under | [7 empty] | 10.0MW load
|  |  | Ground Cable Maintenance. | [7 empty] | interrup.
| 15:29 | 18:34 | Bhandaria 132/33kV S/S Transformer-1 HT Forced S/D Due to Bamna PBS 33 KV feeder Under | [7 empty] | 10.0MW load
|  |  | Ground Cable Maintenance. | [7 empty] | interrup.
|  | 15:38 | Madunaghat-Sikalbaha 132kV Ckt-2 is restored.
| 16:12 |  | Raojan Unit-2 was synchronized.
|  | 16:17 | New Tongi S/S T2(413T) LT is restored.
| 16:28 | 19:13 | Shahjibazar 132/33kV S/S TR-02 LT Scheduled S/D
| 16:28 |  | Shahjibazar 132/33kV S/S TR-06 LT Scheduled S/D
| 16:30 | 19:08 | Shahjibazar 132/33kV S/S TR-02 HT Scheduled S/D
| 16:35 |  | Shahjibazar 132/33kV S/S TR-06 HT Scheduled S/D
| 16:39 | 16:58 | Bheramara P/S-Ishurdi 132 kV Ckt-2 Tripped from Ishurdi 132/33kV end showing Z1, R Phase,
Distance 2.5 KM relays.
| 18:32 | 18:48 | Dhamrai-Kaliakoir 132 kV Ckt-2 Tripped from Dhamrai 132/33kV end showing Dist. Relay | [7 empty] | 60.0MW load
|  |  | relays Due to Thundering | [7 empty] | interrup. Dhamrai
132/33kV end
| 18:32 | 18:50 | Dhamrai-Kaliakoir 132 kV Ckt-1 Tripped from Dhamrai 132/33kV end showing Dist. Relay | [7 empty] | 60.0MW load
|  |  | relays Due to Thundering | [7 empty] | interrup. Dhamrai
132/33kV end
| 19:05 |  | Bagabari-Shatiya 132 CB syn Bagabari S/S end.
|  | 19:06 | Shahjibazar 132/33kV S/S TR-04 HT is restored.
|  | 19:12 | Shahjibazar 132/33kV S/S TR-04 LT is restored.
| 21:20 | 22:48 | Brahmanbaria 132/33kV S/S 402T HT Forced S/D Due to Hotspot maintenance | [7 empty] | 15.0MW load
interrup.
| 22:02 | 22:52 | Barishal 132/33kV S/S T-1 (405T) LT Scheduled S/D Due to To remove red hot problem of | [7 empty] | 40.0MW load
|  |  | Jhalokathi 33 kV feeder (WZPDCL). | [7 empty] | interrup.
| 22:03 | 22:52 | Barishal 132/33kV S/S T-1 (405T) HT Scheduled S/D Due to To remove red hot problem of | [7 empty] | 40.0MW load
|  |  | Jhalokathi 33kV feeder (WZPDCL). | [7 empty] | interrup.
| 01:32 |  | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T HT Tripped showing 50/51 OC relays Due | [7 empty] | 42.0MW load
|  |  | to Tr_4 trip due to conductor flashing between CT and lower contact of 33 KV CB at 33 KV | [7 empty] | interrup.
NESCO Switching sub-station.
| 01:32 |  | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T LT Tripped showing Over current relays | [7 empty] | 42.0MW load
|  |  | Due to Tr_4 trip due to conductor flashing between CT and lower contact of 33 KV CB | [7 empty] | interrup.
| 04:16 | 05:42 | Shahjibazar 132/33kV S/S TR-02 HT Tripped showing lockout relay, OLTC Bucholz. relays Due
to none
| 04:16 | 05:48 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing lockout relay, OLTC Bucholz. relays Due
to none
| 07:00 |  | Minimum Generation is 12627 MW
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 02-08-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10176500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 298 | 4670255 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 11074 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 132 | 4360000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 7928522 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 49 | 231912 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 16 | 118560 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 577815 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 83089 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 28 | 473400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 469800 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 402240 | Fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 45 | 133735 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 33 | 880416 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 85 | 793920 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 53760 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 154 | 982080 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 88751 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 575280 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 415 | 11287355 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 733.79 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 90 | 1426800 | Engine Problem
Dhaka Area Total |  |  |  |  | 6673.514 | 2278 | 45725264
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 100 | 650000 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 30375 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 471840 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 219 | 5307949 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 336153 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 62727 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 36 | 139967 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 906561 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 570240 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 31 | 516000 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 220728 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 7320 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 31 | 607680 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1145 | 24692725 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 14 | 331680 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 765 | 17949090.91 | -
Chattogram Area Total |  |  |  |  | 4895.72 | 2489 | 52801035.91
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 203 | 4869000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 345 | 8497500 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 340 | 8232000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 33 | 755928 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 47 | 1111680 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 86 | 3178182 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1169773 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 10 | 158909 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 37 | 178400 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1241280 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 161 | 3624960 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 46 | 1056960 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 264427 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 420200 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 106 | 1077300 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 60 | 1348200 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 93 | 2068800 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 186927 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1760.2 | 39440426
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 146 | 3525120 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 5350 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 120 | 1939200 | Engine Problem
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 87 | 1987200 | Engine Problem
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 90690 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 288720 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 410040 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 382 | 8246320
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1401120 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 142 | 3549109.1 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1957440 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 448000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 7 | 147480 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 333 | 9184000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 280 | 6919500 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 924 | 23606649.1
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 886 | 13010909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 365 | 9254592 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 11 | 40220 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 343440 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1111 | 22960000 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2411 | 46521161
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 305 | 7330176 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2878000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1120 | 25086545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5364020 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 251 | 4865000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3033 | -
Barishal Area Total |  |  |  |  | 2236 | 2016 | 45526774.45
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 192956 | -
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 36 | 60612 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 61717 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 177 | 4577000 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 177 | 4702091 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 176 | 4723509 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 384 | 9203345 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 14 | 29739 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 42 | 193456 | Engine Problem
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 13980 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1446 | 26612727 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 160504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 419490 | -
Rajshahi Area Total |  |  |  |  | 3516.96 | 2488 | 50951126
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 180 | 4313000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1529001 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 22584 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1620380 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 172676 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 802080 | -
Rangpur Area Total |  |  |  |  | 950 | 408 | 8459721
Eastern Grid Total |  |  |  |  | 17401.505 | 7833.2 | 169819695.01
Western Grid Total |  |  |  |  | 10442.16 | 7323 | 151458782.45
National Grid Total |  |  |  |  | 27843.665 | 15156.2 | 321278477.46
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 02-08-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9761.71 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4774.6 | MW
i) Dhaka area |  |  | 5176.45 |  | MW | i) Khulna area |  |  |  | 1807.9 | MW
ii) Chattogram area |  |  | 1408 |  | MW | ii) Barishal area |  |  |  | 481.5 | MW
iii) Cumilla area |  |  | 1446.26 |  | MW | iii) Rajshahi area |  |  |  | 1486.2 | MW
iv) Mymensingh area |  |  | 1131 |  | MW | iv) Rangpur area |  |  |  | 999 | MW
v) Sylhet area |  |  | 600 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14536.31 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 8 | 18:00 | 67 | Hathazari | 96 | 05:00 | 133 | PHP | 8 | 09:00
2 | AKSML | 116.3 | 06:00 | 68 | Ishurdi | 71 | 19:00 | 134 | Pabna | 117 | 21:00
3 | Aftabnagar | 52 | 13:00 | 69 | Jaldhaka | 90 | 22:00 | 135 | Palashbari | 98 | 00:00
4 | Agargaon | 125 | 13:00 | 70 | Jamalpur | 134 | 22:00 | 136 | Panchagarh | 63 | 01:00
5 | Agrabad | 86 | 19:00 | 71 | Jashore | 146 | 19:30 | 137 | Patuakhali | 71.2 | 23:00
6 | Amnura | 28 | 00:00 | 72 | Jhenaidah | 128 | 19:30 | 138 | Payra | 34 | 22:00
7 | Ashuganj | 96 | 23:00 | 73 | Joydebpur | 149 | 18:30 | 139 | Postogola | 55 | 19:00
8 | BSRM | 202 | 06:00 | 74 | Joypurhat | 64 | 20:00 | 140 | Purbachal | 22 | 22:00
9 | Bagerhat | 86 | 01:00 | 75 | Juldah | 14.5 | 00:00 | 141 | Purbasadipur | 129 | 20:00
10 | Bajitpur | 80 | 21:00 | 76 | KSRM | 24 | 09:00 | 142 | Rahanpur | 42 | 22:00
11 | Bakulia | 90 | 19:30 | 77 | Kabirpur | 231 | 15:00 | 143 | Rahim | 29 | 12:00
12 | Banani | 76 | 14:00 | 78 | Kachua | 94 | 22:00 | 144 | Rajbari | 82 | 23:00
13 | Bangabhaban | 7 | 10:00 | 79 | Kallyanpur | 105 | 22:00 | 145 | Rajendrapur | 128 | 12:00
14 | Barapukuria | 69 | 21:00 | 80 | Kalurghat | 36 | 09:00 | 146 | Rajshahi | 108 | 19:30
15 | Barguna | 24 | 22:00 | 81 | Kamrangirchar | 76 | 19:00 | 147 | Rajshahi-230 | 91 | 13:00
16 | Barishal | 114 | 12:00 | 82 | Kaptai | N/A | N/A | 148 | Ramganj | 118 | 22:00
17 | Barishal-230 | 118 | 23:00 | 83 | Kasba | 36 | 21:00 | 149 | Rampur | 37 | 13:00
18 | Baroaulia | 57 | 13:00 | 84 | Kazla | 98 | 12:00 | 150 | Rangamati | 17 | 19:30
19 | Baroirhat | 69 | 19:30 | 85 | Keranigonj | 98 | 19:00 | 151 | Rangpur | 153 | 21:00
20 | Bashundhara | 192 | 14:00 | 86 | Khagrachori | 30 | 20:00 | 152 | Ruppur | 4.6 | 10:00
21 | BashundharaCement | 15 | 19:30 | 87 | Khulna | 72 | 19:00 | 153 | SSM | 0 | 00:00
22 | Beanibazar | 75 | 01:00 | 88 | Khulshi | 182 | 12:00 | 154 | Saidpur | 115 | 19:30
23 | Benapole | 70 | 21:00 | 89 | Kishoreganj | 124 | 21:00 | 155 | Satkhira | 131 | 21:00
24 | Bhaluka | 143 | 10:00 | 90 | Kodda | 285 | 16:00 | 156 | Satmasjid | 99 | 14:00
25 | Bhandaria | 63 | 00:00 | 91 | Kulaura | 51 | 19:00 | 157 | Savar | 230 | 16:00
26 | Bhangura | 35 | 20:00 | 92 | Kurigram | 68 | 21:00 | 158 | SevenRings | 5.97 | 16:00
27 | Bheramara(GK) | 65 | 19:30 | 93 | Kushtia | 151 | 19:30 | 159 | ShahCement | 7 | 00:00
28 | Bhulta | 245 | 23:00 | 94 | Laksam | 33 | 16:00 | 160 | Shahjadpur | 80 | 19:30
29 | Bog-Sherpur | 64 | 19:00 | 95 | Lakshmipur | 21 | 22:00 | 161 | Shahjibazar | 125 | 22:00
30 | Bogura | 174 | 21:00 | 96 | Lalbag | 54 | 13:00 | 162 | Shahmirpur | 62 | 10:00
31 | Borhanuddin | 93 | 00:00 | 97 | Lalmonirhat | 68 | 22:00 | 163 | Shariatpur | 94 | 23:00
32 | Brahmanbaria | 131 | 23:00 | 98 | MI_Cement | 14.8 | 20:00 | 164 | Sherpur | 148 | 00:00
33 | Cantonment | 142 | 13:00 | 99 | Madanganj | 40 | 12:00 | 165 | Shikalbaha | 15 | 00:00
34 | Chandina | 36.82 | 22:00 | 100 | Madaripur | 119 | 23:00 | 166 | Shitalakhya | 82.8 | 16:00
35 | Chandpur | 82 | 22:00 | 101 | Madartek | 94 | 23:00 | 167 | Sholosohor | 40 | 16:00
36 | Chandraghona | 33 | 19:00 | 102 | Madunaghat | 51 | 19:00 | 168 | Shyampur | 162 | 12:00
37 | Chapai | 66 | 21:00 | 103 | Magura | 66 | 20:00 | 169 | Siddhirganj | 118 | 15:00
38 | Charsaidpur | 30 | 04:00 | 104 | Mahasthangarh | 90 | 00:00 | 170 | Sirajganj | 106 | 21:00
39 | Chauddagram | 71 | 22:00 | 105 | Maijdee | 15 | 22:00 | 171 | Sonargaon | 126 | 15:00
40 | Chhatak | 39 | 00:00 | 106 | Manikganj | 119 | 21:00 | 172 | Sreemongol | 93 | 19:00
41 | Chowmuhani | 200 | 19:30 | 107 | Maniknagar | 74 | 13:00 | 173 | Sreepur | 99 | 12:00
42 | Chuadanga | 112 | 21:00 | 108 | Matarbari | 48 | 00:00 | 174 | Srinagar | 49.35 | 22:00
43 | Coxsbazar | 131 | 00:00 | 109 | Matuail | 64 | 15:00 | 175 | Sunamganj | 56 | 00:00
44 | Cumilla(N) | 130 | 00:00 | 110 | Millgate | 139 | 15:00 | 176 | Sylhet | 49 | 00:00
45 | Cumilla(S) | 154 | 14:00 | 111 | Mirpur | 126.5 | 19:00 | 177 | Sylhet-132 | 119 | 13:00
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 12 | 10:00 | 178 | TK | 34 | 18:00
47 | Daudkandi | 160 | 21:00 | 113 | Mirzapur | 43 | 21:00 | 179 | Tangail | 168 | 22:00
48 | Dhaka | 64 | 13:00 | 114 | Mithapukur | 70 | 19:30 | 180 | Taraganj | 25 | 19:00
49 | Dhamrai | 106 | 22:00 | 115 | Modern | N/A | N/A | 181 | Thakurgaon | 112 | 00:00
50 | Dhanmondi | 140 | 13:00 | 116 | Mogbazar | 148.8 | 15:00 | 182 | Tongi | 105 | 09:00
51 | Dohazari | 104 | 20:00 | 117 | Mongla | 31 | 00:00 | 183 | Ullahpara | 37 | 19:30
52 | Faridpur | 169 | 21:00 | 118 | Motijheel | 43 | 13:00 | 184 | Ullon | 42 | 23:00
53 | Fatullah | 99 | 15:00 | 119 | Muktagacha | 36 | 00:00 | 185 | Uttara | 83 | 13:00
54 | Fenchuganj | 41 | 00:00 | 120 | Munshiganj | 111 | 23:00 | 186 | UttaraNew | 61 | 15:00
55 | Feni | 108 | 14:00 | 121 | Muradnagar | 43 | 21:00 | 187 | Zigatola | 74 | 14:00
56 | GPH | 74 | 20:00 | 122 | Mymensingh | 190 | 00:00
57 | Ghatail | 80 | 00:00 | 123 | Naogaon | 130 | 19:30
58 | Ghorashal | 12 | 12:00 | 124 | Narail | 62 | 20:00
59 | Ghorashal-230 | 82 | 21:00 | 125 | Narinda | 80 | 13:00
60 | Goalpara | 33 | 13:00 | 126 | Narshingdi | 185 | 19:30
61 | Gollamari | 88 | 19:30 | 127 | Natore | 142 | 22:00
62 | Gopalganj | 113 | 22:00 | 128 | Nawabganj | 61.2 | 22:00
63 | Gulshan | 64 | 13:00 | 129 | Netrakona | 139 | 00:00
64 | Halishahar | 66 | 10:00 | 130 | New | 62.9 | 15:00
65 | HaripurSBU | 152 | 16:00 | 131 | Niamatpur | 73 | 00:00
66 | Hasnabad | 72 | 13:00 | 132 | Noapara | 45 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 02-08-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13704.86 | 0 |  | 13704.86
1:00 | 13419.17 | 0 |  | 13419.17
2:00 | 12968.48 | 0 |  | 12968.48
3:00 | 12747.96 | 0 |  | 12747.96
4:00 | 12397.25 | 0 |  | 12397.25
5:00 | 12224.88 | 0 |  | 12224.88
6:00 | 11939.14 | 0 |  | 11939.14
7:00 | 12019.69 | 0 |  | 12019.69
8:00 | 12070.52 | 0 |  | 12070.52
9:00 | 12429.01 | 0 |  | 12429.01
10:00 | 12261.99 | 0 |  | 12261.99
11:00 | 12632.11 | 0 |  | 12632.11
12:00 | 13004.82 | 0 |  | 13004.82
13:00 | 13489.34 | 0 |  | 13489.34
14:00 | 13600.16 | 0 |  | 13600.16
15:00 | 13572.24 | 0 |  | 13572.24
16:00 | 13303.24 | 0 |  | 13303.24
17:00 | 12791.42 | 0 |  | 12791.42
18:00 | 12606.17 | 0 |  | 12606.17
19:00 | 14149 | 0 |  | 14149
19:30 | 14868.2 | 40 |  | 14910.2
20:00 | 15069.3 | 44 |  | 15115.3
21:00 | 15156.2 | 0 |  | 15156.2
22:00 | 14940 | 0 |  | 14940
23:00 | 14852.2 | 0 |  | 14852.2
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 02-08-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7221 | 6483.86 | 13704.86 | DAILY GENERATION CURVE
00:30 | 7110.5 | 6451.515 | 13562.015
01:00 | 7000 | 6419.17 | 13419.17 | 02-08-2025
01:30 | 6903 | 6290.825 | 13193.825
02:00 | 6806 | 6162.48 | 12968.48
02:30 | 6770 | 6088.22 | 12858.22
03:00 | 6734 | 6013.96 | 12747.96
03:30 | 6645.5 | 5927.105 | 12572.605
04:00 | 6557 | 5840.25 | 12397.25
04:30 | 6541.5 | 5769.565 | 12311.065
05:00 | 6526 | 5698.88 | 12224.88
05:30 | 6521.04 | 5560.97 | 12082.01
06:00 | 6516.08 | 5423.06 | 11939.14
06:30 | 6548.125 | 5431.29 | 11979.415
07:00 | 6580.17 | 5439.52 | 12019.69
07:30 | 6571.99 | 5473.115 | 12045.105
08:00 | 6563.81 | 5506.71 | 12070.52
08:30 | 6672.635 | 5577.13 | 12249.765
09:00 | 6781.46 | 5647.55 | 12429.01
09:30 | 6755.86 | 5589.64 | 12345.5
10:00 | 6730.26 | 5531.73 | 12261.99
10:30 | 6779.115 | 5667.935 | 12447.05
11:00 | 6827.97 | 5804.14 | 12632.11
11:30 | 6864.185 | 5954.28 | 12818.465
12:00 | 6900.4 | 6104.42 | 13004.82
12:30 | 6972.725 | 6274.355 | 13247.08
13:00 | 7045.05 | 6444.29 | 13489.34
13:30 | 7112.055 | 6432.695 | 13544.75
14:00 | 7179.06 | 6421.1 | 13600.16
14:30 | 7174.76 | 6411.44 | 13586.2
15:00 | 7170.46 | 6401.78 | 13572.24
15:30 | 7102.495 | 6335.245 | 13437.74
16:00 | 7034.53 | 6268.71 | 13303.24
16:30 | 6928.66 | 6118.67 | 13047.33
17:00 | 6822.79 | 5968.63 | 12791.42
17:30 | 6778.495 | 5920.3 | 12698.795
18:00 | 6734.2 | 5871.97 | 12606.17
18:30 | 7239.1 | 6138.485 | 13377.585
19:00 | 7744 | 6405 | 14149
19:30 | 7811.2 | 7057 | 14868.2
20:00 | 7801.3 | 7268 | 15069.3
20:30 | 7817.25 | 7295.5 | 15112.75 |  | Executive Engineer
21:00 | 7833.2 | 7323 | 15156.2 |  | Network Operation Division
21:30 | 7794.6 | 7253.5 | 15048.1
22:00 | 7756 | 7184 | 14940
22:30 | 7693.6 | 7202.5 | 14896.1
23:00 | 7631.2 | 7221 | 14852.2

## En-Curve
QF-LDC-12
Date | 02-08-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4120 | 1835 | 431 | 38 | 40 | 1213.86 | 220 | 4738 | 0 | 188 | 844 | 0 | 0 | 37 | 0 | DAILY ENERGY CURVE
00:30 | 4041 | 1829.5 | 432 | 38 | 40 | 1206.015 | 220.5 | 4709.5 | 0 | 170 | 843.5 | 0 | 0 | 32 | 0 | 02-08-2025
01:00 | 3962 | 1824 | 433 | 38 | 40 | 1198.17 | 221 | 4681 | 0 | 152 | 843 | 0 | 0 | 27 | 0
01:30 | 3909.5 | 1829 | 433.5 | 38 | 39 | 1166.825 | 221 | 4578 | 0 | 136 | 817 | 0 | 0 | 26 | 0 | Energy Generated | 321.2785 |  | MKWHr
02:00 | 3857 | 1834 | 434 | 38 | 38 | 1135.48 | 221 | 4475 | 0 | 120 | 791 | 0 | 0 | 25 | 0 | Energy not Served | 0.044 |  | MKWHr
02:30 | 3851.5 | 1839.5 | 434 | 38 | 38 | 1122.72 | 221 | 4423.5 | 0 | 94 | 774.5 | 0 | 0 | 21.5 | 0 | Total Energy Requirement | 321.3225 |  | MKWHr
03:00 | 3846 | 1845 | 434 | 38 | 38 | 1109.96 | 221 | 4372 | 0 | 68 | 758 | 0 | 0 | 18 | 0
03:30 | 3856.5 | 1847.5 | 433.5 | 38 | 38 | 1064.105 | 221 | 4300 | 0 | 68 | 690 | 0 | 0 | 16 | 0
04:00 | 3867 | 1850 | 433 | 38 | 38 | 1018.25 | 221 | 4228 | 0 | 68 | 622 | 0 | 0 | 14 | 0
04:30 | 3849.5 | 1850.5 | 433 | 38 | 37 | 967.565 | 220.5 | 4216 | 0 | 68 | 618 | 0 | 0 | 13 | 0
05:00 | 3832 | 1851 | 433 | 38 | 36 | 916.88 | 220 | 4204 | 0 | 68 | 614 | 0 | 0 | 12 | 0
05:30 | 3799.5 | 1873.5 | 433 | 38 | 36 | 916.695 | 219.5 | 4069 | 3.815 | 68 | 614.5 | 0 | 0 | 10.5 | 0
06:00 | 3767 | 1896 | 433 | 38 | 36 | 916.51 | 219 | 3934 | 7.63 | 68 | 615 | 0 | 0 | 9 | 0
06:30 | 3750.5 | 1911 | 433 | 38 | 34 | 918.265 | 219 | 3952 | 42.15 | 72 | 603 | 0 | 0 | 6.5 | 0
07:00 | 3734 | 1926 | 433 | 38 | 32 | 920.02 | 219 | 3970 | 76.67 | 76 | 591 | 0 | 0 | 4 | 0
07:30 | 3720.5 | 1944 | 433 | 38 | 32 | 927.74 | 218.5 | 3918 | 102.865 | 76 | 631 | 0 | 0 | 3.5 | 0
08:00 | 3707 | 1962 | 433 | 38 | 32 | 935.46 | 218 | 3866 | 129.06 | 76 | 671 | 0 | 0 | 3 | 0
08:30 | 3726.5 | 1971 | 433 | 38 | 42 | 928.195 | 218 | 3894 | 199.07 | 113 | 681 | 0 | 0 | 6 | 0
09:00 | 3746 | 1980 | 433 | 38 | 52 | 920.93 | 218 | 3922 | 269.08 | 150 | 691 | 0 | 0 | 9 | 0
09:30 | 3710.5 | 1959 | 433 | 38 | 51 | 912.31 | 218.5 | 3880.5 | 287.69 | 156 | 687 | 0 | 0 | 12 | 0
10:00 | 3675 | 1938 | 433 | 38 | 50 | 903.69 | 219 | 3839 | 306.3 | 162 | 683 | 0 | 0 | 15 | 0
10:30 | 3731 | 1962.5 | 433 | 38 | 52 | 913.885 | 219.5 | 3893.5 | 345.165 | 161.5 | 689 | 0 | 0 | 8 | 0
11:00 | 3787 | 1987 | 433 | 38 | 54 | 924.08 | 220 | 3948 | 384.03 | 161 | 695 | 0 | 0 | 1 | 0
11:30 | 3825 | 1919.5 | 433 | 38 | 54 | 976.4 | 220.5 | 4119 | 381.065 | 160.5 | 687.5 | 0 | 0 | 4 | 0
12:00 | 3863 | 1852 | 433 | 38 | 54 | 1028.72 | 221 | 4290 | 378.1 | 160 | 680 | 0 | 0 | 7 | 0
12:30 | 3891 | 1848 | 433 | 38 | 55 | 1026.075 | 221 | 4488 | 367.005 | 159.5 | 711.5 | 0 | 0 | 9 | 0
13:00 | 3919 | 1844 | 433 | 38 | 56 | 1023.43 | 221 | 4686 | 355.91 | 159 | 743 | 0 | 0 | 11 | 0
13:30 | 3907 | 1859 | 433 | 38 | 58 | 1075.715 | 221 | 4742 | 264.035 | 158 | 782 | 0 | 0 | 7 | 0
14:00 | 3895 | 1874 | 433 | 38 | 60 | 1128 | 221 | 4798 | 172.16 | 157 | 821 | 0 | 0 | 3 | 0
14:30 | 3883.5 | 1862.5 | 433.5 | 38 | 52 | 1126 | 221 | 4792.5 | 172.2 | 139.5 | 860 | 0 | 0 | 5.5 | 0
15:00 | 3872 | 1851 | 434 | 38 | 44 | 1124 | 221 | 4787 | 172.24 | 122 | 899 | 0 | 0 | 8 | 0
15:30 | 3863 | 1854 | 468.5 | 38 | 43 | 1120 | 220.5 | 4664.5 | 138.74 | 124.5 | 890.5 | 0 | 0 | 12.5 | 0
16:00 | 3854 | 1857 | 503 | 38 | 42 | 1116 | 220 | 4542 | 105.24 | 127 | 882 | 0 | 0 | 17 | 0
16:30 | 3853.5 | 1850 | 532 | 38 | 40 | 1039.5 | 220 | 4393 | 106.33 | 117.5 | 840.5 | 0 | 0 | 17 | 0
17:00 | 3853 | 1843 | 561 | 38 | 38 | 963 | 220 | 4244 | 107.42 | 108 | 799 | 0 | 0 | 17 | 0
17:30 | 3836 | 1795 | 561.5 | 38 | 38 | 968 | 220 | 4235.5 | 61.295 | 115 | 816.5 | 0 | 0 | 14 | 0
18:00 | 3819 | 1747 | 562 | 38 | 38 | 973 | 220 | 4227 | 15.17 | 122 | 834 | 0 | 0 | 11 | 0
18:30 | 3861 | 1839.5 | 577 | 38 | 42 | 1063.5 | 219.5 | 4356.5 | 7.585 | 257.5 | 1104 | 0 | 0 | 11.5 | 0
19:00 | 3903 | 1932 | 592 | 38 | 46 | 1154 | 219 | 4486 | 0 | 393 | 1374 | 0 | 0 | 12 | 0
19:30 | 3705 | 1853 | 707 | 38 | 46 | 1398 | 218 | 4788 | 0 | 478 | 1621.2 | 0 | 0 | 16 | 40
20:00 | 3689 | 1876 | 832 | 38 | 46 | 1451 | 218 | 4878 | 0 | 510 | 1509.3 | 0 | 0 | 22 | 44
20:30 | 3739 | 1888 | 859 | 38 | 46 | 1448.5 | 218.5 | 4877.5 | 0 | 496 | 1484.25 | 0 | 0 | 18 | 22
21:00 | 3789 | 1900 | 886 | 38 | 46 | 1446 | 219 | 4877 | 0 | 482 | 1459.2 | 0 | 0 | 14 | 0
21:30 | 3760 | 1890 | 886 | 38 | 47 | 1447.5 | 218.5 | 4869 | 0 | 439 | 1438.6 | 0 | 0 | 14.5 | 0
22:00 | 3731 | 1880 | 886 | 38 | 48 | 1449 | 218 | 4861 | 0 | 396 | 1418 | 0 | 0 | 15 | 0
22:30 | 3829.5 | 1882 | 884 | 38 | 47 | 1449 | 218 | 4873 | 0 | 300 | 1358.6 | 0 | 0 | 17 | 0
23:00 | 3928 | 1884 | 882 | 38 | 46 | 1449 | 218 | 4885 | 0 | 204 | 1299.2 | 0 | 0 | 19 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 02-08-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 385 | 07:00 | 370 | 13:00 | Payra | 416 | 07:00 | 410 | 12:00
Ashuganj | 406 | 6:00 | 380 | 12:00 | Rahanpur | 403 | 10:00 | 382 | 23:00
Bhulta | 402 | 06:00 | 373 | 12:00 | Rampal | 406 | 06:00 | 393 | 13:00
Bibiana | 386 | 05:00 | 377 | 13:00
BIPTC | 409 | 05:00 | 392 | 23:00
Bogura | 385 | 10:00 | 360 | 23:00
Gopalganj | 401 | 06:00 | 386 | 13:00
Kaliakoir | 377 | 06:00 | 361 | 12:00
Madunaghat | 393 | 08:00 | 384 | 13:00
Meghnaghat | 390 | 06:00 | 374 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 226 | 06:00 | 214 | 15:00 | Keranigonj | 224 | 06:00 | 212 | 13:00
AKSML | 231 | 06:00 | 222 | 00:00 | Khulna(S) | 230 | 06:00 | 219 | 23:00
Aminbazar | 225 | 07:00 | 216 | 12:00 | Madunaghat | 232 | 07:00 | 225 | 12:00
Ashuganj | 235 | 06:00 | 222 | 12:00 | Madunaghat-400 | 233 | 10:00 | 226 | 13:00
Ashuganj-400 | 235 | 06:00 | 222 | 12:00 | Maniknagar | 220 | 05:00 | 210 | 13:00
Baghabari | 235 | 05:00 | 225 | 23:00 | Meghnaghat | 228 | 06:00 | 219 | 13:00
Barapukuria | 225 | 18:30 | 214 | 23:00 | Meghnaghat-400 | 224 | 06:00 | 215 | 12:00
Barapukuria-230 | 225 | 18:30 | 214 | 23:00 | Mirsorai | 227 | 08:00 | 218 | 00:00
Barishal | 230 | 08:00 | 221 | 19:00 | Rajshahi | 230 | 06:00 | 218 | 23:00
Bheramara | 231 | 06:00 | 222 | 19:00 | Rampal | 231 | 08:00 | 220 | 14:00
Bhulta | 231 | 06:00 | 210 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 229 | 07:00 | 220 | 00:00 | Rampura | 230 | 06:00 | 211 | 12:00
BIPTC | 234 | 10:00 | 221 | 19:00 | Shikalbaha | 230 | 08:00 | 221 | 23:00
Bogura | 239 | 10:00 | 223 | 21:00 | Shyampur | 223 | 06:00 | 212 | 13:00
Bogura-400 | 238 | 10:00 | 224 | 21:00 | Siddhirganj | 222 | 07:00 | 214 | 13:00
Borhanuddin | 234 | 10:00 | 229 | 00:00 | Sirajgonj | 241 | 10:00 | 234 | 21:00
BSRM | 226 | 05:00 | 218 | 00:00 | Sreepur | 230 | 07:00 | 221 | 12:00
Cumilla(N) | 224 | 09:00 | 215 | 00:00 | Tongi | 228 | 07:00 | 214 | 12:00
Faridpur | 228 | 09:00 | 216 | 23:00
Fenchuganj | 230 | 22:00 | 220 | 23:00
Ghorashal | 235 | 04:00 | 225 | 00:00
Ghorashal-230 | 230 | 06:00 | 216 | 12:00
Gopalganj | 228 | 06:00 | 218 | 23:00
GPH | 229 | 08:00 | 221 | 00:00
Haripur | 221 | 06:00 | 212 | 13:00
Hasnabad | 223 | 06:00 | 213 | 12:00
Hathazari | 227 | 05:00 | 220 | 00:00
Ishurdi | 234 | 06:00 | 225 | 19:00
Jhenaidah | 229 | 09:00 | 216 | 19:00
Kaliakoir | 232 | 05:00 | 220 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 06:00 | 127 | 13:00 | Lalmonirhat | 131 | 18:30 | 122 | 19:30
Agargaon | 133 | 06:00 | 124 | 13:00 | Madanganj | 129 | 04:00 | 123 | 12:00
Agrabad | 131 | 07:00 | 125 | 23:00 | Madaripur | 135 | 05:00 | 129 | 23:00
AKS | 129 | 07:00 | 125 | 00:00 | Madartek | 137 | 06:00 | 127 | 11:00
Aminbazar | 132 | 06:00 | 126 | 12:00 | Madunaghat | 131 | 07:00 | 128 | 00:00
Amnura | 136 | 08:00 | 125 | 22:00 | Magura | 132 | 09:00 | 122 | 13:00
Ashuganj | 142 | 06:00 | 135 | 21:00 | Mahasthangarh | 137 | 10:00 | 125 | 23:00
Bagerhat | 132 | 09:00 | 119 | 19:00 | Maijdee | 118 | 09:00 | 108 | 00:00
Bajitpur | 131 | 05:00 | 125 | 21:00 | Manikganj | 129 | 03:00 | 120 | 12:00
Bakulia | 133 | 08:00 | 127 | 23:00 | Maniknagar | 133 | 05:00 | 125 | 13:00
Banani | 137 | 05:00 | 125 | 12:00 | Matarbari | 123 | 09:00 | 110 | 01:00
Bangabhaban | 133 | 06:00 | 125 | 13:00 | Matuail | 129 | 04:00 | 122 | 13:00
Barapukuria | 136 | 05:00 | 127 | 19:30 | Millgate | 134 | 04:00 | 122 | 13:00
Barguna | 135 | 09:00 | 130 | 00:00 | Mirpur | 133 | 05:00 | 124 | 12:00
Barishal | 134 | 08:00 | 127 | 19:00 | Mirzapur | 130 | 10:00 | 124 | 12:00
Barishal-230 | 134 | 08:00 | 127 | 21:00 | Mithapukur | 129 | 10:00 | 113 | 21:00
Baroaulia | 130 | 00:00 | 127 | 23:00 | MI_Cement | 130 | 06:00 | 122 | 13:00
Baroirhat | 123 | 08:00 | 115 | 00:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 138 | 05:00 | 123 | 15:00 | Mogbazar | 140 | 05:00 | 127 | 13:00
BashundharaCement | 129 | 04:00 | 123 | 12:00 | Mongla | 133 | 09:00 | 121 | 23:00
Beanibazar | 126 | 09:00 | 118 | 00:00 | Motijheel | 133 | 06:00 | 125 | 13:00
Benapole | 133 | 09:00 | 119 | 23:00 | Muktagacha | 135 | 15:00 | 129 | 00:00
Bhaluka | 131 | 07:00 | 126 | 12:00 | Munshiganj | 129 | 05:00 | 122 | 12:00
Bhandaria | 132 | 09:00 | 117 | 00:00 | Muradnagar | 124 | 08:00 | 118 | 15:00
Bhangura | 134 | 06:00 | 128 | 20:00 | Mymensingh | 138 | 15:00 | 119 | 00:00
Bheramara | 137 | 10:00 | 132 | 19:30 | Naogaon | 136 | 10:00 | 121 | 23:00
Bheramara(GK) | 136 | 06:00 | 131 | 23:00 | Narail | 132 | 09:00 | 120 | 19:00
Bhulta | 124 | 04:00 | 118 | 00:00 | Narinda | 133 | 05:00 | 125 | 13:00
Bog-Sherpur | 138 | 10:00 | 127 | 23:00 | Narshingdi | 136 | 06:00 | 119 | 22:00
Bogura | 140 | 09:00 | 130 | 21:00 | Natore | 135 | 09:00 | 127 | 19:30
Bogura-230 | 140 | 09:00 | 129 | 23:00 | Nawabganj | 135 | 06:00 | 125 | 13:00
Brahmanbaria | 137 | 07:00 | 127 | 23:00 | Netrakona | 128 | 16:00 | 117 | 00:00
Cantonment | 133 | 06:00 | 124 | 12:00 | New | 133 | 03:00 | 123 | 12:00
Chandina | 127 | 08:00 | 121 | 00:00 | Niamatpur | 137 | 06:00 | 128 | 21:00
Chandpur | 127 | 09:00 | 119 | 00:00 | Noapara | 134 | 09:00 | 124 | 19:00
Chandraghona | 132 | 05:00 | 128 | 00:00 | Pabna | 134 | 06:00 | 128 | 21:00
Chapai | 136 | 05:00 | 125 | 23:00 | Palashbari | 131 | 10:00 | 112 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 04:00 | 122 | 13:00 | Panchagarh | 137 | 18:30 | 122 | 19:30
Chauddagram | 123 | 09:00 | 114 | 00:00 | Patuakhali | 134 | 09:00 | 131 | 22:00
Chhatak | 125 | 06:00 | 114 | 00:00 | Payra | 136 | 05:00 | 133 | 21:00
Chowmuhani | 119 | 09:00 | 108 | 00:00 | PHP | 122 | 18:00 | 114 | 00:00
Chuadanga | 131 | 09:00 | 120 | 19:00 | Postogola | 132 | 05:00 | 125 | 12:00
Coxsbazar | 124 | 09:00 | 111 | 00:00 | Purbachal | 138 | 06:00 | 122 | 12:00
Cumilla(N) | 127 | 09:00 | 121 | 00:00 | Purbasadipur | 131 | 18:30 | 119 | 23:00
Cumilla(S) | 133 | 05:00 | 119 | 00:00 | Rahanpur | 138 | 04:00 | 126 | 12:00
Daganbhuiyan | 120 | 18:00 | 110 | 00:00 | Rahanpur-400 | 139 | 10:00 | 131 | 21:00
Daudkandi | 122 | 05:00 | 115 | 15:00 | Rahim | 129 | 05:00 | 123 | 13:00
Dhaka | 138 | 05:00 | 125 | 12:00 | Rajbari | 133 | 06:00 | 127 | 21:00
Dhamrai | 135 | 09:00 | 126 | 23:00 | Rajendrapur | 131 | 06:00 | 122 | 15:00
Dhanmondi | 138.6 | 06:00 | 125 | 12:00 | Rajshahi | 133 | 06:00 | 125 | 23:00
Dohazari | 131 | 10:00 | 121 | 22:00 | Rajshahi-230 | 133 | 07:00 | 125 | 23:00
Faridpur | 135 | 06:00 | 128 | 23:00 | Ramganj | 121 | 09:00 | 111 | 00:00
Fatullah | 131 | 05:00 | 124 | 13:00 | Rampur | 131 | 08:00 | 125 | 00:00
Fenchuganj | 134 | 07:00 | 129 | 00:00 | Rampura | 138 | 06:00 | 125 | 12:00
Feni | 122 | 09:00 | 113 | 01:00 | Rangamati | 131 | 05:00 | 127 | 00:00
Ghatail | 131 | 10:00 | 125 | 00:00 | Rangpur | 133 | 18:30 | 123 | 19:30
Ghorashal | 136 | 05:00 | 130 | 11:00 | Ruppur | 137 | 09:00 | 131 | 19:00
Goalpara | 137 | 09:00 | 127 | 19:00 | Saidpur | 133 | 18:30 | 119 | 21:00
Gollamari | 137 | 09:00 | 128 | 19:00 | Satkhira | 134 | 09:00 | 121 | 23:00
Gopalganj | 136 | 09:00 | 127 | 19:00 | Satmasjid | 133 | 06:00 | 123 | 13:00
Gopalganj-400 | 137 | 06:00 | 130 | 23:00 | Savar | 132 | 03:00 | 124 | 12:00
Gulshan | 138 | 05:00 | 125 | 12:00 | SevenRings | 137 | 07:00 | 129 | 12:00
Halishahar | 132 | 06:00 | 125 | 23:00 | ShahCement | 129 | 04:00 | 122 | 13:00
Haripur | 129 | 05:00 | 122 | 13:00 | Shahjadpur | 136 | 08:00 | 133 | 23:00
HaripurSBU | 129 | 05:00 | 122 | 13:00 | Shahjibazar | 137 | 18:00 | 127 | 22:00
Hasnabad | 132 | 03:00 | 125 | 12:00 | Shahmirpur | 134 | 10:00 | 127 | 00:00
Hathazari | 132 | 07:00 | 127 | 00:00 | Shariatpur | 134 | 09:00 | 127 | 20:00
Ishurdi | 138 | 10:00 | 132 | 19:00 | Sherpur | 137 | 18:30 | 125 | 00:00
Jaldhaka | 130 | 18:30 | 116 | 21:00 | Shikalbaha | 123 | 09:00 | 117 | 00:00
Jamalpur | 139 | 09:00 | 128 | 01:00 | Shikalbaha-230 | 134 | 08:00 | 127 | 23:00
Jashore | 130 | 09:00 | 118 | 19:00 | Shitalakhya | 130 | 06:00 | 122 | 13:00
Jhenaidah | 134 | 10:00 | 122 | 19:00 | Sholosohor | 131 | 06:00 | 127 | 00:00
Jhenaidah-230 | 135 | 10:00 | 125 | 19:00 | Shyampur | 130 | 05:00 | 125 | 15:00
Joydebpur | 135 | 03:00 | 124 | 15:00 | Shyampur-230 | 133 | 08:00 | 123 | 13:00
Joypurhat | 134 | 10:00 | 118 | 23:00 | Siddhirganj | 129 | 05:00 | 123 | 15:00
Juldah | 132 | 06:00 | 127 | 23:00 | Sirajganj | 135 | 09:00 | 125 | 23:00
Kabirpur | 132 | 12:00 | 120 | 12:00 | Sonargaon | 126 | 05:00 | 120 | 15:00
Kachua | 125 | 08:00 | 117 | 00:00 | Sreemongol | 134 | 08:00 | 125 | 22:00
Kaliakoir | 136 | 09:00 | 126 | 12:00 | Sreepur | 134 | 07:00 | 128 | 12:00
Kallyanpur | 134 | 06:00 | 126 | 12:00 | Srinagar | 135 | 06:00 | 125 | 14:00
Kalurghat | 131 | 06:00 | 127 | 00:00 | SSM | 134 | 00:00 | 130 | 01:00
Kamrangirchar | 135 | 06:00 | 125 | 13:00 | Sunamganj | 124 | 17:00 | 112 | 00:00
Kaptai | 135 | 9:00 | 131 | 1:00 | Sylhet | 127 | 08:00 | 119 | 00:00
Kasba | 123 | 06:00 | 117 | 14:00 | Sylhet-132 | 128 | 10:00 | 120 | 00:00
Kazla | 133 | 06:00 | 125 | 13:00 | Tangail | 130 | 09:00 | 123 | 01:00
Keranigonj | 135 | 06:00 | 125 | 13:00 | Taraganj | 131 | 18:30 | 119 | 22:00
Khagrachori | 132 | 09:00 | 126 | 00:00 | Thakurgaon | 136 | 18:30 | 121 | 14:00
Khulna | 135 | 09:00 | 125 | 19:00 | TK | 131 | 04:00 | 127 | 23:00
Khulna(S) | 137 | 09:00 | 128 | 23:00 | Tongi | 135 | 07:00 | 125 | 12:00
Khulshi | 132 | 10:00 | 126 | 00:00 | Ullahpara | 135 | 09:00 | 128 | 21:00
Kishoreganj | 130 | 16:00 | 123 | 00:00 | Ullon | 138 | 06:00 | 124 | 12:00
Kodda | 132 | 19:00 | 120 | 12:00 | Uttara | 133 | 06:00 | 124 | 12:00
KSRM | 132 | 09:00 | 127 | 00:00 | UttaraNew | 133 | 04:00 | 122 | 12:00
Kulaura | 133 | 07:00 | 127 | 21:00 | Zigatola | 135 | 06:00 | 126 | 13:00
Kurigram | 130 | 18:30 | 118 | 19:00
Kushtia | 133 | 09:00 | 126 | 23:00
Laksam | 124 | 08:00 | 115 | 00:00
Lakshmipur | 120 | 10:00 | 109 | 00:00
Lalbag | 135 | 05:00 | 125 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division