## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 04-08-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 03-08-2025 | during | 04-08-2025 | during | 04-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 0 | 0 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 0 | 400.75 | 400.75 | 0 | 0 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 301 | 297 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 1 | 30 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 195 | 198 | 208.13 | 208.13 | 198 | 198 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 335 | 335 | 335 | 333 | 333 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 50 | 7 | 50 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 43 | 45 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 30 | 126 | 149.36 | 149.36 | 144 | 144 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 36 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20.5 | 21.5 | 33 | 33 | 28 | 28 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | Fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 45 | 95 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 86 | 149 | 149 | 149 | 130 | 130 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 86 | 87.5 | 87.5 | 87.5 | 87.5 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 8 | 104 | 104 | 16 | 16 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 125 | 140 | 162 | 162 | 162 | 162 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 15 | 0 | 21 | 0 | 21 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 404 | 330 | 583 | 583 | 525 | 525 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 733.79 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 142 | 160 | 160 | 125 | 125 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6673.514 | 2276.5 | 2574.5 | 5814.9 | 5836.9 | 3692.47 | 3714.47
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 130 | 150 | 115 | 115 | 0 | 0 | U#1 Under maintenance, U#2 Running
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 7 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 21 | 40 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 219 | 221 | 210 | 210 | 210 | 210 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 40 | 48 | 72 | 48 | 72 | Machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 65 | 65 | 65 | 65 | 65 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 50 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 5 | 8 | 2 | 20 | 2 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.92 | 0 | 2.5 | 0 | 2.5 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 8 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 35 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1001 | 1040 | 1224 | 1224 | 1194 | 1194 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 46 | 16 | 10 | 12 | 10 | 12 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 745 | 743 | 770 | 770 | 790 | 790 | FGMO
Chattogram Area Total |  |  |  |  | 4959 | 4895.72 | 2214.92 | 2473 | 3685.22 | 3716.72 | 3397.22 | 3428.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 198 | 180 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 341 | 300 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 318.81 | 330 | 315 | 318.81 | 318.81 | 318.81 | 318.81 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 30 | 39 | 46.7 | 46.7 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 47 | 50 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 103 | 63 | 195 | 195 | 182 | 182 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 25 | 142 | 150 | 150 | 140 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 35 | 44 | 47 | 47 | 47 | 47 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 30 | 50 | 163 | 163 | 70 | 70 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 142 | 160 | 200 | 200 | 200 | 200 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 36 | 42 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 49 | 94 | 114 | 114 | 114 | 114 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 45 | 72 | 113 | 113 | 73 | 73 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 92 | 89 | 115 | 115 | 92 | 92 | Engine Problem
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 9 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2853.061 | 1575 | 1763.2 | 2429.56 | 2379.56 | 2235.36 | 2185.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 03-08-2025 | during | 04-08-2025 | during | 04-08-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 106 | 109 | 157.5 | 157.5 | 154 | 154 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 45 | 100 | 200 | 200 | 170.2 | 170.2 | Engine Problem
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 76 | 115 | 115 | 100 | 100 | Engine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 31.09 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 7 | 22 | 22 | 12 | 12 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 9 | 17 | 54.5 | 54.5 | 35 | 35 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 249.09 | 309 | 595.9 | 549 | 518.1 | 471.2
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 60 | 60 | 60 | 60 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 149 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 82 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 7 | 0 | 25 | 25 | 6 | 7 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 40 | 200 | 0 | 0 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 387 | 346 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 300 | 275 | 285 | 285 | 285 | 285 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1008 | 930 | 1062 | 1222 | 973 | 974
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 880 | 886 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 44 | 44 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 347 | 321 | 410 | 410 | 407 | 407
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 53 | 53 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 100 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 893 | 1022 | 1234.2 | 1234.2 | 1204 | 1204 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2258 | 2284 | 3633.2 | 3548.2 | 3458 | 3373
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 305 | 305 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1000 | 1080 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 202 | 272 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.85 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1847.85 | 1997 | 2162 | 2161 | 2152 | 2151
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64 | 36.91 | 0 | 0 | 0 | 0 | 0 | -
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 15 | 47 | 47 | 47 | 47 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 5 | 32 | 32 | 32 | 32 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 12 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 177 | 174 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 178 | 168 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 183 | 174 | 220 | 220 | 198 | 198 | Plant is running as per NLDC demand
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 358 | 391 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 22 | 22 | 22 | 22 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 97 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.98 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 825 | 1220.81 | 1435.88 | 1435.88 | 1355 | 1355 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 68.39 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 90 | 0 | 95 | 0 | 95 | 0 | -
Rajshahi Area Total |  |  |  |  | 3474 | 3516.96 | 1921.28 | 2351.81 | 3179.47 | 3017.87 | 2991.81 | 2830.21
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 182 | 175 | 160 | 160 | 160 | 160 | Machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 35 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 0.6 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 95 | 95 | 95 | 95 | 95 | Schedule Maintenance
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 1 | 0 | 22 | 0 | 22 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 32 | 0 | 71.6 | 0 | 71.6 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 250.6 | 383 | 502.2 | 402 | 502.2 | 402
System Total |  |  |  |  | 28671.2 | 27843.665 | 13601.24 | 15065.51 | 23064.45 | 22833.25 | 19920.16 | 19529.96
Forecast Scenario (04-08-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14860 |  | 0 |  | 14860
|  |  |  | 1:00 | 14440 |  | 0 |  | 14440
|  |  |  | 2:00 | 14110 |  | 0 |  | 14110
|  |  |  | 3:00 | 13730 |  | 0 |  | 13730
|  |  |  | 4:00 | 13410 |  | 0 |  | 13410
|  |  |  | 5:00 | 13160 |  | 0 |  | 13160
|  |  |  | 6:00 | 12710 |  | 0 |  | 12710
|  |  |  | 7:00 | 12640 |  | 0 |  | 12640
|  |  |  | 8:00 | 12600 |  | 0 |  | 12600
|  |  |  | 9:00 | 12830 |  | 0 |  | 12830
|  |  |  | 10:00 | 13040 |  | 0 |  | 13040
|  |  |  | 11:00 | 13170 |  | 0 |  | 13170
|  |  |  | 12:00 | 13600 |  | 0 |  | 13600
|  |  |  | 13:00 | 13830 |  | 0 |  | 13830
|  |  |  | 14:00 | 13450 |  | 0 |  | 13450
|  |  |  | 15:00 | 13370 |  | 0 |  | 13370
|  |  |  | 16:00 | 13280 |  | 0 |  | 13280
|  |  |  | 17:00 | 13060 |  | 0 |  | 13060
|  |  |  | 18:00 | 12620 |  | 0 |  | 12620
|  |  |  | 18:30 | 13300 |  | 0 |  | 13300
|  |  |  | 19:00 | 14390 |  | 0 |  | 14390
|  |  |  | 19:30 | 15060 |  | 0 |  | 15060
|  |  |  | 20:00 | 14830 |  | 0 |  | 14830
|  |  |  | 21:00 | 14850 |  | 0 |  | 14850
|  |  |  | 22:00 | 14800 |  | 0 |  | 14800
|  |  |  | 23:00 | 14700 |  | 0 |  | 14700
Probable Maximum Temperature: |  |  | 31.00°C
Probable Maximum Demand at Day Peak: |  |  | 13600.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15060.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15060.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 327.48 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:11 hrs on 04-08-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 03-08-2025 | [28 empty] | Date: | 03-08-2025 | [28 empty] | Date: | 03-08-2025 | [28 empty] | Date: | 03-08-2025 | [28 empty] | Date: | 03-08-2025 | [12 empty] | Date: | 03-08-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [12 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 733.790 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 318.810 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.000 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 35 | 32 | 16 | 0 | 0 | 0 | 126 | 0 | 450 | 295 | 405 | 0 | 0 | 332 | 196 | 0 | 0 | 52 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 115 | 10 | 33 | 0 | 0 | 12 | 25 | 0 | 219 | 0 | 20 | 767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1125 | 0 | 51 | 0 | 170 | 0 | 352 | 340 | 49 | 194 | 33 | 93 | 70 | 159 | 50 | 19 | 102 | 48 | 52.2 | 0 | 37 | 0 | 285 | 390 | 0 | 60 | 157 | 7 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 87 | 120 | 143 | 0 | 0 | 10 | 7600.2 | 879 | 357 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1128 | 0 | 1450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 198 | 0 | 196 | 0 | 404 | 0 | 0 | 175 | 0 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 120 | 220 | 0 | 305 | 1109 | 0 | 7267 | 14867.2 | 106.57
01:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 19 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 301 | 395 | 0 | 0 | 332 | 196 | 0 | 0 | 52 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 115 | 18 | 33 | 0 | 0 | 12 | 25 | 0 | 220 | 0 | 29 | 756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 0 | 51 | 0 | 177 | 0 | 352 | 340 | 49 | 194 | 33 | 78 | 70 | 160 | 48 | 20 | 100 | 46 | 52.2 | 0 | 37 | 0 | 285 | 367 | 0 | 60 | 154 | 7 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 77 | 120 | 147 | 0 | 0 | 12 | 7325.2 | 880 | 352 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1140 | 0 | 1360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 194 | 0 | 192 | 0 | 402 | 0 | 0 | 177 | 0 | 95 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 120 | 220 | 0 | 305 | 1108 | 0 | 7100 | 14425.2 | 106.6
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.2 | 14 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 296 | 400 | 0 | 0 | 333 | 196 | 0 | 0 | 52 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 115 | 21 | 33 | 0 | 0 | 12 | 25 | 0 | 220 | 0 | 21 | 755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060 | 0 | 51 | 0 | 178 | 0 | 353 | 340 | 50 | 194 | 33 | 86 | 70 | 160 | 50 | 20 | 104 | 46 | 52.2 | 0 | 37 | 0 | 285 | 376 | 0 | 60 | 155 | 7 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 77 | 120 | 151 | 0 | 0 | 12 | 7311.4 | 881 | 352 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1114 | 0 | 1216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 196 | 0 | 194 | 0 | 404 | 0 | 0 | 176 | 0 | 95 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 120 | 220 | 0 | 306 | 1000 | 0 | 6779 | 14090.4 | 106.63
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 297 | 400 | 0 | 0 | 333 | 195 | 0 | 0 | 17 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 115 | 23 | 18 | 0 | 0 | 12 | 25 | 0 | 221 | 0 | 35 | 743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1055 | 0 | 51 | 0 | 182 | 0 | 353 | 340 | 50 | 193 | 33 | 93 | 70 | 160 | 51 | 20 | 101 | 44 | 6 | 0 | 37 | 0 | 285 | 350 | 0 | 60 | 156 | 7 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 77 | 120 | 153 | 0 | 0 | 12 | 7172.6 | 880 | 352 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 902 | 0 | 1209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 189 | 0 | 189 | 0 | 403 | 0 | 0 | 177 | 0 | 95 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 120 | 220 | 0 | 304 | 1000 | 0 | 6545 | 13717.6 | 106.66
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 297 | 415 | 0 | 0 | 332 | 195 | 0 | 0 | 17 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 115 | 17 | 0 | 0 | 0 | 12 | 25 | 0 | 221 | 0 | 38 | 740 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 0 | 51 | 0 | 182 | 0 | 348 | 340 | 50 | 206 | 28 | 93 | 70 | 159 | 64 | 20 | 67 | 44 | 0 | 0 | 37 | 0 | 285 | 390 | 0 | 60 | 158 | 7 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 77 | 100 | 153 | 0 | 0 | 0 | 7025 | 880 | 352 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 905 | 0 | 1215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 192 | 0 | 191 | 0 | 414 | 0 | 0 | 177 | 0 | 50 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 120 | 220 | 0 | 305 | 900 | 0 | 6368 | 13393 | 106.69
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 300 | 410 | 0 | 0 | 333 | 196 | 0 | 0 | 17 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 115 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 38 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 0 | 51 | 0 | 182 | 0 | 353 | 340 | 50 | 199 | 29 | 68 | 70 | 136 | 65 | 20 | 64 | 42 | 0 | 0 | 37 | 0 | 285 | 380 | 0 | 60 | 157 | 7 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 77 | 100 | 151 | 0 | 0 | 0 | 6909 | 880 | 350 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 901 | 0 | 1109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 191 | 0 | 190 | 0 | 408 | 0 | 0 | 178 | 0 | 50 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 120 | 220 | 0 | 305 | 890 | 0 | 6241 | 13150 | 106.72
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 301 | 400 | 0 | 0 | 333 | 196 | 0 | 1 | 17 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 115 | 23 | 0 | 0 | 0 | 0 | 0 | 0.09 | 220 | 0 | 38 | 740 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 855 | 1 | 51 | 0 | 182 | 0 | 354 | 340 | 50 | 196 | 29 | 60 | 30 | 122 | 63 | 20 | 17 | 40 | 0 | 0 | 37 | 0 | 285 | 385 | 0 | 60 | 152 | 7 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 76 | 100 | 152 | 0 | 1.43 | 0 | 6695.02 | 880 | 346 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 822 | 0 | 987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0.32 | 194 | 0 | 185 | 0 | 184 | 0 | 407 | 0 | 0 | 177 | 0 | 35 | 1 | 34 | 0 | 0 | 0 | 1 | 0.03 | 0 | 172 | 120 | 220 | 0 | 306 | 884 | 0 | 6001.35 | 12696.37 | 106.75
07:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 28 | 15 | 0 | 0 | 0 | 0 | 0 | 450 | 301 | 400 | 0 | 0 | 332 | 196 | 0 | 5 | 17 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 120 | 24 | 0 | 0 | 0 | 0 | 0 | 0.28 | 219 | 0 | 36 | 740 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 850 | 5 | 51 | 0 | 143 | 0 | 354 | 340 | 50 | 188 | 29 | 50 | 30 | 124 | 57 | 20 | 15 | 38 | 0 | 3 | 37 | 0 | 285 | 365 | 0 | 60 | 154 | 7 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 76 | 100 | 150 | 0 | 9.82 | 6 | 6693.6 | 880 | 346 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 25 | 790 | 0 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.15 | 17 | 0 | 7.5 | 190 | 0 | 183 | 0 | 187 | 0 | 400 | 0 | 0.49 | 176 | 0 | 35 | 0 | 34 | 0 | 0 | 0.1 | 2 | 0.19 | 0 | 171 | 120 | 220 | 0 | 305 | 880 | 0 | 5936.43 | 12630.03 | 106.78
08:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 33 | 15 | 0 | 0 | 0 | 0 | 0 | 450 | 298 | 410 | 0 | 0 | 330 | 194 | 0 | 9 | 17 | 21.5 | 21 | 0 | 0 | 0 | 0 | 0 | 120 | 18 | 0 | 0 | 0 | 0 | 0 | 1.59 | 219 | 0 | 36 | 740 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 831 | 6 | 51 | 0 | 75 | 0 | 353 | 340 | 50 | 214 | 30 | 45 | 30 | 116 | 55 | 20 | 15 | 36 | 0 | 6 | 36 | 0 | 285 | 380 | 0 | 60 | 152 | 7 | 0 | 84 | 0 | 0 | 18 | 0 | 17 | 75 | 85 | 150 | 0 | 5.61 | 12 | 6623.7 | 880 | 347 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 41 | 785 | 0 | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.15 | 19 | 0 | 9.82 | 187 | 0 | 172 | 0 | 189 | 0 | 405 | 0 | 0.72 | 181 | 0 | 35 | 1 | 34 | 0 | 0 | 0.3 | 8 | 0.21 | 0 | 171 | 120 | 220 | 0 | 305 | 880 | 0 | 5966.2 | 12589.9 | 106.81
09:00 | 0 | 37 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 40 | 30 | 0 | 0 | 7 | 38 | 0 | 450 | 296 | 395 | 0 | 0 | 330 | 194 | 0 | 20 | 35 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 115 | 17 | 0 | 0 | 0 | 12 | 25 | 2.43 | 219 | 0 | 2 | 745 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 910 | 10 | 51 | 0 | 66 | 0 | 348 | 335 | 49 | 194 | 33 | 45 | 30 | 129 | 55 | 20 | 15 | 36 | 0 | 6 | 36 | 0 | 290 | 374 | 0 | 60 | 154 | 7 | 0 | 81 | 0 | 0 | 18 | 0 | 0 | 75 | 45 | 131 | 0 | 10.02 | 12 | 6720.45 | 881 | 347 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 60 | 822 | 0 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.77 | 66 | 0 | 28.6 | 189 | 0 | 177 | 0 | 187 | 0 | 372 | 0 | 3.67 | 180 | 0 | 50 | 0 | 34 | 0 | 0 | 0.1 | 12 | 0.22 | 0 | 170 | 120 | 220 | 0 | 305 | 925 | 0 | 6118.36 | 12838.81 | 106.84
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 18 | 80 | 30 | 15 | 0 | 46 | 49 | 0 | 450 | 293 | 387 | 0 | 0 | 326 | 193 | 0 | 16 | 70 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 115 | 36 | 0 | 0 | 0 | 12 | 25 | 1.38 | 219 | 0 | 2 | 735 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 903 | 18 | 51 | 0 | 66 | 0 | 343 | 340 | 48 | 193 | 32 | 52 | 30 | 141 | 55 | 20 | 34 | 36 | 0 | 1 | 36 | 0 | 290 | 381 | 0 | 60 | 155 | 7 | 0 | 81 | 0 | 0 | 18 | 0 | 0 | 45 | 45 | 119 | 0 | 23.52 | 12 | 6893 | 880 | 348 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 28 | 858 | 0 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.03 | 85 | 0 | 24.87 | 174 | 0 | 165 | 0 | 172 | 0 | 356 | 0 | 3.15 | 181 | 0 | 35 | 3 | 34 | 0 | 0 | 0.4 | 48 | 0.44 | 0 | 171 | 120 | 220 | 0 | 304 | 940 | 0 | 6149.89 | 13042.89 | 106.87
11:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 87 | 30 | 22 | 0 | 35 | 84 | 0 | 450 | 302 | 403 | 0 | 0 | 330 | 193 | 0 | 13 | 70 | 20.9 | 14 | 0 | 0 | 0 | 0 | 0 | 108 | 36 | 0 | 0 | 0 | 12 | 25 | 3.12 | 219 | 0 | 4 | 740 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 920 | 7 | 51 | 5 | 71 | 0 | 349 | 330 | 47 | 203 | 36 | 82 | 30 | 141 | 50 | 20 | 52 | 36 | 0 | 4 | 35 | 0 | 300 | 388 | 0 | 60 | 155 | 7 | 0 | 77 | 0 | 0 | 18 | 0 | 0 | 45 | 45 | 120 | 1 | 17.64 | 12 | 7063.66 | 879 | 348 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 78 | 848 | 0 | 858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.47 | 62 | 0 | 41.04 | 173 | 0 | 165 | 0 | 172 | 0 | 378 | 0 | 3.73 | 180 | 0 | 0 | 4 | 34 | 0 | 0 | 0.7 | 43 | 0.45 | 0 | 171 | 120 | 220 | 0 | 304 | 940 | 0 | 6111.39 | 13175.05 | 106.89
12:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 35 | 86 | 30 | 45 | 1 | 35 | 125 | 0 | 450 | 301 | 404 | 0 | 0 | 330 | 195 | 0 | 15 | 70 | 20.5 | 14 | 0 | 0 | 0 | 0 | 0 | 130 | 46 | 0 | 0 | 0 | 12 | 25 | 3.92 | 219 | 0 | 5 | 745 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 1001 | 7 | 51 | 25 | 103 | 0 | 341 | 330 | 47 | 198 | 30 | 92 | 30 | 142 | 45 | 12 | 49 | 36 | 0 | 9 | 35 | 0 | 300 | 387 | 0 | 60 | 156 | 7 | 0 | 80 | 0 | 0 | 18 | 0 | 9 | 45 | 45 | 106 | 1 | 31.09 | 12 | 7323.51 | 880 | 347 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 100 | 893 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.91 | 90 | 0 | 68.39 | 177 | 0 | 178 | 0 | 183 | 0 | 358 | 0 | 4.98 | 182 | 0 | 0 | 1 | 35 | 0 | 0 | 0.6 | 32 | 0.85 | 0 | 202 | 120 | 220 | 0 | 305 | 1000 | 0 | 6277.73 | 13601.24 | 106.91
13:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 28 | 86 | 30 | 45 | 7 | 35 | 145 | 0 | 450 | 298 | 378 | 0 | 17 | 335 | 135 | 0 | 16 | 52 | 20 | 14 | 0 | 0 | 0 | 0 | 0 | 150 | 39 | 0 | 0 | 0 | 12 | 25 | 2.39 | 219 | 0 | 12 | 745 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 970 | 16 | 51 | 60 | 127 | 0 | 355 | 330 | 48 | 184 | 32 | 68 | 30 | 159 | 46 | 12 | 39 | 42 | 0 | 13 | 35 | 0 | 300 | 317 | 0 | 60 | 149 | 7 | 0 | 80 | 0 | 0 | 18 | 0 | 0 | 77 | 55 | 102 | 0 | 31.71 | 12 | 7300.1 | 886 | 347 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 17 | 877 | 0 | 958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.95 | 110 | 0 | 36.82 | 185 | 0 | 187 | 0 | 186 | 0 | 331 | 0 | 1.19 | 180 | 0 | 35 | 7 | 50 | 0 | 0 | 1.5 | 210 | 0.09 | 0 | 193 | 120 | 180 | 0 | 304 | 1050 | 0 | 6535.55 | 13835.65 | 106.93
14:00 | 0 | 69 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 17 | 90 | 15 | 15 | 15 | 35 | 147 | 0 | 450 | 305 | 393 | 0 | 17 | 280 | 75 | 0 | 15 | 35 | 20 | 21 | 0 | 0 | 0 | 0 | 0 | 150 | 47 | 0 | 0 | 0 | 12 | 25 | 1.38 | 219 | 0 | 2 | 747 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 958 | 9 | 51 | 30 | 143 | 0 | 354 | 280 | 43 | 202 | 33 | 65 | 30 | 147 | 46 | 12 | 33 | 38 | 0 | 10 | 43 | 0 | 300 | 342 | 0 | 60 | 135 | 7 | 0 | 82 | 0 | 0 | 18 | 0 | 2 | 77 | 65 | 102 | 0 | 5.21 | 12 | 7061.59 | 886 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 81 | 839 | 0 | 975.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.82 | 31 | 0 | 49.98 | 175 | 0 | 174 | 0 | 184 | 0 | 373 | 0 | 5.31 | 177 | 0 | 35 | 10 | 55 | 0 | 0 | 0.6 | 119 | 0.12 | 0 | 200 | 120 | 180 | 0 | 306 | 1030 | 0 | 6388.71 | 13450.3 | 106.94
15:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.7 | 17 | 58 | 15 | 0 | 15 | 37 | 108 | 0 | 450 | 299 | 395 | 0 | 0 | 335 | 198 | 0 | 7 | 35 | 21.5 | 21 | 0 | 0 | 0 | 0 | 0 | 150 | 36 | 0 | 0 | 0 | 12 | 25 | 0.35 | 221 | 0 | 2 | 746 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 948 | 9 | 51 | 24 | 143 | 0 | 355 | 330 | 42 | 191 | 34 | 65 | 30 | 148 | 45 | 20 | 31 | 30 | 0 | 28 | 43 | 0 | 270 | 360 | 0 | 60 | 151 | 0 | 0 | 80 | 0 | 0 | 18 | 0 | 17 | 65 | 55 | 102 | 0 | 3.36 | 12 | 7110.91 | 886 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 39 | 813 | 0 | 952.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.25 | 72 | 0 | 17.19 | 176 | 0 | 180 | 0 | 181 | 0 | 341 | 0 | 1.93 | 178 | 0 | 35 | 11 | 34 | 0 | 0 | 1.5 | 129 | 0.37 | 0 | 197 | 120 | 220 | 0 | 304 | 1000 | 0 | 6261.77 | 13372.68 | 106.94
16:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.9 | 17 | 58 | 15 | 0 | 15 | 37 | 98 | 0 | 450 | 303 | 405 | 0 | 0 | 335 | 196 | 0 | 5 | 35 | 21.5 | 21 | 0 | 0 | 0 | 0 | 0 | 150 | 35 | 0 | 0 | 0 | 36 | 25 | 0.48 | 221 | 0 | 2 | 744 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 955 | 9 | 51 | 12 | 145 | 0 | 352 | 330 | 49 | 199 | 34 | 67 | 30 | 161 | 46 | 20 | 31 | 32 | 0 | 27 | 43 | 0 | 270 | 385 | 0 | 60 | 156 | 0 | 0 | 79 | 0 | 0 | 18 | 0 | 17 | 65 | 55 | 102 | 0 | 1.39 | 12 | 7174.27 | 886 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 53 | 796 | 0 | 970.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.31 | 40 | 0 | 4.32 | 173 | 0 | 176 | 0 | 174 | 0 | 363 | 0 | 0.53 | 177 | 0 | 35 | 8 | 34 | 0 | 0 | 1.1 | 29 | 0.08 | 0 | 201 | 120 | 220 | 0 | 305 | 999 | 0 | 6107.65 | 13281.92 | 106.97
17:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.6 | 17 | 42 | 15 | 0 | 15 | 36 | 71 | 0 | 450 | 300 | 397 | 0 | 0 | 335 | 198 | 0 | 4 | 35 | 21.2 | 21 | 0 | 0 | 0 | 0 | 0 | 150 | 21 | 0 | 0 | 0 | 51 | 25 | 0.47 | 221 | 0 | 6 | 744 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 955 | 6 | 51 | 12 | 115 | 0 | 352 | 330 | 49 | 192 | 36 | 66 | 30 | 160 | 47 | 20 | 33 | 32 | 0 | 4 | 43 | 0 | 275 | 370 | 0 | 60 | 156 | 0 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 65 | 55 | 101 | 0 | 2.22 | 12 | 7059.49 | 886 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 19 | 796 | 0 | 964.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 13 | 0 | 0.44 | 173 | 0 | 175 | 0 | 174 | 0 | 345 | 0 | 0 | 176 | 0 | 35 | 2 | 34 | 0 | 0 | 0.9 | 23 | 0.01 | 0 | 200 | 120 | 220 | 0 | 304 | 1000 | 0 | 6002.86 | 13062.35 | 106.99
18:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 17 | 42 | 15 | 0 | 15 | 36 | 63 | 0 | 380 | 304 | 406 | 0 | 0 | 335 | 196 | 0 | 1 | 35 | 21.2 | 21 | 0 | 0 | 0 | 0 | 0 | 150 | 15 | 0 | 0 | 0 | 51 | 25 | 0.09 | 221 | 0 | 3 | 740 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 930 | 1 | 43 | 12 | 63 | 0 | 350 | 330 | 49 | 184 | 39 | 64 | 30 | 161 | 52 | 20 | 32 | 16 | 0 | 1 | 43 | 0 | 275 | 345 | 0 | 60 | 144 | 0 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 65 | 55 | 100 | 0 | 1 | 12 | 6821.29 | 886 | 300 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5 | 780 | 0 | 973.94 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 2.06 | 0 | 0 | 1.18 | 169 | 0 | 170 | 0 | 169 | 0 | 364 | 0 | 0.12 | 175 | 0 | 35 | 3 | 34 | 0 | 0 | 0.3 | 6 | 0.02 | 0 | 201 | 100 | 180 | 0 | 305 | 900 | 0 | 5801.62 | 12622.91 | 107.01
19:00 | 0 | 60 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 21 | 52 | 102 | 40 | 15 | 36 | 145 | 0 | 420 | 305 | 416 | 0 | 35 | 333 | 194 | 0 | 0 | 125 | 21.5 | 21 | 0 | 0 | 0 | 10 | 0 | 150 | 17 | 65 | 30 | 0 | 50 | 25 | 0 | 221 | 0 | 7 | 740 | 10 | 0 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 1040 | 0 | 51 | 50 | 63 | 0 | 350 | 330 | 49 | 182 | 39 | 72 | 50 | 160 | 68 | 20 | 112 | 44 | 48 | 0 | 43 | 0 | 275 | 386 | 0 | 60 | 142 | 0 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 86 | 100 | 101 | 0 | 0 | 12 | 7823.5 | 885 | 314 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 897 | 17 | 1107.3 | 0 | 0 | 0 | 25 | 6 | 5 | 97 | 12 | 0 | 0 | 0 | 20 | 0 | 176 | 0 | 178 | 0 | 177 | 0 | 407 | 0 | 0 | 175 | 0 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 252 | 120 | 220 | 0 | 305 | 930 | 0 | 6571.3 | 14394.8 | 107.03
19:30 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 35 | 149 | 126 | 95 | 30 | 36 | 140 | 8 | 420 | 297 | 330 | 0 | 35 | 335 | 198 | 0 | 0 | 142 | 21.5 | 21 | 0 | 0 | 0 | 15 | 0 | 150 | 16 | 65 | 40 | 0 | 50 | 25 | 0 | 221 | 8 | 8 | 743 | 35 | 0 | 40 | 0 | 17 | 0 | 0 | 0 | 0 | 1040 | 0 | 51 | 142 | 63 | 0 | 300 | 315 | 50 | 180 | 39 | 89 | 50 | 160 | 72 | 20 | 94 | 42 | 52.2 | 0 | 44 | 0 | 275 | 346 | 0 | 60 | 149 | 0 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 76 | 100 | 109 | 0 | 0 | 7 | 8049.7 | 886 | 321 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1022 | 17 | 1220.81 | 0 | 15 | 0 | 35 | 35 | 5 | 97 | 12 | 0 | 0 | 0 | 25 | 0 | 174 | 0 | 168 | 0 | 174 | 0 | 391 | 0 | 0 | 175 | 0 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 120 | 220 | 0 | 305 | 1080 | 0 | 7015.81 | 15065.51
20:00 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.5 | 35 | 140 | 94 | 0 | 0 | 30 | 143 | 16 | 350 | 298 | 341 | 0 | 35 | 280 | 136 | 0 | 0 | 125 | 21.5 | 21 | 0 | 0 | 0 | 15 | 0 | 150 | 15 | 65 | 55 | 0 | 50 | 25 | 0 | 221 | 15 | 14 | 745 | 0 | 0 | 39 | 1 | 17 | 0 | 0 | 0 | 0 | 1122 | 0 | 51 | 100 | 63 | 0 | 352 | 285 | 50 | 211 | 39 | 85 | 50 | 161 | 73 | 20 | 101 | 42 | 25 | 0 | 40 | 0 | 275 | 362 | 0 | 60 | 150 | 6 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 77 | 100 | 110 | 0 | 0 | 8 | 7766 | 886 | 330 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1038 | 17 | 1331.73 | 0 | 37 | 0 | 0 | 0 | 5 | 97 | 0 | 0 | 0 | 0 | 27 | 0 | 175 | 0 | 166 | 0 | 170 | 0 | 401 | 0 | 0 | 172 | 0 | 94 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 120 | 180 | 0 | 305 | 1090 | 0 | 7069.73 | 14835.73 | 107.06
21:00 | 0 | 69 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 35 | 90 | 80 | 0 | 0 | 0 | 72 | 17 | 450 | 300 | 400 | 0 | 0 | 335 | 198 | 0 | 0 | 125 | 21.5 | 21 | 0 | 0 | 0 | 0 | 0 | 150 | 11 | 65 | 23 | 0 | 50 | 25 | 0 | 220 | 0 | 20 | 745 | 0 | 0 | 19 | 7 | 0 | 0 | 0 | 0 | 0 | 1145 | 0 | 51 | 24 | 63 | 0 | 355 | 330 | 50 | 192 | 39 | 85 | 70 | 161 | 72 | 20 | 103 | 38 | 8 | 0 | 44 | 0 | 275 | 380 | 0 | 60 | 155 | 6 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 86 | 100 | 110 | 0 | 0 | 12 | 7754.5 | 886 | 348 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1090 | 17 | 1358.97 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 173 | 0 | 168 | 0 | 414 | 0 | 0 | 176 | 0 | 94 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 120 | 220 | 0 | 305 | 1114 | 0 | 7101.97 | 14856.47 | 107.09
22:00 | 0 | 69 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.9 | 35 | 85 | 62 | 0 | 0 | 0 | 65 | 0 | 450 | 306 | 400 | 0 | 0 | 335 | 197 | 0 | 0 | 108 | 21.5 | 21 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 51 | 23 | 0 | 50 | 25 | 0 | 219 | 0 | 25 | 744 | 0 | 0 | 19 | 8 | 0 | 0 | 0 | 0 | 0 | 1140 | 0 | 51 | 24 | 63 | 0 | 354 | 330 | 50 | 176 | 39 | 85 | 70 | 160 | 72 | 20 | 103 | 42 | 8 | 0 | 44 | 0 | 275 | 365 | 0 | 60 | 153 | 6 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 86 | 100 | 112 | 0 | 0 | 12 | 7631.4 | 886 | 347 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1087 | 17 | 1361.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 173 | 0 | 171 | 0 | 404 | 0 | 0 | 176 | 0 | 70 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 120 | 220 | 0 | 305 | 1113 | 0 | 7039.74 | 14671.14 | 107.13
23:00 | 0 | 69 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.7 | 19 | 80 | 62 | 0 | 0 | 0 | 64 | 0 | 450 | 306 | 405 | 0 | 0 | 335 | 198 | 0 | 0 | 90 | 21.5 | 21 | 0 | 0 | 0 | 0 | 0 | 150 | 11 | 65 | 22 | 0 | 50 | 25 | 0 | 219 | 0 | 26 | 746 | 0 | 0 | 19 | 8 | 0 | 0 | 0 | 0 | 0 | 1135 | 0 | 51 | 24 | 63 | 0 | 351 | 330 | 50 | 171 | 39 | 86 | 70 | 160 | 71 | 20 | 103 | 42 | 8 | 0 | 44 | 0 | 275 | 385 | 0 | 60 | 155 | 6 | 0 | 82 | 0 | 0 | 18 | 0 | 17 | 86 | 100 | 112 | 0 | 0 | 12 | 7628.2 | 886 | 348 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1094 | 17 | 1353.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 174 | 0 | 172 | 0 | 414 | 0 | 0 | 176 | 0 | 70 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 120 | 220 | 0 | 303 | 1108 | 0 | 7048.33 | 14676.53 | 107.17
Total KWH | 0 | 982080 | 448800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585000 | 540360 | 1438416 | 684000 | 248651 | 125935 | 435029 | 1478880 | 42240 | 10297000 | 7256291 | 9453182 | 0 | 111522 | 7938558 | 4728000 | 0 | 152985 | 1336800 | 523200 | 496440 | 0 | 0 | 0 | 26847 | 0 | 3300000 | 548160 | 458712 | 146016 | 0 | 509760 | 502080 | 18121 | 5295551 | 31780 | 386880 | 17970909.09 | 13382 | 0 | 464640 | 33481.8 | 35127 | 0 | 0 | 0 | 0 | 23814543 | 106515 | 1194308 | 546981 | 2826909 | 0 | 8758700 | 7966000 | 1168800 | 4734000 | 831096 | 1782720 | 1149580 | 3611040 | 1377600 | 418360 | 1448940 | 915840 | 222542 | 113745 | 947744 | 0 | 6778800 | 9343000 | 0 | 1398360 | 3669545.5 | 133992 | 0 | 1977600 | 0 | 0 | 432000 | 0 | 359280 | 1714800 | 2049600 | 2885760 | 4800 | 128940 | 258480 | 174115736.39 | 21365818 | 8349696 | 0 | 0 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 534240 | 21796360 | 90240 | 26132728 | 0 | 18744 | 0 | 34848 | 37056 | 16446 | 183504 | 14850 | 0 | 291346 | 645600 | 51266 | 254248 | 4466182 | 0 | 4494255 | 0 | 4576873 | 0 | 9317090 | 0 | 23340 | 4375000 | 0 | 1383049 | 49460 | 1516080 | 0 | 0 | 7984.8 | 630720 | 3528 | 0 | 5040000 | 2849000 | 5343180 | 0 | 7337448 | 24673454.55 | 0 | 156815634.35 | 330931370.74

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 03-08-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13601.24 | MW | 12:00 Hr. | Energy Generated |  |  | 330.9314 |  | MKWHr.
| Day Peak Demand |  |  | 13601.24 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.128 |  | MKWHr.
| Evening Peak Generation |  |  | 15065.51 | MW | 19:30 Hr. | Energy Demand |  |  | 331.0594 |  | MKWHr.
| Evening Peak Demand |  |  | 15065.51 | MW | 19:30 Hr. | Maximum Temperature |  |  | 31.1 |  | °C
| Minimum Generation of the Day |  |  | 12589.9 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 1013.59 |  | MMCFD
| Maximum Generation of the Day |  |  | 15065.51 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 5.9444 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.6927 | 0 | 8.4577 | 0 | 0 | 0.15299 | 0 | 0 | 49.3034 | Gas | 139.4426 | Gas | 520828940.795
| Chattogram Zone |  |  | 3.6869 | 41.7855 | 2.2218 | 0 | 5.2956 | 0.12464 | 0 | 0.54816 | 53.6625 | Coal | 105.0077 | Coal | 625467686.2159
| Cumilla Zone |  |  | 29.0478 | 0 | 9.9376 | 0 | 0 | 0.11374 | 0.91584 | 0 | 40.0149 | HFO | 28.3453 | HFO | 520992433.716
| Mymensingh Zone |  |  | 2.8858 | 0 | 4.3822 | 0 | 0 | 0.13374 | 0 | 0 | 7.4017 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 23.7333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.7333 | Hydro | 5.2956 | Hydro | 529555.1
| Khulna Zone |  |  | 8.3497 | 21.7964 | 0.09024 | 0 | 0 | 0.53424 | 22.2778 | 0 | 53.0484 | Solar | 2.9656 | Solar | 43307788.818
| Barishal Zone |  |  | 8.1922 | 37.0509 | 0 | 0 | 0 | 0.003528 | 0 | 0 | 45.2466 | Import | 49.3264 | Import | 248039192.5
| Rajshahi Zone |  |  | 22.8544 | 0 | 0.35671 | 0 | 0 | 1.2145 | 26.1327 | 0 | 50.5584 | Wind | 0.54816 | Wind | 8025062.4
| Rangpur Zone |  |  | 0 | 4.375 | 2.8991 | 0 | 0 | 0.68816 | 0 | 0 | 7.9623
| Total |  |  | 139.4426 | 105.0077 | 28.3453 | 0 | 5.2956 | 2.9656 | 49.3264 | 0.54816 | 330.9314
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 520828940.795 |  | Hydro | 529555.1
|  |  |  | Coal | 625467686.2159 |  | Solar | 43307788.818
|  |  |  | HFO | 520992433.716 |  | Import | 248039192.5
|  |  |  | HSD | 0 |  | Wind | 8025062.4
[5 empty] | Total: | 196,71,90,659 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.3658 | Peak Hr Flow | 886.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 46586509.2 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.1327 | Peak Hr Flow | 1220.81 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 726 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.91584 | Peak Hr Flow | 42.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 924 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 48.4144 | Peak Hr Flow | 2148.81 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5213
|  |  |  | Chattogram |  | 0 |  | 1511
|  |  |  | Cumilla |  | 0 |  | 1369
|  |  |  | Mymensingh |  | 0 |  | 1192
|  |  |  | Sylhet |  | 0 |  | 501
|  |  |  | Khulna |  | 0 |  | 1836
|  |  |  | Barishal |  | 0 |  | 466
|  |  |  | Rajshahi |  | 0 |  | 1450
|  |  |  | Rangpur |  | 0 |  | 944
|  |  |  | Total |  | 0 |  | 14482
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Bhola Nutan Biddut BD LTD GT-2 |  |  | 76
[7 empty] | 4 | Sylhet 225 MW CCPP GT |  |  | 142
[7 empty] | 5 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 707
|  |  |  | Total Unavailable Capacity |  |  |  | 1007
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:35 |  | Hasnabad 132/33kV S/S 33kv Reserve Bus Scheduled S/D Due to Pbs maintainence
| 09:42 | 13:45 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T LT Forced S/D
| 09:42 | 13:01 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T HT Forced S/D Due to Conductor flashing
between CT and lower contact of 33 KV circuit breaker at 33 KV NESCO Switching sub-station.
| 09:52 | 20:58 | Gopalganj 400/132kV S/S 400kV Rooppur Project Work S/D
| 10:09 | 19:45 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 LT Scheduled S/D Due to Rev.bus DS alignment correction
| 10:46 | 19:45 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 HT Scheduled S/D Due to Rev.bus DS alignment correction
| 11:35 | 17:39 | New Tongi S/S T1(403T) HT Scheduled S/D Due to For DESCO Project work
| 12:00 |  | Day Peak Generation=13596 MW.
| 12:42 |  | Bagabari-Shatiya 132 ckt CB open Bagabari S/S end. ( Protection work)
|  | 13:03 | Shahjibazar 132/33kV S/S TR-06 HT is restored.
|  | 13:05 | Shahjibazar 132/33kV S/S TR-06 LT is restored.
| 13:25 | 21:13 | Shahjibazar 132/33kV S/S TR-02 HT Scheduled S/D Due to For CT checking
| 13:27 | 21:15 | Shahjibazar 132/33kV S/S TR-02 LT Scheduled S/D Due to For CT checking
| 17:12 | 18:41 | Hathazari-Madunaghat 132kV Ckt-1 Tripped from Madunaghat 132/33kV end showing REL-670
relays Due to R and B phase fault, dist zone-01,z-com trip
| 18:22 |  | Chandpur CCPP ST was sync.
| 18:57 | 21:32 | Agargaon 230/132kV S/S 132kV Transformer-1 (405T1) HT Tripped showing Differential Relay(
87T) relays Due to 132/33 kV Transformer -1 Shutdown due to PRD False Trip
|  | 18:58 | Chauddagram-Feni 132 kV Ckt-1 is restored.
| 19:00 | 21:32 | Agargaon 230/132kV S/S 132kV Transformer-1 (405T1) HT Scheduled S/D Due to 132/33kV
Transformer PRD Problem.
| 19:00 | 21:35 | Agargaon 230/132kV S/S 132kV Transformer-1 (405T1) LT Scheduled S/D Due to 132/33 kV
Transformer-1 PRD Problem
| 19:30 |  | Evening Peak Generation 15064 MW.
| 19:56 |  | Raozan 25 MW PP Synchronized
| 19:59 |  | Chandpur CCPP ST tripped.
| 21:31 |  | Shyampur-Shyampur(New) 132kV Ckt-1 Tripped from Shyampur 230/132kV end showing Distance
protection Relay-F21 relays Due to Line Fault
| 21:31 |  | Haripur-Madanganj 132kV Ckt-1 Tripped from Haripur 230/132kV end showing Optimho: DEF Aided. relays.
|  | 21:35 | Agargaon 230/132kV S/S 132kV Transformer-1 (405T1) LT is restored.
| 22:03 |  | Haripur-Madanganj 132kV Ckt-1 Forced S/D from Madanganj 132/33kV end Due to Haripur
ckt-1 trip from Haripur side so for check line
| 02:57 |  | Raozan 25 MW PP Shutdown
| 05:36 | 06:02 | Bogura 132/33kV S/S Transformer-3 LT Tripped showing 50/51 trip relays Due to Bogura | [7 empty] | 20.0MW load
|  |  | PBS-2 feeder fault under Ins.O/C & Ins.E/F. | [7 empty] | interrup.
| 05:36 | 06:02 | Bogura 132/33kV S/S Transformer-3 HT Tripped showing Diff. R-phase Diff. Y-phase Diff. | [7 empty] | 20.0MW load
|  |  | B-phase relays Due to Bogura PBS feeder trip under Ins. O/C & Ins. E/F | [7 empty] | interrup.
| 06:00 |  | Minimum Generation 11638 MW
| 06:02 |  | Khulna (C) S/S TR-1 425T HT Forced S/D Due to Redhot maintenance
| 06:02 |  | Khulna (C) S/S TR-1 425T LT Forced S/D Due to Redhot maintenance
| 06:07 | 07:51 | Barishal 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to High temperature remedy work | [7 empty] | 13.0MW load interrup.
| 06:08 | 07:51 | Barishal 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to High temperature remedy work | [7 empty] | 13.0MW load interrup.
| 06:27 |  | Chauddagram-Feni 132 kV Ckt-2 Scheduled S/D from Chauddagram 132/33kV end Due to Feni - 2 | [7 empty] | and 13.0MW load
|  |  | gone under shutdown for their scheduled maintenance. and from Feni 132/33kV end Due to | [7 empty] | interrup. Feni
|  |  | Ptoject work of 230 kv feni s/s | [7 empty] | 132/33kV end
| 06:34 | 07:55 | Jhenaidah 132/33kV S/S Transformer T-2 LT Scheduled S/D Due to Red hot maintenance by Wzpdcl
| 06:35 | 07:54 | Jhenaidah 132/33kV S/S Transformer T-2 HT Scheduled S/D Due to Red hot maintenance by Wzpdcl
| 07:14 |  | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to Shutdown taken by PBS
| 07:14 |  | Shahjibazar 132/33kV S/S TR-06 LT Scheduled S/D Due to Shutdown taken by PBS
| 07:15 |  | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to Shutdown taken by PBS
| 07:23 |  | Shahjibazar 132/33kV S/S TR-06 HT Scheduled S/D Due to Shutdown taken by PBS
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 03-08-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Fault at Electrical Interconnection Facility(EIF)
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 0 | 0 | GT TI works going on
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 10297000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 297 | 7256291 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 30 | 125935 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 198 | 4728000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7938558 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 45 | 585000 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 126 | 684000 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 36 | 435029 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 111522 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21.5 | 523200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 496440 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 448800 | Fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 95 | 248651 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1438416 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 86 | 982080 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 8 | 42240 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 140 | 1478880 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 152985 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 540360 | Engine Problem
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 330 | 9453182 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 733.79 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 142 | 1336800 | -
Dhaka Area Total |  |  |  |  | 6673.514 | 2574.5 | 49303369
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 150 | 3300000 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 33481.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 106515 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 40 | 464640 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 221 | 5295551 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 0 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 35127 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 40 | 146016 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 458712 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 509760 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 8 | 386880 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 18121 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 26847 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 8 | 31780 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 502080 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 35 | 13382 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1040 | 23814543 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 16 | 548160 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 743 | 17970909.09 | -
Chattogram Area Total |  |  |  |  | 4895.72 | 2473 | 53662504.89
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 180 | 4734000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 300 | 8758700 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 318.81 | 315 | 7966000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | machine problem
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 39 | 831096 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 50 | 1168800 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 63 | 2826909 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1194308 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 142 | 546981 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 44 | 947744 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1149580 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 160 | 3611040 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 42 | 915840 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 222542 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 418360 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 94 | 1448940 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 72 | 1377600 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 89 | 1782720 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 113745 | -
Cumilla Area Total |  |  |  |  | 2853.061 | 1763.2 | 40014905
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 109 | 2885760 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 4800 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 100 | 2049600 | Engine Problem
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 76 | 1714800 | Engine Problem
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 128940 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 7 | 258480 | To be dispatched 12 MW, due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 359280 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 309 | 7401660
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1398360 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 149 | 3669545.5 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1977600 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 432000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 133992 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Partial Shutdown due to maintenance
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 346 | 9343000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 275 | 6778800 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 930 | 23733297.5
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 886 | 21365818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 321 | 8349696 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 90240 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 534240 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1022 | 21796360 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2284 | 53048354
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 305 | 7337448 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2849000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1080 | 24673454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5343180 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 272 | 5040000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3528 | -
Barishal Area Total |  |  |  |  | 2236 | 1997 | 45246610.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64 | 0 | 291346 | -
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 15 | 18744 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 5 | 16446 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 12 | 14850 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 174 | 4466182 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 168 | 4494255 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 174 | 4576873 | Plant is running as per NLDC demand
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 391 | 9317090 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 51266 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 97 | 183504 | Engine Problem
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 37056 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 34848 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 23340 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1220.81 | 26132728 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 254248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 645600 | -
Rajshahi Area Total |  |  |  |  | 3516.96 | 2351.81 | 50558376
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 175 | 4375000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1516080 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 7984.8 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 1383049 | Schedule Maintenance
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 49460 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 630720 | -
Rangpur Area Total |  |  |  |  | 950 | 383 | 7962293.8
Eastern Grid Total |  |  |  |  | 17401.505 | 8049.7 | 174115736.39
Western Grid Total |  |  |  |  | 10442.16 | 7015.81 | 156815634.35
National Grid Total |  |  |  |  | 27843.665 | 15065.51 | 330931370.74
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 03-08-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9786.31 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4696.2 | MW
i) Dhaka area |  |  | 5213.38 |  | MW | i) Khulna area |  |  |  | 1836 | MW
ii) Chattogram area |  |  | 1511 |  | MW | ii) Barishal area |  |  |  | 466 | MW
iii) Cumilla area |  |  | 1368.93 |  | MW | iii) Rajshahi area |  |  |  | 1450.2 | MW
iv) Mymensingh area |  |  | 1192 |  | MW | iv) Rangpur area |  |  |  | 944 | MW
v) Sylhet area |  |  | 501 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14482.51 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 13 | 12:00 | 67 | Hathazari | 81 | 19:30 | 133 | PHP | 9 | 18:00
2 | AKSML | 133 | 11:00 | 68 | Ishurdi | 82 | 19:30 | 134 | Pabna | 131 | 19:30
3 | Aftabnagar | 56 | 13:00 | 69 | Jaldhaka | 87 | 00:00 | 135 | Palashbari | 98 | 01:00
4 | Agargaon | 138 | 13:00 | 70 | Jamalpur | 126 | 00:00 | 136 | Panchagarh | 59 | 20:00
5 | Agrabad | 92 | 15:00 | 71 | Jashore | 142 | 21:00 | 137 | Patuakhali | 73 | 22:00
6 | Amnura | 27 | 00:00 | 72 | Jhenaidah | 132 | 19:30 | 138 | Payra | 36 | 23:00
7 | Ashuganj | 100 | 00:00 | 73 | Joydebpur | 151 | 12:00 | 139 | Postogola | 58 | 13:00
8 | BSRM | 205 | 07:00 | 74 | Joypurhat | 64 | 00:00 | 140 | Purbachal | 21 | 00:00
9 | Bagerhat | 86 | 19:30 | 75 | Juldah | 14.5 | 00:00 | 141 | Purbasadipur | 131 | 00:00
10 | Bajitpur | 74 | 00:00 | 76 | KSRM | 42 | 18:00 | 142 | Rahanpur | 40 | 00:00
11 | Bakulia | 95 | 19:30 | 77 | Kabirpur | 218 | 10:00 | 143 | Rahim | 26 | 05:00
12 | Banani | 96.2 | 13:00 | 78 | Kachua | 90 | 00:00 | 144 | Rajbari | 85 | 19:30
13 | Bangabhaban | 20 | 10:00 | 79 | Kallyanpur | 114 | 21:00 | 145 | Rajendrapur | 134 | 19:30
14 | Barapukuria | 63 | 00:00 | 80 | Kalurghat | 68 | 10:00 | 146 | Rajshahi | 103 | 19:30
15 | Barguna | 22 | 00:00 | 81 | Kamrangirchar | 78 | 12:00 | 147 | Rajshahi-230 | 100 | 13:00
16 | Barishal | 114 | 19:00 | 82 | Kaptai | N/A | N/A | 148 | Ramganj | 116 | 00:00
17 | Barishal-230 | 106 | 00:00 | 83 | Kasba | 34 | 00:00 | 149 | Rampur | 40 | 23:00
18 | Baroaulia | 61 | 13:00 | 84 | Kazla | 88 | 00:00 | 150 | Rangamati | 24 | 20:00
19 | Baroirhat | 70 | 19:30 | 85 | Keranigonj | 91 | 00:00 | 151 | Rangpur | 145 | 19:00
20 | Bashundhara | 209 | 13:00 | 86 | Khagrachori | 32 | 19:00 | 152 | Ruppur | 7 | 15:00
21 | BashundharaCement | 14 | 10:00 | 87 | Khulna | 68 | 13:00 | 153 | SSM | 0 | 00:00
22 | Beanibazar | 68 | 01:00 | 88 | Khulshi | 162 | 21:00 | 154 | Saidpur | 107 | 19:00
23 | Benapole | 70 | 19:30 | 89 | Kishoreganj | 136 | 22:00 | 155 | Satkhira | 134 | 19:30
24 | Bhaluka | 152 | 19:00 | 90 | Kodda | 302 | 09:00 | 156 | Satmasjid | 105 | 13:00
25 | Bhandaria | 58 | 22:00 | 91 | Kulaura | 51 | 02:00 | 157 | Savar | 245 | 10:00
26 | Bhangura | 37 | 19:30 | 92 | Kurigram | 68 | 21:00 | 158 | SevenRings | 6.56 | 18:00
27 | Bheramara(GK) | 66 | 19:30 | 93 | Kushtia | 158 | 18:00 | 159 | ShahCement | 4 | 00:00
28 | Bhulta | 267 | 00:00 | 94 | Laksam | 32 | 01:00 | 160 | Shahjadpur | 79 | 20:00
29 | Bog-Sherpur | 66 | 03:00 | 95 | Lakshmipur | 25 | 19:00 | 161 | Shahjibazar | 118 | 00:00
30 | Bogura | 161 | 00:00 | 96 | Lalbag | 57 | 13:00 | 162 | Shahmirpur | 61 | 00:00
31 | Borhanuddin | 95 | 19:00 | 97 | Lalmonirhat | 67 | 19:00 | 163 | Shariatpur | 93 | 00:00
32 | Brahmanbaria | 131 | 00:00 | 98 | MI_Cement | 13.8 | 02:00 | 164 | Sherpur | 138 | 22:00
33 | Cantonment | 146 | 19:30 | 99 | Madanganj | 41 | 12:00 | 165 | Shikalbaha | 8 | 09:00
34 | Chandina | 35.05 | 13:00 | 100 | Madaripur | 115 | 22:00 | 166 | Shitalakhya | 84.8 | 12:00
35 | Chandpur | 79 | 00:00 | 101 | Madartek | 94 | 00:00 | 167 | Sholosohor | 44 | 15:00
36 | Chandraghona | 38 | 22:00 | 102 | Madunaghat | 60 | 20:00 | 168 | Shyampur | 154 | 00:00
37 | Chapai | 63 | 00:00 | 103 | Magura | 69 | 19:30 | 169 | Siddhirganj | 120 | 12:00
38 | Charsaidpur | 40 | 13:00 | 104 | Mahasthangarh | 90 | 00:00 | 170 | Sirajganj | 110 | 21:00
39 | Chauddagram | 69 | 01:00 | 105 | Maijdee | 15 | 00:00 | 171 | Sonargaon | 120 | 01:00
40 | Chhatak | 39 | 01:00 | 106 | Manikganj | 126 | 19:30 | 172 | Sreemongol | 81 | 00:00
41 | Chowmuhani | 193 | 19:00 | 107 | Maniknagar | 88 | 13:00 | 173 | Sreepur | 107 | 19:00
42 | Chuadanga | 115 | 19:00 | 108 | Matarbari | 52 | 19:30 | 174 | Srinagar | 48.02 | 21:00
43 | Coxsbazar | 134 | 19:30 | 109 | Matuail | 68 | 11:00 | 175 | Sunamganj | 52 | 22:00
44 | Cumilla(N) | 130 | 14:00 | 110 | Millgate | 129 | 10:00 | 176 | Sylhet | 46 | 14:00
45 | Cumilla(S) | 151 | 12:00 | 111 | Mirpur | 129 | 21:00 | 177 | Sylhet-132 | 116 | 19:30
46 | Daganbhuiyan | 0 | 00:00 | 112 | Mirsorai | 11 | 15:00 | 178 | TK | 36 | 22:00
47 | Daudkandi | 151 | 22:00 | 113 | Mirzapur | 46 | 22:00 | 179 | Tangail | 184 | 19:30
48 | Dhaka | 82 | 13:00 | 114 | Mithapukur | 66 | 02:00 | 180 | Taraganj | 23 | 00:00
49 | Dhamrai | 116 | 13:00 | 115 | Modern | N/A | N/A | 181 | Thakurgaon | 105 | 19:30
50 | Dhanmondi | 153.6 | 13:00 | 116 | Mogbazar | 164.6 | 12:00 | 182 | Tongi | 115 | 12:00
51 | Dohazari | 109 | 20:00 | 117 | Mongla | 34 | 01:00 | 183 | Ullahpara | 39 | 19:30
52 | Faridpur | 172 | 22:00 | 118 | Motijheel | 47 | 13:00 | 184 | Ullon | 42 | 00:00
53 | Fatullah | 94 | 12:00 | 119 | Muktagacha | 34 | 19:00 | 185 | Uttara | 91 | 12:00
54 | Fenchuganj | 39 | 00:00 | 120 | Munshiganj | 115 | 00:00 | 186 | UttaraNew | 61 | 13:00
55 | Feni | 100 | 19:00 | 121 | Muradnagar | 40 | 00:00 | 187 | Zigatola | 74 | 13:00
56 | GPH | 89 | 18:00 | 122 | Mymensingh | 188 | 20:00
57 | Ghatail | 80 | 19:30 | 123 | Naogaon | 127 | 19:30
58 | Ghorashal | 13 | 21:00 | 124 | Narail | 63 | 19:30
59 | Ghorashal-230 | 81 | 22:00 | 125 | Narinda | 86 | 13:00
60 | Goalpara | 36 | 19:00 | 126 | Narshingdi | 186 | 00:00
61 | Gollamari | 96 | 23:00 | 127 | Natore | 140 | 19:30
62 | Gopalganj | 114.4 | 21:00 | 128 | Nawabganj | 61.2 | 22:00
63 | Gulshan | 74 | 11:00 | 129 | Netrakona | 127 | 21:00
64 | Halishahar | 69.5 | 15:00 | 130 | New | 63.9 | 12:00
65 | HaripurSBU | 150 | 11:00 | 131 | Niamatpur | 71 | 00:00
66 | Hasnabad | 78 | 23:00 | 132 | Noapara | 45 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 03-08-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14867.2 | 0 |  | 14867.2
1:00 | 14425.2 | 19 |  | 14445.2
2:00 | 14090.4 | 19 |  | 14110.4
3:00 | 13717.6 | 17 |  | 13735.6
4:00 | 13393 | 16 |  | 13410
5:00 | 13150 | 14 |  | 13165
6:00 | 12696.37 | 14 |  | 12711
7:00 | 12630.03 | 12 |  | 12643.03
8:00 | 12589.9 | 17 |  | 12607.67
9:00 | 12838.81 | 0 |  | 12838.81
10:00 | 13042.89 | 0 |  | 13042.89
11:00 | 13175.05 | 0 |  | 13175.05
12:00 | 13601.24 | 0 |  | 13601.24
13:00 | 13835.65 | 0 |  | 13835.65
14:00 | 13450.3 | 0 |  | 13450.3
15:00 | 13372.68 | 0 |  | 13372.68
16:00 | 13281.92 | 0 |  | 13281.92
17:00 | 13062.35 | 0 |  | 13062.35
18:00 | 12622.91 | 0 |  | 12622.91
19:00 | 14394.8 | 0 |  | 14394.8
19:30 | 15065.51 | 0 |  | 15065.51
20:00 | 14835.73 | 0 |  | 14835.73
21:00 | 14856.47 | 0 |  | 14856.47
22:00 | 14671.14 | 0 |  | 14671.14
23:00 | 14676.53 | 0 |  | 14676.53
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 03-08-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7600.2 | 7267 | 14867.2 | DAILY GENERATION CURVE
00:30 | 7462.7 | 7183.5 | 14646.2
01:00 | 7325.2 | 7100 | 14425.2 | 03-08-2025
01:30 | 7318.3 | 6939.5 | 14257.8
02:00 | 7311.4 | 6779 | 14090.4
02:30 | 7242 | 6662 | 13904
03:00 | 7172.6 | 6545 | 13717.6
03:30 | 7098.8 | 6456.5 | 13555.3
04:00 | 7025 | 6368 | 13393
04:30 | 6967 | 6304.5 | 13271.5
05:00 | 6909 | 6241 | 13150
05:30 | 6802.01 | 6121.175 | 12923.185
06:00 | 6695.02 | 6001.35 | 12696.37
06:30 | 6694.31 | 5968.89 | 12663.2
07:00 | 6693.6 | 5936.43 | 12630.03
07:30 | 6658.65 | 5951.315 | 12609.965
08:00 | 6623.7 | 5966.2 | 12589.9
08:30 | 6672.075 | 6042.28 | 12714.355
09:00 | 6720.45 | 6118.36 | 12838.81
09:30 | 6806.725 | 6134.125 | 12940.85
10:00 | 6893 | 6149.89 | 13042.89
10:30 | 6978.33 | 6130.64 | 13108.97
11:00 | 7063.66 | 6111.39 | 13175.05
11:30 | 7193.585 | 6194.56 | 13388.145
12:00 | 7323.51 | 6277.73 | 13601.24
12:30 | 7311.805 | 6406.64 | 13718.445
13:00 | 7300.1 | 6535.55 | 13835.65
13:30 | 7180.845 | 6462.13 | 13642.975
14:00 | 7061.59 | 6388.71 | 13450.3
14:30 | 7086.25 | 6325.24 | 13411.49
15:00 | 7110.91 | 6261.77 | 13372.68
15:30 | 7142.59 | 6184.71 | 13327.3
16:00 | 7174.27 | 6107.65 | 13281.92
16:30 | 7116.88 | 6055.255 | 13172.135
17:00 | 7059.49 | 6002.86 | 13062.35
17:30 | 6940.39 | 5902.24 | 12842.63
18:00 | 6821.29 | 5801.62 | 12622.91
18:30 | 7322.395 | 6186.46 | 13508.855
19:00 | 7823.5 | 6571.3 | 14394.8
19:30 | 8049.7 | 7015.81 | 15065.51
20:00 | 7766 | 7069.73 | 14835.73
20:30 | 7760.25 | 7085.85 | 14846.1 |  | Executive Engineer
21:00 | 7754.5 | 7101.97 | 14856.47 |  | Network Operation Division
21:30 | 7692.95 | 7070.855 | 14763.805
22:00 | 7631.4 | 7039.74 | 14671.14
22:30 | 7629.8 | 7044.035 | 14673.835
23:00 | 7628.2 | 7048.33 | 14676.53

## En-Curve
QF-LDC-12
Date | 03-08-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4000 | 1973 | 879 | 38 | 48 | 1450 | 219 | 4887 | 0 | 197 | 1166.2 | 0 | 0 | 10 | 0 | DAILY ENERGY CURVE
00:30 | 3980.5 | 1978 | 879.5 | 38 | 47 | 1405 | 219.5 | 4825 | 0 | 189 | 1070.7 | 0 | 0 | 14 | 9.5 | 03-08-2025
01:00 | 3961 | 1983 | 880 | 38 | 46 | 1360 | 220 | 4763 | 0 | 181 | 975.2 | 0 | 0 | 18 | 19
01:30 | 3970.5 | 1980.5 | 880.5 | 38 | 46 | 1288 | 220 | 4676.5 | 0 | 164 | 974.3 | 0 | 0 | 19.5 | 19 | Energy Generated | 330.9314 |  | MKWHr
02:00 | 3980 | 1978 | 881 | 38 | 46 | 1216 | 220 | 4590 | 0 | 147 | 973.4 | 0 | 0 | 21 | 19 | Energy not Served | 0.128 |  | MKWHr
02:30 | 3960.5 | 1988 | 880.5 | 38 | 45 | 1212.5 | 220.5 | 4475 | 0 | 109.5 | 952.5 | 0 | 0 | 22 | 18 | Total Energy Requirement | 331.0594 |  | MKWHr
03:00 | 3941 | 1998 | 880 | 38 | 44 | 1209 | 221 | 4360 | 0 | 72 | 931.6 | 0 | 0 | 23 | 17
03:30 | 3972 | 2008 | 880 | 38 | 44 | 1212 | 221 | 4259 | 0 | 63 | 838.3 | 0 | 0 | 20 | 16.5
04:00 | 4003 | 2018 | 880 | 38 | 44 | 1215 | 221 | 4158 | 0 | 54 | 745 | 0 | 0 | 17 | 16
04:30 | 3993 | 2016 | 880 | 38 | 43 | 1162 | 221 | 4154 | 0 | 54 | 694.5 | 0 | 0 | 16 | 15
05:00 | 3983 | 2014 | 880 | 38 | 42 | 1109 | 221 | 4150 | 0 | 54 | 644 | 0 | 0 | 15 | 14
05:30 | 3956 | 2006.25 | 880 | 38 | 41 | 1048 | 220.5 | 4053 | 6.935 | 54 | 600.5 | 0 | 0 | 19 | 14
06:00 | 3929 | 1998.5 | 880 | 38 | 40 | 987 | 220 | 3956 | 13.87 | 54 | 557 | 0 | 0 | 23 | 14
06:30 | 3911 | 1979 | 880 | 38 | 39 | 955 | 219.5 | 3934 | 47.7 | 78.5 | 558 | 0 | 0 | 23.5 | 13
07:00 | 3893 | 1959.5 | 880 | 38 | 38 | 923 | 219 | 3912 | 81.53 | 103 | 559 | 0 | 0 | 24 | 12
07:30 | 3908.5 | 1927.5 | 880 | 38 | 37 | 925 | 219 | 3902.5 | 99.965 | 102.5 | 549 | 0 | 0 | 21 | 14.5
08:00 | 3924 | 1895.5 | 880 | 38 | 36 | 927 | 219 | 3893 | 118.4 | 102 | 539 | 0 | 0 | 18 | 17
08:30 | 3884 | 1864.25 | 880.5 | 38 | 36 | 919.5 | 219 | 3975 | 178.105 | 132.5 | 570 | 0 | 0 | 17.5 | 8.5
09:00 | 3844 | 1833 | 881 | 38 | 36 | 912 | 219 | 4057 | 237.81 | 163 | 601 | 0 | 0 | 17 | 0
09:30 | 3809.5 | 1827.5 | 880.5 | 38 | 36 | 912 | 219 | 4074.5 | 269.8 | 188 | 659.55 | 0 | 0 | 26.5 | 0
10:00 | 3775 | 1822 | 880 | 38 | 36 | 912 | 219 | 4092 | 301.79 | 213 | 718.1 | 0 | 0 | 36 | 0
10:30 | 3798 | 1831.95 | 879.5 | 38 | 36 | 885 | 219 | 4097.5 | 315.47 | 212.5 | 760.05 | 0 | 0 | 36 | 0
11:00 | 3821 | 1841.9 | 879 | 38 | 36 | 858 | 219 | 4103 | 329.15 | 212 | 802 | 0 | 0 | 36 | 0
11:30 | 3819.5 | 1856.2 | 879.5 | 38 | 36 | 841.5 | 219 | 4215.5 | 365.445 | 212 | 864.5 | 0 | 0 | 41 | 0
12:00 | 3818 | 1870.5 | 880 | 38 | 36 | 825 | 219 | 4328 | 401.74 | 212 | 927 | 0 | 0 | 46 | 0
12:30 | 3761 | 1848.25 | 883 | 38 | 39 | 891.5 | 219 | 4323.5 | 454.695 | 212 | 1006 | 0 | 0 | 42.5 | 0
13:00 | 3704 | 1826 | 886 | 38 | 42 | 958 | 219 | 4319 | 507.65 | 212 | 1085 | 0 | 0 | 39 | 0
13:30 | 3628 | 1835 | 886 | 38 | 40 | 966.94 | 219 | 4288 | 444.535 | 199.5 | 1055 | 0 | 0 | 43 | 0
14:00 | 3552 | 1844 | 886 | 38 | 38 | 975.88 | 219 | 4257 | 381.42 | 187 | 1025 | 0 | 0 | 47 | 0
14:30 | 3641.5 | 1869.75 | 886 | 38 | 34 | 964.205 | 220 | 4221.5 | 367.685 | 169.5 | 957.85 | 0 | 0 | 41.5 | 0
15:00 | 3731 | 1895.5 | 886 | 38 | 30 | 952.53 | 221 | 4186 | 353.95 | 152 | 890.7 | 0 | 0 | 36 | 0
15:30 | 3749 | 1909 | 886 | 38 | 31 | 961.42 | 221 | 4181.5 | 268.58 | 147.5 | 898.8 | 0 | 0 | 35.5 | 0
16:00 | 3767 | 1922.5 | 886 | 38 | 32 | 970.31 | 221 | 4177 | 183.21 | 143 | 906.9 | 0 | 0 | 35 | 0
16:30 | 3750.5 | 1905.35 | 886 | 38 | 32 | 967.61 | 221 | 4176 | 130.925 | 143 | 893.75 | 0 | 0 | 28 | 0
17:00 | 3734 | 1888.2 | 886 | 38 | 32 | 964.91 | 221 | 4175 | 78.64 | 143 | 880.6 | 0 | 0 | 21 | 0
17:30 | 3709 | 1802.2 | 886 | 38 | 24 | 969.425 | 221 | 4103 | 50.205 | 145 | 876.8 | 0 | 0 | 18 | 0
18:00 | 3684 | 1716.2 | 886 | 38 | 16 | 973.94 | 221 | 4031 | 21.77 | 147 | 873 | 0 | 0 | 15 | 0
18:30 | 3762 | 1766.85 | 885.5 | 38 | 30 | 1040.62 | 221 | 4185 | 10.885 | 361 | 1192 | 0 | 0 | 16 | 0
19:00 | 3840 | 1817.5 | 885 | 38 | 44 | 1107.3 | 221 | 4339 | 0 | 575 | 1511 | 0 | 0 | 17 | 0
19:30 | 3723 | 1732.5 | 886 | 38 | 42 | 1220.81 | 221 | 4637 | 0 | 682 | 1867.2 | 0 | 0 | 16 | 0
20:00 | 3690 | 1647.5 | 886 | 38 | 42 | 1331.73 | 221 | 4749 | 0 | 638 | 1577.5 | 0 | 0 | 15 | 0
20:30 | 3804 | 1753.5 | 886 | 38 | 40 | 1345.35 | 220.5 | 4801.5 | 0 | 537 | 1407.25 | 0 | 0 | 13 | 0
21:00 | 3918 | 1859.5 | 886 | 38 | 38 | 1358.97 | 220 | 4854 | 0 | 436 | 1237 | 0 | 0 | 11 | 0
21:30 | 3898.5 | 1864 | 886 | 38 | 40 | 1360.355 | 219.5 | 4848.5 | 0 | 409 | 1190.95 | 0 | 0 | 9 | 0
22:00 | 3879 | 1868.5 | 886 | 38 | 42 | 1361.74 | 219 | 4843 | 0 | 382 | 1144.9 | 0 | 0 | 7 | 0
22:30 | 3893.5 | 1872.5 | 886 | 38 | 42 | 1357.535 | 219 | 4842 | 0 | 379.5 | 1134.8 | 0 | 0 | 9 | 0
23:00 | 3908 | 1876.5 | 886 | 38 | 42 | 1353.33 | 219 | 4841 | 0 | 377 | 1124.7 | 0 | 0 | 11 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 03-08-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 385 | 07:00 | 374 | 12:00 | Payra | 414 | 04:00 | 409 | 21:00
Ashuganj | 403 | 7:00 | 384 | 11:00 | Rahanpur | 404 | 10:00 | 382 | 00:00
Bhulta | 399 | 07:00 | 379 | 12:00 | Rampal | 407 | 08:00 | 392 | 00:00
Bibiana | 387 | 07:00 | 378 | 00:00
BIPTC | 402 | 06:00 | 393 | 00:00
Bogura | 386 | 09:00 | 359 | 00:00
Gopalganj | 399 | 07:00 | 387 | 00:00
Kaliakoir | 375 | 07:00 | 364 | 00:00
Madunaghat | 392 | 07:00 | 384 | 00:00
Meghnaghat | 388 | 07:00 | 377 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 224 | 06:00 | 216 | 11:00 | Keranigonj | 222 | 06:00 | 214 | 00:00
AKSML | 227 | 01:00 | 222 | 00:00 | Khulna(S) | 233 | 08:00 | 220 | 00:00
Aminbazar | 225 | 04:00 | 217 | 11:00 | Madunaghat | 231 | 18:00 | 226 | 00:00
Ashuganj | 234 | 07:00 | 224 | 00:00 | Madunaghat-400 | 231 | 08:00 | 226 | 00:00
Ashuganj-400 | 234 | 7:00 | 220 | 11:00 | Maniknagar | 219 | 06:00 | 212 | 11:00
Baghabari | 236 | 06:00 | 226 | 00:00 | Meghnaghat | 225 | 02:00 | 220 | 22:00
Barapukuria | 226 | 13:00 | 215 | 00:00 | Meghnaghat-400 | 228 | 08:00 | 216 | 12:00
Barapukuria-230 | 226 | 13:00 | 216 | 23:00 | Mirsorai | 226 | 19:30 | 219 | 00:00
Barishal | 228 | 09:00 | 220 | 00:00 | Rajshahi | 234 | 07:00 | 220 | 00:00
Bheramara | 234 | 06:00 | 223 | 00:00 | Rampal | 232 | 08:00 | 220 | 00:00
Bhulta | 229 | 03:00 | 212 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 227 | 15:00 | 220 | 00:00 | Rampura | 228 | 03:00 | 213 | 12:00
BIPTC | 237 | 06:00 | 223 | 00:00 | Shikalbaha | 228 | 19:00 | 223 | 00:00
Bogura | 238 | 08:00 | 224 | 00:00 | Shyampur | 221 | 06:00 | 214 | 00:00
Bogura-400 | 238 | 07:00 | 224 | 00:00 | Siddhirganj | 221 | 05:00 | 215 | 00:00
Borhanuddin | 233 | 08:00 | 227 | 00:00 | Sirajgonj | 241 | 07:00 | 234 | 00:00
BSRM | 225 | 18:30 | 218 | 00:00 | Sreepur | 230 | 05:00 | 222 | 00:00
Cumilla(N) | 222 | 18:30 | 215 | 00:00 | Tongi | 226 | 07:00 | 217 | 12:00
Faridpur | 225 | 06:00 | 216 | 00:00
Fenchuganj | 230 | 15:00 | 220 | 00:00
Ghorashal | 230 | 04:00 | 225 | 00:00
Ghorashal-230 | 228 | 07:00 | 216 | 12:00
Gopalganj | 226 | 06:00 | 219 | 00:00
GPH | 227 | 06:00 | 222 | 00:00
Haripur | 220 | 07:00 | 214 | 00:00
Hasnabad | 221 | 08:00 | 215 | 00:00
Hathazari | 228 | 07:00 | 222 | 00:00
Ishurdi | 236 | 06:00 | 226 | 00:00
Jhenaidah | 232 | 08:00 | 218 | 00:00
Kaliakoir | 230 | 05:00 | 223 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 03:00 | 126 | 11:00 | Lalmonirhat | 132 | 18:30 | 122 | 11:00
Agargaon | 132 | 06:00 | 125 | 11:00 | Madanganj | 128 | 18:30 | 124 | 00:00
Agrabad | 129 | 19:30 | 125 | 00:00 | Madaripur | 134 | 08:00 | 128 | 00:00
AKS | 127 | 19:00 | 125 | 00:00 | Madartek | 137 | 02:00 | 126 | 12:00
Aminbazar | 132 | 04:00 | 126 | 01:00 | Madunaghat | 130 | 06:00 | 128 | 00:00
Amnura | 137 | 08:00 | 127 | 00:00 | Magura | 136 | 06:00 | 126 | 00:00
Ashuganj | 143 | 14:00 | 135 | 00:00 | Mahasthangarh | 138 | 07:00 | 125 | 00:00
Bagerhat | 133 | 09:00 | 120 | 00:00 | Maijdee | 119 | 18:00 | 111 | 01:00
Bajitpur | 131 | 05:00 | 127 | 00:00 | Manikganj | 127 | 07:00 | 121 | 00:00
Bakulia | 131 | 18:30 | 126 | 00:00 | Maniknagar | 132 | 05:00 | 127 | 10:00
Banani | 137 | 02:00 | 126 | 11:00 | Matarbari | 118 | 11:00 | 109 | 21:00
Bangabhaban | 132 | 06:00 | 127 | 11:00 | Matuail | 128 | 06:00 | 123 | 11:00
Barapukuria | 138 | 13:00 | 128 | 00:00 | Millgate | 132 | 06:00 | 125 | 12:00
Barguna | 134 | 09:00 | 129 | 22:00 | Mirpur | 131 | 04:00 | 125 | 10:00
Barishal | 133 | 18:00 | 126 | 23:00 | Mirzapur | 129 | 05:00 | 125 | 00:00
Barishal-230 | 133 | 07:00 | 126 | 23:00 | Mithapukur | 133 | 09:00 | 112 | 00:00
Baroaulia | 130 | 05:00 | 127 | 00:00 | MI_Cement | 129 | 18:30 | 124 | 10:00
Baroirhat | 123 | 19:00 | 118 | 00:00 | Modern | N/A | N/A | N/A | N/A
Bashundhara | 138 | 03:00 | 125 | 09:00 | Mogbazar | 140 | 02:00 | 127 | 11:00
BashundharaCement | 128 | 18:30 | 124 | 00:00 | Mongla | 134 | 08:00 | 121 | 00:00
Beanibazar | 129 | 18:30 | 119 | 00:00 | Motijheel | 132 | 06:00 | 126 | 12:00
Benapole | 133 | 18:00 | 120 | 00:00 | Muktagacha | 136 | 08:00 | 132 | 00:00
Bhaluka | 132 | 15:00 | 125 | 00:00 | Munshiganj | 128 | 18:00 | 123 | 09:00
Bhandaria | 128 | 18:00 | 117 | 23:00 | Muradnagar | 124 | 07:00 | 119 | 00:00
Bhangura | 135 | 11:00 | 128 | 00:00 | Mymensingh | 138 | 09:00 | 120 | 00:00
Bheramara | 138 | 06:00 | 132 | 00:00 | Naogaon | 136 | 08:00 | 122 | 00:00
Bheramara(GK) | 137 | 05:00 | 132 | 00:00 | Narail | 137 | 09:00 | 125 | 00:00
Bhulta | 123 | 19:00 | 118 | 10:00 | Narinda | 132 | 5:00 | 127 | 10:00
Bog-Sherpur | 138 | 08:00 | 128 | 00:00 | Narshingdi | 136 | 19:30 | 118 | 00:00
Bogura | 140 | 07:00 | 130 | 00:00 | Natore | 136 | 06:00 | 127 | 00:00
Bogura-230 | 141 | 08:00 | 130 | 00:00 | Nawabganj | 132 | 04:00 | 126 | 11:00
Brahmanbaria | 138 | 14:00 | 128 | 00:00 | Netrakona | 127 | 06:00 | 119 | 21:00
Cantonment | 131 | 04:00 | 125 | 10:00 | New | 133 | 06:00 | 127 | 00:00
Chandina | 127 | 18:00 | 122 | 01:00 | Niamatpur | 137 | 07:00 | 128 | 00:00
Chandpur | 126 | 12:00 | 121 | 00:00 | Noapara | 136 | 09:00 | 125 | 00:00
Chandraghona | 131 | 03:00 | 129 | 00:00 | Pabna | 135 | 06:00 | 128 | 21:00
Chapai | 137 | 18:30 | 128 | 01:00 | Palashbari | 131 | 08:00 | 114 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 18:30 | 124 | 00:00 | Panchagarh | 139 | 21:00 | 122 | 12:00
Chauddagram | 123 | 19:30 | 117 | 23:00 | Patuakhali | 134 | 07:00 | 130 | 00:00
Chhatak | 134 | 15:00 | 115 | 00:00 | Payra | 136 | 06:00 | 133 | 00:00
Chowmuhani | 119 | 12:00 | 111 | 01:00 | PHP | 123 | 20:00 | 117 | 00:00
Chuadanga | 134 | 07:00 | 122 | 00:00 | Postogola | 131 | 07:00 | 126 | 11:00
Coxsbazar | 118 | 03:00 | 110 | 23:00 | Purbachal | 137 | 02:00 | 125 | 11:00
Cumilla(N) | 129 | 17:00 | 121 | 23:00 | Purbasadipur | 134 | 18:30 | 121 | 00:00
Cumilla(S) | 133 | 06:00 | 120 | 23:00 | Rahanpur | 138 | 08:00 | 130 | 05:00
Daganbhuiyan | 121 | 19:30 | 113 | 01:00 | Rahanpur-400 | 139 | 08:00 | 132 | 00:00
Daudkandi | 123 | 06:00 | 117 | 00:00 | Rahim | 128 | 06:00 | 124 | 10:00
Dhaka | 140 | 05:00 | 127 | 12:00 | Rajbari | 133 | 08:00 | 126 | 00:00
Dhamrai | 131 | 05:00 | 125 | 12:00 | Rajendrapur | 132 | 19:30 | 123 | 00:00
Dhanmondi | 138 | 03:00 | 126 | 11:00 | Rajshahi | 135 | 06:00 | 126 | 23:00
Dohazari | 126 | 18:00 | 119 | 00:00 | Rajshahi-230 | 134 | 06:00 | 126 | 00:00
Faridpur | 134 | 09:00 | 128 | 00:00 | Ramganj | 121 | 11:00 | 113 | 01:00
Fatullah | 130 | 06:00 | 125 | 10:00 | Rampur | 129 | 03:00 | 126 | 00:00
Fenchuganj | 138 | 15:00 | 128 | 00:00 | Rampura | 138 | 03:00 | 126 | 11:00
Feni | 121 | 18:30 | 117 | 16:00 | Rangamati | 130 | 04:00 | 127 | 00:00
Ghatail | 131 | 13:00 | 126 | 00:00 | Rangpur | 133 | 13:00 | 123 | 12:00
Ghorashal | 137 | 19:30 | 130 | 01:00 | Ruppur | 138 | 07:00 | 132 | 00:00
Goalpara | 138 | 08:00 | 128 | 00:00 | Saidpur | 132 | 13:00 | 121 | 00:00
Gollamari | 138 | 09:00 | 128 | 00:00 | Satkhira | 135 | 09:00 | 122 | 00:00
Gopalganj | 135 | 09:00 | 128 | 00:00 | Satmasjid | 132 | 06:00 | 124 | 12:00
Gopalganj-400 | 136 | 07:00 | 131 | 00:00 | Savar | 131 | 19:00 | 124 | 10:00
Gulshan | 136 | 06:00 | 127 | 11:00 | SevenRings | 136 | 07:00 | 131 | 00:00
Halishahar | 130 | 03:00 | 126 | 00:00 | ShahCement | 129 | 18:30 | 124 | 00:00
Haripur | 128 | 07:00 | 124 | 00:00 | Shahjadpur | 139 | 06:00 | 132 | 00:00
HaripurSBU | 128 | 04:00 | 124 | 10:00 | Shahjibazar | 138 | 14:00 | 127 | 00:00
Hasnabad | 132 | 18:30 | 125 | 11:00 | Shahmirpur | 130 | 05:00 | 127 | 00:00
Hathazari | 132 | 02:00 | 129 | 12:00 | Shariatpur | 133 | 08:00 | 125 | 00:00
Ishurdi | 138 | 06:00 | 132 | 00:00 | Sherpur | 139 | 09:00 | 131 | 12:00
Jaldhaka | 131 | 18:30 | 118 | 00:00 | Shikalbaha | 120 | 06:00 | 116 | 00:00
Jamalpur | 140 | 09:00 | 133 | 12:00 | Shikalbaha-230 | 131 | 05:00 | 128 | 00:00
Jashore | 136 | 10:00 | 123 | 23:00 | Shitalakhya | 129 | 18:30 | 124 | 10:00
Jhenaidah | 137 | 05:00 | 122 | 22:00 | Sholosohor | 130 | 19:30 | 127 | 00:00
Jhenaidah-230 | 138 | 08:00 | 128 | 00:00 | Shyampur | 129 | 18:00 | 125 | 10:00
Joydebpur | 136 | 19:00 | 123 | 08:00 | Shyampur-230 | 130 | 07:00 | 125 | 00:00
Joypurhat | 134 | 07:00 | 120 | 00:00 | Siddhirganj | 129 | 05:00 | 124 | 11:00
Juldah | 131 | 19:00 | 127 | 00:00 | Sirajganj | 135 | 10:00 | 127 | 00:00
Kabirpur | 133 | 19:30 | 124 | 00:00 | Sonargaon | 126 | 05:00 | 121 | 11:00
Kachua | 125 | 18:30 | 119 | 00:00 | Sreemongol | 136 | 09:00 | 125 | 00:00
Kaliakoir | 134 | 18:30 | 128 | 11:00 | Sreepur | 134 | 07:00 | 129 | 00:00
Kallyanpur | 132 | 06:00 | 126 | 10:00 | Srinagar | 133 | 06:00 | 127 | 11:00
Kalurghat | 130 | 06:00 | 127 | 00:00 | SSM | 132 | 02:00 | 130 | 00:00
Kamrangirchar | 133 | 05:00 | 126 | 12:00 | Sunamganj | 132 | 15:00 | 114 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 133 | 16:00 | 121 | 01:00
Kasba | 124 | 18:00 | 118 | 00:00 | Sylhet-132 | 135 | 15:00 | 120 | 00:00
Kazla | 132 | 08:00 | 126 | 12:00 | Tangail | 128 | 07:00 | 124 | 00:00
Keranigonj | 133 | 06:00 | 127 | 00:00 | Taraganj | 133 | 18:30 | 120 | 01:00
Khagrachori | 131 | 07:00 | 126 | 00:00 | Thakurgaon | 137 | 21:00 | 119 | 12:00
Khulna | 137 | 09:00 | 126 | 00:00 | TK | 131 | 19:30 | 127 | 00:00
Khulna(S) | 139 | 18:30 | 129 | 00:00 | Tongi | 134 | 05:00 | 127 | 08:00
Khulshi | 129 | 19:30 | 125 | 00:00 | Ullahpara | 135 | 05:00 | 128 | 00:00
Kishoreganj | 131 | 14:00 | 125 | 00:00 | Ullon | 138 | 03:00 | 126 | 12:00
Kodda | 135 | 19:30 | 123 | 00:00 | Uttara | 131 | 06:00 | 124 | 21:00
KSRM | 130 | 11:00 | 126 | 00:00 | UttaraNew | 131 | 05:00 | 125 | 00:00
Kulaura | 138 | 15:00 | 127 | 00:00 | Zigatola | 133 | 08:00 | 127 | 11:00
Kurigram | 130 | 13:00 | 120 | 12:00
Kushtia | 134 | 09:00 | 127 | 00:00
Laksam | 124 | 15:00 | 118 | 00:00
Lakshmipur | 120 | 18:00 | 112 | 01:00
Lalbag | 133 | 07:00 | 126 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division